## Instructions
[8 empty] | a |  | b
| Type of Intervention |  | Natural Ventilation | Season | HEPA | AHS | Cumulative Dose (#/m3) |  | Cumulative Dose (#/m3) |  | Fold Change
[7 empty] | Light Breeze |  | Fresh Breeze |  | LB | FB
1 | Control |  | Leakage only | Summer | no | no | 501.2822 |  | - |  | 1
2 | Natural Ventilation |  | 1 window fully open during breaks | Summer | no | no | 319.2608 |  | 290.7961 |  | 1.5701 | 1.7238
3 |  |  | 1 window fully open at all time | Summer | no | no | 206.9352 |  | 152.36 |  | 2.4224 | 3.2901
4 |  |  | 1 window fully open during breaks | Winter | no | no | 337.7978 |  | 293.6727 |  | 1.484 | 1.7069
5 |  |  | 1 window fully open at all time | Winter | no | no | 123.1803 |  | 125.3068 |  | 4.0695 | 4.0004
6 |  |  | 2 window fully open during breaks | Summer | no | no | 307.0062 |  | 288.0015 |  | 1.6328 | 1.7406
7 |  |  | 2 window fully open at all time | Summer | no | no | 150.243 |  | 100.4494 |  | 3.3365 | 4.9904
8 |  |  | 2 window fully open during breaks | Winter | no | no | 314.0021 |  | 291.7675 |  | 1.5964 | 1.7181
9 |  |  | 2 window fully open at all time | Winter | no | no | 73.1345 |  | 77.6656 |  | 6.8542 | 6.4544
10 |  |  | 3 window fully open during breaks | Summer | no | no | 304.7191 |  | 287.7428 |  | 1.6451 | 1.7421
11 |  |  | 3 window fully open at all time | Summer | no | no | 119.0521 |  | 74.5973 |  | 4.2106 | 6.7198
12 |  |  | 3 window fully open during breaks | Winter | no | no | 306.9614 |  | 291.628 |  | 1.633 | 1.7189
13 |  |  | 3 window fully open at all time | Winter | no | no | 52.091 |  | 56.0404 |  | 9.6232 | 8.945
14 | HEPA Filtration |  | Leakage only | Summer | 3.1 ACH | no | 144.2772 |  | - |  | 3.4744
|  |  |  | Summer | 5.5 ACH | NO |  |  |  | #VALUE!
15 | AHS |  | Leakage only | Summer | no | 5 ACH | 99.0937 |  | - |  | 5.0587
16 | Combined |  | Leakage only | Summer | 3.1 ACH | 5 ACH | 68.1404 |  | 67.0791 |  | 7.3566 | 7.473
17 |  |  | 1 window fully open at all time | Winter | 3.1 ACH | no | 123.1803 |  | 125.3068 |  | 4.0695 | 4.0004
18 |  |  | 1 window fully open at all time | Winter | 5.5 ACH | no | 61.185 |  | 62.3213 |  | 8.1929 | 8.0435
19
Breath rate
| 10 | litre/min
| 0.01 | m3/min

## Heat Map
Natural Ventilation
Summer Light Breeze
Summer Light Breeze |  |  |  |  | Winter Light Breeze |  |  |  |  | Window Opening
Window Opening | Session Breaks | 1.5701 | 1.6328 | 1.6451 | Window Opening | Session Breaks | 1.484 | 1.5964 | 1.633 |  | Leakge Only | 3.4744 | 5.0587 | 7.3566
| All Day | 2.4224 | 3.3365 | 4.2106 |  | All Day | 4.0695 | 6.8542 | 9.6232 |  |  | HEPA | AHS | HEPA + AHS
|  | 1 | 2 | 3 |  |  | 1 | 2 | 3
|  | Number of Windows |  |  |  |  | Number of Windows
Summer Fresh Breeze |  |  |  |  | Winter Fresh Breeze
Window Opening | Session Breaks | 1.7238 | 1.7406 | 1.7421 | Window Opening | Session Breaks | 1.7069 | 1.7181 | 1.7189
| All Day | 3.2901 | 4.9904 | 6.7198 |  | All Day | 4.0004 | 6.4544 | 8.945
|  | 1 | 2 | 3 |  |  | 1 | 2 | 3
|  | Number of Windows |  |  |  |  | Number of Windows
1 Window at all time
HEPA Device Mode
[16 empty] | 3.1 ACH | 4.0695 | 4.0004
[16 empty] | 5.5 ACH | 8.1929 | 8.0435
[17 empty] | Light Breeze | Fresh Breeze
Winter Wind Condition

## Data Sheet
| 1 | [6 empty] | 2a | [6 empty] | 2b | [6 empty] | 3a | [6 empty] | 3b | [6 empty] | 4a | [6 empty] | 4b | [6 empty] | 5a | [6 empty] | 5b | [7 empty] | 6a | [7 empty] | 6b | [6 empty] | 7a | [6 empty] | 7b | [6 empty] | 8a | [6 empty] | 8b | [6 empty] | 9a | [6 empty] | 9b | [6 empty] | 10a | [6 empty] | 10b | [6 empty] | 11a | [6 empty] | 11b | [6 empty] | 12a | [6 empty] | 12b | [6 empty] | 13a | [6 empty] | 13b |  |  |  |  | 14 | [8 empty] | 15 | [6 empty] | 16a | [6 empty] | 16b | [6 empty] | 17a | [6 empty] | 17b | [6 empty] | 18a | [6 empty] | 18b
| Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0 | [5 empty] | Project File: | Classroom Simulation Ver 2.0.0
| level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1 |  |  |  | level: | Ground_floor | zone: | Room_1
| date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2 |  |  |  | date | time | time | SARS-CoV-2
Hour |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum |  | of day | [s] | [#/m^3] | Intake | Cumulative dose | Intake sum
0 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 501.2822 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 319.2608 | 2006-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 290.7961 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 206.9352 | 2006-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 152.36 | 2028-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 337.7978 | 2007-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 293.6727 | 2028-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 123.1803 | 2007-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 125.3068 | 2029-09-01 | 0.375 | 32400 | 0 | 0 | 0 | 307.0062 | 2006-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 288.0015 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 150.243 | 2006-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 100.4494 | 2028-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 314.0021 | 2007-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 291.7675 | 2028-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 73.1345 | 2007-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 77.6656 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 304.7191 | 2006-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 287.7428 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 119.0521 | 2006-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 74.5973 | 2028-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 306.9614 | 2007-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 291.628 | 2028-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 52.091 | 2007-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 56.0404 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 144.2772 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 99.0937 | 2029-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 68.1404 | 2006-09-01 | 9:00 | 32400 | 0 | 0 | 0 | 67.0791 | 2028-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 123.1803 | 2007-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 125.3068 | 2028-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 61.185 | 2007-01-01 | 9:00 | 32400 | 0 | 0 | 0 | 62.3213
| 2029-09-01 | 9:01 | 32460 | 6.4542 | 0.038725 | 0.038725 |  | 2029-09-01 | 9:01 | 32460 | 6.4542 | 0.038725 | 0.038725 |  | 2006-09-01 | 9:01 | 32460 | 6.441 | 0.038646 | 0.038646 |  | 2029-09-01 | 9:01 | 32460 | 6.2728 | 0.037637 | 0.037637 |  | 2006-09-01 | 9:01 | 32460 | 6.2384 | 0.037431 | 0.037431 |  | 2028-01-01 | 9:01 | 32460 | 6.4524 | 0.038714 | 0.038714 |  | 2007-01-01 | 9:01 | 32460 | 6.4464 | 0.038679 | 0.038679 |  | 2028-01-01 | 9:01 | 32460 | 6.0595 | 0.036357 | 0.036357 |  | 2007-01-01 | 9:01 | 32460 | 6.0907 | 0.036544 | 0.036544 |  | 2029-09-01 | 9:01 | 32460 | 6.4542 | 0.038725 | 0.038725 |  | 2006-09-01 | 9:01 | 32460 | 6.441 | 0.038646 | 0.038646 |  | 2029-09-01 | 9:01 | 32460 | 6.1018 | 0.036611 | 0.036611 |  | 2006-09-01 | 9:01 | 32460 | 6.0477 | 0.036286 | 0.036286 |  | 2028-01-01 | 9:01 | 32460 | 6.4524 | 0.038714 | 0.038714 |  | 2007-01-01 | 9:01 | 32460 | 6.4464 | 0.038679 | 0.038679 |  | 2028-01-01 | 9:01 | 32460 | 5.7179 | 0.034307 | 0.034307 |  | 2007-01-01 | 9:01 | 32460 | 5.7771 | 0.034663 | 0.034663 |  | 2029-09-01 | 9:01 | 32460 | 6.4542 | 0.038725 | 0.038725 |  | 2006-09-01 | 9:01 | 32460 | 6.441 | 0.038646 | 0.038646 |  | 2029-09-01 | 9:01 | 32460 | 5.9398 | 0.035639 | 0.035639 |  | 2006-09-01 | 9:01 | 32460 | 5.8684 | 0.03521 | 0.03521 |  | 2028-01-01 | 9:01 | 32460 | 6.4524 | 0.038714 | 0.038714 |  | 2007-01-01 | 9:01 | 32460 | 6.4464 | 0.038679 | 0.038679 |  | 2028-01-01 | 9:01 | 32460 | 5.4126 | 0.032476 | 0.032476 |  | 2007-01-01 | 9:01 | 32460 | 5.4939 | 0.032963 | 0.032963 |  | 2029-09-01 | 9:01 | 32460 | 6.1461 | 0.036876 | 0.036876 |  | 2029-09-01 | 9:01 | 32460 | 5.9522 | 0.035713 | 0.035713 |  | 2029-09-01 | 9:01 | 32460 | 5.6892 | 0.034135 | 0.034135 |  | 2006-09-01 | 9:01 | 32460 | 5.679 | 0.034074 | 0.034074 |  | 2028-01-01 | 9:01 | 32460 | 6.0595 | 0.036357 | 0.036357 |  | 2007-01-01 | 9:01 | 32460 | 6.0907 | 0.036544 | 0.036544 |  | 2028-01-01 | 9:01 | 32460 | 5.5838 | 0.033503 | 0.033503 |  | 2007-01-01 | 9:01 | 32460 | 5.6102 | 0.033661 | 0.033661
| 2029-09-01 | 9:02 | 32520 | 12.8277 | 0.076966 | 0.11569 |  | 2029-09-01 | 9:02 | 32520 | 12.8277 | 0.076966 | 0.11569 |  | 2006-09-01 | 9:02 | 32520 | 12.7884 | 0.07673 | 0.11538 |  | 2029-09-01 | 9:02 | 32520 | 12.2948 | 0.073769 | 0.11141 |  | 2006-09-01 | 9:02 | 32520 | 12.1909 | 0.073145 | 0.11058 |  | 2028-01-01 | 9:02 | 32520 | 12.8146 | 0.076888 | 0.1156 |  | 2007-01-01 | 9:02 | 32520 | 12.7987 | 0.076792 | 0.11547 |  | 2028-01-01 | 9:02 | 32520 | 11.6706 | 0.070024 | 0.10638 |  | 2007-01-01 | 9:02 | 32520 | 11.7618 | 0.070571 | 0.10712 |  | 2029-09-01 | 9:02 | 32520 | 12.8277 | 0.076966 | 0.11569 |  | 2006-09-01 | 9:02 | 32520 | 12.7884 | 0.07673 | 0.11538 |  | 2029-09-01 | 9:02 | 32520 | 11.8013 | 0.070808 | 0.10742 |  | 2006-09-01 | 9:02 | 32520 | 11.64 | 0.06984 | 0.10613 |  | 2028-01-01 | 9:02 | 32520 | 12.8146 | 0.076888 | 0.1156 |  | 2007-01-01 | 9:02 | 32520 | 12.7987 | 0.076792 | 0.11547 |  | 2028-01-01 | 9:02 | 32520 | 10.7141 | 0.064285 | 0.098592 |  | 2007-01-01 | 9:02 | 32520 | 10.8794 | 0.065276 | 0.099939 |  | 2029-09-01 | 9:02 | 32520 | 12.8277 | 0.076966 | 0.11569 |  | 2006-09-01 | 9:02 | 32520 | 12.7884 | 0.07673 | 0.11538 |  | 2029-09-01 | 9:02 | 32520 | 11.3421 | 0.068053 | 0.10369 |  | 2006-09-01 | 9:02 | 32520 | 11.1323 | 0.066794 | 0.102 |  | 2028-01-01 | 9:02 | 32520 | 12.8146 | 0.076888 | 0.1156 |  | 2007-01-01 | 9:02 | 32520 | 12.7987 | 0.076792 | 0.11547 |  | 2028-01-01 | 9:02 | 32520 | 9.8897 | 0.059338 | 0.091814 |  | 2007-01-01 | 9:02 | 32520 | 10.1086 | 0.060652 | 0.093615 |  | 2029-09-01 | 9:02 | 32520 | 11.9257 | 0.071554 | 0.10843 |  | 2029-09-01 | 9:02 | 32520 | 11.3729 | 0.068237 | 0.10395 |  | 2029-09-01 | 9:02 | 32520 | 10.6415 | 0.063849 | 0.097984 |  | 2006-09-01 | 9:02 | 32520 | 10.6134 | 0.06368 | 0.097754 |  | 2028-01-01 | 9:02 | 32520 | 11.6706 | 0.070024 | 0.10638 |  | 2007-01-01 | 9:02 | 32520 | 11.7618 | 0.070571 | 0.10712 |  | 2028-01-01 | 9:02 | 32520 | 10.3485 | 0.062091 | 0.095594 |  | 2007-01-01 | 9:02 | 32520 | 10.4216 | 0.06253 | 0.096191
| 2029-09-01 | 9:03 | 32580 | 19.1216 | 0.11473 | 0.23042 |  | 2029-09-01 | 9:03 | 32580 | 19.1216 | 0.11473 | 0.23042 |  | 2006-09-01 | 9:03 | 32580 | 19.0436 | 0.11426 | 0.22964 |  | 2029-09-01 | 9:03 | 32580 | 18.0775 | 0.10847 | 0.21987 |  | 2006-09-01 | 9:03 | 32580 | 17.8688 | 0.10721 | 0.21779 |  | 2028-01-01 | 9:03 | 32580 | 19.088 | 0.11453 | 0.23013 |  | 2007-01-01 | 9:03 | 32580 | 19.0582 | 0.11435 | 0.22982 |  | 2028-01-01 | 9:03 | 32580 | 16.8665 | 0.1012 | 0.20758 |  | 2007-01-01 | 9:03 | 32580 | 17.0423 | 0.10225 | 0.20937 |  | 2029-09-01 | 9:03 | 32580 | 19.1216 | 0.11473 | 0.23042 |  | 2006-09-01 | 9:03 | 32580 | 19.0436 | 0.11426 | 0.22964 |  | 2029-09-01 | 9:03 | 32580 | 17.1278 | 0.10277 | 0.21019 |  | 2006-09-01 | 9:03 | 32580 | 16.8079 | 0.10085 | 0.20697 |  | 2028-01-01 | 9:03 | 32580 | 19.088 | 0.11453 | 0.23013 |  | 2007-01-01 | 9:03 | 32580 | 19.0582 | 0.11435 | 0.22982 |  | 2028-01-01 | 9:03 | 32580 | 15.0798 | 0.090479 | 0.18907 |  | 2007-01-01 | 9:03 | 32580 | 15.3864 | 0.092318 | 0.19226 |  | 2029-09-01 | 9:03 | 32580 | 19.1216 | 0.11473 | 0.23042 |  | 2006-09-01 | 9:03 | 32580 | 19.0436 | 0.11426 | 0.22964 |  | 2029-09-01 | 9:03 | 32580 | 16.2593 | 0.097556 | 0.20125 |  | 2006-09-01 | 9:03 | 32580 | 15.8494 | 0.095096 | 0.1971 |  | 2028-01-01 | 9:03 | 32580 | 19.088 | 0.11453 | 0.23013 |  | 2007-01-01 | 9:03 | 32580 | 19.0582 | 0.11435 | 0.22982 |  | 2028-01-01 | 9:03 | 32580 | 13.593 | 0.081558 | 0.17337 |  | 2007-01-01 | 9:03 | 32580 | 13.9855 | 0.083913 | 0.17753 |  | 2029-09-01 | 9:03 | 32580 | 17.3606 | 0.10416 | 0.21259 |  | 2029-09-01 | 9:03 | 32580 | 16.3095 | 0.097857 | 0.20181 |  | 2029-09-01 | 9:03 | 32580 | 14.9522 | 0.089713 | 0.1877 |  | 2006-09-01 | 9:03 | 32580 | 14.9007 | 0.089404 | 0.18716 |  | 2028-01-01 | 9:03 | 32580 | 16.8665 | 0.1012 | 0.20758 |  | 2007-01-01 | 9:03 | 32580 | 17.0423 | 0.10225 | 0.20937 |  | 2028-01-01 | 9:03 | 32580 | 14.4142 | 0.086485 | 0.18208 |  | 2007-01-01 | 9:03 | 32580 | 14.5483 | 0.08729 | 0.18348
| 2029-09-01 | 9:04 | 32640 | 25.3365 | 0.15202 | 0.38244 |  | 2029-09-01 | 9:04 | 32640 | 25.3365 | 0.15202 | 0.38244 |  | 2006-09-01 | 9:04 | 32640 | 25.2081 | 0.15125 | 0.38089 |  | 2029-09-01 | 9:04 | 32640 | 23.6321 | 0.14179 | 0.36166 |  | 2006-09-01 | 9:04 | 32640 | 23.283 | 0.1397 | 0.35749 |  | 2028-01-01 | 9:04 | 32640 | 25.2737 | 0.15164 | 0.38177 |  | 2007-01-01 | 9:04 | 32640 | 25.2262 | 0.15136 | 0.38118 |  | 2028-01-01 | 9:04 | 32640 | 21.6779 | 0.13007 | 0.33765 |  | 2007-01-01 | 9:04 | 32640 | 21.9596 | 0.13176 | 0.34113 |  | 2029-09-01 | 9:04 | 32640 | 25.3365 | 0.15202 | 0.38244 |  | 2006-09-01 | 9:04 | 32640 | 25.2081 | 0.15125 | 0.38089 |  | 2029-09-01 | 9:04 | 32640 | 22.1084 | 0.13265 | 0.34284 |  | 2006-09-01 | 9:04 | 32640 | 21.5804 | 0.12948 | 0.33646 |  | 2028-01-01 | 9:04 | 32640 | 25.2737 | 0.15164 | 0.38177 |  | 2007-01-01 | 9:04 | 32640 | 25.2262 | 0.15136 | 0.38118 |  | 2028-01-01 | 9:04 | 32640 | 18.8946 | 0.11337 | 0.30244 |  | 2007-01-01 | 9:04 | 32640 | 19.3681 | 0.11621 | 0.30847 |  | 2029-09-01 | 9:04 | 32640 | 25.3365 | 0.15202 | 0.38244 |  | 2006-09-01 | 9:04 | 32640 | 25.2081 | 0.15125 | 0.38089 |  | 2029-09-01 | 9:04 | 32640 | 20.7386 | 0.12443 | 0.32568 |  | 2006-09-01 | 9:04 | 32640 | 20.0721 | 0.12043 | 0.31753 |  | 2028-01-01 | 9:04 | 32640 | 25.2737 | 0.15164 | 0.38177 |  | 2007-01-01 | 9:04 | 32640 | 25.2262 | 0.15136 | 0.38118 |  | 2028-01-01 | 9:04 | 32640 | 16.6561 | 0.099937 | 0.27331 |  | 2007-01-01 | 9:04 | 32640 | 17.2433 | 0.10346 | 0.28099 |  | 2029-09-01 | 9:04 | 32640 | 22.4712 | 0.13483 | 0.34742 |  | 2029-09-01 | 9:04 | 32640 | 20.8051 | 0.12483 | 0.32664 |  | 2029-09-01 | 9:04 | 32640 | 18.7043 | 0.11223 | 0.29992 |  | 2006-09-01 | 9:04 | 32640 | 18.626 | 0.11176 | 0.29891 |  | 2028-01-01 | 9:04 | 32640 | 21.6779 | 0.13007 | 0.33765 |  | 2007-01-01 | 9:04 | 32640 | 21.9596 | 0.13176 | 0.34113 |  | 2028-01-01 | 9:04 | 32640 | 17.8836 | 0.1073 | 0.28938 |  | 2007-01-01 | 9:04 | 32640 | 18.0879 | 0.10853 | 0.29201
| 2029-09-01 | 9:05 | 32700 | 31.4734 | 0.18884 | 0.57128 |  | 2029-09-01 | 9:05 | 32700 | 31.4734 | 0.18884 | 0.57128 |  | 2006-09-01 | 9:05 | 32700 | 31.2831 | 0.1877 | 0.56859 |  | 2029-09-01 | 9:05 | 32700 | 28.9689 | 0.17381 | 0.53548 |  | 2006-09-01 | 9:05 | 32700 | 28.4442 | 0.17067 | 0.52815 |  | 2028-01-01 | 9:05 | 32700 | 31.3729 | 0.18824 | 0.57001 |  | 2007-01-01 | 9:05 | 32700 | 31.3038 | 0.18782 | 0.569 |  | 2028-01-01 | 9:05 | 32700 | 26.1334 | 0.1568 | 0.49445 |  | 2007-01-01 | 9:05 | 32700 | 26.5389 | 0.15923 | 0.50036 |  | 2029-09-01 | 9:05 | 32700 | 31.4734 | 0.18884 | 0.57128 |  | 2006-09-01 | 9:05 | 32700 | 31.2831 | 0.1877 | 0.56859 |  | 2029-09-01 | 9:05 | 32700 | 26.7682 | 0.16061 | 0.50344 |  | 2006-09-01 | 9:05 | 32700 | 25.9846 | 0.15591 | 0.49236 |  | 2028-01-01 | 9:05 | 32700 | 31.3729 | 0.18824 | 0.57001 |  | 2007-01-01 | 9:05 | 32700 | 31.3038 | 0.18782 | 0.569 |  | 2028-01-01 | 9:05 | 32700 | 22.2279 | 0.13337 | 0.43581 |  | 2007-01-01 | 9:05 | 32700 | 22.8862 | 0.13732 | 0.44578 |  | 2029-09-01 | 9:05 | 32700 | 31.4734 | 0.18884 | 0.57128 |  | 2006-09-01 | 9:05 | 32700 | 31.2831 | 0.1877 | 0.56859 |  | 2029-09-01 | 9:05 | 32700 | 24.8224 | 0.14893 | 0.47461 |  | 2006-09-01 | 9:05 | 32700 | 23.848 | 0.14309 | 0.46062 |  | 2028-01-01 | 9:05 | 32700 | 31.3729 | 0.18824 | 0.57001 |  | 2007-01-01 | 9:05 | 32700 | 31.3038 | 0.18782 | 0.569 |  | 2028-01-01 | 9:05 | 32700 | 19.1899 | 0.11514 | 0.38845 |  | 2007-01-01 | 9:05 | 32700 | 19.9816 | 0.11989 | 0.40088 |  | 2029-09-01 | 9:05 | 32700 | 27.2767 | 0.16366 | 0.51108 |  | 2029-09-01 | 9:05 | 32700 | 24.8989 | 0.14939 | 0.47603 |  | 2029-09-01 | 9:05 | 32700 | 21.9701 | 0.13182 | 0.43174 |  | 2006-09-01 | 9:05 | 32700 | 21.863 | 0.13118 | 0.43009 |  | 2028-01-01 | 9:05 | 32700 | 26.1334 | 0.1568 | 0.49445 |  | 2007-01-01 | 9:05 | 32700 | 26.5389 | 0.15923 | 0.50036 |  | 2028-01-01 | 9:05 | 32700 | 20.844 | 0.12506 | 0.41444 |  | 2007-01-01 | 9:05 | 32700 | 21.1242 | 0.12675 | 0.41875
| 2029-09-01 | 9:06 | 32760 | 37.533 | 0.2252 | 0.79648 |  | 2029-09-01 | 9:06 | 32760 | 37.533 | 0.2252 | 0.79648 |  | 2006-09-01 | 9:06 | 32760 | 37.27 | 0.22362 | 0.79221 |  | 2029-09-01 | 9:06 | 32760 | 34.0982 | 0.20459 | 0.74007 |  | 2006-09-01 | 9:06 | 32760 | 33.3626 | 0.20018 | 0.72833 |  | 2028-01-01 | 9:06 | 32760 | 37.3867 | 0.22432 | 0.79433 |  | 2007-01-01 | 9:06 | 32760 | 37.2925 | 0.22375 | 0.79275 |  | 2028-01-01 | 9:06 | 32760 | 30.2592 | 0.18156 | 0.676 |  | 2007-01-01 | 9:06 | 32760 | 30.8037 | 0.18482 | 0.68518 |  | 2029-09-01 | 9:06 | 32760 | 37.533 | 0.2252 | 0.79648 |  | 2006-09-01 | 9:06 | 32760 | 37.27 | 0.22362 | 0.79221 |  | 2029-09-01 | 9:06 | 32760 | 31.1304 | 0.18678 | 0.69023 |  | 2006-09-01 | 9:06 | 32760 | 30.0461 | 0.18028 | 0.67264 |  | 2028-01-01 | 9:06 | 32760 | 37.3867 | 0.22432 | 0.79433 |  | 2007-01-01 | 9:06 | 32760 | 37.2925 | 0.22375 | 0.79275 |  | 2028-01-01 | 9:06 | 32760 | 25.1406 | 0.15084 | 0.58665 |  | 2007-01-01 | 9:06 | 32760 | 25.9952 | 0.15597 | 0.60175 |  | 2029-09-01 | 9:06 | 32760 | 37.533 | 0.2252 | 0.79648 |  | 2006-09-01 | 9:06 | 32760 | 37.27 | 0.22362 | 0.79221 |  | 2029-09-01 | 9:06 | 32760 | 28.5493 | 0.1713 | 0.64591 |  | 2006-09-01 | 9:06 | 32760 | 27.2205 | 0.16332 | 0.62394 |  | 2028-01-01 | 9:06 | 32760 | 37.3867 | 0.22432 | 0.79433 |  | 2007-01-01 | 9:06 | 32760 | 37.2925 | 0.22375 | 0.79275 |  | 2028-01-01 | 9:06 | 32760 | 21.2857 | 0.12771 | 0.51616 |  | 2007-01-01 | 9:06 | 32760 | 22.2839 | 0.1337 | 0.53458 |  | 2029-09-01 | 9:06 | 32760 | 31.7951 | 0.19077 | 0.70185 |  | 2029-09-01 | 9:06 | 32760 | 28.6268 | 0.17176 | 0.64779 |  | 2029-09-01 | 9:06 | 32760 | 24.8126 | 0.14888 | 0.58062 |  | 2006-09-01 | 9:06 | 32760 | 24.6756 | 0.14805 | 0.57815 |  | 2028-01-01 | 9:06 | 32760 | 30.2592 | 0.18156 | 0.676 |  | 2007-01-01 | 9:06 | 32760 | 30.8037 | 0.18482 | 0.68518 |  | 2028-01-01 | 9:06 | 32760 | 23.3703 | 0.14022 | 0.55467 |  | 2007-01-01 | 9:06 | 32760 | 23.7289 | 0.14237 | 0.56113
| 2029-09-01 | 9:07 | 32820 | 43.516 | 0.2611 | 1.0576 |  | 2029-09-01 | 9:07 | 32820 | 43.516 | 0.2611 | 1.0576 |  | 2006-09-01 | 9:07 | 32820 | 43.1703 | 0.25902 | 1.0512 |  | 2029-09-01 | 9:07 | 32820 | 39.0293 | 0.23418 | 0.97424 |  | 2006-09-01 | 9:07 | 32820 | 38.0479 | 0.22829 | 0.95662 |  | 2028-01-01 | 9:07 | 32820 | 43.3165 | 0.2599 | 1.0542 |  | 2007-01-01 | 9:07 | 32820 | 43.1935 | 0.25916 | 1.0519 |  | 2028-01-01 | 9:07 | 32820 | 34.0798 | 0.20448 | 0.88048 |  | 2007-01-01 | 9:07 | 32820 | 34.7759 | 0.20866 | 0.89384 |  | 2029-09-01 | 9:07 | 32820 | 43.516 | 0.2611 | 1.0576 |  | 2006-09-01 | 9:07 | 32820 | 43.1703 | 0.25902 | 1.0512 |  | 2029-09-01 | 9:07 | 32820 | 35.2168 | 0.2113 | 0.90153 |  | 2006-09-01 | 9:07 | 32820 | 33.7886 | 0.20273 | 0.87537 |  | 2028-01-01 | 9:07 | 32820 | 43.3165 | 0.2599 | 1.0542 |  | 2007-01-01 | 9:07 | 32820 | 43.1935 | 0.25916 | 1.0519 |  | 2028-01-01 | 9:07 | 32820 | 27.6858 | 0.16611 | 0.75276 |  | 2007-01-01 | 9:07 | 32820 | 28.7432 | 0.17246 | 0.77421 |  | 2029-09-01 | 9:07 | 32820 | 43.516 | 0.2611 | 1.0576 |  | 2006-09-01 | 9:07 | 32820 | 43.1703 | 0.25902 | 1.0512 |  | 2029-09-01 | 9:07 | 32820 | 31.9539 | 0.19172 | 0.83763 |  | 2006-09-01 | 9:07 | 32820 | 30.2288 | 0.18137 | 0.80532 |  | 2028-01-01 | 9:07 | 32820 | 43.3165 | 0.2599 | 1.0542 |  | 2007-01-01 | 9:07 | 32820 | 43.1935 | 0.25916 | 1.0519 |  | 2028-01-01 | 9:07 | 32820 | 23.0193 | 0.13812 | 0.65428 |  | 2007-01-01 | 9:07 | 32820 | 24.2202 | 0.14532 | 0.6799 |  | 2029-09-01 | 9:07 | 32820 | 36.0435 | 0.21626 | 0.91811 |  | 2029-09-01 | 9:07 | 32820 | 32.0212 | 0.19213 | 0.83992 |  | 2029-09-01 | 9:07 | 32820 | 27.2865 | 0.16372 | 0.74434 |  | 2006-09-01 | 9:07 | 32820 | 27.1196 | 0.16272 | 0.74086 |  | 2028-01-01 | 9:07 | 32820 | 34.0798 | 0.20448 | 0.88048 |  | 2007-01-01 | 9:07 | 32820 | 34.7759 | 0.20866 | 0.89384 |  | 2028-01-01 | 9:07 | 32820 | 25.5259 | 0.15316 | 0.70782 |  | 2007-01-01 | 9:07 | 32820 | 25.9635 | 0.15578 | 0.71691
| 2029-09-01 | 9:08 | 32880 | 49.4234 | 0.29654 | 1.3541 |  | 2029-09-01 | 9:08 | 32880 | 49.4234 | 0.29654 | 1.3541 |  | 2006-09-01 | 9:08 | 32880 | 48.9851 | 0.29391 | 1.3451 |  | 2029-09-01 | 9:08 | 32880 | 43.7703 | 0.26262 | 1.2369 |  | 2006-09-01 | 9:08 | 32880 | 42.5098 | 0.25506 | 1.2117 |  | 2028-01-01 | 9:08 | 32880 | 49.1633 | 0.29498 | 1.3492 |  | 2007-01-01 | 9:08 | 32880 | 49.0079 | 0.29405 | 1.346 |  | 2028-01-01 | 9:08 | 32880 | 37.6178 | 0.22571 | 1.1062 |  | 2007-01-01 | 9:08 | 32880 | 38.4758 | 0.23085 | 1.1247 |  | 2029-09-01 | 9:08 | 32880 | 49.4234 | 0.29654 | 1.3541 |  | 2006-09-01 | 9:08 | 32880 | 48.9851 | 0.29391 | 1.3451 |  | 2029-09-01 | 9:08 | 32880 | 39.0462 | 0.23428 | 1.1358 |  | 2006-09-01 | 9:08 | 32880 | 37.2345 | 0.22341 | 1.0988 |  | 2028-01-01 | 9:08 | 32880 | 49.1633 | 0.29498 | 1.3492 |  | 2007-01-01 | 9:08 | 32880 | 49.0079 | 0.29405 | 1.346 |  | 2028-01-01 | 9:08 | 32880 | 29.9098 | 0.17946 | 0.93222 |  | 2007-01-01 | 9:08 | 32880 | 31.1725 | 0.18703 | 0.96125 |  | 2029-09-01 | 9:08 | 32880 | 49.4234 | 0.29654 | 1.3541 |  | 2006-09-01 | 9:08 | 32880 | 48.9851 | 0.29391 | 1.3451 |  | 2029-09-01 | 9:08 | 32880 | 35.0664 | 0.2104 | 1.048 |  | 2006-09-01 | 9:08 | 32880 | 32.9087 | 0.19745 | 1.0028 |  | 2028-01-01 | 9:08 | 32880 | 49.1633 | 0.29498 | 1.3492 |  | 2007-01-01 | 9:08 | 32880 | 49.0079 | 0.29405 | 1.346 |  | 2028-01-01 | 9:08 | 32880 | 24.4533 | 0.14672 | 0.801 |  | 2007-01-01 | 9:08 | 32880 | 25.8494 | 0.1551 | 0.835 |  | 2029-09-01 | 9:08 | 32880 | 40.0378 | 0.24023 | 1.1583 |  | 2029-09-01 | 9:08 | 32880 | 35.112 | 0.21067 | 1.0506 |  | 2029-09-01 | 9:08 | 32880 | 29.4394 | 0.17664 | 0.92097 |  | 2006-09-01 | 9:08 | 32880 | 29.2433 | 0.17546 | 0.91632 |  | 2028-01-01 | 9:08 | 32880 | 37.6178 | 0.22571 | 1.1062 |  | 2007-01-01 | 9:08 | 32880 | 38.4758 | 0.23085 | 1.1247 |  | 2028-01-01 | 9:08 | 32880 | 27.3654 | 0.16419 | 0.87201 |  | 2007-01-01 | 9:08 | 32880 | 27.8809 | 0.16729 | 0.88419
| 2029-09-01 | 9:09 | 32940 | 55.2559 | 0.33154 | 1.6856 |  | 2029-09-01 | 9:09 | 32940 | 55.2559 | 0.33154 | 1.6856 |  | 2006-09-01 | 9:09 | 32940 | 54.7159 | 0.3283 | 1.6734 |  | 2029-09-01 | 9:09 | 32940 | 48.329 | 0.28997 | 1.5268 |  | 2006-09-01 | 9:09 | 32940 | 46.7575 | 0.28054 | 1.4922 |  | 2028-01-01 | 9:09 | 32940 | 54.9283 | 0.32957 | 1.6788 |  | 2007-01-01 | 9:09 | 32940 | 54.737 | 0.32842 | 1.6744 |  | 2028-01-01 | 9:09 | 32940 | 40.8941 | 0.24536 | 1.3516 |  | 2007-01-01 | 9:09 | 32940 | 41.9224 | 0.25153 | 1.3762 |  | 2029-09-01 | 9:09 | 32940 | 55.2559 | 0.33154 | 1.6856 |  | 2006-09-01 | 9:09 | 32940 | 54.7159 | 0.3283 | 1.6734 |  | 2029-09-01 | 9:09 | 32940 | 42.6365 | 0.25582 | 1.3916 |  | 2006-09-01 | 9:09 | 32940 | 40.4047 | 0.24243 | 1.3412 |  | 2028-01-01 | 9:09 | 32940 | 54.9283 | 0.32957 | 1.6788 |  | 2007-01-01 | 9:09 | 32940 | 54.737 | 0.32842 | 1.6744 |  | 2028-01-01 | 9:09 | 32940 | 31.8533 | 0.19112 | 1.1233 |  | 2007-01-01 | 9:09 | 32940 | 33.3207 | 0.19992 | 1.1612 |  | 2029-09-01 | 9:09 | 32940 | 55.2559 | 0.33154 | 1.6856 |  | 2006-09-01 | 9:09 | 32940 | 54.7159 | 0.3283 | 1.6734 |  | 2029-09-01 | 9:09 | 32940 | 37.9145 | 0.22749 | 1.2755 |  | 2006-09-01 | 9:09 | 32940 | 35.2925 | 0.21175 | 1.2145 |  | 2028-01-01 | 9:09 | 32940 | 54.9283 | 0.32957 | 1.6788 |  | 2007-01-01 | 9:09 | 32940 | 54.737 | 0.32842 | 1.6744 |  | 2028-01-01 | 9:09 | 32940 | 25.6395 | 0.15384 | 0.95483 |  | 2007-01-01 | 9:09 | 32940 | 27.2206 | 0.16332 | 0.99832 |  | 2029-09-01 | 9:09 | 32940 | 43.7932 | 0.26276 | 1.4211 |  | 2029-09-01 | 9:09 | 32940 | 37.9261 | 0.22756 | 1.2781 |  | 2029-09-01 | 9:09 | 32940 | 31.313 | 0.18788 | 1.1089 |  | 2006-09-01 | 9:09 | 32940 | 31.0887 | 0.18653 | 1.1029 |  | 2028-01-01 | 9:09 | 32940 | 40.8941 | 0.24536 | 1.3516 |  | 2007-01-01 | 9:09 | 32940 | 41.9224 | 0.25153 | 1.3762 |  | 2028-01-01 | 9:09 | 32940 | 28.9352 | 0.17361 | 1.0456 |  | 2007-01-01 | 9:09 | 32940 | 29.5263 | 0.17716 | 1.0614
| 2029-09-01 | 9:10 | 33000 | 61.0141 | 0.36608 | 2.0517 |  | 2029-09-01 | 9:10 | 33000 | 61.0141 | 0.36608 | 2.0517 |  | 2006-09-01 | 9:10 | 33000 | 60.3639 | 0.36218 | 2.0356 |  | 2029-09-01 | 9:10 | 33000 | 52.7138 | 0.31628 | 1.8431 |  | 2006-09-01 | 9:10 | 33000 | 50.7997 | 0.3048 | 1.797 |  | 2028-01-01 | 9:10 | 33000 | 60.6125 | 0.36368 | 2.0425 |  | 2007-01-01 | 9:10 | 33000 | 60.3819 | 0.36229 | 2.0367 |  | 2028-01-01 | 9:10 | 33000 | 43.928 | 0.26357 | 1.6151 |  | 2007-01-01 | 9:10 | 33000 | 45.1333 | 0.2708 | 1.647 |  | 2029-09-01 | 9:10 | 33000 | 61.0141 | 0.36608 | 2.0517 |  | 2006-09-01 | 9:10 | 33000 | 60.3639 | 0.36218 | 2.0356 |  | 2029-09-01 | 9:10 | 33000 | 46.0048 | 0.27603 | 1.6677 |  | 2006-09-01 | 9:10 | 33000 | 43.3187 | 0.25991 | 1.6011 |  | 2028-01-01 | 9:10 | 33000 | 60.6125 | 0.36368 | 2.0425 |  | 2007-01-01 | 9:10 | 33000 | 60.3819 | 0.36229 | 2.0367 |  | 2028-01-01 | 9:10 | 33000 | 33.5515 | 0.20131 | 1.3247 |  | 2007-01-01 | 9:10 | 33000 | 35.2206 | 0.21132 | 1.3725 |  | 2029-09-01 | 9:10 | 33000 | 61.0141 | 0.36608 | 2.0517 |  | 2006-09-01 | 9:10 | 33000 | 60.3639 | 0.36218 | 2.0356 |  | 2029-09-01 | 9:10 | 33000 | 40.5236 | 0.24314 | 1.5187 |  | 2006-09-01 | 9:10 | 33000 | 37.4095 | 0.22446 | 1.439 |  | 2028-01-01 | 9:10 | 33000 | 60.6125 | 0.36368 | 2.0425 |  | 2007-01-01 | 9:10 | 33000 | 60.3819 | 0.36229 | 2.0367 |  | 2028-01-01 | 9:10 | 33000 | 26.6207 | 0.15972 | 1.1146 |  | 2007-01-01 | 9:10 | 33000 | 28.3754 | 0.17025 | 1.1686 |  | 2029-09-01 | 9:10 | 33000 | 47.3237 | 0.28394 | 1.705 |  | 2029-09-01 | 9:10 | 33000 | 40.4883 | 0.24293 | 1.5211 |  | 2029-09-01 | 9:10 | 33000 | 32.9434 | 0.19766 | 1.3065 |  | 2006-09-01 | 9:10 | 33000 | 32.6924 | 0.19615 | 1.299 |  | 2028-01-01 | 9:10 | 33000 | 43.928 | 0.26357 | 1.6151 |  | 2007-01-01 | 9:10 | 33000 | 45.1333 | 0.2708 | 1.647 |  | 2028-01-01 | 9:10 | 33000 | 30.2747 | 0.18165 | 1.2273 |  | 2007-01-01 | 9:10 | 33000 | 30.9384 | 0.18563 | 1.247
| 2029-09-01 | 9:11 | 33060 | 66.6989 | 0.40019 | 2.4519 |  | 2029-09-01 | 9:11 | 33060 | 66.6989 | 0.40019 | 2.4519 |  | 2006-09-01 | 9:11 | 33060 | 65.9303 | 0.39558 | 2.4312 |  | 2029-09-01 | 9:11 | 33060 | 56.9325 | 0.34159 | 2.1847 |  | 2006-09-01 | 9:11 | 33060 | 54.6451 | 0.32787 | 2.1249 |  | 2028-01-01 | 9:11 | 33060 | 66.2171 | 0.3973 | 2.4398 |  | 2007-01-01 | 9:11 | 33060 | 65.9439 | 0.39566 | 2.4323 |  | 2028-01-01 | 9:11 | 33060 | 46.7375 | 0.28042 | 1.8955 |  | 2007-01-01 | 9:11 | 33060 | 48.1248 | 0.28875 | 1.9358 |  | 2029-09-01 | 9:11 | 33060 | 66.6989 | 0.40019 | 2.4519 |  | 2006-09-01 | 9:11 | 33060 | 65.9303 | 0.39558 | 2.4312 |  | 2029-09-01 | 9:11 | 33060 | 49.1671 | 0.295 | 1.9627 |  | 2006-09-01 | 9:11 | 33060 | 45.9947 | 0.27597 | 1.8771 |  | 2028-01-01 | 9:11 | 33060 | 66.2171 | 0.3973 | 2.4398 |  | 2007-01-01 | 9:11 | 33060 | 65.9439 | 0.39566 | 2.4323 |  | 2028-01-01 | 9:11 | 33060 | 35.0354 | 0.21021 | 1.5349 |  | 2007-01-01 | 9:11 | 33060 | 36.9013 | 0.22141 | 1.5939 |  | 2029-09-01 | 9:11 | 33060 | 66.6989 | 0.40019 | 2.4519 |  | 2006-09-01 | 9:11 | 33060 | 65.9303 | 0.39558 | 2.4312 |  | 2029-09-01 | 9:11 | 33060 | 42.9165 | 0.2575 | 1.7762 |  | 2006-09-01 | 9:11 | 33060 | 39.2863 | 0.23572 | 1.6747 |  | 2028-01-01 | 9:11 | 33060 | 66.2171 | 0.3973 | 2.4398 |  | 2007-01-01 | 9:11 | 33060 | 65.9439 | 0.39566 | 2.4323 |  | 2028-01-01 | 9:11 | 33060 | 27.4324 | 0.16459 | 1.2792 |  | 2007-01-01 | 9:11 | 33060 | 29.3483 | 0.17609 | 1.3447 |  | 2029-09-01 | 9:11 | 33060 | 50.6427 | 0.30386 | 2.0089 |  | 2029-09-01 | 9:11 | 33060 | 42.8208 | 0.25692 | 1.778 |  | 2029-09-01 | 9:11 | 33060 | 34.362 | 0.20617 | 1.5127 |  | 2006-09-01 | 9:11 | 33060 | 34.086 | 0.20452 | 1.5035 |  | 2028-01-01 | 9:11 | 33060 | 46.7375 | 0.28042 | 1.8955 |  | 2007-01-01 | 9:11 | 33060 | 48.1248 | 0.28875 | 1.9358 |  | 2028-01-01 | 9:11 | 33060 | 31.4178 | 0.18851 | 1.4158 |  | 2007-01-01 | 9:11 | 33060 | 32.1505 | 0.1929 | 1.4399
| 2029-09-01 | 9:12 | 33120 | 72.311 | 0.43387 | 2.8858 |  | 2029-09-01 | 9:12 | 33120 | 72.311 | 0.43387 | 2.8858 |  | 2006-09-01 | 9:12 | 33120 | 71.4165 | 0.4285 | 2.8597 |  | 2029-09-01 | 9:12 | 33120 | 60.9925 | 0.36596 | 2.5507 |  | 2006-09-01 | 9:12 | 33120 | 58.3019 | 0.34981 | 2.4747 |  | 2028-01-01 | 9:12 | 33120 | 71.7432 | 0.43046 | 2.8702 |  | 2007-01-01 | 9:12 | 33120 | 71.4241 | 0.42854 | 2.8609 |  | 2028-01-01 | 9:12 | 33120 | 49.3392 | 0.29604 | 2.1916 |  | 2007-01-01 | 9:12 | 33120 | 50.9122 | 0.30547 | 2.2412 |  | 2029-09-01 | 9:12 | 33120 | 72.311 | 0.43387 | 2.8858 |  | 2006-09-01 | 9:12 | 33120 | 71.4165 | 0.4285 | 2.8597 |  | 2029-09-01 | 9:12 | 33120 | 52.138 | 0.31283 | 2.2755 |  | 2006-09-01 | 9:12 | 33120 | 48.4497 | 0.2907 | 2.1678 |  | 2028-01-01 | 9:12 | 33120 | 71.7432 | 0.43046 | 2.8702 |  | 2007-01-01 | 9:12 | 33120 | 71.4241 | 0.42854 | 2.8609 |  | 2028-01-01 | 9:12 | 33120 | 36.3322 | 0.21799 | 1.7529 |  | 2007-01-01 | 9:12 | 33120 | 38.3887 | 0.23033 | 1.8242 |  | 2029-09-01 | 9:12 | 33120 | 72.311 | 0.43387 | 2.8858 |  | 2006-09-01 | 9:12 | 33120 | 71.4165 | 0.4285 | 2.8597 |  | 2029-09-01 | 9:12 | 33120 | 45.1141 | 0.27068 | 2.0468 |  | 2006-09-01 | 9:12 | 33120 | 40.947 | 0.24568 | 1.9204 |  | 2028-01-01 | 9:12 | 33120 | 71.7432 | 0.43046 | 2.8702 |  | 2007-01-01 | 9:12 | 33120 | 71.4241 | 0.42854 | 2.8609 |  | 2028-01-01 | 9:12 | 33120 | 28.1038 | 0.16862 | 1.4478 |  | 2007-01-01 | 9:12 | 33120 | 30.1687 | 0.18101 | 1.5257 |  | 2029-09-01 | 9:12 | 33120 | 53.7627 | 0.32258 | 2.3315 |  | 2029-09-01 | 9:12 | 33120 | 44.9443 | 0.26967 | 2.0477 |  | 2029-09-01 | 9:12 | 33120 | 35.5962 | 0.21358 | 1.7263 |  | 2006-09-01 | 9:12 | 33120 | 35.297 | 0.21178 | 1.7153 |  | 2028-01-01 | 9:12 | 33120 | 49.3392 | 0.29604 | 2.1916 |  | 2007-01-01 | 9:12 | 33120 | 50.9122 | 0.30547 | 2.2412 |  | 2028-01-01 | 9:12 | 33120 | 32.3932 | 0.19436 | 1.6101 |  | 2007-01-01 | 9:12 | 33120 | 33.191 | 0.19915 | 1.639
| 2029-09-01 | 9:13 | 33180 | 77.8512 | 0.46711 | 3.3529 |  | 2029-09-01 | 9:13 | 33180 | 77.8512 | 0.46711 | 3.3529 |  | 2006-09-01 | 9:13 | 33180 | 76.8235 | 0.46094 | 3.3206 |  | 2029-09-01 | 9:13 | 33180 | 64.9009 | 0.38941 | 2.9401 |  | 2006-09-01 | 9:13 | 33180 | 61.7779 | 0.37067 | 2.8454 |  | 2028-01-01 | 9:13 | 33180 | 77.1918 | 0.46315 | 3.3334 |  | 2007-01-01 | 9:13 | 33180 | 76.8236 | 0.46094 | 3.3218 |  | 2028-01-01 | 9:13 | 33180 | 51.7486 | 0.31049 | 2.5021 |  | 2007-01-01 | 9:13 | 33180 | 53.5096 | 0.32106 | 2.5623 |  | 2029-09-01 | 9:13 | 33180 | 77.8512 | 0.46711 | 3.3529 |  | 2006-09-01 | 9:13 | 33180 | 76.8235 | 0.46094 | 3.3206 |  | 2029-09-01 | 9:13 | 33180 | 54.9312 | 0.32959 | 2.6051 |  | 2006-09-01 | 9:13 | 33180 | 50.6997 | 0.3042 | 2.472 |  | 2028-01-01 | 9:13 | 33180 | 77.1918 | 0.46315 | 3.3334 |  | 2007-01-01 | 9:13 | 33180 | 76.8236 | 0.46094 | 3.3218 |  | 2028-01-01 | 9:13 | 33180 | 37.4654 | 0.22479 | 1.9776 |  | 2007-01-01 | 9:13 | 33180 | 39.7052 | 0.23823 | 2.0625 |  | 2029-09-01 | 9:13 | 33180 | 77.8512 | 0.46711 | 3.3529 |  | 2006-09-01 | 9:13 | 33180 | 76.8235 | 0.46094 | 3.3206 |  | 2029-09-01 | 9:13 | 33180 | 47.1349 | 0.28281 | 2.3297 |  | 2006-09-01 | 9:13 | 33180 | 42.4133 | 0.25448 | 2.1749 |  | 2028-01-01 | 9:13 | 33180 | 77.1918 | 0.46315 | 3.3334 |  | 2007-01-01 | 9:13 | 33180 | 76.8236 | 0.46094 | 3.3218 |  | 2028-01-01 | 9:13 | 33180 | 28.6593 | 0.17196 | 1.6197 |  | 2007-01-01 | 9:13 | 33180 | 30.8608 | 0.18516 | 1.7108 |  | 2029-09-01 | 9:13 | 33180 | 56.6954 | 0.34017 | 2.6716 |  | 2029-09-01 | 9:13 | 33180 | 46.8772 | 0.28126 | 2.3289 |  | 2029-09-01 | 9:13 | 33180 | 36.67 | 0.22002 | 1.9463 |  | 2006-09-01 | 9:13 | 33180 | 36.3495 | 0.2181 | 1.9334 |  | 2028-01-01 | 9:13 | 33180 | 51.7486 | 0.31049 | 2.5021 |  | 2007-01-01 | 9:13 | 33180 | 53.5096 | 0.32106 | 2.5623 |  | 2028-01-01 | 9:13 | 33180 | 33.2256 | 0.19935 | 1.8095 |  | 2007-01-01 | 9:13 | 33180 | 34.0845 | 0.20451 | 1.8435
| 2029-09-01 | 9:14 | 33240 | 83.32 | 0.49992 | 3.8528 |  | 2029-09-01 | 9:14 | 33240 | 83.32 | 0.49992 | 3.8528 |  | 2006-09-01 | 9:14 | 33240 | 82.1526 | 0.49292 | 3.8136 |  | 2029-09-01 | 9:14 | 33240 | 68.6644 | 0.41199 | 3.3521 |  | 2006-09-01 | 9:14 | 33240 | 65.0809 | 0.39049 | 3.2359 |  | 2028-01-01 | 9:14 | 33240 | 82.5639 | 0.49538 | 3.8287 |  | 2007-01-01 | 9:14 | 33240 | 82.1435 | 0.49286 | 3.8147 |  | 2028-01-01 | 9:14 | 33240 | 53.9798 | 0.32388 | 2.826 |  | 2007-01-01 | 9:14 | 33240 | 55.9302 | 0.33558 | 2.8979 |  | 2029-09-01 | 9:14 | 33240 | 83.32 | 0.49992 | 3.8528 |  | 2006-09-01 | 9:14 | 33240 | 82.1526 | 0.49292 | 3.8136 |  | 2029-09-01 | 9:14 | 33240 | 57.5592 | 0.34536 | 2.9504 |  | 2006-09-01 | 9:14 | 33240 | 52.7595 | 0.31656 | 2.7885 |  | 2028-01-01 | 9:14 | 33240 | 82.5639 | 0.49538 | 3.8287 |  | 2007-01-01 | 9:14 | 33240 | 82.1435 | 0.49286 | 3.8147 |  | 2028-01-01 | 9:14 | 33240 | 38.4557 | 0.23073 | 2.2084 |  | 2007-01-01 | 9:14 | 33240 | 40.871 | 0.24523 | 2.3077 |  | 2029-09-01 | 9:14 | 33240 | 83.32 | 0.49992 | 3.8528 |  | 2006-09-01 | 9:14 | 33240 | 82.1526 | 0.49292 | 3.8136 |  | 2029-09-01 | 9:14 | 33240 | 48.9957 | 0.29397 | 2.6236 |  | 2006-09-01 | 9:14 | 33240 | 43.7049 | 0.26223 | 2.4371 |  | 2028-01-01 | 9:14 | 33240 | 82.5639 | 0.49538 | 3.8287 |  | 2007-01-01 | 9:14 | 33240 | 82.1435 | 0.49286 | 3.8147 |  | 2028-01-01 | 9:14 | 33240 | 29.1187 | 0.17471 | 1.7944 |  | 2007-01-01 | 9:14 | 33240 | 31.4454 | 0.18867 | 1.8995 |  | 2029-09-01 | 9:14 | 33240 | 59.452 | 0.35671 | 3.0284 |  | 2029-09-01 | 9:14 | 33240 | 48.6366 | 0.29182 | 2.6208 |  | 2029-09-01 | 9:14 | 33240 | 37.604 | 0.22562 | 2.1719 |  | 2006-09-01 | 9:14 | 33240 | 37.2642 | 0.22359 | 2.157 |  | 2028-01-01 | 9:14 | 33240 | 53.9798 | 0.32388 | 2.826 |  | 2007-01-01 | 9:14 | 33240 | 55.9302 | 0.33558 | 2.8979 |  | 2028-01-01 | 9:14 | 33240 | 33.936 | 0.20362 | 2.0131 |  | 2007-01-01 | 9:14 | 33240 | 34.8519 | 0.20911 | 2.0526
| 2029-09-01 | 9:15 | 33300 | 88.7183 | 0.53231 | 4.3851 |  | 2029-09-01 | 9:15 | 33300 | 88.7183 | 0.53231 | 4.3851 |  | 2006-09-01 | 9:15 | 33300 | 87.4051 | 0.52443 | 4.338 |  | 2029-09-01 | 9:15 | 33300 | 72.2895 | 0.43374 | 3.7858 |  | 2006-09-01 | 9:15 | 33300 | 68.2182 | 0.40931 | 3.6452 |  | 2028-01-01 | 9:15 | 33300 | 87.8607 | 0.52716 | 4.3559 |  | 2007-01-01 | 9:15 | 33300 | 87.3851 | 0.52431 | 4.339 |  | 2028-01-01 | 9:15 | 33300 | 56.046 | 0.33628 | 3.1622 |  | 2007-01-01 | 9:15 | 33300 | 58.1864 | 0.34912 | 3.247 |  | 2029-09-01 | 9:15 | 33300 | 88.7183 | 0.53231 | 4.3851 |  | 2006-09-01 | 9:15 | 33300 | 87.4051 | 0.52443 | 4.338 |  | 2029-09-01 | 9:15 | 33300 | 60.0337 | 0.3602 | 3.3106 |  | 2006-09-01 | 9:15 | 33300 | 54.6429 | 0.32786 | 3.1164 |  | 2028-01-01 | 9:15 | 33300 | 87.8607 | 0.52716 | 4.3559 |  | 2007-01-01 | 9:15 | 33300 | 87.3851 | 0.52431 | 4.339 |  | 2028-01-01 | 9:15 | 33300 | 39.321 | 0.23593 | 2.4443 |  | 2007-01-01 | 9:15 | 33300 | 41.9037 | 0.25142 | 2.5591 |  | 2029-09-01 | 9:15 | 33300 | 88.7183 | 0.53231 | 4.3851 |  | 2006-09-01 | 9:15 | 33300 | 87.4051 | 0.52443 | 4.338 |  | 2029-09-01 | 9:15 | 33300 | 50.7119 | 0.30427 | 2.9279 |  | 2006-09-01 | 9:15 | 33300 | 44.8397 | 0.26904 | 2.7061 |  | 2028-01-01 | 9:15 | 33300 | 87.8607 | 0.52716 | 4.3559 |  | 2007-01-01 | 9:15 | 33300 | 87.3851 | 0.52431 | 4.339 |  | 2028-01-01 | 9:15 | 33300 | 29.4989 | 0.17699 | 1.9714 |  | 2007-01-01 | 9:15 | 33300 | 31.9395 | 0.19164 | 2.0912 |  | 2029-09-01 | 9:15 | 33300 | 62.0429 | 0.37226 | 3.4006 |  | 2029-09-01 | 9:15 | 33300 | 50.238 | 0.30143 | 2.9222 |  | 2029-09-01 | 9:15 | 33300 | 38.4164 | 0.2305 | 2.4024 |  | 2006-09-01 | 9:15 | 33300 | 38.0592 | 0.22836 | 2.3853 |  | 2028-01-01 | 9:15 | 33300 | 56.046 | 0.33628 | 3.1622 |  | 2007-01-01 | 9:15 | 33300 | 58.1864 | 0.34912 | 3.247 |  | 2028-01-01 | 9:15 | 33300 | 34.5423 | 0.20725 | 2.2204 |  | 2007-01-01 | 9:15 | 33300 | 35.5111 | 0.21307 | 2.2657
| 2029-09-01 | 9:16 | 33360 | 94.0467 | 0.56428 | 4.9494 |  | 2029-09-01 | 9:16 | 33360 | 94.0467 | 0.56428 | 4.9494 |  | 2006-09-01 | 9:16 | 33360 | 92.582 | 0.55549 | 4.8935 |  | 2029-09-01 | 9:16 | 33360 | 75.7823 | 0.45469 | 4.2405 |  | 2006-09-01 | 9:16 | 33360 | 71.1968 | 0.42718 | 4.0723 |  | 2028-01-01 | 9:16 | 33360 | 93.0831 | 0.5585 | 4.9144 |  | 2007-01-01 | 9:16 | 33360 | 92.5493 | 0.5553 | 4.8943 |  | 2028-01-01 | 9:16 | 33360 | 57.9594 | 0.34776 | 3.51 |  | 2007-01-01 | 9:16 | 33360 | 60.2894 | 0.36174 | 3.6087 |  | 2029-09-01 | 9:16 | 33360 | 94.0467 | 0.56428 | 4.9494 |  | 2006-09-01 | 9:16 | 33360 | 92.582 | 0.55549 | 4.8935 |  | 2029-09-01 | 9:16 | 33360 | 62.3657 | 0.37419 | 3.6848 |  | 2006-09-01 | 9:16 | 33360 | 56.3628 | 0.33818 | 3.4546 |  | 2028-01-01 | 9:16 | 33360 | 93.0831 | 0.5585 | 4.9144 |  | 2007-01-01 | 9:16 | 33360 | 92.5493 | 0.5553 | 4.8943 |  | 2028-01-01 | 9:16 | 33360 | 40.0773 | 0.24046 | 2.6848 |  | 2007-01-01 | 9:16 | 33360 | 42.8189 | 0.25691 | 2.816 |  | 2029-09-01 | 9:16 | 33360 | 94.0467 | 0.56428 | 4.9494 |  | 2006-09-01 | 9:16 | 33360 | 92.582 | 0.55549 | 4.8935 |  | 2029-09-01 | 9:16 | 33360 | 52.2971 | 0.31378 | 3.2417 |  | 2006-09-01 | 9:16 | 33360 | 45.8337 | 0.275 | 2.9811 |  | 2028-01-01 | 9:16 | 33360 | 93.0831 | 0.5585 | 4.9144 |  | 2007-01-01 | 9:16 | 33360 | 92.5493 | 0.5553 | 4.8943 |  | 2028-01-01 | 9:16 | 33360 | 29.8133 | 0.17888 | 2.1503 |  | 2007-01-01 | 9:16 | 33360 | 32.3577 | 0.19415 | 2.2853 |  | 2029-09-01 | 9:16 | 33360 | 64.4778 | 0.38687 | 3.7875 |  | 2029-09-01 | 9:16 | 33360 | 51.6953 | 0.31017 | 3.2324 |  | 2029-09-01 | 9:16 | 33360 | 39.1228 | 0.23474 | 2.6371 |  | 2006-09-01 | 9:16 | 33360 | 38.7502 | 0.2325 | 2.6178 |  | 2028-01-01 | 9:16 | 33360 | 57.9594 | 0.34776 | 3.51 |  | 2007-01-01 | 9:16 | 33360 | 60.2894 | 0.36174 | 3.6087 |  | 2028-01-01 | 9:16 | 33360 | 35.0596 | 0.21036 | 2.4307 |  | 2007-01-01 | 9:16 | 33360 | 36.0775 | 0.21646 | 2.4822
| 2029-09-01 | 9:17 | 33420 | 99.3058 | 0.59583 | 5.5452 |  | 2029-09-01 | 9:17 | 33420 | 99.3058 | 0.59583 | 5.5452 |  | 2006-09-01 | 9:17 | 33420 | 97.6846 | 0.58611 | 5.4796 |  | 2029-09-01 | 9:17 | 33420 | 79.1486 | 0.47489 | 4.7154 |  | 2006-09-01 | 9:17 | 33420 | 74.0236 | 0.44414 | 4.5165 |  | 2028-01-01 | 9:17 | 33420 | 98.2322 | 0.58939 | 5.5038 |  | 2007-01-01 | 9:17 | 33420 | 97.6373 | 0.58582 | 5.4801 |  | 2028-01-01 | 9:17 | 33420 | 59.7314 | 0.35839 | 3.8684 |  | 2007-01-01 | 9:17 | 33420 | 62.25 | 0.3735 | 3.9822 |  | 2029-09-01 | 9:17 | 33420 | 99.3058 | 0.59583 | 5.5452 |  | 2006-09-01 | 9:17 | 33420 | 97.6846 | 0.58611 | 5.4796 |  | 2029-09-01 | 9:17 | 33420 | 64.5653 | 0.38739 | 4.0722 |  | 2006-09-01 | 9:17 | 33420 | 57.9313 | 0.34759 | 3.8022 |  | 2028-01-01 | 9:17 | 33420 | 98.2322 | 0.58939 | 5.5038 |  | 2007-01-01 | 9:17 | 33420 | 97.6373 | 0.58582 | 5.4801 |  | 2028-01-01 | 9:17 | 33420 | 40.7382 | 0.24443 | 2.9292 |  | 2007-01-01 | 9:17 | 33420 | 43.6303 | 0.26178 | 3.0778 |  | 2029-09-01 | 9:17 | 33420 | 99.3058 | 0.59583 | 5.5452 |  | 2006-09-01 | 9:17 | 33420 | 97.6846 | 0.58611 | 5.4796 |  | 2029-09-01 | 9:17 | 33420 | 53.7638 | 0.32258 | 3.5643 |  | 2006-09-01 | 9:17 | 33420 | 46.7014 | 0.28021 | 3.2613 |  | 2028-01-01 | 9:17 | 33420 | 98.2322 | 0.58939 | 5.5038 |  | 2007-01-01 | 9:17 | 33420 | 97.6373 | 0.58582 | 5.4801 |  | 2028-01-01 | 9:17 | 33420 | 30.0735 | 0.18044 | 2.3308 |  | 2007-01-01 | 9:17 | 33420 | 32.7121 | 0.19627 | 2.4816 |  | 2029-09-01 | 9:17 | 33420 | 66.7661 | 0.4006 | 4.1881 |  | 2029-09-01 | 9:17 | 33420 | 53.0215 | 0.31813 | 3.5505 |  | 2029-09-01 | 9:17 | 33420 | 39.7371 | 0.23842 | 2.8756 |  | 2006-09-01 | 9:17 | 33420 | 39.3508 | 0.2361 | 2.854 |  | 2028-01-01 | 9:17 | 33420 | 59.7314 | 0.35839 | 3.8684 |  | 2007-01-01 | 9:17 | 33420 | 62.25 | 0.3735 | 3.9822 |  | 2028-01-01 | 9:17 | 33420 | 35.5012 | 0.21301 | 2.6437 |  | 2007-01-01 | 9:17 | 33420 | 36.5643 | 0.21939 | 2.7016
| 2029-09-01 | 9:18 | 33480 | 104.497 | 0.62698 | 6.1722 |  | 2029-09-01 | 9:18 | 33480 | 104.497 | 0.62698 | 6.1722 |  | 2006-09-01 | 9:18 | 33480 | 102.714 | 0.61628 | 6.0959 |  | 2029-09-01 | 9:18 | 33480 | 82.3941 | 0.49436 | 5.2097 |  | 2006-09-01 | 9:18 | 33480 | 76.7052 | 0.46023 | 4.9767 |  | 2028-01-01 | 9:18 | 33480 | 103.309 | 0.61985 | 6.1237 |  | 2007-01-01 | 9:18 | 33480 | 102.65 | 0.6159 | 6.096 |  | 2028-01-01 | 9:18 | 33480 | 61.3725 | 0.36824 | 4.2366 |  | 2007-01-01 | 9:18 | 33480 | 64.0779 | 0.38447 | 4.3667 |  | 2029-09-01 | 9:18 | 33480 | 104.497 | 0.62698 | 6.1722 |  | 2006-09-01 | 9:18 | 33480 | 102.714 | 0.61628 | 6.0959 |  | 2029-09-01 | 9:18 | 33480 | 66.6418 | 0.39985 | 4.4721 |  | 2006-09-01 | 9:18 | 33480 | 59.3596 | 0.35616 | 4.1583 |  | 2028-01-01 | 9:18 | 33480 | 103.309 | 0.61985 | 6.1237 |  | 2007-01-01 | 9:18 | 33480 | 102.65 | 0.6159 | 6.096 |  | 2028-01-01 | 9:18 | 33480 | 41.3157 | 0.24789 | 3.1771 |  | 2007-01-01 | 9:18 | 33480 | 44.3501 | 0.2661 | 3.3439 |  | 2029-09-01 | 9:18 | 33480 | 104.497 | 0.62698 | 6.1722 |  | 2006-09-01 | 9:18 | 33480 | 102.714 | 0.61628 | 6.0959 |  | 2029-09-01 | 9:18 | 33480 | 55.1233 | 0.33074 | 3.895 |  | 2006-09-01 | 9:18 | 33480 | 47.4559 | 0.28474 | 3.5461 |  | 2028-01-01 | 9:18 | 33480 | 103.309 | 0.61985 | 6.1237 |  | 2007-01-01 | 9:18 | 33480 | 102.65 | 0.6159 | 6.096 |  | 2028-01-01 | 9:18 | 33480 | 30.2888 | 0.18173 | 2.5125 |  | 2007-01-01 | 9:18 | 33480 | 33.0129 | 0.19808 | 2.6796 |  | 2029-09-01 | 9:18 | 33480 | 68.9164 | 0.4135 | 4.6016 |  | 2029-09-01 | 9:18 | 33480 | 54.2281 | 0.32537 | 3.8758 |  | 2029-09-01 | 9:18 | 33480 | 40.2711 | 0.24163 | 3.1172 |  | 2006-09-01 | 9:18 | 33480 | 39.8729 | 0.23924 | 3.0932 |  | 2028-01-01 | 9:18 | 33480 | 61.3725 | 0.36824 | 4.2366 |  | 2007-01-01 | 9:18 | 33480 | 64.0779 | 0.38447 | 4.3667 |  | 2028-01-01 | 9:18 | 33480 | 35.878 | 0.21527 | 2.859 |  | 2007-01-01 | 9:18 | 33480 | 36.983 | 0.2219 | 2.9235
| 2029-09-01 | 9:19 | 33540 | 109.619 | 0.65771 | 6.8299 |  | 2029-09-01 | 9:19 | 33540 | 109.619 | 0.65771 | 6.8299 |  | 2006-09-01 | 9:19 | 33540 | 107.671 | 0.64603 | 6.7419 |  | 2029-09-01 | 9:19 | 33540 | 85.5241 | 0.51314 | 5.7229 |  | 2006-09-01 | 9:19 | 33540 | 79.2479 | 0.47549 | 5.4522 |  | 2028-01-01 | 9:19 | 33540 | 108.314 | 0.64988 | 6.7735 |  | 2007-01-01 | 9:19 | 33540 | 107.589 | 0.64553 | 6.7416 |  | 2028-01-01 | 9:19 | 33540 | 62.8922 | 0.37735 | 4.614 |  | 2007-01-01 | 9:19 | 33540 | 65.7824 | 0.39469 | 4.7614 |  | 2029-09-01 | 9:19 | 33540 | 109.619 | 0.65771 | 6.8299 |  | 2006-09-01 | 9:19 | 33540 | 107.671 | 0.64603 | 6.7419 |  | 2029-09-01 | 9:19 | 33540 | 68.6039 | 0.41162 | 4.8837 |  | 2006-09-01 | 9:19 | 33540 | 60.6582 | 0.36395 | 4.5223 |  | 2028-01-01 | 9:19 | 33540 | 108.314 | 0.64988 | 6.7735 |  | 2007-01-01 | 9:19 | 33540 | 107.589 | 0.64553 | 6.7416 |  | 2028-01-01 | 9:19 | 33540 | 41.8205 | 0.25092 | 3.428 |  | 2007-01-01 | 9:19 | 33540 | 44.9889 | 0.26993 | 3.6138 |  | 2029-09-01 | 9:19 | 33540 | 109.619 | 0.65771 | 6.8299 |  | 2006-09-01 | 9:19 | 33540 | 107.671 | 0.64603 | 6.7419 |  | 2029-09-01 | 9:19 | 33540 | 56.3858 | 0.33831 | 4.2333 |  | 2006-09-01 | 9:19 | 33540 | 48.109 | 0.28865 | 3.8347 |  | 2028-01-01 | 9:19 | 33540 | 108.314 | 0.64988 | 6.7735 |  | 2007-01-01 | 9:19 | 33540 | 107.589 | 0.64553 | 6.7416 |  | 2028-01-01 | 9:19 | 33540 | 30.4669 | 0.1828 | 2.6953 |  | 2007-01-01 | 9:19 | 33540 | 33.2687 | 0.19961 | 2.8793 |  | 2029-09-01 | 9:19 | 33540 | 70.9369 | 0.42562 | 5.0272 |  | 2029-09-01 | 9:19 | 33540 | 55.326 | 0.33196 | 4.2078 |  | 2029-09-01 | 9:19 | 33540 | 40.7352 | 0.24441 | 3.3616 |  | 2006-09-01 | 9:19 | 33540 | 40.3267 | 0.24196 | 3.3351 |  | 2028-01-01 | 9:19 | 33540 | 62.8922 | 0.37735 | 4.614 |  | 2007-01-01 | 9:19 | 33540 | 65.7824 | 0.39469 | 4.7614 |  | 2028-01-01 | 9:19 | 33540 | 36.1996 | 0.2172 | 3.0762 |  | 2007-01-01 | 9:19 | 33540 | 37.3431 | 0.22406 | 3.1475
| 2029-09-01 | 9:20 | 33600 | 114.675 | 0.68805 | 7.518 |  | 2029-09-01 | 9:20 | 33600 | 114.675 | 0.68805 | 7.518 |  | 2006-09-01 | 9:20 | 33600 | 112.557 | 0.67534 | 7.4172 |  | 2029-09-01 | 9:20 | 33600 | 88.5437 | 0.53126 | 6.2542 |  | 2006-09-01 | 9:20 | 33600 | 81.6576 | 0.48995 | 5.9421 |  | 2028-01-01 | 9:20 | 33600 | 113.249 | 0.67949 | 7.453 |  | 2007-01-01 | 9:20 | 33600 | 112.454 | 0.67472 | 7.4163 |  | 2028-01-01 | 9:20 | 33600 | 64.2996 | 0.3858 | 4.9998 |  | 2007-01-01 | 9:20 | 33600 | 67.372 | 0.40423 | 5.1656 |  | 2029-09-01 | 9:20 | 33600 | 114.675 | 0.68805 | 7.518 |  | 2006-09-01 | 9:20 | 33600 | 112.557 | 0.67534 | 7.4172 |  | 2029-09-01 | 9:20 | 33600 | 70.4597 | 0.42276 | 5.3064 |  | 2006-09-01 | 9:20 | 33600 | 61.8366 | 0.37102 | 4.8933 |  | 2028-01-01 | 9:20 | 33600 | 113.249 | 0.67949 | 7.453 |  | 2007-01-01 | 9:20 | 33600 | 112.454 | 0.67472 | 7.4163 |  | 2028-01-01 | 9:20 | 33600 | 42.2616 | 0.25357 | 3.6816 |  | 2007-01-01 | 9:20 | 33600 | 45.5562 | 0.27334 | 3.8872 |  | 2029-09-01 | 9:20 | 33600 | 114.675 | 0.68805 | 7.518 |  | 2006-09-01 | 9:20 | 33600 | 112.557 | 0.67534 | 7.4172 |  | 2029-09-01 | 9:20 | 33600 | 57.5606 | 0.34536 | 4.5787 |  | 2006-09-01 | 9:20 | 33600 | 48.6713 | 0.29203 | 4.1268 |  | 2028-01-01 | 9:20 | 33600 | 113.249 | 0.67949 | 7.453 |  | 2007-01-01 | 9:20 | 33600 | 112.454 | 0.67472 | 7.4163 |  | 2028-01-01 | 9:20 | 33600 | 30.6142 | 0.18369 | 2.879 |  | 2007-01-01 | 9:20 | 33600 | 33.4867 | 0.20092 | 3.0802 |  | 2029-09-01 | 9:20 | 33600 | 72.8353 | 0.43701 | 5.4642 |  | 2029-09-01 | 9:20 | 33600 | 56.3246 | 0.33795 | 4.5458 |  | 2029-09-01 | 9:20 | 33600 | 41.1385 | 0.24683 | 3.6084 |  | 2006-09-01 | 9:20 | 33600 | 40.7213 | 0.24433 | 3.5795 |  | 2028-01-01 | 9:20 | 33600 | 64.2996 | 0.3858 | 4.9998 |  | 2007-01-01 | 9:20 | 33600 | 67.372 | 0.40423 | 5.1656 |  | 2028-01-01 | 9:20 | 33600 | 36.4741 | 0.21884 | 3.295 |  | 2007-01-01 | 9:20 | 33600 | 37.653 | 0.22592 | 3.3734
| 2029-09-01 | 9:21 | 33660 | 119.664 | 0.71798 | 8.236 |  | 2029-09-01 | 9:21 | 33660 | 119.664 | 0.71798 | 8.236 |  | 2006-09-01 | 9:21 | 33660 | 117.373 | 0.70424 | 8.1215 |  | 2029-09-01 | 9:21 | 33660 | 91.4579 | 0.54875 | 6.8029 |  | 2006-09-01 | 9:21 | 33660 | 83.9404 | 0.50364 | 6.4458 |  | 2028-01-01 | 9:21 | 33660 | 118.115 | 0.70869 | 8.1617 |  | 2007-01-01 | 9:21 | 33660 | 117.248 | 0.70349 | 8.1198 |  | 2028-01-01 | 9:21 | 33660 | 65.603 | 0.39362 | 5.3934 |  | 2007-01-01 | 9:21 | 33660 | 68.8547 | 0.41313 | 5.5788 |  | 2029-09-01 | 9:21 | 33660 | 119.664 | 0.71798 | 8.236 |  | 2006-09-01 | 9:21 | 33660 | 117.373 | 0.70424 | 8.1215 |  | 2029-09-01 | 9:21 | 33660 | 72.2168 | 0.4333 | 5.7397 |  | 2006-09-01 | 9:21 | 33660 | 62.9041 | 0.37742 | 5.2707 |  | 2028-01-01 | 9:21 | 33660 | 118.115 | 0.70869 | 8.1617 |  | 2007-01-01 | 9:21 | 33660 | 117.248 | 0.70349 | 8.1198 |  | 2028-01-01 | 9:21 | 33660 | 42.6472 | 0.25588 | 3.9375 |  | 2007-01-01 | 9:21 | 33660 | 46.0605 | 0.27636 | 4.1635 |  | 2029-09-01 | 9:21 | 33660 | 119.664 | 0.71798 | 8.236 |  | 2006-09-01 | 9:21 | 33660 | 117.373 | 0.70424 | 8.1215 |  | 2029-09-01 | 9:21 | 33660 | 58.6559 | 0.35194 | 4.9306 |  | 2006-09-01 | 9:21 | 33660 | 49.1526 | 0.29492 | 4.4217 |  | 2028-01-01 | 9:21 | 33660 | 118.115 | 0.70869 | 8.1617 |  | 2007-01-01 | 9:21 | 33660 | 117.248 | 0.70349 | 8.1198 |  | 2028-01-01 | 9:21 | 33660 | 30.7362 | 0.18442 | 3.0634 |  | 2007-01-01 | 9:21 | 33660 | 33.6729 | 0.20204 | 3.2822 |  | 2029-09-01 | 9:21 | 33660 | 74.6189 | 0.44771 | 5.9119 |  | 2029-09-01 | 9:21 | 33660 | 57.233 | 0.3434 | 4.8892 |  | 2029-09-01 | 9:21 | 33660 | 41.4888 | 0.24893 | 3.8574 |  | 2006-09-01 | 9:21 | 33660 | 41.0644 | 0.24639 | 3.8259 |  | 2028-01-01 | 9:21 | 33660 | 65.603 | 0.39362 | 5.3934 |  | 2007-01-01 | 9:21 | 33660 | 68.8547 | 0.41313 | 5.5788 |  | 2028-01-01 | 9:21 | 33660 | 36.7084 | 0.22025 | 3.5153 |  | 2007-01-01 | 9:21 | 33660 | 37.9199 | 0.22752 | 3.601
| 2029-09-01 | 9:22 | 33720 | 124.588 | 0.74753 | 8.9835 |  | 2029-09-01 | 9:22 | 33720 | 124.588 | 0.74753 | 8.9835 |  | 2006-09-01 | 9:22 | 33720 | 122.12 | 0.73272 | 8.8542 |  | 2029-09-01 | 9:22 | 33720 | 94.2712 | 0.56563 | 7.3685 |  | 2006-09-01 | 9:22 | 33720 | 86.1017 | 0.51661 | 6.9624 |  | 2028-01-01 | 9:22 | 33720 | 122.911 | 0.73747 | 8.8992 |  | 2007-01-01 | 9:22 | 33720 | 121.97 | 0.73182 | 8.8516 |  | 2028-01-01 | 9:22 | 33720 | 66.8102 | 0.40086 | 5.7942 |  | 2007-01-01 | 9:22 | 33720 | 70.2378 | 0.42143 | 6.0002 |  | 2029-09-01 | 9:22 | 33720 | 124.588 | 0.74753 | 8.9835 |  | 2006-09-01 | 9:22 | 33720 | 122.12 | 0.73272 | 8.8542 |  | 2029-09-01 | 9:22 | 33720 | 73.8821 | 0.44329 | 6.183 |  | 2006-09-01 | 9:22 | 33720 | 63.869 | 0.38321 | 5.6539 |  | 2028-01-01 | 9:22 | 33720 | 122.911 | 0.73747 | 8.8992 |  | 2007-01-01 | 9:22 | 33720 | 121.97 | 0.73182 | 8.8516 |  | 2028-01-01 | 9:22 | 33720 | 42.9841 | 0.2579 | 4.1954 |  | 2007-01-01 | 9:22 | 33720 | 46.509 | 0.27905 | 4.4426 |  | 2029-09-01 | 9:22 | 33720 | 124.588 | 0.74753 | 8.9835 |  | 2006-09-01 | 9:22 | 33720 | 122.12 | 0.73272 | 8.8542 |  | 2029-09-01 | 9:22 | 33720 | 59.6794 | 0.35808 | 5.2887 |  | 2006-09-01 | 9:22 | 33720 | 49.5613 | 0.29737 | 4.719 |  | 2028-01-01 | 9:22 | 33720 | 122.911 | 0.73747 | 8.8992 |  | 2007-01-01 | 9:22 | 33720 | 121.97 | 0.73182 | 8.8516 |  | 2028-01-01 | 9:22 | 33720 | 30.8371 | 0.18502 | 3.2484 |  | 2007-01-01 | 9:22 | 33720 | 33.8324 | 0.20299 | 3.4852 |  | 2029-09-01 | 9:22 | 33720 | 76.2943 | 0.45777 | 6.3697 |  | 2029-09-01 | 9:22 | 33720 | 58.0592 | 0.34836 | 5.2375 |  | 2029-09-01 | 9:22 | 33720 | 41.793 | 0.25076 | 4.1081 |  | 2006-09-01 | 9:22 | 33720 | 41.3627 | 0.24818 | 4.074 |  | 2028-01-01 | 9:22 | 33720 | 66.8102 | 0.40086 | 5.7942 |  | 2007-01-01 | 9:22 | 33720 | 70.2378 | 0.42143 | 6.0002 |  | 2028-01-01 | 9:22 | 33720 | 36.9084 | 0.22145 | 3.7367 |  | 2007-01-01 | 9:22 | 33720 | 38.1499 | 0.2289 | 3.8299
| 2029-09-01 | 9:23 | 33780 | 129.446 | 0.77668 | 9.7602 |  | 2029-09-01 | 9:23 | 33780 | 129.446 | 0.77668 | 9.7602 |  | 2006-09-01 | 9:23 | 33780 | 126.8 | 0.7608 | 9.615 |  | 2029-09-01 | 9:23 | 33780 | 96.9881 | 0.58193 | 7.9505 |  | 2006-09-01 | 9:23 | 33780 | 88.147 | 0.52888 | 7.4913 |  | 2028-01-01 | 9:23 | 33780 | 127.641 | 0.76585 | 9.665 |  | 2007-01-01 | 9:23 | 33780 | 126.622 | 0.75973 | 9.6113 |  | 2028-01-01 | 9:23 | 33780 | 67.9281 | 0.40757 | 6.2018 |  | 2007-01-01 | 9:23 | 33780 | 71.5283 | 0.42917 | 6.4294 |  | 2029-09-01 | 9:23 | 33780 | 129.446 | 0.77668 | 9.7602 |  | 2006-09-01 | 9:23 | 33780 | 126.8 | 0.7608 | 9.615 |  | 2029-09-01 | 9:23 | 33780 | 75.4622 | 0.45277 | 6.6358 |  | 2006-09-01 | 9:23 | 33780 | 64.7391 | 0.38843 | 6.0424 |  | 2028-01-01 | 9:23 | 33780 | 127.641 | 0.76585 | 9.665 |  | 2007-01-01 | 9:23 | 33780 | 126.622 | 0.75973 | 9.6113 |  | 2028-01-01 | 9:23 | 33780 | 43.2787 | 0.25967 | 4.455 |  | 2007-01-01 | 9:23 | 33780 | 46.9082 | 0.28145 | 4.724 |  | 2029-09-01 | 9:23 | 33780 | 129.446 | 0.77668 | 9.7602 |  | 2006-09-01 | 9:23 | 33780 | 126.8 | 0.7608 | 9.615 |  | 2029-09-01 | 9:23 | 33780 | 60.6378 | 0.36383 | 5.6525 |  | 2006-09-01 | 9:23 | 33780 | 49.9053 | 0.29943 | 5.0185 |  | 2028-01-01 | 9:23 | 33780 | 127.641 | 0.76585 | 9.665 |  | 2007-01-01 | 9:23 | 33780 | 126.622 | 0.75973 | 9.6113 |  | 2028-01-01 | 9:23 | 33780 | 30.9207 | 0.18552 | 3.4339 |  | 2007-01-01 | 9:23 | 33780 | 33.9695 | 0.20382 | 3.689 |  | 2029-09-01 | 9:23 | 33780 | 77.8681 | 0.46721 | 6.8369 |  | 2029-09-01 | 9:23 | 33780 | 58.8104 | 0.35286 | 5.5904 |  | 2029-09-01 | 9:23 | 33780 | 42.0571 | 0.25234 | 4.3605 |  | 2006-09-01 | 9:23 | 33780 | 41.6221 | 0.24973 | 4.3238 |  | 2028-01-01 | 9:23 | 33780 | 67.9281 | 0.40757 | 6.2018 |  | 2007-01-01 | 9:23 | 33780 | 71.5283 | 0.42917 | 6.4294 |  | 2028-01-01 | 9:23 | 33780 | 37.0791 | 0.22247 | 3.9592 |  | 2007-01-01 | 9:23 | 33780 | 38.3482 | 0.23009 | 4.0599
| 2029-09-01 | 9:24 | 33840 | 134.24 | 0.80544 | 10.5656 |  | 2029-09-01 | 9:24 | 33840 | 134.24 | 0.80544 | 10.5656 |  | 2006-09-01 | 9:24 | 33840 | 131.412 | 0.78847 | 10.4035 |  | 2029-09-01 | 9:24 | 33840 | 99.613 | 0.59768 | 8.5481 |  | 2006-09-01 | 9:24 | 33840 | 90.0814 | 0.54049 | 8.0318 |  | 2028-01-01 | 9:24 | 33840 | 132.304 | 0.79382 | 10.4589 |  | 2007-01-01 | 9:24 | 33840 | 131.206 | 0.78724 | 10.3986 |  | 2028-01-01 | 9:24 | 33840 | 68.9635 | 0.41378 | 6.6156 |  | 2007-01-01 | 9:24 | 33840 | 72.7326 | 0.4364 | 6.8658 |  | 2029-09-01 | 9:24 | 33840 | 134.24 | 0.80544 | 10.5656 |  | 2006-09-01 | 9:24 | 33840 | 131.412 | 0.78847 | 10.4035 |  | 2029-09-01 | 9:24 | 33840 | 76.9631 | 0.46178 | 7.0976 |  | 2006-09-01 | 9:24 | 33840 | 65.5217 | 0.39313 | 6.4355 |  | 2028-01-01 | 9:24 | 33840 | 132.304 | 0.79382 | 10.4589 |  | 2007-01-01 | 9:24 | 33840 | 131.206 | 0.78724 | 10.3986 |  | 2028-01-01 | 9:24 | 33840 | 43.5361 | 0.26122 | 4.7163 |  | 2007-01-01 | 9:24 | 33840 | 47.2639 | 0.28358 | 5.0076 |  | 2029-09-01 | 9:24 | 33840 | 134.24 | 0.80544 | 10.5656 |  | 2006-09-01 | 9:24 | 33840 | 131.412 | 0.78847 | 10.4035 |  | 2029-09-01 | 9:24 | 33840 | 61.5376 | 0.36923 | 6.0217 |  | 2006-09-01 | 9:24 | 33840 | 50.1915 | 0.30115 | 5.3196 |  | 2028-01-01 | 9:24 | 33840 | 132.304 | 0.79382 | 10.4589 |  | 2007-01-01 | 9:24 | 33840 | 131.206 | 0.78724 | 10.3986 |  | 2028-01-01 | 9:24 | 33840 | 30.9898 | 0.18594 | 3.6199 |  | 2007-01-01 | 9:24 | 33840 | 34.0877 | 0.20453 | 3.8936 |  | 2029-09-01 | 9:24 | 33840 | 79.3463 | 0.47608 | 7.313 |  | 2029-09-01 | 9:24 | 33840 | 59.4933 | 0.35696 | 5.9473 |  | 2029-09-01 | 9:24 | 33840 | 42.2862 | 0.25372 | 4.6142 |  | 2006-09-01 | 9:24 | 33840 | 41.8477 | 0.25109 | 4.5749 |  | 2028-01-01 | 9:24 | 33840 | 68.9635 | 0.41378 | 6.6156 |  | 2007-01-01 | 9:24 | 33840 | 72.7326 | 0.4364 | 6.8658 |  | 2028-01-01 | 9:24 | 33840 | 37.2248 | 0.22335 | 4.1826 |  | 2007-01-01 | 9:24 | 33840 | 38.5193 | 0.23112 | 4.2911
| 2029-09-01 | 9:25 | 33900 | 138.969 | 0.83381 | 11.3994 |  | 2029-09-01 | 9:25 | 33900 | 138.969 | 0.83381 | 11.3994 |  | 2006-09-01 | 9:25 | 33900 | 135.959 | 0.81575 | 11.2192 |  | 2029-09-01 | 9:25 | 33900 | 102.15 | 0.6129 | 9.161 |  | 2006-09-01 | 9:25 | 33900 | 91.91 | 0.55146 | 8.5832 |  | 2028-01-01 | 9:25 | 33900 | 136.901 | 0.82141 | 11.2803 |  | 2007-01-01 | 9:25 | 33900 | 135.721 | 0.81433 | 11.2129 |  | 2028-01-01 | 9:25 | 33900 | 69.9224 | 0.41953 | 7.0351 |  | 2007-01-01 | 9:25 | 33900 | 73.8565 | 0.44314 | 7.3089 |  | 2029-09-01 | 9:25 | 33900 | 138.969 | 0.83381 | 11.3994 |  | 2006-09-01 | 9:25 | 33900 | 135.959 | 0.81575 | 11.2192 |  | 2029-09-01 | 9:25 | 33900 | 78.3905 | 0.47034 | 7.5679 |  | 2006-09-01 | 9:25 | 33900 | 66.2236 | 0.39734 | 6.8328 |  | 2028-01-01 | 9:25 | 33900 | 136.901 | 0.82141 | 11.2803 |  | 2007-01-01 | 9:25 | 33900 | 135.721 | 0.81433 | 11.2129 |  | 2028-01-01 | 9:25 | 33900 | 43.7612 | 0.26257 | 4.9788 |  | 2007-01-01 | 9:25 | 33900 | 47.5813 | 0.28549 | 5.2931 |  | 2029-09-01 | 9:25 | 33900 | 138.969 | 0.83381 | 11.3994 |  | 2006-09-01 | 9:25 | 33900 | 135.959 | 0.81575 | 11.2192 |  | 2029-09-01 | 9:25 | 33900 | 62.3843 | 0.37431 | 6.3961 |  | 2006-09-01 | 9:25 | 33900 | 50.4262 | 0.30256 | 5.6222 |  | 2028-01-01 | 9:25 | 33900 | 136.901 | 0.82141 | 11.2803 |  | 2007-01-01 | 9:25 | 33900 | 135.721 | 0.81433 | 11.2129 |  | 2028-01-01 | 9:25 | 33900 | 31.0471 | 0.18628 | 3.8062 |  | 2007-01-01 | 9:25 | 33900 | 34.1901 | 0.20514 | 4.0987 |  | 2029-09-01 | 9:25 | 33900 | 80.7344 | 0.48441 | 7.7974 |  | 2029-09-01 | 9:25 | 33900 | 60.1141 | 0.36068 | 6.308 |  | 2029-09-01 | 9:25 | 33900 | 42.4849 | 0.25491 | 4.8691 |  | 2006-09-01 | 9:25 | 33900 | 42.044 | 0.25226 | 4.8271 |  | 2028-01-01 | 9:25 | 33900 | 69.9224 | 0.41953 | 7.0351 |  | 2007-01-01 | 9:25 | 33900 | 73.8565 | 0.44314 | 7.3089 |  | 2028-01-01 | 9:25 | 33900 | 37.3493 | 0.2241 | 4.4067 |  | 2007-01-01 | 9:25 | 33900 | 38.6671 | 0.232 | 4.5231
| 2029-09-01 | 9:26 | 33960 | 143.636 | 0.86182 | 12.2612 |  | 2029-09-01 | 9:26 | 33960 | 143.636 | 0.86182 | 12.2612 |  | 2006-09-01 | 9:26 | 33960 | 140.441 | 0.84265 | 12.0619 |  | 2029-09-01 | 9:26 | 33960 | 104.603 | 0.62762 | 9.7887 |  | 2006-09-01 | 9:26 | 33960 | 93.6374 | 0.56182 | 9.1451 |  | 2028-01-01 | 9:26 | 33960 | 141.433 | 0.8486 | 12.1289 |  | 2007-01-01 | 9:26 | 33960 | 140.169 | 0.84101 | 12.0539 |  | 2028-01-01 | 9:26 | 33960 | 70.8105 | 0.42486 | 7.46 |  | 2007-01-01 | 9:26 | 33960 | 74.9058 | 0.44943 | 7.7583 |  | 2029-09-01 | 9:26 | 33960 | 143.636 | 0.86182 | 12.2612 |  | 2006-09-01 | 9:26 | 33960 | 140.441 | 0.84265 | 12.0619 |  | 2029-09-01 | 9:26 | 33960 | 79.7495 | 0.4785 | 8.0464 |  | 2006-09-01 | 9:26 | 33960 | 66.851 | 0.40111 | 7.2339 |  | 2028-01-01 | 9:26 | 33960 | 141.433 | 0.8486 | 12.1289 |  | 2007-01-01 | 9:26 | 33960 | 140.169 | 0.84101 | 12.0539 |  | 2028-01-01 | 9:26 | 33960 | 43.9579 | 0.26375 | 5.2426 |  | 2007-01-01 | 9:26 | 33960 | 47.8646 | 0.28719 | 5.5803 |  | 2029-09-01 | 9:26 | 33960 | 143.636 | 0.86182 | 12.2612 |  | 2006-09-01 | 9:26 | 33960 | 140.441 | 0.84265 | 12.0619 |  | 2029-09-01 | 9:26 | 33960 | 63.183 | 0.3791 | 6.7751 |  | 2006-09-01 | 9:26 | 33960 | 50.6151 | 0.30369 | 5.9259 |  | 2028-01-01 | 9:26 | 33960 | 141.433 | 0.8486 | 12.1289 |  | 2007-01-01 | 9:26 | 33960 | 140.169 | 0.84101 | 12.0539 |  | 2028-01-01 | 9:26 | 33960 | 31.0945 | 0.18657 | 3.9927 |  | 2007-01-01 | 9:26 | 33960 | 34.2792 | 0.20568 | 4.3044 |  | 2029-09-01 | 9:26 | 33960 | 82.0379 | 0.49223 | 8.2896 |  | 2029-09-01 | 9:26 | 33960 | 60.6782 | 0.36407 | 6.6721 |  | 2029-09-01 | 9:26 | 33960 | 42.6572 | 0.25594 | 5.125 |  | 2006-09-01 | 9:26 | 33960 | 42.2148 | 0.25329 | 5.0804 |  | 2028-01-01 | 9:26 | 33960 | 70.8105 | 0.42486 | 7.46 |  | 2007-01-01 | 9:26 | 33960 | 74.9058 | 0.44943 | 7.7583 |  | 2028-01-01 | 9:26 | 33960 | 37.4555 | 0.22473 | 4.6314 |  | 2007-01-01 | 9:26 | 33960 | 38.7949 | 0.23277 | 4.7558
| 2029-09-01 | 9:27 | 34020 | 148.239 | 0.88943 | 13.1507 |  | 2029-09-01 | 9:27 | 34020 | 148.239 | 0.88943 | 13.1507 |  | 2006-09-01 | 9:27 | 34020 | 144.859 | 0.86915 | 12.931 |  | 2029-09-01 | 9:27 | 34020 | 106.975 | 0.64185 | 10.4305 |  | 2006-09-01 | 9:27 | 34020 | 95.2684 | 0.57161 | 9.7167 |  | 2028-01-01 | 9:27 | 34020 | 145.901 | 0.87541 | 13.0043 |  | 2007-01-01 | 9:27 | 34020 | 144.551 | 0.86731 | 12.9212 |  | 2028-01-01 | 9:27 | 34020 | 71.633 | 0.4298 | 7.8898 |  | 2007-01-01 | 9:27 | 34020 | 75.8854 | 0.45531 | 8.2136 |  | 2029-09-01 | 9:27 | 34020 | 148.239 | 0.88943 | 13.1507 |  | 2006-09-01 | 9:27 | 34020 | 144.859 | 0.86915 | 12.931 |  | 2029-09-01 | 9:27 | 34020 | 81.0451 | 0.48627 | 8.5327 |  | 2006-09-01 | 9:27 | 34020 | 67.4098 | 0.40446 | 7.6384 |  | 2028-01-01 | 9:27 | 34020 | 145.901 | 0.87541 | 13.0043 |  | 2007-01-01 | 9:27 | 34020 | 144.551 | 0.86731 | 12.9212 |  | 2028-01-01 | 9:27 | 34020 | 44.1298 | 0.26478 | 5.5074 |  | 2007-01-01 | 9:27 | 34020 | 48.118 | 0.28871 | 5.869 |  | 2029-09-01 | 9:27 | 34020 | 148.239 | 0.88943 | 13.1507 |  | 2006-09-01 | 9:27 | 34020 | 144.859 | 0.86915 | 12.931 |  | 2029-09-01 | 9:27 | 34020 | 63.9384 | 0.38363 | 7.1588 |  | 2006-09-01 | 9:27 | 34020 | 50.7633 | 0.30458 | 6.2304 |  | 2028-01-01 | 9:27 | 34020 | 145.901 | 0.87541 | 13.0043 |  | 2007-01-01 | 9:27 | 34020 | 144.551 | 0.86731 | 12.9212 |  | 2028-01-01 | 9:27 | 34020 | 31.1338 | 0.1868 | 4.1795 |  | 2007-01-01 | 9:27 | 34020 | 34.357 | 0.20614 | 4.5105 |  | 2029-09-01 | 9:27 | 34020 | 83.2618 | 0.49957 | 8.7892 |  | 2029-09-01 | 9:27 | 34020 | 61.1907 | 0.36714 | 7.0392 |  | 2029-09-01 | 9:27 | 34020 | 42.8063 | 0.25684 | 5.3819 |  | 2006-09-01 | 9:27 | 34020 | 42.3634 | 0.25418 | 5.3346 |  | 2028-01-01 | 9:27 | 34020 | 71.633 | 0.4298 | 7.8898 |  | 2007-01-01 | 9:27 | 34020 | 75.8854 | 0.45531 | 8.2136 |  | 2028-01-01 | 9:27 | 34020 | 37.5462 | 0.22528 | 4.8567 |  | 2007-01-01 | 9:27 | 34020 | 38.9056 | 0.23343 | 4.9893
| 2029-09-01 | 9:28 | 34080 | 152.781 | 0.91669 | 14.0674 |  | 2029-09-01 | 9:28 | 34080 | 152.781 | 0.91669 | 14.0674 |  | 2006-09-01 | 9:28 | 34080 | 149.215 | 0.89529 | 13.8263 |  | 2029-09-01 | 9:28 | 34080 | 109.271 | 0.65563 | 11.0861 |  | 2006-09-01 | 9:28 | 34080 | 96.8072 | 0.58084 | 10.2975 |  | 2028-01-01 | 9:28 | 34080 | 150.306 | 0.90184 | 13.9061 |  | 2007-01-01 | 9:28 | 34080 | 148.867 | 0.8932 | 13.8144 |  | 2028-01-01 | 9:28 | 34080 | 72.3949 | 0.43437 | 8.3242 |  | 2007-01-01 | 9:28 | 34080 | 76.8003 | 0.4608 | 8.6744 |  | 2029-09-01 | 9:28 | 34080 | 152.781 | 0.91669 | 14.0674 |  | 2006-09-01 | 9:28 | 34080 | 149.215 | 0.89529 | 13.8263 |  | 2029-09-01 | 9:28 | 34080 | 82.2818 | 0.49369 | 9.0264 |  | 2006-09-01 | 9:28 | 34080 | 67.9053 | 0.40743 | 8.0458 |  | 2028-01-01 | 9:28 | 34080 | 150.306 | 0.90184 | 13.9061 |  | 2007-01-01 | 9:28 | 34080 | 148.867 | 0.8932 | 13.8144 |  | 2028-01-01 | 9:28 | 34080 | 44.2802 | 0.26568 | 5.773 |  | 2007-01-01 | 9:28 | 34080 | 48.3449 | 0.29007 | 6.1591 |  | 2029-09-01 | 9:28 | 34080 | 152.781 | 0.91669 | 14.0674 |  | 2006-09-01 | 9:28 | 34080 | 149.215 | 0.89529 | 13.8263 |  | 2029-09-01 | 9:28 | 34080 | 64.6547 | 0.38793 | 7.5467 |  | 2006-09-01 | 9:28 | 34080 | 50.8752 | 0.30525 | 6.5357 |  | 2028-01-01 | 9:28 | 34080 | 150.306 | 0.90184 | 13.9061 |  | 2007-01-01 | 9:28 | 34080 | 148.867 | 0.8932 | 13.8144 |  | 2028-01-01 | 9:28 | 34080 | 31.1663 | 0.187 | 4.3665 |  | 2007-01-01 | 9:28 | 34080 | 34.4255 | 0.20655 | 4.7171 |  | 2029-09-01 | 9:28 | 34080 | 84.4107 | 0.50646 | 9.2956 |  | 2029-09-01 | 9:28 | 34080 | 61.6562 | 0.36994 | 7.4092 |  | 2029-09-01 | 9:28 | 34080 | 42.9354 | 0.25761 | 5.6395 |  | 2006-09-01 | 9:28 | 34080 | 42.4928 | 0.25496 | 5.5895 |  | 2028-01-01 | 9:28 | 34080 | 72.3949 | 0.43437 | 8.3242 |  | 2007-01-01 | 9:28 | 34080 | 76.8003 | 0.4608 | 8.6744 |  | 2028-01-01 | 9:28 | 34080 | 37.6237 | 0.22574 | 5.0824 |  | 2007-01-01 | 9:28 | 34080 | 39.0016 | 0.23401 | 5.2233
| 2029-09-01 | 9:29 | 34140 | 157.261 | 0.94357 | 15.0109 |  | 2029-09-01 | 9:29 | 34140 | 157.261 | 0.94357 | 15.0109 |  | 2006-09-01 | 9:29 | 34140 | 153.508 | 0.92105 | 14.7474 |  | 2029-09-01 | 9:29 | 34140 | 111.493 | 0.66896 | 11.7551 |  | 2006-09-01 | 9:29 | 34140 | 98.2582 | 0.58955 | 10.8871 |  | 2028-01-01 | 9:29 | 34140 | 154.649 | 0.92789 | 14.834 |  | 2007-01-01 | 9:29 | 34140 | 153.119 | 0.91871 | 14.7331 |  | 2028-01-01 | 9:29 | 34140 | 73.1005 | 0.4386 | 8.7628 |  | 2007-01-01 | 9:29 | 34140 | 77.6549 | 0.46593 | 9.1404 |  | 2029-09-01 | 9:29 | 34140 | 157.261 | 0.94357 | 15.0109 |  | 2006-09-01 | 9:29 | 34140 | 153.508 | 0.92105 | 14.7474 |  | 2029-09-01 | 9:29 | 34140 | 83.4638 | 0.50078 | 9.5272 |  | 2006-09-01 | 9:29 | 34140 | 68.3426 | 0.41006 | 8.4559 |  | 2028-01-01 | 9:29 | 34140 | 154.649 | 0.92789 | 14.834 |  | 2007-01-01 | 9:29 | 34140 | 153.119 | 0.91871 | 14.7331 |  | 2028-01-01 | 9:29 | 34140 | 44.4117 | 0.26647 | 6.0395 |  | 2007-01-01 | 9:29 | 34140 | 48.5484 | 0.29129 | 6.4504 |  | 2029-09-01 | 9:29 | 34140 | 157.261 | 0.94357 | 15.0109 |  | 2006-09-01 | 9:29 | 34140 | 153.508 | 0.92105 | 14.7474 |  | 2029-09-01 | 9:29 | 34140 | 65.3357 | 0.39201 | 7.9387 |  | 2006-09-01 | 9:29 | 34140 | 50.9549 | 0.30573 | 6.8414 |  | 2028-01-01 | 9:29 | 34140 | 154.649 | 0.92789 | 14.834 |  | 2007-01-01 | 9:29 | 34140 | 153.119 | 0.91871 | 14.7331 |  | 2028-01-01 | 9:29 | 34140 | 31.1933 | 0.18716 | 4.5537 |  | 2007-01-01 | 9:29 | 34140 | 34.4861 | 0.20692 | 4.924 |  | 2029-09-01 | 9:29 | 34140 | 85.4891 | 0.51293 | 9.8086 |  | 2029-09-01 | 9:29 | 34140 | 62.0789 | 0.37247 | 7.7816 |  | 2029-09-01 | 9:29 | 34140 | 43.047 | 0.25828 | 5.8978 |  | 2006-09-01 | 9:29 | 34140 | 42.6054 | 0.25563 | 5.8452 |  | 2028-01-01 | 9:29 | 34140 | 73.1005 | 0.4386 | 8.7628 |  | 2007-01-01 | 9:29 | 34140 | 77.6549 | 0.46593 | 9.1404 |  | 2028-01-01 | 9:29 | 34140 | 37.6898 | 0.22614 | 5.3085 |  | 2007-01-01 | 9:29 | 34140 | 39.085 | 0.23451 | 5.4578
| 2029-09-01 | 9:30 | 34200 | 161.68 | 0.97008 | 15.981 |  | 2029-09-01 | 9:30 | 34200 | 161.68 | 0.97008 | 15.981 |  | 2006-09-01 | 9:30 | 34200 | 157.741 | 0.94645 | 15.6938 |  | 2029-09-01 | 9:30 | 34200 | 113.644 | 0.68186 | 12.437 |  | 2006-09-01 | 9:30 | 34200 | 99.6253 | 0.59775 | 11.4848 |  | 2028-01-01 | 9:30 | 34200 | 158.93 | 0.95358 | 15.7876 |  | 2007-01-01 | 9:30 | 34200 | 157.308 | 0.94385 | 15.677 |  | 2028-01-01 | 9:30 | 34200 | 73.754 | 0.44252 | 9.2053 |  | 2007-01-01 | 9:30 | 34200 | 78.4534 | 0.47072 | 9.6111 |  | 2029-09-01 | 9:30 | 34200 | 161.68 | 0.97008 | 15.981 |  | 2006-09-01 | 9:30 | 34200 | 157.741 | 0.94645 | 15.6938 |  | 2029-09-01 | 9:30 | 34200 | 84.595 | 0.50757 | 10.0347 |  | 2006-09-01 | 9:30 | 34200 | 68.7262 | 0.41236 | 8.8682 |  | 2028-01-01 | 9:30 | 34200 | 158.93 | 0.95358 | 15.7876 |  | 2007-01-01 | 9:30 | 34200 | 157.308 | 0.94385 | 15.677 |  | 2028-01-01 | 9:30 | 34200 | 44.5266 | 0.26716 | 6.3067 |  | 2007-01-01 | 9:30 | 34200 | 48.7313 | 0.29239 | 6.7428 |  | 2029-09-01 | 9:30 | 34200 | 161.68 | 0.97008 | 15.981 |  | 2006-09-01 | 9:30 | 34200 | 157.741 | 0.94645 | 15.6938 |  | 2029-09-01 | 9:30 | 34200 | 65.985 | 0.39591 | 8.3346 |  | 2006-09-01 | 9:30 | 34200 | 51.0062 | 0.30604 | 7.1475 |  | 2028-01-01 | 9:30 | 34200 | 158.93 | 0.95358 | 15.7876 |  | 2007-01-01 | 9:30 | 34200 | 157.308 | 0.94385 | 15.677 |  | 2028-01-01 | 9:30 | 34200 | 31.2157 | 0.18729 | 4.741 |  | 2007-01-01 | 9:30 | 34200 | 34.54 | 0.20724 | 5.1312 |  | 2029-09-01 | 9:30 | 34200 | 86.5012 | 0.51901 | 10.3276 |  | 2029-09-01 | 9:30 | 34200 | 62.4626 | 0.37478 | 8.1564 |  | 2029-09-01 | 9:30 | 34200 | 43.1433 | 0.25886 | 6.1566 |  | 2006-09-01 | 9:30 | 34200 | 42.7036 | 0.25622 | 6.1014 |  | 2028-01-01 | 9:30 | 34200 | 73.754 | 0.44252 | 9.2053 |  | 2007-01-01 | 9:30 | 34200 | 78.4534 | 0.47072 | 9.6111 |  | 2028-01-01 | 9:30 | 34200 | 37.7464 | 0.22648 | 5.535 |  | 2007-01-01 | 9:30 | 34200 | 39.1575 | 0.23494 | 5.6927
| 2029-09-01 | 9:31 | 34260 | 166.038 | 0.99623 | 16.9772 |  | 2029-09-01 | 9:31 | 34260 | 166.038 | 0.99623 | 16.9772 |  | 2006-09-01 | 9:31 | 34260 | 161.913 | 0.97148 | 16.6653 |  | 2029-09-01 | 9:31 | 34260 | 115.729 | 0.69437 | 13.1313 |  | 2006-09-01 | 9:31 | 34260 | 100.913 | 0.60548 | 12.0903 |  | 2028-01-01 | 9:31 | 34260 | 163.15 | 0.9789 | 16.7665 |  | 2007-01-01 | 9:31 | 34260 | 161.434 | 0.9686 | 16.6456 |  | 2028-01-01 | 9:31 | 34260 | 74.3594 | 0.44616 | 9.6514 |  | 2007-01-01 | 9:31 | 34260 | 79.1996 | 0.4752 | 10.0863 |  | 2029-09-01 | 9:31 | 34260 | 166.038 | 0.99623 | 16.9772 |  | 2006-09-01 | 9:31 | 34260 | 161.913 | 0.97148 | 16.6653 |  | 2029-09-01 | 9:31 | 34260 | 85.6792 | 0.51408 | 10.5488 |  | 2006-09-01 | 9:31 | 34260 | 69.0607 | 0.41436 | 9.2826 |  | 2028-01-01 | 9:31 | 34260 | 163.15 | 0.9789 | 16.7665 |  | 2007-01-01 | 9:31 | 34260 | 161.434 | 0.9686 | 16.6456 |  | 2028-01-01 | 9:31 | 34260 | 44.6272 | 0.26776 | 6.5744 |  | 2007-01-01 | 9:31 | 34260 | 48.8958 | 0.29337 | 7.0361 |  | 2029-09-01 | 9:31 | 34260 | 166.038 | 0.99623 | 16.9772 |  | 2006-09-01 | 9:31 | 34260 | 161.913 | 0.97148 | 16.6653 |  | 2029-09-01 | 9:31 | 34260 | 66.6058 | 0.39963 | 8.7343 |  | 2006-09-01 | 9:31 | 34260 | 51.0322 | 0.30619 | 7.4537 |  | 2028-01-01 | 9:31 | 34260 | 163.15 | 0.9789 | 16.7665 |  | 2007-01-01 | 9:31 | 34260 | 161.434 | 0.9686 | 16.6456 |  | 2028-01-01 | 9:31 | 34260 | 31.2342 | 0.18741 | 4.9284 |  | 2007-01-01 | 9:31 | 34260 | 34.5883 | 0.20753 | 5.3388 |  | 2029-09-01 | 9:31 | 34260 | 87.451 | 0.52471 | 10.8523 |  | 2029-09-01 | 9:31 | 34260 | 62.8108 | 0.37686 | 8.5333 |  | 2029-09-01 | 9:31 | 34260 | 43.2264 | 0.25936 | 6.416 |  | 2006-09-01 | 9:31 | 34260 | 42.789 | 0.25673 | 6.3581 |  | 2028-01-01 | 9:31 | 34260 | 74.3594 | 0.44616 | 9.6514 |  | 2007-01-01 | 9:31 | 34260 | 79.1996 | 0.4752 | 10.0863 |  | 2028-01-01 | 9:31 | 34260 | 37.7946 | 0.22677 | 5.7618 |  | 2007-01-01 | 9:31 | 34260 | 39.2208 | 0.23532 | 5.9281
| 2029-09-01 | 9:32 | 34320 | 170.337 | 1.022 | 17.9993 |  | 2029-09-01 | 9:32 | 34320 | 170.337 | 1.022 | 17.9993 |  | 2006-09-01 | 9:32 | 34320 | 166.027 | 0.99616 | 17.6614 |  | 2029-09-01 | 9:32 | 34320 | 117.75 | 0.7065 | 13.8378 |  | 2006-09-01 | 9:32 | 34320 | 102.124 | 0.61274 | 12.703 |  | 2028-01-01 | 9:32 | 34320 | 167.311 | 1.0039 | 17.7703 |  | 2007-01-01 | 9:32 | 34320 | 165.498 | 0.99299 | 17.6386 |  | 2028-01-01 | 9:32 | 34320 | 74.9201 | 0.44952 | 10.101 |  | 2007-01-01 | 9:32 | 34320 | 79.8971 | 0.47938 | 10.5657 |  | 2029-09-01 | 9:32 | 34320 | 170.337 | 1.022 | 17.9993 |  | 2006-09-01 | 9:32 | 34320 | 166.027 | 0.99616 | 17.6614 |  | 2029-09-01 | 9:32 | 34320 | 86.7197 | 0.52032 | 11.0691 |  | 2006-09-01 | 9:32 | 34320 | 69.3498 | 0.4161 | 9.6987 |  | 2028-01-01 | 9:32 | 34320 | 167.311 | 1.0039 | 17.7703 |  | 2007-01-01 | 9:32 | 34320 | 165.498 | 0.99299 | 17.6386 |  | 2028-01-01 | 9:32 | 34320 | 44.7151 | 0.26829 | 6.8427 |  | 2007-01-01 | 9:32 | 34320 | 49.0442 | 0.29427 | 7.3304 |  | 2029-09-01 | 9:32 | 34320 | 170.337 | 1.022 | 17.9993 |  | 2006-09-01 | 9:32 | 34320 | 166.027 | 0.99616 | 17.6614 |  | 2029-09-01 | 9:32 | 34320 | 67.2009 | 0.40321 | 9.1375 |  | 2006-09-01 | 9:32 | 34320 | 51.0359 | 0.30622 | 7.7599 |  | 2028-01-01 | 9:32 | 34320 | 167.311 | 1.0039 | 17.7703 |  | 2007-01-01 | 9:32 | 34320 | 165.498 | 0.99299 | 17.6386 |  | 2028-01-01 | 9:32 | 34320 | 31.2496 | 0.1875 | 5.1159 |  | 2007-01-01 | 9:32 | 34320 | 34.632 | 0.20779 | 5.5465 |  | 2029-09-01 | 9:32 | 34320 | 88.342 | 0.53005 | 11.3823 |  | 2029-09-01 | 9:32 | 34320 | 63.1266 | 0.37876 | 8.912 |  | 2029-09-01 | 9:32 | 34320 | 43.2979 | 0.25979 | 6.6758 |  | 2006-09-01 | 9:32 | 34320 | 42.8636 | 0.25718 | 6.6153 |  | 2028-01-01 | 9:32 | 34320 | 74.9201 | 0.44952 | 10.101 |  | 2007-01-01 | 9:32 | 34320 | 79.8971 | 0.47938 | 10.5657 |  | 2028-01-01 | 9:32 | 34320 | 37.8359 | 0.22702 | 5.9888 |  | 2007-01-01 | 9:32 | 34320 | 39.2761 | 0.23566 | 6.1637
| 2029-09-01 | 9:33 | 34380 | 174.577 | 1.0475 | 19.0467 |  | 2029-09-01 | 9:33 | 34380 | 174.577 | 1.0475 | 19.0467 |  | 2006-09-01 | 9:33 | 34380 | 170.082 | 1.0205 | 18.6819 |  | 2029-09-01 | 9:33 | 34380 | 119.709 | 0.71825 | 14.5561 |  | 2006-09-01 | 9:33 | 34380 | 103.262 | 0.61957 | 13.3226 |  | 2028-01-01 | 9:33 | 34380 | 171.412 | 1.0285 | 18.7988 |  | 2007-01-01 | 9:33 | 34380 | 169.502 | 1.017 | 18.6556 |  | 2028-01-01 | 9:33 | 34380 | 75.4395 | 0.45264 | 10.5536 |  | 2007-01-01 | 9:33 | 34380 | 80.5493 | 0.4833 | 11.049 |  | 2029-09-01 | 9:33 | 34380 | 174.577 | 1.0475 | 19.0467 |  | 2006-09-01 | 9:33 | 34380 | 170.082 | 1.0205 | 18.6819 |  | 2029-09-01 | 9:33 | 34380 | 87.7198 | 0.52632 | 11.5955 |  | 2006-09-01 | 9:33 | 34380 | 69.5973 | 0.41758 | 10.1163 |  | 2028-01-01 | 9:33 | 34380 | 171.412 | 1.0285 | 18.7988 |  | 2007-01-01 | 9:33 | 34380 | 169.502 | 1.017 | 18.6556 |  | 2028-01-01 | 9:33 | 34380 | 44.792 | 0.26875 | 7.1115 |  | 2007-01-01 | 9:33 | 34380 | 49.1784 | 0.29507 | 7.6255 |  | 2029-09-01 | 9:33 | 34380 | 174.577 | 1.0475 | 19.0467 |  | 2006-09-01 | 9:33 | 34380 | 170.082 | 1.0205 | 18.6819 |  | 2029-09-01 | 9:33 | 34380 | 67.7729 | 0.40664 | 9.5441 |  | 2006-09-01 | 9:33 | 34380 | 51.02 | 0.30612 | 8.066 |  | 2028-01-01 | 9:33 | 34380 | 171.412 | 1.0285 | 18.7988 |  | 2007-01-01 | 9:33 | 34380 | 169.502 | 1.017 | 18.6556 |  | 2028-01-01 | 9:33 | 34380 | 31.2624 | 0.18757 | 5.3035 |  | 2007-01-01 | 9:33 | 34380 | 34.6717 | 0.20803 | 5.7546 |  | 2029-09-01 | 9:33 | 34380 | 89.1778 | 0.53507 | 11.9174 |  | 2029-09-01 | 9:33 | 34380 | 63.4129 | 0.38048 | 9.2925 |  | 2029-09-01 | 9:33 | 34380 | 43.3594 | 0.26016 | 6.9359 |  | 2006-09-01 | 9:33 | 34380 | 42.9285 | 0.25757 | 6.8729 |  | 2028-01-01 | 9:33 | 34380 | 75.4395 | 0.45264 | 10.5536 |  | 2007-01-01 | 9:33 | 34380 | 80.5493 | 0.4833 | 11.049 |  | 2028-01-01 | 9:33 | 34380 | 37.8712 | 0.22723 | 6.216 |  | 2007-01-01 | 9:33 | 34380 | 39.3245 | 0.23595 | 6.3997
| 2029-09-01 | 9:34 | 34440 | 178.759 | 1.0726 | 20.1193 |  | 2029-09-01 | 9:34 | 34440 | 178.759 | 1.0726 | 20.1193 |  | 2006-09-01 | 9:34 | 34440 | 174.08 | 1.0445 | 19.7264 |  | 2029-09-01 | 9:34 | 34440 | 121.611 | 0.72967 | 15.2857 |  | 2006-09-01 | 9:34 | 34440 | 104.331 | 0.62599 | 13.9486 |  | 2028-01-01 | 9:34 | 34440 | 175.455 | 1.0527 | 19.8516 |  | 2007-01-01 | 9:34 | 34440 | 173.446 | 1.0407 | 19.6962 |  | 2028-01-01 | 9:34 | 34440 | 75.9205 | 0.45552 | 11.0091 |  | 2007-01-01 | 9:34 | 34440 | 81.1594 | 0.48696 | 11.5359 |  | 2029-09-01 | 9:34 | 34440 | 178.759 | 1.0726 | 20.1193 |  | 2006-09-01 | 9:34 | 34440 | 174.08 | 1.0445 | 19.7264 |  | 2029-09-01 | 9:34 | 34440 | 88.683 | 0.5321 | 12.1276 |  | 2006-09-01 | 9:34 | 34440 | 69.8067 | 0.41884 | 10.5351 |  | 2028-01-01 | 9:34 | 34440 | 175.455 | 1.0527 | 19.8516 |  | 2007-01-01 | 9:34 | 34440 | 173.446 | 1.0407 | 19.6962 |  | 2028-01-01 | 9:34 | 34440 | 44.8593 | 0.26916 | 7.3806 |  | 2007-01-01 | 9:34 | 34440 | 49.2999 | 0.2958 | 7.9213 |  | 2029-09-01 | 9:34 | 34440 | 178.759 | 1.0726 | 20.1193 |  | 2006-09-01 | 9:34 | 34440 | 174.08 | 1.0445 | 19.7264 |  | 2029-09-01 | 9:34 | 34440 | 68.3248 | 0.40995 | 9.9541 |  | 2006-09-01 | 9:34 | 34440 | 50.9867 | 0.30592 | 8.3719 |  | 2028-01-01 | 9:34 | 34440 | 175.455 | 1.0527 | 19.8516 |  | 2007-01-01 | 9:34 | 34440 | 173.446 | 1.0407 | 19.6962 |  | 2028-01-01 | 9:34 | 34440 | 31.273 | 0.18764 | 5.4911 |  | 2007-01-01 | 9:34 | 34440 | 34.7081 | 0.20825 | 5.9628 |  | 2029-09-01 | 9:34 | 34440 | 89.9621 | 0.53977 | 12.4572 |  | 2029-09-01 | 9:34 | 34440 | 63.6726 | 0.38204 | 9.6745 |  | 2029-09-01 | 9:34 | 34440 | 43.4123 | 0.26047 | 7.1964 |  | 2006-09-01 | 9:34 | 34440 | 42.9852 | 0.25791 | 7.1308 |  | 2028-01-01 | 9:34 | 34440 | 75.9205 | 0.45552 | 11.0091 |  | 2007-01-01 | 9:34 | 34440 | 81.1594 | 0.48696 | 11.5359 |  | 2028-01-01 | 9:34 | 34440 | 37.9013 | 0.22741 | 6.4434 |  | 2007-01-01 | 9:34 | 34440 | 39.3671 | 0.2362 | 6.6359
| 2029-09-01 | 9:35 | 34500 | 182.884 | 1.0973 | 21.2166 |  | 2029-09-01 | 9:35 | 34500 | 182.884 | 1.0973 | 21.2166 |  | 2006-09-01 | 9:35 | 34500 | 178.022 | 1.0681 | 20.7945 |  | 2029-09-01 | 9:35 | 34500 | 123.458 | 0.74075 | 16.0265 |  | 2006-09-01 | 9:35 | 34500 | 105.334 | 0.632 | 14.5806 |  | 2028-01-01 | 9:35 | 34500 | 179.441 | 1.0766 | 20.9282 |  | 2007-01-01 | 9:35 | 34500 | 177.33 | 1.064 | 20.7602 |  | 2028-01-01 | 9:35 | 34500 | 76.3662 | 0.4582 | 11.4673 |  | 2007-01-01 | 9:35 | 34500 | 81.7302 | 0.49038 | 12.0263 |  | 2029-09-01 | 9:35 | 34500 | 182.884 | 1.0973 | 21.2166 |  | 2006-09-01 | 9:35 | 34500 | 178.022 | 1.0681 | 20.7945 |  | 2029-09-01 | 9:35 | 34500 | 89.6125 | 0.53767 | 12.6652 |  | 2006-09-01 | 9:35 | 34500 | 69.9811 | 0.41989 | 10.955 |  | 2028-01-01 | 9:35 | 34500 | 179.441 | 1.0766 | 20.9282 |  | 2007-01-01 | 9:35 | 34500 | 177.33 | 1.064 | 20.7602 |  | 2028-01-01 | 9:35 | 34500 | 44.9182 | 0.26951 | 7.6501 |  | 2007-01-01 | 9:35 | 34500 | 49.4104 | 0.29646 | 8.2177 |  | 2029-09-01 | 9:35 | 34500 | 182.884 | 1.0973 | 21.2166 |  | 2006-09-01 | 9:35 | 34500 | 178.022 | 1.0681 | 20.7945 |  | 2029-09-01 | 9:35 | 34500 | 68.859 | 0.41315 | 10.3672 |  | 2006-09-01 | 9:35 | 34500 | 50.9382 | 0.30563 | 8.6775 |  | 2028-01-01 | 9:35 | 34500 | 179.441 | 1.0766 | 20.9282 |  | 2007-01-01 | 9:35 | 34500 | 177.33 | 1.064 | 20.7602 |  | 2028-01-01 | 9:35 | 34500 | 31.2819 | 0.18769 | 5.6788 |  | 2007-01-01 | 9:35 | 34500 | 34.7417 | 0.20845 | 6.1713 |  | 2029-09-01 | 9:35 | 34500 | 90.6981 | 0.54419 | 13.0014 |  | 2029-09-01 | 9:35 | 34500 | 63.9082 | 0.38345 | 10.058 |  | 2029-09-01 | 9:35 | 34500 | 43.4578 | 0.26075 | 7.4572 |  | 2006-09-01 | 9:35 | 34500 | 43.0347 | 0.25821 | 7.389 |  | 2028-01-01 | 9:35 | 34500 | 76.3662 | 0.4582 | 11.4673 |  | 2007-01-01 | 9:35 | 34500 | 81.7302 | 0.49038 | 12.0263 |  | 2028-01-01 | 9:35 | 34500 | 37.9271 | 0.22756 | 6.671 |  | 2007-01-01 | 9:35 | 34500 | 39.4047 | 0.23643 | 6.8723
| 2029-09-01 | 9:36 | 34560 | 186.953 | 1.1217 | 22.3383 |  | 2029-09-01 | 9:36 | 34560 | 186.953 | 1.1217 | 22.3383 |  | 2006-09-01 | 9:36 | 34560 | 181.908 | 1.0914 | 21.886 |  | 2029-09-01 | 9:36 | 34560 | 125.253 | 0.75152 | 16.778 |  | 2006-09-01 | 9:36 | 34560 | 106.275 | 0.63765 | 15.2182 |  | 2028-01-01 | 9:36 | 34560 | 183.369 | 1.1002 | 22.0284 |  | 2007-01-01 | 9:36 | 34560 | 181.156 | 1.0869 | 21.8472 |  | 2028-01-01 | 9:36 | 34560 | 76.779 | 0.46067 | 11.928 |  | 2007-01-01 | 9:36 | 34560 | 82.2644 | 0.49359 | 12.5199 |  | 2029-09-01 | 9:36 | 34560 | 186.953 | 1.1217 | 22.3383 |  | 2006-09-01 | 9:36 | 34560 | 181.908 | 1.0914 | 21.886 |  | 2029-09-01 | 9:36 | 34560 | 90.5108 | 0.54306 | 13.2083 |  | 2006-09-01 | 9:36 | 34560 | 70.1234 | 0.42074 | 11.3758 |  | 2028-01-01 | 9:36 | 34560 | 183.369 | 1.1002 | 22.0284 |  | 2007-01-01 | 9:36 | 34560 | 181.156 | 1.0869 | 21.8472 |  | 2028-01-01 | 9:36 | 34560 | 44.9697 | 0.26982 | 7.92 |  | 2007-01-01 | 9:36 | 34560 | 49.5109 | 0.29707 | 8.5148 |  | 2029-09-01 | 9:36 | 34560 | 186.953 | 1.1217 | 22.3383 |  | 2006-09-01 | 9:36 | 34560 | 181.908 | 1.0914 | 21.886 |  | 2029-09-01 | 9:36 | 34560 | 69.3774 | 0.41626 | 10.7835 |  | 2006-09-01 | 9:36 | 34560 | 50.8763 | 0.30526 | 8.9828 |  | 2028-01-01 | 9:36 | 34560 | 183.369 | 1.1002 | 22.0284 |  | 2007-01-01 | 9:36 | 34560 | 181.156 | 1.0869 | 21.8472 |  | 2028-01-01 | 9:36 | 34560 | 31.2893 | 0.18774 | 5.8665 |  | 2007-01-01 | 9:36 | 34560 | 34.7729 | 0.20864 | 6.3799 |  | 2029-09-01 | 9:36 | 34560 | 91.3887 | 0.54833 | 13.5497 |  | 2029-09-01 | 9:36 | 34560 | 64.1219 | 0.38473 | 10.4427 |  | 2029-09-01 | 9:36 | 34560 | 43.4969 | 0.26098 | 7.7181 |  | 2006-09-01 | 9:36 | 34560 | 43.0779 | 0.25847 | 7.6475 |  | 2028-01-01 | 9:36 | 34560 | 76.779 | 0.46067 | 11.928 |  | 2007-01-01 | 9:36 | 34560 | 82.2644 | 0.49359 | 12.5199 |  | 2028-01-01 | 9:36 | 34560 | 37.9492 | 0.2277 | 6.8987 |  | 2007-01-01 | 9:36 | 34560 | 39.438 | 0.23663 | 7.1089
| 2029-09-01 | 9:37 | 34620 | 190.967 | 1.1458 | 23.4841 |  | 2029-09-01 | 9:37 | 34620 | 190.967 | 1.1458 | 23.4841 |  | 2006-09-01 | 9:37 | 34620 | 185.739 | 1.1144 | 23.0004 |  | 2029-09-01 | 9:37 | 34620 | 126.999 | 0.76199 | 17.54 |  | 2006-09-01 | 9:37 | 34620 | 107.156 | 0.64294 | 15.8612 |  | 2028-01-01 | 9:37 | 34620 | 187.242 | 1.1235 | 23.1519 |  | 2007-01-01 | 9:37 | 34620 | 184.925 | 1.1096 | 22.9567 |  | 2028-01-01 | 9:37 | 34620 | 77.1614 | 0.46297 | 12.391 |  | 2007-01-01 | 9:37 | 34620 | 82.7646 | 0.49659 | 13.0165 |  | 2029-09-01 | 9:37 | 34620 | 190.967 | 1.1458 | 23.4841 |  | 2006-09-01 | 9:37 | 34620 | 185.739 | 1.1144 | 23.0004 |  | 2029-09-01 | 9:37 | 34620 | 91.3805 | 0.54828 | 13.7566 |  | 2006-09-01 | 9:37 | 34620 | 70.2363 | 0.42142 | 11.7972 |  | 2028-01-01 | 9:37 | 34620 | 187.242 | 1.1235 | 23.1519 |  | 2007-01-01 | 9:37 | 34620 | 184.925 | 1.1096 | 22.9567 |  | 2028-01-01 | 9:37 | 34620 | 45.0148 | 0.27009 | 8.19 |  | 2007-01-01 | 9:37 | 34620 | 49.6028 | 0.29762 | 8.8124 |  | 2029-09-01 | 9:37 | 34620 | 190.967 | 1.1458 | 23.4841 |  | 2006-09-01 | 9:37 | 34620 | 185.739 | 1.1144 | 23.0004 |  | 2029-09-01 | 9:37 | 34620 | 69.882 | 0.41929 | 11.2028 |  | 2006-09-01 | 9:37 | 34620 | 50.8028 | 0.30482 | 9.2876 |  | 2028-01-01 | 9:37 | 34620 | 187.242 | 1.1235 | 23.1519 |  | 2007-01-01 | 9:37 | 34620 | 184.925 | 1.1096 | 22.9567 |  | 2028-01-01 | 9:37 | 34620 | 31.2954 | 0.18777 | 6.0543 |  | 2007-01-01 | 9:37 | 34620 | 34.8022 | 0.20881 | 6.5887 |  | 2029-09-01 | 9:37 | 34620 | 92.0366 | 0.55222 | 14.1019 |  | 2029-09-01 | 9:37 | 34620 | 64.3156 | 0.38589 | 10.8286 |  | 2029-09-01 | 9:37 | 34620 | 43.5303 | 0.26118 | 7.9793 |  | 2006-09-01 | 9:37 | 34620 | 43.1157 | 0.25869 | 7.9062 |  | 2028-01-01 | 9:37 | 34620 | 77.1614 | 0.46297 | 12.391 |  | 2007-01-01 | 9:37 | 34620 | 82.7646 | 0.49659 | 13.0165 |  | 2028-01-01 | 9:37 | 34620 | 37.9681 | 0.22781 | 7.1265 |  | 2007-01-01 | 9:37 | 34620 | 39.4675 | 0.2368 | 7.3457
| 2029-09-01 | 9:38 | 34680 | 194.925 | 1.1696 | 24.6537 |  | 2029-09-01 | 9:38 | 34680 | 194.925 | 1.1696 | 24.6537 |  | 2006-09-01 | 9:38 | 34680 | 189.517 | 1.1371 | 24.1375 |  | 2029-09-01 | 9:38 | 34680 | 128.697 | 0.77218 | 18.3122 |  | 2006-09-01 | 9:38 | 34680 | 107.979 | 0.64787 | 16.5091 |  | 2028-01-01 | 9:38 | 34680 | 191.059 | 1.1464 | 24.2982 |  | 2007-01-01 | 9:38 | 34680 | 188.637 | 1.1318 | 24.0885 |  | 2028-01-01 | 9:38 | 34680 | 77.5157 | 0.46509 | 12.856 |  | 2007-01-01 | 9:38 | 34680 | 83.2331 | 0.4994 | 13.5159 |  | 2029-09-01 | 9:38 | 34680 | 194.925 | 1.1696 | 24.6537 |  | 2006-09-01 | 9:38 | 34680 | 189.517 | 1.1371 | 24.1375 |  | 2029-09-01 | 9:38 | 34680 | 92.2237 | 0.55334 | 14.3099 |  | 2006-09-01 | 9:38 | 34680 | 70.3224 | 0.42193 | 12.2191 |  | 2028-01-01 | 9:38 | 34680 | 191.059 | 1.1464 | 24.2982 |  | 2007-01-01 | 9:38 | 34680 | 188.637 | 1.1318 | 24.0885 |  | 2028-01-01 | 9:38 | 34680 | 45.0543 | 0.27033 | 8.4604 |  | 2007-01-01 | 9:38 | 34680 | 49.687 | 0.29812 | 9.1105 |  | 2029-09-01 | 9:38 | 34680 | 194.925 | 1.1696 | 24.6537 |  | 2006-09-01 | 9:38 | 34680 | 189.517 | 1.1371 | 24.1375 |  | 2029-09-01 | 9:38 | 34680 | 70.3743 | 0.42225 | 11.625 |  | 2006-09-01 | 9:38 | 34680 | 50.719 | 0.30431 | 9.5919 |  | 2028-01-01 | 9:38 | 34680 | 191.059 | 1.1464 | 24.2982 |  | 2007-01-01 | 9:38 | 34680 | 188.637 | 1.1318 | 24.0885 |  | 2028-01-01 | 9:38 | 34680 | 31.3006 | 0.1878 | 6.2421 |  | 2007-01-01 | 9:38 | 34680 | 34.8299 | 0.20898 | 6.7977 |  | 2029-09-01 | 9:38 | 34680 | 92.6444 | 0.55587 | 14.6578 |  | 2029-09-01 | 9:38 | 34680 | 64.4912 | 0.38695 | 11.2156 |  | 2029-09-01 | 9:38 | 34680 | 43.559 | 0.26135 | 8.2407 |  | 2006-09-01 | 9:38 | 34680 | 43.1488 | 0.25889 | 8.1651 |  | 2028-01-01 | 9:38 | 34680 | 77.5157 | 0.46509 | 12.856 |  | 2007-01-01 | 9:38 | 34680 | 83.2331 | 0.4994 | 13.5159 |  | 2028-01-01 | 9:38 | 34680 | 37.9843 | 0.22791 | 7.3544 |  | 2007-01-01 | 9:38 | 34680 | 39.4939 | 0.23696 | 7.5827
| 2029-09-01 | 9:39 | 34740 | 198.83 | 1.193 | 25.8466 |  | 2029-09-01 | 9:39 | 34740 | 198.83 | 1.193 | 25.8466 |  | 2006-09-01 | 9:39 | 34740 | 193.241 | 1.1594 | 25.297 |  | 2029-09-01 | 9:39 | 34740 | 130.351 | 0.78211 | 19.0943 |  | 2006-09-01 | 9:39 | 34740 | 108.749 | 0.65249 | 17.1615 |  | 2028-01-01 | 9:39 | 34740 | 194.821 | 1.1689 | 25.4671 |  | 2007-01-01 | 9:39 | 34740 | 192.293 | 1.1538 | 25.2423 |  | 2028-01-01 | 9:39 | 34740 | 77.8439 | 0.46706 | 13.3231 |  | 2007-01-01 | 9:39 | 34740 | 83.672 | 0.50203 | 14.0179 |  | 2029-09-01 | 9:39 | 34740 | 198.83 | 1.193 | 25.8466 |  | 2006-09-01 | 9:39 | 34740 | 193.241 | 1.1594 | 25.297 |  | 2029-09-01 | 9:39 | 34740 | 93.0427 | 0.55826 | 14.8682 |  | 2006-09-01 | 9:39 | 34740 | 70.3839 | 0.4223 | 12.6414 |  | 2028-01-01 | 9:39 | 34740 | 194.821 | 1.1689 | 25.4671 |  | 2007-01-01 | 9:39 | 34740 | 192.293 | 1.1538 | 25.2423 |  | 2028-01-01 | 9:39 | 34740 | 45.0889 | 0.27053 | 8.7309 |  | 2007-01-01 | 9:39 | 34740 | 49.7644 | 0.29859 | 9.4091 |  | 2029-09-01 | 9:39 | 34740 | 198.83 | 1.193 | 25.8466 |  | 2006-09-01 | 9:39 | 34740 | 193.241 | 1.1594 | 25.297 |  | 2029-09-01 | 9:39 | 34740 | 70.8558 | 0.42513 | 12.0502 |  | 2006-09-01 | 9:39 | 34740 | 50.6264 | 0.30376 | 9.8957 |  | 2028-01-01 | 9:39 | 34740 | 194.821 | 1.1689 | 25.4671 |  | 2007-01-01 | 9:39 | 34740 | 192.293 | 1.1538 | 25.2423 |  | 2028-01-01 | 9:39 | 34740 | 31.3049 | 0.18783 | 6.4299 |  | 2007-01-01 | 9:39 | 34740 | 34.8562 | 0.20914 | 7.0068 |  | 2029-09-01 | 9:39 | 34740 | 93.2146 | 0.55929 | 15.2171 |  | 2029-09-01 | 9:39 | 34740 | 64.6504 | 0.3879 | 11.6035 |  | 2029-09-01 | 9:39 | 34740 | 43.5835 | 0.2615 | 8.5022 |  | 2006-09-01 | 9:39 | 34740 | 43.1777 | 0.25907 | 8.4241 |  | 2028-01-01 | 9:39 | 34740 | 77.8439 | 0.46706 | 13.3231 |  | 2007-01-01 | 9:39 | 34740 | 83.672 | 0.50203 | 14.0179 |  | 2028-01-01 | 9:39 | 34740 | 37.9982 | 0.22799 | 7.5824 |  | 2007-01-01 | 9:39 | 34740 | 39.5176 | 0.23711 | 7.8198
| 2029-09-01 | 9:40 | 34800 | 202.681 | 1.2161 | 27.0627 |  | 2029-09-01 | 9:40 | 34800 | 202.681 | 1.2161 | 27.0627 |  | 2006-09-01 | 9:40 | 34800 | 196.913 | 1.1815 | 26.4785 |  | 2029-09-01 | 9:40 | 34800 | 131.961 | 0.79177 | 19.8861 |  | 2006-09-01 | 9:40 | 34800 | 109.468 | 0.65681 | 17.8184 |  | 2028-01-01 | 9:40 | 34800 | 198.528 | 1.1912 | 26.6583 |  | 2007-01-01 | 9:40 | 34800 | 195.894 | 1.1754 | 26.4177 |  | 2028-01-01 | 9:40 | 34800 | 78.148 | 0.46889 | 13.792 |  | 2007-01-01 | 9:40 | 34800 | 84.0835 | 0.5045 | 14.5224 |  | 2029-09-01 | 9:40 | 34800 | 202.681 | 1.2161 | 27.0627 |  | 2006-09-01 | 9:40 | 34800 | 196.913 | 1.1815 | 26.4785 |  | 2029-09-01 | 9:40 | 34800 | 93.8395 | 0.56304 | 15.4312 |  | 2006-09-01 | 9:40 | 34800 | 70.423 | 0.42254 | 13.064 |  | 2028-01-01 | 9:40 | 34800 | 198.528 | 1.1912 | 26.6583 |  | 2007-01-01 | 9:40 | 34800 | 195.894 | 1.1754 | 26.4177 |  | 2028-01-01 | 9:40 | 34800 | 45.1192 | 0.27072 | 9.0016 |  | 2007-01-01 | 9:40 | 34800 | 49.8358 | 0.29901 | 9.7081 |  | 2029-09-01 | 9:40 | 34800 | 202.681 | 1.2161 | 27.0627 |  | 2006-09-01 | 9:40 | 34800 | 196.913 | 1.1815 | 26.4785 |  | 2029-09-01 | 9:40 | 34800 | 71.3281 | 0.42797 | 12.4781 |  | 2006-09-01 | 9:40 | 34800 | 50.5261 | 0.30316 | 10.1988 |  | 2028-01-01 | 9:40 | 34800 | 198.528 | 1.1912 | 26.6583 |  | 2007-01-01 | 9:40 | 34800 | 195.894 | 1.1754 | 26.4177 |  | 2028-01-01 | 9:40 | 34800 | 31.3085 | 0.18785 | 6.6178 |  | 2007-01-01 | 9:40 | 34800 | 34.8813 | 0.20929 | 7.2161 |  | 2029-09-01 | 9:40 | 34800 | 93.7494 | 0.5625 | 15.7796 |  | 2029-09-01 | 9:40 | 34800 | 64.7944 | 0.38877 | 11.9922 |  | 2029-09-01 | 9:40 | 34800 | 43.6042 | 0.26163 | 8.7638 |  | 2006-09-01 | 9:40 | 34800 | 43.2031 | 0.25922 | 8.6833 |  | 2028-01-01 | 9:40 | 34800 | 78.148 | 0.46889 | 13.792 |  | 2007-01-01 | 9:40 | 34800 | 84.0835 | 0.5045 | 14.5224 |  | 2028-01-01 | 9:40 | 34800 | 38.0101 | 0.22806 | 7.8105 |  | 2007-01-01 | 9:40 | 34800 | 39.5389 | 0.23723 | 8.057
| 2029-09-01 | 9:41 | 34860 | 206.48 | 1.2389 | 28.3016 |  | 2029-09-01 | 9:41 | 34860 | 206.48 | 1.2389 | 28.3016 |  | 2006-09-01 | 9:41 | 34860 | 200.533 | 1.2032 | 27.6817 |  | 2029-09-01 | 9:41 | 34860 | 133.531 | 0.80119 | 20.6872 |  | 2006-09-01 | 9:41 | 34860 | 110.137 | 0.66082 | 18.4792 |  | 2028-01-01 | 9:41 | 34860 | 202.181 | 1.2131 | 27.8714 |  | 2007-01-01 | 9:41 | 34860 | 199.441 | 1.1966 | 27.6143 |  | 2028-01-01 | 9:41 | 34860 | 78.4297 | 0.47058 | 14.2626 |  | 2007-01-01 | 9:41 | 34860 | 84.4693 | 0.50682 | 15.0292 |  | 2029-09-01 | 9:41 | 34860 | 206.48 | 1.2389 | 28.3016 |  | 2006-09-01 | 9:41 | 34860 | 200.533 | 1.2032 | 27.6817 |  | 2029-09-01 | 9:41 | 34860 | 94.6158 | 0.56769 | 15.9989 |  | 2006-09-01 | 9:41 | 34860 | 70.4417 | 0.42265 | 13.4866 |  | 2028-01-01 | 9:41 | 34860 | 202.181 | 1.2131 | 27.8714 |  | 2007-01-01 | 9:41 | 34860 | 199.441 | 1.1966 | 27.6143 |  | 2028-01-01 | 9:41 | 34860 | 45.1458 | 0.27087 | 9.2725 |  | 2007-01-01 | 9:41 | 34860 | 49.902 | 0.29941 | 10.0076 |  | 2029-09-01 | 9:41 | 34860 | 206.48 | 1.2389 | 28.3016 |  | 2006-09-01 | 9:41 | 34860 | 200.533 | 1.2032 | 27.6817 |  | 2029-09-01 | 9:41 | 34860 | 71.7924 | 0.43075 | 12.9089 |  | 2006-09-01 | 9:41 | 34860 | 50.4192 | 0.30252 | 10.5014 |  | 2028-01-01 | 9:41 | 34860 | 202.181 | 1.2131 | 27.8714 |  | 2007-01-01 | 9:41 | 34860 | 199.441 | 1.1966 | 27.6143 |  | 2028-01-01 | 9:41 | 34860 | 31.3116 | 0.18787 | 6.8057 |  | 2007-01-01 | 9:41 | 34860 | 34.9055 | 0.20943 | 7.4256 |  | 2029-09-01 | 9:41 | 34860 | 94.2509 | 0.56551 | 16.3451 |  | 2029-09-01 | 9:41 | 34860 | 64.9249 | 0.38955 | 12.3818 |  | 2029-09-01 | 9:41 | 34860 | 43.6219 | 0.26173 | 9.0255 |  | 2006-09-01 | 9:41 | 34860 | 43.2254 | 0.25935 | 8.9427 |  | 2028-01-01 | 9:41 | 34860 | 78.4297 | 0.47058 | 14.2626 |  | 2007-01-01 | 9:41 | 34860 | 84.4693 | 0.50682 | 15.0292 |  | 2028-01-01 | 9:41 | 34860 | 38.0203 | 0.22812 | 8.0386 |  | 2007-01-01 | 9:41 | 34860 | 39.5582 | 0.23735 | 8.2944
| 2029-09-01 | 9:42 | 34920 | 210.226 | 1.2614 | 29.563 |  | 2029-09-01 | 9:42 | 34920 | 210.226 | 1.2614 | 29.563 |  | 2006-09-01 | 9:42 | 34920 | 204.103 | 1.2246 | 28.9063 |  | 2029-09-01 | 9:42 | 34920 | 135.063 | 0.81038 | 21.4976 |  | 2006-09-01 | 9:42 | 34920 | 110.76 | 0.66456 | 19.1437 |  | 2028-01-01 | 9:42 | 34920 | 205.781 | 1.2347 | 29.1061 |  | 2007-01-01 | 9:42 | 34920 | 202.934 | 1.2176 | 28.8319 |  | 2028-01-01 | 9:42 | 34920 | 78.6908 | 0.47214 | 14.7347 |  | 2007-01-01 | 9:42 | 34920 | 84.8314 | 0.50899 | 15.5382 |  | 2029-09-01 | 9:42 | 34920 | 210.226 | 1.2614 | 29.563 |  | 2006-09-01 | 9:42 | 34920 | 204.103 | 1.2246 | 28.9063 |  | 2029-09-01 | 9:42 | 34920 | 95.3736 | 0.57224 | 16.5712 |  | 2006-09-01 | 9:42 | 34920 | 70.4418 | 0.42265 | 13.9093 |  | 2028-01-01 | 9:42 | 34920 | 205.781 | 1.2347 | 29.1061 |  | 2007-01-01 | 9:42 | 34920 | 202.934 | 1.2176 | 28.8319 |  | 2028-01-01 | 9:42 | 34920 | 45.1691 | 0.27101 | 9.5435 |  | 2007-01-01 | 9:42 | 34920 | 49.9634 | 0.29978 | 10.3073 |  | 2029-09-01 | 9:42 | 34920 | 210.226 | 1.2614 | 29.563 |  | 2006-09-01 | 9:42 | 34920 | 204.103 | 1.2246 | 28.9063 |  | 2029-09-01 | 9:42 | 34920 | 72.2499 | 0.4335 | 13.3424 |  | 2006-09-01 | 9:42 | 34920 | 50.3065 | 0.30184 | 10.8032 |  | 2028-01-01 | 9:42 | 34920 | 205.781 | 1.2347 | 29.1061 |  | 2007-01-01 | 9:42 | 34920 | 202.934 | 1.2176 | 28.8319 |  | 2028-01-01 | 9:42 | 34920 | 31.3141 | 0.18788 | 6.9935 |  | 2007-01-01 | 9:42 | 34920 | 34.9288 | 0.20957 | 7.6351 |  | 2029-09-01 | 9:42 | 34920 | 94.7211 | 0.56833 | 16.9134 |  | 2029-09-01 | 9:42 | 34920 | 65.0429 | 0.39026 | 12.772 |  | 2029-09-01 | 9:42 | 34920 | 43.6367 | 0.26182 | 9.2873 |  | 2006-09-01 | 9:42 | 34920 | 43.245 | 0.25947 | 9.2022 |  | 2028-01-01 | 9:42 | 34920 | 78.6908 | 0.47214 | 14.7347 |  | 2007-01-01 | 9:42 | 34920 | 84.8314 | 0.50899 | 15.5382 |  | 2028-01-01 | 9:42 | 34920 | 38.0291 | 0.22817 | 8.2668 |  | 2007-01-01 | 9:42 | 34920 | 39.5758 | 0.23745 | 8.5318
| 2029-09-01 | 9:43 | 34980 | 213.92 | 1.2835 | 30.8465 |  | 2029-09-01 | 9:43 | 34980 | 213.92 | 1.2835 | 30.8465 |  | 2006-09-01 | 9:43 | 34980 | 207.623 | 1.2457 | 30.152 |  | 2029-09-01 | 9:43 | 34980 | 136.557 | 0.81934 | 22.317 |  | 2006-09-01 | 9:43 | 34980 | 111.339 | 0.66803 | 19.8118 |  | 2028-01-01 | 9:43 | 34980 | 209.33 | 1.256 | 30.3621 |  | 2007-01-01 | 9:43 | 34980 | 206.375 | 1.2383 | 30.0702 |  | 2028-01-01 | 9:43 | 34980 | 78.9326 | 0.4736 | 15.2083 |  | 2007-01-01 | 9:43 | 34980 | 85.1712 | 0.51103 | 16.0492 |  | 2029-09-01 | 9:43 | 34980 | 213.92 | 1.2835 | 30.8465 |  | 2006-09-01 | 9:43 | 34980 | 207.623 | 1.2457 | 30.152 |  | 2029-09-01 | 9:43 | 34980 | 96.1144 | 0.57669 | 17.1478 |  | 2006-09-01 | 9:43 | 34980 | 70.425 | 0.42255 | 14.3318 |  | 2028-01-01 | 9:43 | 34980 | 209.33 | 1.256 | 30.3621 |  | 2007-01-01 | 9:43 | 34980 | 206.375 | 1.2383 | 30.0702 |  | 2028-01-01 | 9:43 | 34980 | 45.1895 | 0.27114 | 9.8146 |  | 2007-01-01 | 9:43 | 34980 | 50.0207 | 0.30012 | 10.6075 |  | 2029-09-01 | 9:43 | 34980 | 213.92 | 1.2835 | 30.8465 |  | 2006-09-01 | 9:43 | 34980 | 207.623 | 1.2457 | 30.152 |  | 2029-09-01 | 9:43 | 34980 | 72.7017 | 0.43621 | 13.7786 |  | 2006-09-01 | 9:43 | 34980 | 50.1891 | 0.30113 | 11.1043 |  | 2028-01-01 | 9:43 | 34980 | 209.33 | 1.256 | 30.3621 |  | 2007-01-01 | 9:43 | 34980 | 206.375 | 1.2383 | 30.0702 |  | 2028-01-01 | 9:43 | 34980 | 31.3163 | 0.1879 | 7.1814 |  | 2007-01-01 | 9:43 | 34980 | 34.9515 | 0.20971 | 7.8448 |  | 2029-09-01 | 9:43 | 34980 | 95.162 | 0.57097 | 17.4844 |  | 2029-09-01 | 9:43 | 34980 | 65.1496 | 0.3909 | 13.1629 |  | 2029-09-01 | 9:43 | 34980 | 43.6492 | 0.2619 | 9.5492 |  | 2006-09-01 | 9:43 | 34980 | 43.2623 | 0.25957 | 9.4617 |  | 2028-01-01 | 9:43 | 34980 | 78.9326 | 0.4736 | 15.2083 |  | 2007-01-01 | 9:43 | 34980 | 85.1712 | 0.51103 | 16.0492 |  | 2028-01-01 | 9:43 | 34980 | 38.0366 | 0.22822 | 8.495 |  | 2007-01-01 | 9:43 | 34980 | 39.5919 | 0.23755 | 8.7694
| 2029-09-01 | 9:44 | 35040 | 217.564 | 1.3054 | 32.1519 |  | 2029-09-01 | 9:44 | 35040 | 217.564 | 1.3054 | 32.1519 |  | 2006-09-01 | 9:44 | 35040 | 211.094 | 1.2666 | 31.4186 |  | 2029-09-01 | 9:44 | 35040 | 138.017 | 0.8281 | 23.1451 |  | 2006-09-01 | 9:44 | 35040 | 111.877 | 0.67126 | 20.483 |  | 2028-01-01 | 9:44 | 35040 | 212.827 | 1.277 | 31.639 |  | 2007-01-01 | 9:44 | 35040 | 209.763 | 1.2586 | 31.3287 |  | 2028-01-01 | 9:44 | 35040 | 79.1568 | 0.47494 | 15.6833 |  | 2007-01-01 | 9:44 | 35040 | 85.4903 | 0.51294 | 16.5622 |  | 2029-09-01 | 9:44 | 35040 | 217.564 | 1.3054 | 32.1519 |  | 2006-09-01 | 9:44 | 35040 | 211.094 | 1.2666 | 31.4186 |  | 2029-09-01 | 9:44 | 35040 | 96.8398 | 0.58104 | 17.7289 |  | 2006-09-01 | 9:44 | 35040 | 70.3928 | 0.42236 | 14.7542 |  | 2028-01-01 | 9:44 | 35040 | 212.827 | 1.277 | 31.639 |  | 2007-01-01 | 9:44 | 35040 | 209.763 | 1.2586 | 31.3287 |  | 2028-01-01 | 9:44 | 35040 | 45.2074 | 0.27124 | 10.0859 |  | 2007-01-01 | 9:44 | 35040 | 50.0743 | 0.30045 | 10.9079 |  | 2029-09-01 | 9:44 | 35040 | 217.564 | 1.3054 | 32.1519 |  | 2006-09-01 | 9:44 | 35040 | 211.094 | 1.2666 | 31.4186 |  | 2029-09-01 | 9:44 | 35040 | 73.1487 | 0.43889 | 14.2175 |  | 2006-09-01 | 9:44 | 35040 | 50.0675 | 0.3004 | 11.4047 |  | 2028-01-01 | 9:44 | 35040 | 212.827 | 1.277 | 31.639 |  | 2007-01-01 | 9:44 | 35040 | 209.763 | 1.2586 | 31.3287 |  | 2028-01-01 | 9:44 | 35040 | 31.3182 | 0.18791 | 7.3693 |  | 2007-01-01 | 9:44 | 35040 | 34.9736 | 0.20984 | 8.0547 |  | 2029-09-01 | 9:44 | 35040 | 95.5753 | 0.57345 | 18.0578 |  | 2029-09-01 | 9:44 | 35040 | 65.246 | 0.39148 | 13.5544 |  | 2029-09-01 | 9:44 | 35040 | 43.6596 | 0.26196 | 9.8112 |  | 2006-09-01 | 9:44 | 35040 | 43.2776 | 0.25967 | 9.7214 |  | 2028-01-01 | 9:44 | 35040 | 79.1568 | 0.47494 | 15.6833 |  | 2007-01-01 | 9:44 | 35040 | 85.4903 | 0.51294 | 16.5622 |  | 2028-01-01 | 9:44 | 35040 | 38.0431 | 0.22826 | 8.7232 |  | 2007-01-01 | 9:44 | 35040 | 39.6068 | 0.23764 | 9.007
| 2029-09-01 | 9:45 | 35100 | 221.158 | 1.3269 | 33.4788 |  | 2029-09-01 | 9:45 | 35100 | 221.158 | 1.3269 | 33.4788 |  | 2006-09-01 | 9:45 | 35100 | 214.517 | 1.2871 | 32.7057 |  | 2029-09-01 | 9:45 | 35100 | 139.444 | 0.83666 | 23.9817 |  | 2006-09-01 | 9:45 | 35100 | 112.374 | 0.67424 | 21.1573 |  | 2028-01-01 | 9:45 | 35100 | 216.274 | 1.2976 | 32.9367 |  | 2007-01-01 | 9:45 | 35100 | 213.1 | 1.2786 | 32.6073 |  | 2028-01-01 | 9:45 | 35100 | 79.3644 | 0.47619 | 16.1594 |  | 2007-01-01 | 9:45 | 35100 | 85.7902 | 0.51474 | 17.0769 |  | 2029-09-01 | 9:45 | 35100 | 221.158 | 1.3269 | 33.4788 |  | 2006-09-01 | 9:45 | 35100 | 214.517 | 1.2871 | 32.7057 |  | 2029-09-01 | 9:45 | 35100 | 97.5512 | 0.58531 | 18.3142 |  | 2006-09-01 | 9:45 | 35100 | 70.3467 | 0.42208 | 15.1762 |  | 2028-01-01 | 9:45 | 35100 | 216.274 | 1.2976 | 32.9367 |  | 2007-01-01 | 9:45 | 35100 | 213.1 | 1.2786 | 32.6073 |  | 2028-01-01 | 9:45 | 35100 | 45.2232 | 0.27134 | 10.3572 |  | 2007-01-01 | 9:45 | 35100 | 50.1247 | 0.30075 | 11.2087 |  | 2029-09-01 | 9:45 | 35100 | 221.158 | 1.3269 | 33.4788 |  | 2006-09-01 | 9:45 | 35100 | 214.517 | 1.2871 | 32.7057 |  | 2029-09-01 | 9:45 | 35100 | 73.592 | 0.44155 | 14.659 |  | 2006-09-01 | 9:45 | 35100 | 49.9425 | 0.29966 | 11.7044 |  | 2028-01-01 | 9:45 | 35100 | 216.274 | 1.2976 | 32.9367 |  | 2007-01-01 | 9:45 | 35100 | 213.1 | 1.2786 | 32.6073 |  | 2028-01-01 | 9:45 | 35100 | 31.3198 | 0.18792 | 7.5573 |  | 2007-01-01 | 9:45 | 35100 | 34.9952 | 0.20997 | 8.2647 |  | 2029-09-01 | 9:45 | 35100 | 95.9627 | 0.57578 | 18.6336 |  | 2029-09-01 | 9:45 | 35100 | 65.3331 | 0.392 | 13.9464 |  | 2029-09-01 | 9:45 | 35100 | 43.6683 | 0.26201 | 10.0732 |  | 2006-09-01 | 9:45 | 35100 | 43.2911 | 0.25975 | 9.9812 |  | 2028-01-01 | 9:45 | 35100 | 79.3644 | 0.47619 | 16.1594 |  | 2007-01-01 | 9:45 | 35100 | 85.7902 | 0.51474 | 17.0769 |  | 2028-01-01 | 9:45 | 35100 | 38.0487 | 0.22829 | 8.9515 |  | 2007-01-01 | 9:45 | 35100 | 39.6205 | 0.23772 | 9.2447
| 2029-09-01 | 9:46 | 35160 | 224.702 | 1.3482 | 34.827 |  | 2029-09-01 | 9:46 | 35160 | 224.702 | 1.3482 | 34.827 |  | 2006-09-01 | 9:46 | 35160 | 217.892 | 1.3074 | 34.013 |  | 2029-09-01 | 9:46 | 35160 | 140.839 | 0.84503 | 24.8268 |  | 2006-09-01 | 9:46 | 35160 | 112.834 | 0.677 | 21.8343 |  | 2028-01-01 | 9:46 | 35160 | 219.671 | 1.318 | 34.2547 |  | 2007-01-01 | 9:46 | 35160 | 216.387 | 1.2983 | 33.9057 |  | 2028-01-01 | 9:46 | 35160 | 79.5569 | 0.47734 | 16.6368 |  | 2007-01-01 | 9:46 | 35160 | 86.0722 | 0.51643 | 17.5934 |  | 2029-09-01 | 9:46 | 35160 | 224.702 | 1.3482 | 34.827 |  | 2006-09-01 | 9:46 | 35160 | 217.892 | 1.3074 | 34.013 |  | 2029-09-01 | 9:46 | 35160 | 98.2501 | 0.5895 | 18.9037 |  | 2006-09-01 | 9:46 | 35160 | 70.288 | 0.42173 | 15.598 |  | 2028-01-01 | 9:46 | 35160 | 219.671 | 1.318 | 34.2547 |  | 2007-01-01 | 9:46 | 35160 | 216.387 | 1.2983 | 33.9057 |  | 2028-01-01 | 9:46 | 35160 | 45.2371 | 0.27142 | 10.6287 |  | 2007-01-01 | 9:46 | 35160 | 50.1723 | 0.30103 | 11.5097 |  | 2029-09-01 | 9:46 | 35160 | 224.702 | 1.3482 | 34.827 |  | 2006-09-01 | 9:46 | 35160 | 217.892 | 1.3074 | 34.013 |  | 2029-09-01 | 9:46 | 35160 | 74.0325 | 0.4442 | 15.1032 |  | 2006-09-01 | 9:46 | 35160 | 49.8146 | 0.29889 | 12.0033 |  | 2028-01-01 | 9:46 | 35160 | 219.671 | 1.318 | 34.2547 |  | 2007-01-01 | 9:46 | 35160 | 216.387 | 1.2983 | 33.9057 |  | 2028-01-01 | 9:46 | 35160 | 31.3211 | 0.18793 | 7.7452 |  | 2007-01-01 | 9:46 | 35160 | 35.0165 | 0.2101 | 8.4748 |  | 2029-09-01 | 9:46 | 35160 | 96.3258 | 0.57795 | 19.2116 |  | 2029-09-01 | 9:46 | 35160 | 65.4118 | 0.39247 | 14.3389 |  | 2029-09-01 | 9:46 | 35160 | 43.6754 | 0.26205 | 10.3353 |  | 2006-09-01 | 9:46 | 35160 | 43.3031 | 0.25982 | 10.241 |  | 2028-01-01 | 9:46 | 35160 | 79.5569 | 0.47734 | 16.6368 |  | 2007-01-01 | 9:46 | 35160 | 86.0722 | 0.51643 | 17.5934 |  | 2028-01-01 | 9:46 | 35160 | 38.0536 | 0.22832 | 9.1799 |  | 2007-01-01 | 9:46 | 35160 | 39.6334 | 0.2378 | 9.4825
| 2029-09-01 | 9:47 | 35220 | 228.196 | 1.3692 | 36.1962 |  | 2029-09-01 | 9:47 | 35220 | 228.196 | 1.3692 | 36.1962 |  | 2006-09-01 | 9:47 | 35220 | 221.22 | 1.3273 | 35.3403 |  | 2029-09-01 | 9:47 | 35220 | 142.204 | 0.85322 | 25.68 |  | 2006-09-01 | 9:47 | 35220 | 113.258 | 0.67955 | 22.5138 |  | 2028-01-01 | 9:47 | 35220 | 223.02 | 1.3381 | 35.5928 |  | 2007-01-01 | 9:47 | 35220 | 219.624 | 1.3177 | 35.2234 |  | 2028-01-01 | 9:47 | 35220 | 79.7353 | 0.47841 | 17.1152 |  | 2007-01-01 | 9:47 | 35220 | 86.3375 | 0.51803 | 18.1114 |  | 2029-09-01 | 9:47 | 35220 | 228.196 | 1.3692 | 36.1962 |  | 2006-09-01 | 9:47 | 35220 | 221.22 | 1.3273 | 35.3403 |  | 2029-09-01 | 9:47 | 35220 | 98.9377 | 0.59363 | 19.4973 |  | 2006-09-01 | 9:47 | 35220 | 70.2179 | 0.42131 | 16.0193 |  | 2028-01-01 | 9:47 | 35220 | 223.02 | 1.3381 | 35.5928 |  | 2007-01-01 | 9:47 | 35220 | 219.624 | 1.3177 | 35.2234 |  | 2028-01-01 | 9:47 | 35220 | 45.2492 | 0.2715 | 10.9002 |  | 2007-01-01 | 9:47 | 35220 | 50.2173 | 0.3013 | 11.811 |  | 2029-09-01 | 9:47 | 35220 | 228.196 | 1.3692 | 36.1962 |  | 2006-09-01 | 9:47 | 35220 | 221.22 | 1.3273 | 35.3403 |  | 2029-09-01 | 9:47 | 35220 | 74.4708 | 0.44682 | 15.55 |  | 2006-09-01 | 9:47 | 35220 | 49.6844 | 0.29811 | 12.3014 |  | 2028-01-01 | 9:47 | 35220 | 223.02 | 1.3381 | 35.5928 |  | 2007-01-01 | 9:47 | 35220 | 219.624 | 1.3177 | 35.2234 |  | 2028-01-01 | 9:47 | 35220 | 31.3223 | 0.18793 | 7.9331 |  | 2007-01-01 | 9:47 | 35220 | 35.0374 | 0.21022 | 8.685 |  | 2029-09-01 | 9:47 | 35220 | 96.666 | 0.58 | 19.7916 |  | 2029-09-01 | 9:47 | 35220 | 65.4827 | 0.3929 | 14.7318 |  | 2029-09-01 | 9:47 | 35220 | 43.6811 | 0.26209 | 10.5973 |  | 2006-09-01 | 9:47 | 35220 | 43.3138 | 0.25988 | 10.5009 |  | 2028-01-01 | 9:47 | 35220 | 79.7353 | 0.47841 | 17.1152 |  | 2007-01-01 | 9:47 | 35220 | 86.3375 | 0.51803 | 18.1114 |  | 2028-01-01 | 9:47 | 35220 | 38.0578 | 0.22835 | 9.4082 |  | 2007-01-01 | 9:47 | 35220 | 39.6454 | 0.23787 | 9.7204
| 2029-09-01 | 9:48 | 35280 | 231.643 | 1.3899 | 37.5861 |  | 2029-09-01 | 9:48 | 35280 | 231.643 | 1.3899 | 37.5861 |  | 2006-09-01 | 9:48 | 35280 | 224.502 | 1.347 | 36.6874 |  | 2029-09-01 | 9:48 | 35280 | 143.541 | 0.86125 | 26.5412 |  | 2006-09-01 | 9:48 | 35280 | 113.648 | 0.68189 | 23.1957 |  | 2028-01-01 | 9:48 | 35280 | 226.32 | 1.3579 | 36.9507 |  | 2007-01-01 | 9:48 | 35280 | 222.811 | 1.3369 | 36.5603 |  | 2028-01-01 | 9:48 | 35280 | 79.9006 | 0.4794 | 17.5946 |  | 2007-01-01 | 9:48 | 35280 | 86.5872 | 0.51952 | 18.6309 |  | 2029-09-01 | 9:48 | 35280 | 231.643 | 1.3899 | 37.5861 |  | 2006-09-01 | 9:48 | 35280 | 224.502 | 1.347 | 36.6874 |  | 2029-09-01 | 9:48 | 35280 | 99.6153 | 0.59769 | 20.095 |  | 2006-09-01 | 9:48 | 35280 | 70.1376 | 0.42083 | 16.4401 |  | 2028-01-01 | 9:48 | 35280 | 226.32 | 1.3579 | 36.9507 |  | 2007-01-01 | 9:48 | 35280 | 222.811 | 1.3369 | 36.5603 |  | 2028-01-01 | 9:48 | 35280 | 45.26 | 0.27156 | 11.1717 |  | 2007-01-01 | 9:48 | 35280 | 50.2602 | 0.30156 | 12.1125 |  | 2029-09-01 | 9:48 | 35280 | 231.643 | 1.3899 | 37.5861 |  | 2006-09-01 | 9:48 | 35280 | 224.502 | 1.347 | 36.6874 |  | 2029-09-01 | 9:48 | 35280 | 74.9078 | 0.44945 | 15.9995 |  | 2006-09-01 | 9:48 | 35280 | 49.5523 | 0.29731 | 12.5987 |  | 2028-01-01 | 9:48 | 35280 | 226.32 | 1.3579 | 36.9507 |  | 2007-01-01 | 9:48 | 35280 | 222.811 | 1.3369 | 36.5603 |  | 2028-01-01 | 9:48 | 35280 | 31.3234 | 0.18794 | 8.1211 |  | 2007-01-01 | 9:48 | 35280 | 35.058 | 0.21035 | 8.8953 |  | 2029-09-01 | 9:48 | 35280 | 96.9848 | 0.58191 | 20.3735 |  | 2029-09-01 | 9:48 | 35280 | 65.5466 | 0.39328 | 15.1251 |  | 2029-09-01 | 9:48 | 35280 | 43.6857 | 0.26211 | 10.8595 |  | 2006-09-01 | 9:48 | 35280 | 43.3233 | 0.25994 | 10.7608 |  | 2028-01-01 | 9:48 | 35280 | 79.9006 | 0.4794 | 17.5946 |  | 2007-01-01 | 9:48 | 35280 | 86.5872 | 0.51952 | 18.6309 |  | 2028-01-01 | 9:48 | 35280 | 38.0614 | 0.22837 | 9.6366 |  | 2007-01-01 | 9:48 | 35280 | 39.6568 | 0.23794 | 9.9584
| 2029-09-01 | 9:49 | 35340 | 235.042 | 1.4103 | 38.9963 |  | 2029-09-01 | 9:49 | 35340 | 235.042 | 1.4103 | 38.9963 |  | 2006-09-01 | 9:49 | 35340 | 227.738 | 1.3664 | 38.0538 |  | 2029-09-01 | 9:49 | 35340 | 144.852 | 0.86911 | 27.4103 |  | 2006-09-01 | 9:49 | 35340 | 114.006 | 0.68404 | 23.8798 |  | 2028-01-01 | 9:49 | 35340 | 229.573 | 1.3774 | 38.3282 |  | 2007-01-01 | 9:49 | 35340 | 225.951 | 1.3557 | 37.916 |  | 2028-01-01 | 9:49 | 35340 | 80.0539 | 0.48032 | 18.0749 |  | 2007-01-01 | 9:49 | 35340 | 86.8225 | 0.52094 | 19.1518 |  | 2029-09-01 | 9:49 | 35340 | 235.042 | 1.4103 | 38.9963 |  | 2006-09-01 | 9:49 | 35340 | 227.738 | 1.3664 | 38.0538 |  | 2029-09-01 | 9:49 | 35340 | 100.284 | 0.6017 | 20.6967 |  | 2006-09-01 | 9:49 | 35340 | 70.0481 | 0.42029 | 16.8604 |  | 2028-01-01 | 9:49 | 35340 | 229.573 | 1.3774 | 38.3282 |  | 2007-01-01 | 9:49 | 35340 | 225.951 | 1.3557 | 37.916 |  | 2028-01-01 | 9:49 | 35340 | 45.2694 | 0.27162 | 11.4433 |  | 2007-01-01 | 9:49 | 35340 | 50.301 | 0.30181 | 12.4144 |  | 2029-09-01 | 9:49 | 35340 | 235.042 | 1.4103 | 38.9963 |  | 2006-09-01 | 9:49 | 35340 | 227.738 | 1.3664 | 38.0538 |  | 2029-09-01 | 9:49 | 35340 | 75.3442 | 0.45207 | 16.4516 |  | 2006-09-01 | 9:49 | 35340 | 49.4188 | 0.29651 | 12.8952 |  | 2028-01-01 | 9:49 | 35340 | 229.573 | 1.3774 | 38.3282 |  | 2007-01-01 | 9:49 | 35340 | 225.951 | 1.3557 | 37.916 |  | 2028-01-01 | 9:49 | 35340 | 31.3243 | 0.18795 | 8.309 |  | 2007-01-01 | 9:49 | 35340 | 35.0784 | 0.21047 | 9.1058 |  | 2029-09-01 | 9:49 | 35340 | 97.2834 | 0.5837 | 20.9572 |  | 2029-09-01 | 9:49 | 35340 | 65.6042 | 0.39363 | 15.5187 |  | 2029-09-01 | 9:49 | 35340 | 43.6893 | 0.26214 | 11.1216 |  | 2006-09-01 | 9:49 | 35340 | 43.3318 | 0.25999 | 11.0208 |  | 2028-01-01 | 9:49 | 35340 | 80.0539 | 0.48032 | 18.0749 |  | 2007-01-01 | 9:49 | 35340 | 86.8225 | 0.52094 | 19.1518 |  | 2028-01-01 | 9:49 | 35340 | 38.0646 | 0.22839 | 9.865 |  | 2007-01-01 | 9:49 | 35340 | 39.6676 | 0.23801 | 10.1964
| 2029-09-01 | 9:50 | 35400 | 238.394 | 1.4304 | 40.4267 |  | 2029-09-01 | 9:50 | 35400 | 238.394 | 1.4304 | 40.4267 |  | 2006-09-01 | 9:50 | 35400 | 230.93 | 1.3856 | 39.4394 |  | 2029-09-01 | 9:50 | 35400 | 146.137 | 0.87682 | 28.2872 |  | 2006-09-01 | 9:50 | 35400 | 114.335 | 0.68601 | 24.5658 |  | 2028-01-01 | 9:50 | 35400 | 232.779 | 1.3967 | 39.7248 |  | 2007-01-01 | 9:50 | 35400 | 229.042 | 1.3743 | 39.2902 |  | 2028-01-01 | 9:50 | 35400 | 80.1959 | 0.48118 | 18.5561 |  | 2007-01-01 | 9:50 | 35400 | 87.0442 | 0.52227 | 19.6741 |  | 2029-09-01 | 9:50 | 35400 | 238.394 | 1.4304 | 40.4267 |  | 2006-09-01 | 9:50 | 35400 | 230.93 | 1.3856 | 39.4394 |  | 2029-09-01 | 9:50 | 35400 | 100.945 | 0.60567 | 21.3024 |  | 2006-09-01 | 9:50 | 35400 | 69.9503 | 0.4197 | 17.2801 |  | 2028-01-01 | 9:50 | 35400 | 232.779 | 1.3967 | 39.7248 |  | 2007-01-01 | 9:50 | 35400 | 229.042 | 1.3743 | 39.2902 |  | 2028-01-01 | 9:50 | 35400 | 45.2778 | 0.27167 | 11.715 |  | 2007-01-01 | 9:50 | 35400 | 50.3402 | 0.30204 | 12.7164 |  | 2029-09-01 | 9:50 | 35400 | 238.394 | 1.4304 | 40.4267 |  | 2006-09-01 | 9:50 | 35400 | 230.93 | 1.3856 | 39.4394 |  | 2029-09-01 | 9:50 | 35400 | 75.7806 | 0.45468 | 16.9062 |  | 2006-09-01 | 9:50 | 35400 | 49.2842 | 0.29571 | 13.1909 |  | 2028-01-01 | 9:50 | 35400 | 232.779 | 1.3967 | 39.7248 |  | 2007-01-01 | 9:50 | 35400 | 229.042 | 1.3743 | 39.2902 |  | 2028-01-01 | 9:50 | 35400 | 31.3251 | 0.18795 | 8.497 |  | 2007-01-01 | 9:50 | 35400 | 35.0987 | 0.21059 | 9.3164 |  | 2029-09-01 | 9:50 | 35400 | 97.5631 | 0.58538 | 21.5425 |  | 2029-09-01 | 9:50 | 35400 | 65.6561 | 0.39394 | 15.9126 |  | 2029-09-01 | 9:50 | 35400 | 43.6921 | 0.26215 | 11.3838 |  | 2006-09-01 | 9:50 | 35400 | 43.3395 | 0.26004 | 11.2808 |  | 2028-01-01 | 9:50 | 35400 | 80.1959 | 0.48118 | 18.5561 |  | 2007-01-01 | 9:50 | 35400 | 87.0442 | 0.52227 | 19.6741 |  | 2028-01-01 | 9:50 | 35400 | 38.0673 | 0.2284 | 10.0934 |  | 2007-01-01 | 9:50 | 35400 | 39.6778 | 0.23807 | 10.4344
| 2029-09-01 | 9:51 | 35460 | 241.699 | 1.4502 | 41.8769 |  | 2029-09-01 | 9:51 | 35460 | 241.699 | 1.4502 | 41.8769 |  | 2006-09-01 | 9:51 | 35460 | 234.077 | 1.4045 | 40.8438 |  | 2029-09-01 | 9:51 | 35460 | 147.398 | 0.88439 | 29.1716 |  | 2006-09-01 | 9:51 | 35460 | 114.634 | 0.6878 | 25.2536 |  | 2028-01-01 | 9:51 | 35460 | 235.939 | 1.4156 | 41.1405 |  | 2007-01-01 | 9:51 | 35460 | 232.086 | 1.3925 | 40.6827 |  | 2028-01-01 | 9:51 | 35460 | 80.3276 | 0.48197 | 19.0381 |  | 2007-01-01 | 9:51 | 35460 | 87.2534 | 0.52352 | 20.1976 |  | 2029-09-01 | 9:51 | 35460 | 241.699 | 1.4502 | 41.8769 |  | 2006-09-01 | 9:51 | 35460 | 234.077 | 1.4045 | 40.8438 |  | 2029-09-01 | 9:51 | 35460 | 101.599 | 0.60959 | 21.912 |  | 2006-09-01 | 9:51 | 35460 | 69.8453 | 0.41907 | 17.6992 |  | 2028-01-01 | 9:51 | 35460 | 235.939 | 1.4156 | 41.1405 |  | 2007-01-01 | 9:51 | 35460 | 232.086 | 1.3925 | 40.6827 |  | 2028-01-01 | 9:51 | 35460 | 45.2851 | 0.27171 | 11.9867 |  | 2007-01-01 | 9:51 | 35460 | 50.3778 | 0.30227 | 13.0187 |  | 2029-09-01 | 9:51 | 35460 | 241.699 | 1.4502 | 41.8769 |  | 2006-09-01 | 9:51 | 35460 | 234.077 | 1.4045 | 40.8438 |  | 2029-09-01 | 9:51 | 35460 | 76.2177 | 0.45731 | 17.3635 |  | 2006-09-01 | 9:51 | 35460 | 49.1488 | 0.29489 | 13.4858 |  | 2028-01-01 | 9:51 | 35460 | 235.939 | 1.4156 | 41.1405 |  | 2007-01-01 | 9:51 | 35460 | 232.086 | 1.3925 | 40.6827 |  | 2028-01-01 | 9:51 | 35460 | 31.3258 | 0.18795 | 8.6849 |  | 2007-01-01 | 9:51 | 35460 | 35.1187 | 0.21071 | 9.5271 |  | 2029-09-01 | 9:51 | 35460 | 97.8251 | 0.58695 | 22.1295 |  | 2029-09-01 | 9:51 | 35460 | 65.7027 | 0.39422 | 16.3068 |  | 2029-09-01 | 9:51 | 35460 | 43.6941 | 0.26216 | 11.6459 |  | 2006-09-01 | 9:51 | 35460 | 43.3463 | 0.26008 | 11.5409 |  | 2028-01-01 | 9:51 | 35460 | 80.3276 | 0.48197 | 19.0381 |  | 2007-01-01 | 9:51 | 35460 | 87.2534 | 0.52352 | 20.1976 |  | 2028-01-01 | 9:51 | 35460 | 38.0698 | 0.22842 | 10.3218 |  | 2007-01-01 | 9:51 | 35460 | 39.6877 | 0.23813 | 10.6726
| 2029-09-01 | 9:52 | 35520 | 244.959 | 1.4698 | 43.3466 |  | 2029-09-01 | 9:52 | 35520 | 244.959 | 1.4698 | 43.3466 |  | 2006-09-01 | 9:52 | 35520 | 237.181 | 1.4231 | 42.2669 |  | 2029-09-01 | 9:52 | 35520 | 148.636 | 0.89182 | 30.0634 |  | 2006-09-01 | 9:52 | 35520 | 114.907 | 0.68944 | 25.943 |  | 2028-01-01 | 9:52 | 35520 | 239.053 | 1.4343 | 42.5748 |  | 2007-01-01 | 9:52 | 35520 | 235.084 | 1.4105 | 42.0932 |  | 2028-01-01 | 9:52 | 35520 | 80.4497 | 0.4827 | 19.5208 |  | 2007-01-01 | 9:52 | 35520 | 87.4509 | 0.52471 | 20.7223 |  | 2029-09-01 | 9:52 | 35520 | 244.959 | 1.4698 | 43.3466 |  | 2006-09-01 | 9:52 | 35520 | 237.181 | 1.4231 | 42.2669 |  | 2029-09-01 | 9:52 | 35520 | 102.247 | 0.61348 | 22.5255 |  | 2006-09-01 | 9:52 | 35520 | 69.7337 | 0.4184 | 18.1176 |  | 2028-01-01 | 9:52 | 35520 | 239.053 | 1.4343 | 42.5748 |  | 2007-01-01 | 9:52 | 35520 | 235.084 | 1.4105 | 42.0932 |  | 2028-01-01 | 9:52 | 35520 | 45.2917 | 0.27175 | 12.2585 |  | 2007-01-01 | 9:52 | 35520 | 50.414 | 0.30248 | 13.3211 |  | 2029-09-01 | 9:52 | 35520 | 244.959 | 1.4698 | 43.3466 |  | 2006-09-01 | 9:52 | 35520 | 237.181 | 1.4231 | 42.2669 |  | 2029-09-01 | 9:52 | 35520 | 76.6561 | 0.45994 | 17.8235 |  | 2006-09-01 | 9:52 | 35520 | 49.013 | 0.29408 | 13.7799 |  | 2028-01-01 | 9:52 | 35520 | 239.053 | 1.4343 | 42.5748 |  | 2007-01-01 | 9:52 | 35520 | 235.084 | 1.4105 | 42.0932 |  | 2028-01-01 | 9:52 | 35520 | 31.3265 | 0.18796 | 8.8729 |  | 2007-01-01 | 9:52 | 35520 | 35.1387 | 0.21083 | 9.7379 |  | 2029-09-01 | 9:52 | 35520 | 98.0704 | 0.58842 | 22.7179 |  | 2029-09-01 | 9:52 | 35520 | 65.7445 | 0.39447 | 16.7013 |  | 2029-09-01 | 9:52 | 35520 | 43.6956 | 0.26217 | 11.9081 |  | 2006-09-01 | 9:52 | 35520 | 43.3526 | 0.26012 | 11.801 |  | 2028-01-01 | 9:52 | 35520 | 80.4497 | 0.4827 | 19.5208 |  | 2007-01-01 | 9:52 | 35520 | 87.4509 | 0.52471 | 20.7223 |  | 2028-01-01 | 9:52 | 35520 | 38.0719 | 0.22843 | 10.5502 |  | 2007-01-01 | 9:52 | 35520 | 39.6972 | 0.23818 | 10.9107
| 2029-09-01 | 9:53 | 35580 | 248.173 | 1.489 | 44.8357 |  | 2029-09-01 | 9:53 | 35580 | 248.173 | 1.489 | 44.8357 |  | 2006-09-01 | 9:53 | 35580 | 240.242 | 1.4415 | 43.7084 |  | 2029-09-01 | 9:53 | 35580 | 149.854 | 0.89912 | 30.9625 |  | 2006-09-01 | 9:53 | 35580 | 115.154 | 0.69092 | 26.6339 |  | 2028-01-01 | 9:53 | 35580 | 242.123 | 1.4527 | 44.0275 |  | 2007-01-01 | 9:53 | 35580 | 238.036 | 1.4282 | 43.5215 |  | 2028-01-01 | 9:53 | 35580 | 80.5629 | 0.48338 | 20.0041 |  | 2007-01-01 | 9:53 | 35580 | 87.6375 | 0.52582 | 21.2482 |  | 2029-09-01 | 9:53 | 35580 | 248.173 | 1.489 | 44.8357 |  | 2006-09-01 | 9:53 | 35580 | 240.242 | 1.4415 | 43.7084 |  | 2029-09-01 | 9:53 | 35580 | 102.891 | 0.61735 | 23.1428 |  | 2006-09-01 | 9:53 | 35580 | 69.6164 | 0.4177 | 18.5353 |  | 2028-01-01 | 9:53 | 35580 | 242.123 | 1.4527 | 44.0275 |  | 2007-01-01 | 9:53 | 35580 | 238.036 | 1.4282 | 43.5215 |  | 2028-01-01 | 9:53 | 35580 | 45.2974 | 0.27178 | 12.5302 |  | 2007-01-01 | 9:53 | 35580 | 50.4491 | 0.30269 | 13.6238 |  | 2029-09-01 | 9:53 | 35580 | 248.173 | 1.489 | 44.8357 |  | 2006-09-01 | 9:53 | 35580 | 240.242 | 1.4415 | 43.7084 |  | 2029-09-01 | 9:53 | 35580 | 77.0962 | 0.46258 | 18.2861 |  | 2006-09-01 | 9:53 | 35580 | 48.8771 | 0.29326 | 14.0732 |  | 2028-01-01 | 9:53 | 35580 | 242.123 | 1.4527 | 44.0275 |  | 2007-01-01 | 9:53 | 35580 | 238.036 | 1.4282 | 43.5215 |  | 2028-01-01 | 9:53 | 35580 | 31.3271 | 0.18796 | 9.0608 |  | 2007-01-01 | 9:53 | 35580 | 35.1586 | 0.21095 | 9.9489 |  | 2029-09-01 | 9:53 | 35580 | 98.3001 | 0.5898 | 23.3077 |  | 2029-09-01 | 9:53 | 35580 | 65.7821 | 0.39469 | 17.096 |  | 2029-09-01 | 9:53 | 35580 | 43.6965 | 0.26218 | 12.1703 |  | 2006-09-01 | 9:53 | 35580 | 43.3582 | 0.26015 | 12.0612 |  | 2028-01-01 | 9:53 | 35580 | 80.5629 | 0.48338 | 20.0041 |  | 2007-01-01 | 9:53 | 35580 | 87.6375 | 0.52582 | 21.2482 |  | 2028-01-01 | 9:53 | 35580 | 38.0738 | 0.22844 | 10.7787 |  | 2007-01-01 | 9:53 | 35580 | 39.7063 | 0.23824 | 11.149
| 2029-09-01 | 9:54 | 35640 | 251.343 | 1.5081 | 46.3437 |  | 2029-09-01 | 9:54 | 35640 | 251.343 | 1.5081 | 46.3437 |  | 2006-09-01 | 9:54 | 35640 | 243.261 | 1.4596 | 45.1679 |  | 2029-09-01 | 9:54 | 35640 | 151.052 | 0.90631 | 31.8688 |  | 2006-09-01 | 9:54 | 35640 | 115.377 | 0.69226 | 27.3262 |  | 2028-01-01 | 9:54 | 35640 | 245.148 | 1.4709 | 45.4984 |  | 2007-01-01 | 9:54 | 35640 | 240.943 | 1.4457 | 44.9671 |  | 2028-01-01 | 9:54 | 35640 | 80.6679 | 0.48401 | 20.4882 |  | 2007-01-01 | 9:54 | 35640 | 87.814 | 0.52688 | 21.775 |  | 2029-09-01 | 9:54 | 35640 | 251.343 | 1.5081 | 46.3437 |  | 2006-09-01 | 9:54 | 35640 | 243.261 | 1.4596 | 45.1679 |  | 2029-09-01 | 9:54 | 35640 | 103.53 | 0.62118 | 23.764 |  | 2006-09-01 | 9:54 | 35640 | 69.4942 | 0.41697 | 18.9522 |  | 2028-01-01 | 9:54 | 35640 | 245.148 | 1.4709 | 45.4984 |  | 2007-01-01 | 9:54 | 35640 | 240.943 | 1.4457 | 44.9671 |  | 2028-01-01 | 9:54 | 35640 | 45.3026 | 0.27182 | 12.8021 |  | 2007-01-01 | 9:54 | 35640 | 50.4831 | 0.3029 | 13.9267 |  | 2029-09-01 | 9:54 | 35640 | 251.343 | 1.5081 | 46.3437 |  | 2006-09-01 | 9:54 | 35640 | 243.261 | 1.4596 | 45.1679 |  | 2029-09-01 | 9:54 | 35640 | 77.5388 | 0.46523 | 18.7513 |  | 2006-09-01 | 9:54 | 35640 | 48.7413 | 0.29245 | 14.3656 |  | 2028-01-01 | 9:54 | 35640 | 245.148 | 1.4709 | 45.4984 |  | 2007-01-01 | 9:54 | 35640 | 240.943 | 1.4457 | 44.9671 |  | 2028-01-01 | 9:54 | 35640 | 31.3276 | 0.18797 | 9.2488 |  | 2007-01-01 | 9:54 | 35640 | 35.1783 | 0.21107 | 10.16 |  | 2029-09-01 | 9:54 | 35640 | 98.5152 | 0.59109 | 23.8988 |  | 2029-09-01 | 9:54 | 35640 | 65.8158 | 0.39489 | 17.4909 |  | 2029-09-01 | 9:54 | 35640 | 43.6969 | 0.26218 | 12.4324 |  | 2006-09-01 | 9:54 | 35640 | 43.3634 | 0.26018 | 12.3213 |  | 2028-01-01 | 9:54 | 35640 | 80.6679 | 0.48401 | 20.4882 |  | 2007-01-01 | 9:54 | 35640 | 87.814 | 0.52688 | 21.775 |  | 2028-01-01 | 9:54 | 35640 | 38.0754 | 0.22845 | 11.0071 |  | 2007-01-01 | 9:54 | 35640 | 39.7152 | 0.23829 | 11.3873
| 2029-09-01 | 9:55 | 35700 | 254.469 | 1.5268 | 47.8705 |  | 2029-09-01 | 9:55 | 35700 | 254.469 | 1.5268 | 47.8705 |  | 2006-09-01 | 9:55 | 35700 | 246.239 | 1.4774 | 46.6454 |  | 2029-09-01 | 9:55 | 35700 | 152.231 | 0.91339 | 32.7822 |  | 2006-09-01 | 9:55 | 35700 | 115.579 | 0.69347 | 28.0197 |  | 2028-01-01 | 9:55 | 35700 | 248.13 | 1.4888 | 46.9872 |  | 2007-01-01 | 9:55 | 35700 | 243.806 | 1.4628 | 46.4299 |  | 2028-01-01 | 9:55 | 35700 | 80.7653 | 0.48459 | 20.9727 |  | 2007-01-01 | 9:55 | 35700 | 87.981 | 0.52789 | 22.3029 |  | 2029-09-01 | 9:55 | 35700 | 254.469 | 1.5268 | 47.8705 |  | 2006-09-01 | 9:55 | 35700 | 246.239 | 1.4774 | 46.6454 |  | 2029-09-01 | 9:55 | 35700 | 104.167 | 0.625 | 24.389 |  | 2006-09-01 | 9:55 | 35700 | 69.3677 | 0.41621 | 19.3684 |  | 2028-01-01 | 9:55 | 35700 | 248.13 | 1.4888 | 46.9872 |  | 2007-01-01 | 9:55 | 35700 | 243.806 | 1.4628 | 46.4299 |  | 2028-01-01 | 9:55 | 35700 | 45.3071 | 0.27184 | 13.0739 |  | 2007-01-01 | 9:55 | 35700 | 50.5162 | 0.3031 | 14.2298 |  | 2029-09-01 | 9:55 | 35700 | 254.469 | 1.5268 | 47.8705 |  | 2006-09-01 | 9:55 | 35700 | 246.239 | 1.4774 | 46.6454 |  | 2029-09-01 | 9:55 | 35700 | 77.9841 | 0.4679 | 19.2192 |  | 2006-09-01 | 9:55 | 35700 | 48.6058 | 0.29163 | 14.6572 |  | 2028-01-01 | 9:55 | 35700 | 248.13 | 1.4888 | 46.9872 |  | 2007-01-01 | 9:55 | 35700 | 243.806 | 1.4628 | 46.4299 |  | 2028-01-01 | 9:55 | 35700 | 31.3281 | 0.18797 | 9.4368 |  | 2007-01-01 | 9:55 | 35700 | 35.1981 | 0.21119 | 10.3711 |  | 2029-09-01 | 9:55 | 35700 | 98.7165 | 0.5923 | 24.4911 |  | 2029-09-01 | 9:55 | 35700 | 65.846 | 0.39508 | 17.886 |  | 2029-09-01 | 9:55 | 35700 | 43.697 | 0.26218 | 12.6946 |  | 2006-09-01 | 9:55 | 35700 | 43.3681 | 0.26021 | 12.5816 |  | 2028-01-01 | 9:55 | 35700 | 80.7653 | 0.48459 | 20.9727 |  | 2007-01-01 | 9:55 | 35700 | 87.981 | 0.52789 | 22.3029 |  | 2028-01-01 | 9:55 | 35700 | 38.0769 | 0.22846 | 11.2356 |  | 2007-01-01 | 9:55 | 35700 | 39.7239 | 0.23834 | 11.6256
| 2029-09-01 | 9:56 | 35760 | 257.551 | 1.5453 | 49.4158 |  | 2029-09-01 | 9:56 | 35760 | 257.551 | 1.5453 | 49.4158 |  | 2006-09-01 | 9:56 | 35760 | 249.175 | 1.495 | 48.1404 |  | 2029-09-01 | 9:56 | 35760 | 153.393 | 0.92036 | 33.7026 |  | 2006-09-01 | 9:56 | 35760 | 115.759 | 0.69455 | 28.7142 |  | 2028-01-01 | 9:56 | 35760 | 251.069 | 1.5064 | 48.4936 |  | 2007-01-01 | 9:56 | 35760 | 246.624 | 1.4797 | 47.9097 |  | 2028-01-01 | 9:56 | 35760 | 80.8556 | 0.48513 | 21.4579 |  | 2007-01-01 | 9:56 | 35760 | 88.1392 | 0.52884 | 22.8318 |  | 2029-09-01 | 9:56 | 35760 | 257.551 | 1.5453 | 49.4158 |  | 2006-09-01 | 9:56 | 35760 | 249.175 | 1.495 | 48.1404 |  | 2029-09-01 | 9:56 | 35760 | 104.801 | 0.62881 | 25.0178 |  | 2006-09-01 | 9:56 | 35760 | 69.2377 | 0.41543 | 19.7839 |  | 2028-01-01 | 9:56 | 35760 | 251.069 | 1.5064 | 48.4936 |  | 2007-01-01 | 9:56 | 35760 | 246.624 | 1.4797 | 47.9097 |  | 2028-01-01 | 9:56 | 35760 | 45.3112 | 0.27187 | 13.3458 |  | 2007-01-01 | 9:56 | 35760 | 50.5485 | 0.30329 | 14.5331 |  | 2029-09-01 | 9:56 | 35760 | 257.551 | 1.5453 | 49.4158 |  | 2006-09-01 | 9:56 | 35760 | 249.175 | 1.495 | 48.1404 |  | 2029-09-01 | 9:56 | 35760 | 78.4328 | 0.4706 | 19.6898 |  | 2006-09-01 | 9:56 | 35760 | 48.4709 | 0.29083 | 14.9481 |  | 2028-01-01 | 9:56 | 35760 | 251.069 | 1.5064 | 48.4936 |  | 2007-01-01 | 9:56 | 35760 | 246.624 | 1.4797 | 47.9097 |  | 2028-01-01 | 9:56 | 35760 | 31.3286 | 0.18797 | 9.6247 |  | 2007-01-01 | 9:56 | 35760 | 35.2177 | 0.21131 | 10.5824 |  | 2029-09-01 | 9:56 | 35760 | 98.905 | 0.59343 | 25.0845 |  | 2029-09-01 | 9:56 | 35760 | 65.873 | 0.39524 | 18.2812 |  | 2029-09-01 | 9:56 | 35760 | 43.6968 | 0.26218 | 12.9568 |  | 2006-09-01 | 9:56 | 35760 | 43.3724 | 0.26023 | 12.8418 |  | 2028-01-01 | 9:56 | 35760 | 80.8556 | 0.48513 | 21.4579 |  | 2007-01-01 | 9:56 | 35760 | 88.1392 | 0.52884 | 22.8318 |  | 2028-01-01 | 9:56 | 35760 | 38.0782 | 0.22847 | 11.464 |  | 2007-01-01 | 9:56 | 35760 | 39.7323 | 0.23839 | 11.864
| 2029-09-01 | 9:57 | 35820 | 260.591 | 1.5635 | 50.9794 |  | 2029-09-01 | 9:57 | 35820 | 260.591 | 1.5635 | 50.9794 |  | 2006-09-01 | 9:57 | 35820 | 252.071 | 1.5124 | 49.6528 |  | 2029-09-01 | 9:57 | 35820 | 154.539 | 0.92723 | 34.6298 |  | 2006-09-01 | 9:57 | 35820 | 115.921 | 0.69553 | 29.4097 |  | 2028-01-01 | 9:57 | 35820 | 253.966 | 1.5238 | 50.0174 |  | 2007-01-01 | 9:57 | 35820 | 249.4 | 1.4964 | 49.4061 |  | 2028-01-01 | 9:57 | 35820 | 80.9393 | 0.48564 | 21.9435 |  | 2007-01-01 | 9:57 | 35820 | 88.2892 | 0.52974 | 23.3615 |  | 2029-09-01 | 9:57 | 35820 | 260.591 | 1.5635 | 50.9794 |  | 2006-09-01 | 9:57 | 35820 | 252.071 | 1.5124 | 49.6528 |  | 2029-09-01 | 9:57 | 35820 | 105.434 | 0.6326 | 25.6504 |  | 2006-09-01 | 9:57 | 35820 | 69.1049 | 0.41463 | 20.1985 |  | 2028-01-01 | 9:57 | 35820 | 253.966 | 1.5238 | 50.0174 |  | 2007-01-01 | 9:57 | 35820 | 249.4 | 1.4964 | 49.4061 |  | 2028-01-01 | 9:57 | 35820 | 45.3149 | 0.27189 | 13.6177 |  | 2007-01-01 | 9:57 | 35820 | 50.5801 | 0.30348 | 14.8366 |  | 2029-09-01 | 9:57 | 35820 | 260.591 | 1.5635 | 50.9794 |  | 2006-09-01 | 9:57 | 35820 | 252.071 | 1.5124 | 49.6528 |  | 2029-09-01 | 9:57 | 35820 | 78.8853 | 0.47331 | 20.1631 |  | 2006-09-01 | 9:57 | 35820 | 48.3368 | 0.29002 | 15.2381 |  | 2028-01-01 | 9:57 | 35820 | 253.966 | 1.5238 | 50.0174 |  | 2007-01-01 | 9:57 | 35820 | 249.4 | 1.4964 | 49.4061 |  | 2028-01-01 | 9:57 | 35820 | 31.3291 | 0.18797 | 9.8127 |  | 2007-01-01 | 9:57 | 35820 | 35.2374 | 0.21142 | 10.7939 |  | 2029-09-01 | 9:57 | 35820 | 99.0814 | 0.59449 | 25.679 |  | 2029-09-01 | 9:57 | 35820 | 65.8971 | 0.39538 | 18.6766 |  | 2029-09-01 | 9:57 | 35820 | 43.6963 | 0.26218 | 13.219 |  | 2006-09-01 | 9:57 | 35820 | 43.3764 | 0.26026 | 13.102 |  | 2028-01-01 | 9:57 | 35820 | 80.9393 | 0.48564 | 21.9435 |  | 2007-01-01 | 9:57 | 35820 | 88.2892 | 0.52974 | 23.3615 |  | 2028-01-01 | 9:57 | 35820 | 38.0794 | 0.22848 | 11.6925 |  | 2007-01-01 | 9:57 | 35820 | 39.7406 | 0.23844 | 12.1025
| 2029-09-01 | 9:58 | 35880 | 263.589 | 1.5815 | 52.5609 |  | 2029-09-01 | 9:58 | 35880 | 263.589 | 1.5815 | 52.5609 |  | 2006-09-01 | 9:58 | 35880 | 254.928 | 1.5296 | 51.1824 |  | 2029-09-01 | 9:58 | 35880 | 155.669 | 0.93401 | 35.5638 |  | 2006-09-01 | 9:58 | 35880 | 116.065 | 0.69639 | 30.1061 |  | 2028-01-01 | 9:58 | 35880 | 256.82 | 1.5409 | 51.5583 |  | 2007-01-01 | 9:58 | 35880 | 252.132 | 1.5128 | 50.9189 |  | 2028-01-01 | 9:58 | 35880 | 81.0171 | 0.4861 | 22.4296 |  | 2007-01-01 | 9:58 | 35880 | 88.4316 | 0.53059 | 23.8921 |  | 2029-09-01 | 9:58 | 35880 | 263.589 | 1.5815 | 52.5609 |  | 2006-09-01 | 9:58 | 35880 | 254.928 | 1.5296 | 51.1824 |  | 2029-09-01 | 9:58 | 35880 | 106.067 | 0.6364 | 26.2868 |  | 2006-09-01 | 9:58 | 35880 | 68.9702 | 0.41382 | 20.6123 |  | 2028-01-01 | 9:58 | 35880 | 256.82 | 1.5409 | 51.5583 |  | 2007-01-01 | 9:58 | 35880 | 252.132 | 1.5128 | 50.9189 |  | 2028-01-01 | 9:58 | 35880 | 45.3181 | 0.27191 | 13.8896 |  | 2007-01-01 | 9:58 | 35880 | 50.611 | 0.30367 | 15.1403 |  | 2029-09-01 | 9:58 | 35880 | 263.589 | 1.5815 | 52.5609 |  | 2006-09-01 | 9:58 | 35880 | 254.928 | 1.5296 | 51.1824 |  | 2029-09-01 | 9:58 | 35880 | 79.3421 | 0.47605 | 20.6392 |  | 2006-09-01 | 9:58 | 35880 | 48.2042 | 0.28923 | 15.5273 |  | 2028-01-01 | 9:58 | 35880 | 256.82 | 1.5409 | 51.5583 |  | 2007-01-01 | 9:58 | 35880 | 252.132 | 1.5128 | 50.9189 |  | 2028-01-01 | 9:58 | 35880 | 31.3295 | 0.18798 | 10.0007 |  | 2007-01-01 | 9:58 | 35880 | 35.257 | 0.21154 | 11.0054 |  | 2029-09-01 | 9:58 | 35880 | 99.2465 | 0.59548 | 26.2745 |  | 2029-09-01 | 9:58 | 35880 | 65.9186 | 0.39551 | 19.0721 |  | 2029-09-01 | 9:58 | 35880 | 43.6956 | 0.26217 | 13.4812 |  | 2006-09-01 | 9:58 | 35880 | 43.3801 | 0.26028 | 13.3623 |  | 2028-01-01 | 9:58 | 35880 | 81.0171 | 0.4861 | 22.4296 |  | 2007-01-01 | 9:58 | 35880 | 88.4316 | 0.53059 | 23.8921 |  | 2028-01-01 | 9:58 | 35880 | 38.0805 | 0.22848 | 11.921 |  | 2007-01-01 | 9:58 | 35880 | 39.7488 | 0.23849 | 12.3409
| 2029-09-01 | 9:59 | 35940 | 266.545 | 1.5993 | 54.1602 |  | 2029-09-01 | 9:59 | 35940 | 266.545 | 1.5993 | 54.1602 |  | 2006-09-01 | 9:59 | 35940 | 257.745 | 1.5465 | 52.7289 |  | 2029-09-01 | 9:59 | 35940 | 156.786 | 0.94072 | 36.5045 |  | 2006-09-01 | 9:59 | 35940 | 116.196 | 0.69718 | 30.8033 |  | 2028-01-01 | 9:59 | 35940 | 259.634 | 1.5578 | 53.1161 |  | 2007-01-01 | 9:59 | 35940 | 254.823 | 1.5289 | 52.4478 |  | 2028-01-01 | 9:59 | 35940 | 81.0892 | 0.48654 | 22.9161 |  | 2007-01-01 | 9:59 | 35940 | 88.5669 | 0.5314 | 24.4235 |  | 2029-09-01 | 9:59 | 35940 | 266.545 | 1.5993 | 54.1602 |  | 2006-09-01 | 9:59 | 35940 | 257.745 | 1.5465 | 52.7289 |  | 2029-09-01 | 9:59 | 35940 | 106.699 | 0.64019 | 26.927 |  | 2006-09-01 | 9:59 | 35940 | 68.8351 | 0.41301 | 21.0253 |  | 2028-01-01 | 9:59 | 35940 | 259.634 | 1.5578 | 53.1161 |  | 2007-01-01 | 9:59 | 35940 | 254.823 | 1.5289 | 52.4478 |  | 2028-01-01 | 9:59 | 35940 | 45.3211 | 0.27193 | 14.1615 |  | 2007-01-01 | 9:59 | 35940 | 50.6414 | 0.30385 | 15.4441 |  | 2029-09-01 | 9:59 | 35940 | 266.545 | 1.5993 | 54.1602 |  | 2006-09-01 | 9:59 | 35940 | 257.745 | 1.5465 | 52.7289 |  | 2029-09-01 | 9:59 | 35940 | 79.8035 | 0.47882 | 21.118 |  | 2006-09-01 | 9:59 | 35940 | 48.0736 | 0.28844 | 15.8158 |  | 2028-01-01 | 9:59 | 35940 | 259.634 | 1.5578 | 53.1161 |  | 2007-01-01 | 9:59 | 35940 | 254.823 | 1.5289 | 52.4478 |  | 2028-01-01 | 9:59 | 35940 | 31.3299 | 0.18798 | 10.1887 |  | 2007-01-01 | 9:59 | 35940 | 35.2766 | 0.21166 | 11.2171 |  | 2029-09-01 | 9:59 | 35940 | 99.401 | 0.59641 | 26.8709 |  | 2029-09-01 | 9:59 | 35940 | 65.9378 | 0.39563 | 19.4677 |  | 2029-09-01 | 9:59 | 35940 | 43.6947 | 0.26217 | 13.7433 |  | 2006-09-01 | 9:59 | 35940 | 43.3836 | 0.2603 | 13.6226 |  | 2028-01-01 | 9:59 | 35940 | 81.0892 | 0.48654 | 22.9161 |  | 2007-01-01 | 9:59 | 35940 | 88.5669 | 0.5314 | 24.4235 |  | 2028-01-01 | 9:59 | 35940 | 38.0815 | 0.22849 | 12.1495 |  | 2007-01-01 | 9:59 | 35940 | 39.7568 | 0.23854 | 12.5795
1 | 2029-09-01 | 10:00 | 36000 | 269.461 | 1.6168 | 55.777 |  | 2029-09-01 | 10:00 | 36000 | 269.461 | 1.6168 | 55.777 |  | 2006-09-01 | 10:00 | 36000 | 260.524 | 1.5631 | 54.292 |  | 2029-09-01 | 10:00 | 36000 | 157.889 | 0.94733 | 37.4519 |  | 2006-09-01 | 10:00 | 36000 | 116.312 | 0.69787 | 31.5012 |  | 2028-01-01 | 10:00 | 36000 | 262.407 | 1.5744 | 54.6906 |  | 2007-01-01 | 10:00 | 36000 | 257.473 | 1.5448 | 53.9927 |  | 2028-01-01 | 10:00 | 36000 | 81.1561 | 0.48694 | 23.4031 |  | 2007-01-01 | 10:00 | 36000 | 88.6955 | 0.53217 | 24.9557 |  | 2029-09-01 | 10:00 | 36000 | 269.461 | 1.6168 | 55.777 |  | 2006-09-01 | 10:00 | 36000 | 260.524 | 1.5631 | 54.292 |  | 2029-09-01 | 10:00 | 36000 | 107.332 | 0.64399 | 27.571 |  | 2006-09-01 | 10:00 | 36000 | 68.6993 | 0.4122 | 21.4375 |  | 2028-01-01 | 10:00 | 36000 | 262.407 | 1.5744 | 54.6906 |  | 2007-01-01 | 10:00 | 36000 | 257.473 | 1.5448 | 53.9927 |  | 2028-01-01 | 10:00 | 36000 | 45.3237 | 0.27194 | 14.4334 |  | 2007-01-01 | 10:00 | 36000 | 50.6714 | 0.30403 | 15.7482 |  | 2029-09-01 | 10:00 | 36000 | 269.461 | 1.6168 | 55.777 |  | 2006-09-01 | 10:00 | 36000 | 260.524 | 1.5631 | 54.292 |  | 2029-09-01 | 10:00 | 36000 | 80.2701 | 0.48162 | 21.5996 |  | 2006-09-01 | 10:00 | 36000 | 47.9446 | 0.28767 | 16.1034 |  | 2028-01-01 | 10:00 | 36000 | 262.407 | 1.5744 | 54.6906 |  | 2007-01-01 | 10:00 | 36000 | 257.473 | 1.5448 | 53.9927 |  | 2028-01-01 | 10:00 | 36000 | 31.3303 | 0.18798 | 10.3767 |  | 2007-01-01 | 10:00 | 36000 | 35.2962 | 0.21178 | 11.4289 |  | 2029-09-01 | 10:00 | 36000 | 99.5455 | 0.59727 | 27.4682 |  | 2029-09-01 | 10:00 | 36000 | 65.9549 | 0.39573 | 19.8635 |  | 2029-09-01 | 10:00 | 36000 | 43.6937 | 0.26216 | 14.0055 |  | 2006-09-01 | 10:00 | 36000 | 43.3868 | 0.26032 | 13.883 |  | 2028-01-01 | 10:00 | 36000 | 81.1561 | 0.48694 | 23.4031 |  | 2007-01-01 | 10:00 | 36000 | 88.6955 | 0.53217 | 24.9557 |  | 2028-01-01 | 10:00 | 36000 | 38.0824 | 0.22849 | 12.378 |  | 2007-01-01 | 10:00 | 36000 | 39.7647 | 0.23859 | 12.8181
| 2029-09-01 | 10:01 | 36060 | 272.336 | 1.634 | 57.411 |  | 2029-09-01 | 10:01 | 36060 | 272.336 | 1.634 | 57.411 |  | 2006-09-01 | 10:01 | 36060 | 263.255 | 1.5795 | 55.8716 |  | 2029-09-01 | 10:01 | 36060 | 158.982 | 0.95389 | 38.4057 |  | 2006-09-01 | 10:01 | 36060 | 116.405 | 0.69843 | 32.1996 |  | 2028-01-01 | 10:01 | 36060 | 265.145 | 1.5909 | 56.2815 |  | 2007-01-01 | 10:01 | 36060 | 260.082 | 1.5605 | 55.5532 |  | 2028-01-01 | 10:01 | 36060 | 81.2219 | 0.48733 | 23.8904 |  | 2007-01-01 | 10:01 | 36060 | 88.8124 | 0.53287 | 25.4885 |  | 2029-09-01 | 10:01 | 36060 | 272.336 | 1.634 | 57.411 |  | 2006-09-01 | 10:01 | 36060 | 263.255 | 1.5795 | 55.8716 |  | 2029-09-01 | 10:01 | 36060 | 107.967 | 0.6478 | 28.2188 |  | 2006-09-01 | 10:01 | 36060 | 68.5657 | 0.41139 | 21.8489 |  | 2028-01-01 | 10:01 | 36060 | 265.145 | 1.5909 | 56.2815 |  | 2007-01-01 | 10:01 | 36060 | 260.082 | 1.5605 | 55.5532 |  | 2028-01-01 | 10:01 | 36060 | 45.3293 | 0.27198 | 14.7054 |  | 2007-01-01 | 10:01 | 36060 | 50.6962 | 0.30418 | 16.0523 |  | 2029-09-01 | 10:01 | 36060 | 272.336 | 1.634 | 57.411 |  | 2006-09-01 | 10:01 | 36060 | 263.255 | 1.5795 | 55.8716 |  | 2029-09-01 | 10:01 | 36060 | 80.7425 | 0.48446 | 22.0841 |  | 2006-09-01 | 10:01 | 36060 | 47.8248 | 0.28695 | 16.3904 |  | 2028-01-01 | 10:01 | 36060 | 265.145 | 1.5909 | 56.2815 |  | 2007-01-01 | 10:01 | 36060 | 260.082 | 1.5605 | 55.5532 |  | 2028-01-01 | 10:01 | 36060 | 31.3336 | 0.188 | 10.5647 |  | 2007-01-01 | 10:01 | 36060 | 35.3117 | 0.21187 | 11.6407 |  | 2029-09-01 | 10:01 | 36060 | 99.6807 | 0.59808 | 28.0663 |  | 2029-09-01 | 10:01 | 36060 | 65.97 | 0.39582 | 20.2593 |  | 2029-09-01 | 10:01 | 36060 | 43.6925 | 0.26215 | 14.2676 |  | 2006-09-01 | 10:01 | 36060 | 43.3884 | 0.26033 | 14.1433 |  | 2028-01-01 | 10:01 | 36060 | 81.2219 | 0.48733 | 23.8904 |  | 2007-01-01 | 10:01 | 36060 | 88.8124 | 0.53287 | 25.4885 |  | 2028-01-01 | 10:01 | 36060 | 38.0848 | 0.22851 | 12.6065 |  | 2007-01-01 | 10:01 | 36060 | 39.7703 | 0.23862 | 13.0567
| 2029-09-01 | 10:02 | 36120 | 275.171 | 1.651 | 59.062 |  | 2029-09-01 | 10:02 | 36120 | 275.171 | 1.651 | 59.062 |  | 2006-09-01 | 10:02 | 36120 | 265.939 | 1.5956 | 57.4672 |  | 2029-09-01 | 10:02 | 36120 | 160.064 | 0.96038 | 39.3661 |  | 2006-09-01 | 10:02 | 36120 | 116.48 | 0.69888 | 32.8985 |  | 2028-01-01 | 10:02 | 36120 | 267.848 | 1.6071 | 57.8885 |  | 2007-01-01 | 10:02 | 36120 | 262.652 | 1.5759 | 57.1291 |  | 2028-01-01 | 10:02 | 36120 | 81.2867 | 0.48772 | 24.3781 |  | 2007-01-01 | 10:02 | 36120 | 88.9183 | 0.53351 | 26.022 |  | 2029-09-01 | 10:02 | 36120 | 275.171 | 1.651 | 59.062 |  | 2006-09-01 | 10:02 | 36120 | 265.939 | 1.5956 | 57.4672 |  | 2029-09-01 | 10:02 | 36120 | 108.604 | 0.65162 | 28.8704 |  | 2006-09-01 | 10:02 | 36120 | 68.4363 | 0.41062 | 22.2595 |  | 2028-01-01 | 10:02 | 36120 | 267.848 | 1.6071 | 57.8885 |  | 2007-01-01 | 10:02 | 36120 | 262.652 | 1.5759 | 57.1291 |  | 2028-01-01 | 10:02 | 36120 | 45.3375 | 0.27202 | 14.9774 |  | 2007-01-01 | 10:02 | 36120 | 50.7166 | 0.3043 | 16.3566 |  | 2029-09-01 | 10:02 | 36120 | 275.171 | 1.651 | 59.062 |  | 2006-09-01 | 10:02 | 36120 | 265.939 | 1.5956 | 57.4672 |  | 2029-09-01 | 10:02 | 36120 | 81.2209 | 0.48733 | 22.5714 |  | 2006-09-01 | 10:02 | 36120 | 47.7145 | 0.28629 | 16.6767 |  | 2028-01-01 | 10:02 | 36120 | 267.848 | 1.6071 | 57.8885 |  | 2007-01-01 | 10:02 | 36120 | 262.652 | 1.5759 | 57.1291 |  | 2028-01-01 | 10:02 | 36120 | 31.3394 | 0.18804 | 10.7527 |  | 2007-01-01 | 10:02 | 36120 | 35.3237 | 0.21194 | 11.8527 |  | 2029-09-01 | 10:02 | 36120 | 99.8069 | 0.59884 | 28.6651 |  | 2029-09-01 | 10:02 | 36120 | 65.9833 | 0.3959 | 20.6552 |  | 2029-09-01 | 10:02 | 36120 | 43.6912 | 0.26215 | 14.5298 |  | 2006-09-01 | 10:02 | 36120 | 43.3887 | 0.26033 | 14.4036 |  | 2028-01-01 | 10:02 | 36120 | 81.2867 | 0.48772 | 24.3781 |  | 2007-01-01 | 10:02 | 36120 | 88.9183 | 0.53351 | 26.022 |  | 2028-01-01 | 10:02 | 36120 | 38.0885 | 0.22853 | 12.835 |  | 2007-01-01 | 10:02 | 36120 | 39.7738 | 0.23864 | 13.2953
| 2029-09-01 | 10:03 | 36180 | 277.965 | 1.6678 | 60.7298 |  | 2029-09-01 | 10:03 | 36180 | 277.965 | 1.6678 | 60.7298 |  | 2006-09-01 | 10:03 | 36180 | 268.576 | 1.6115 | 59.0786 |  | 2029-09-01 | 10:03 | 36180 | 161.136 | 0.96682 | 40.3329 |  | 2006-09-01 | 10:03 | 36180 | 116.54 | 0.69924 | 33.5977 |  | 2028-01-01 | 10:03 | 36180 | 270.517 | 1.6231 | 59.5116 |  | 2007-01-01 | 10:03 | 36180 | 265.184 | 1.5911 | 58.7202 |  | 2028-01-01 | 10:03 | 36180 | 81.3506 | 0.4881 | 24.8662 |  | 2007-01-01 | 10:03 | 36180 | 89.0141 | 0.53408 | 26.5561 |  | 2029-09-01 | 10:03 | 36180 | 277.965 | 1.6678 | 60.7298 |  | 2006-09-01 | 10:03 | 36180 | 268.576 | 1.6115 | 59.0786 |  | 2029-09-01 | 10:03 | 36180 | 109.244 | 0.65546 | 29.5259 |  | 2006-09-01 | 10:03 | 36180 | 68.3123 | 0.40987 | 22.6694 |  | 2028-01-01 | 10:03 | 36180 | 270.517 | 1.6231 | 59.5116 |  | 2007-01-01 | 10:03 | 36180 | 265.184 | 1.5911 | 58.7202 |  | 2028-01-01 | 10:03 | 36180 | 45.348 | 0.27209 | 15.2495 |  | 2007-01-01 | 10:03 | 36180 | 50.7331 | 0.3044 | 16.661 |  | 2029-09-01 | 10:03 | 36180 | 277.965 | 1.6678 | 60.7298 |  | 2006-09-01 | 10:03 | 36180 | 268.576 | 1.6115 | 59.0786 |  | 2029-09-01 | 10:03 | 36180 | 81.706 | 0.49024 | 23.0616 |  | 2006-09-01 | 10:03 | 36180 | 47.6136 | 0.28568 | 16.9623 |  | 2028-01-01 | 10:03 | 36180 | 270.517 | 1.6231 | 59.5116 |  | 2007-01-01 | 10:03 | 36180 | 265.184 | 1.5911 | 58.7202 |  | 2028-01-01 | 10:03 | 36180 | 31.3471 | 0.18808 | 10.9408 |  | 2007-01-01 | 10:03 | 36180 | 35.3327 | 0.212 | 12.0647 |  | 2029-09-01 | 10:03 | 36180 | 99.9248 | 0.59955 | 29.2647 |  | 2029-09-01 | 10:03 | 36180 | 65.9949 | 0.39597 | 21.0512 |  | 2029-09-01 | 10:03 | 36180 | 43.6898 | 0.26214 | 14.7919 |  | 2006-09-01 | 10:03 | 36180 | 43.3876 | 0.26033 | 14.6639 |  | 2028-01-01 | 10:03 | 36180 | 81.3506 | 0.4881 | 24.8662 |  | 2007-01-01 | 10:03 | 36180 | 89.0141 | 0.53408 | 26.5561 |  | 2028-01-01 | 10:03 | 36180 | 38.0933 | 0.22856 | 13.0636 |  | 2007-01-01 | 10:03 | 36180 | 39.7755 | 0.23865 | 13.534
| 2029-09-01 | 10:04 | 36240 | 280.721 | 1.6843 | 62.4141 |  | 2029-09-01 | 10:04 | 36240 | 280.721 | 1.6843 | 62.4141 |  | 2006-09-01 | 10:04 | 36240 | 271.166 | 1.627 | 60.7056 |  | 2029-09-01 | 10:04 | 36240 | 162.199 | 0.97319 | 41.3061 |  | 2006-09-01 | 10:04 | 36240 | 116.587 | 0.69952 | 34.2973 |  | 2028-01-01 | 10:04 | 36240 | 273.152 | 1.6389 | 61.1506 |  | 2007-01-01 | 10:04 | 36240 | 267.677 | 1.6061 | 60.3262 |  | 2028-01-01 | 10:04 | 36240 | 81.4136 | 0.48848 | 25.3547 |  | 2007-01-01 | 10:04 | 36240 | 89.1003 | 0.5346 | 27.0907 |  | 2029-09-01 | 10:04 | 36240 | 280.721 | 1.6843 | 62.4141 |  | 2006-09-01 | 10:04 | 36240 | 271.166 | 1.627 | 60.7056 |  | 2029-09-01 | 10:04 | 36240 | 109.887 | 0.65932 | 30.1852 |  | 2006-09-01 | 10:04 | 36240 | 68.1938 | 0.40916 | 23.0786 |  | 2028-01-01 | 10:04 | 36240 | 273.152 | 1.6389 | 61.1506 |  | 2007-01-01 | 10:04 | 36240 | 267.677 | 1.6061 | 60.3262 |  | 2028-01-01 | 10:04 | 36240 | 45.3605 | 0.27216 | 15.5217 |  | 2007-01-01 | 10:04 | 36240 | 50.7461 | 0.30448 | 16.9655 |  | 2029-09-01 | 10:04 | 36240 | 280.721 | 1.6843 | 62.4141 |  | 2006-09-01 | 10:04 | 36240 | 271.166 | 1.627 | 60.7056 |  | 2029-09-01 | 10:04 | 36240 | 82.1979 | 0.49319 | 23.5548 |  | 2006-09-01 | 10:04 | 36240 | 47.5213 | 0.28513 | 17.2475 |  | 2028-01-01 | 10:04 | 36240 | 273.152 | 1.6389 | 61.1506 |  | 2007-01-01 | 10:04 | 36240 | 267.677 | 1.6061 | 60.3262 |  | 2028-01-01 | 10:04 | 36240 | 31.3566 | 0.18814 | 11.1289 |  | 2007-01-01 | 10:04 | 36240 | 35.3393 | 0.21204 | 12.2767 |  | 2029-09-01 | 10:04 | 36240 | 100.035 | 0.60021 | 29.8649 |  | 2029-09-01 | 10:04 | 36240 | 66.005 | 0.39603 | 21.4472 |  | 2029-09-01 | 10:04 | 36240 | 43.6882 | 0.26213 | 15.0541 |  | 2006-09-01 | 10:04 | 36240 | 43.3855 | 0.26031 | 14.9243 |  | 2028-01-01 | 10:04 | 36240 | 81.4136 | 0.48848 | 25.3547 |  | 2007-01-01 | 10:04 | 36240 | 89.1003 | 0.5346 | 27.0907 |  | 2028-01-01 | 10:04 | 36240 | 38.0991 | 0.22859 | 13.2922 |  | 2007-01-01 | 10:04 | 36240 | 39.7757 | 0.23865 | 13.7726
| 2029-09-01 | 10:05 | 36300 | 283.438 | 1.7006 | 64.1147 |  | 2029-09-01 | 10:05 | 36300 | 283.438 | 1.7006 | 64.1147 |  | 2006-09-01 | 10:05 | 36300 | 273.71 | 1.6423 | 62.3479 |  | 2029-09-01 | 10:05 | 36300 | 163.255 | 0.97953 | 42.2857 |  | 2006-09-01 | 10:05 | 36300 | 116.622 | 0.69973 | 34.997 |  | 2028-01-01 | 10:05 | 36300 | 275.754 | 1.6545 | 62.8051 |  | 2007-01-01 | 10:05 | 36300 | 270.133 | 1.6208 | 61.947 |  | 2028-01-01 | 10:05 | 36300 | 81.4758 | 0.48885 | 25.8436 |  | 2007-01-01 | 10:05 | 36300 | 89.1777 | 0.53507 | 27.6258 |  | 2029-09-01 | 10:05 | 36300 | 283.438 | 1.7006 | 64.1147 |  | 2006-09-01 | 10:05 | 36300 | 273.71 | 1.6423 | 62.3479 |  | 2029-09-01 | 10:05 | 36300 | 110.535 | 0.66321 | 30.8484 |  | 2006-09-01 | 10:05 | 36300 | 68.0807 | 0.40848 | 23.4871 |  | 2028-01-01 | 10:05 | 36300 | 275.754 | 1.6545 | 62.8051 |  | 2007-01-01 | 10:05 | 36300 | 270.133 | 1.6208 | 61.947 |  | 2028-01-01 | 10:05 | 36300 | 45.3747 | 0.27225 | 15.7939 |  | 2007-01-01 | 10:05 | 36300 | 50.756 | 0.30454 | 17.27 |  | 2029-09-01 | 10:05 | 36300 | 283.438 | 1.7006 | 64.1147 |  | 2006-09-01 | 10:05 | 36300 | 273.71 | 1.6423 | 62.3479 |  | 2029-09-01 | 10:05 | 36300 | 82.6971 | 0.49618 | 24.051 |  | 2006-09-01 | 10:05 | 36300 | 47.4369 | 0.28462 | 17.5321 |  | 2028-01-01 | 10:05 | 36300 | 275.754 | 1.6545 | 62.8051 |  | 2007-01-01 | 10:05 | 36300 | 270.133 | 1.6208 | 61.947 |  | 2028-01-01 | 10:05 | 36300 | 31.3674 | 0.1882 | 11.3171 |  | 2007-01-01 | 10:05 | 36300 | 35.3438 | 0.21206 | 12.4888 |  | 2029-09-01 | 10:05 | 36300 | 100.137 | 0.60082 | 30.4657 |  | 2029-09-01 | 10:05 | 36300 | 66.0137 | 0.39608 | 21.8433 |  | 2029-09-01 | 10:05 | 36300 | 43.6866 | 0.26212 | 15.3162 |  | 2006-09-01 | 10:05 | 36300 | 43.3823 | 0.26029 | 15.1845 |  | 2028-01-01 | 10:05 | 36300 | 81.4758 | 0.48885 | 25.8436 |  | 2007-01-01 | 10:05 | 36300 | 89.1777 | 0.53507 | 27.6258 |  | 2028-01-01 | 10:05 | 36300 | 38.1057 | 0.22863 | 13.5208 |  | 2007-01-01 | 10:05 | 36300 | 39.7747 | 0.23865 | 14.0113
| 2029-09-01 | 10:06 | 36360 | 286.116 | 1.7167 | 65.8314 |  | 2029-09-01 | 10:06 | 36360 | 286.116 | 1.7167 | 65.8314 |  | 2006-09-01 | 10:06 | 36360 | 276.208 | 1.6572 | 64.0052 |  | 2029-09-01 | 10:06 | 36360 | 164.304 | 0.98582 | 43.2715 |  | 2006-09-01 | 10:06 | 36360 | 116.647 | 0.69988 | 35.6969 |  | 2028-01-01 | 10:06 | 36360 | 278.323 | 1.6699 | 64.475 |  | 2007-01-01 | 10:06 | 36360 | 272.553 | 1.6353 | 63.5823 |  | 2028-01-01 | 10:06 | 36360 | 81.5372 | 0.48922 | 26.3328 |  | 2007-01-01 | 10:06 | 36360 | 89.247 | 0.53548 | 28.1613 |  | 2029-09-01 | 10:06 | 36360 | 286.116 | 1.7167 | 65.8314 |  | 2006-09-01 | 10:06 | 36360 | 276.208 | 1.6572 | 64.0052 |  | 2029-09-01 | 10:06 | 36360 | 111.187 | 0.66712 | 31.5155 |  | 2006-09-01 | 10:06 | 36360 | 67.9728 | 0.40784 | 23.8949 |  | 2028-01-01 | 10:06 | 36360 | 278.323 | 1.6699 | 64.475 |  | 2007-01-01 | 10:06 | 36360 | 272.553 | 1.6353 | 63.5823 |  | 2028-01-01 | 10:06 | 36360 | 45.3904 | 0.27234 | 16.0663 |  | 2007-01-01 | 10:06 | 36360 | 50.7632 | 0.30458 | 17.5746 |  | 2029-09-01 | 10:06 | 36360 | 286.116 | 1.7167 | 65.8314 |  | 2006-09-01 | 10:06 | 36360 | 276.208 | 1.6572 | 64.0052 |  | 2029-09-01 | 10:06 | 36360 | 83.2039 | 0.49922 | 24.5502 |  | 2006-09-01 | 10:06 | 36360 | 47.3597 | 0.28416 | 17.8162 |  | 2028-01-01 | 10:06 | 36360 | 278.323 | 1.6699 | 64.475 |  | 2007-01-01 | 10:06 | 36360 | 272.553 | 1.6353 | 63.5823 |  | 2028-01-01 | 10:06 | 36360 | 31.3793 | 0.18828 | 11.5054 |  | 2007-01-01 | 10:06 | 36360 | 35.3466 | 0.21208 | 12.7008 |  | 2029-09-01 | 10:06 | 36360 | 100.233 | 0.6014 | 31.0671 |  | 2029-09-01 | 10:06 | 36360 | 66.0212 | 0.39613 | 22.2394 |  | 2029-09-01 | 10:06 | 36360 | 43.6849 | 0.26211 | 15.5783 |  | 2006-09-01 | 10:06 | 36360 | 43.3783 | 0.26027 | 15.4448 |  | 2028-01-01 | 10:06 | 36360 | 81.5372 | 0.48922 | 26.3328 |  | 2007-01-01 | 10:06 | 36360 | 89.247 | 0.53548 | 28.1613 |  | 2028-01-01 | 10:06 | 36360 | 38.113 | 0.22868 | 13.7495 |  | 2007-01-01 | 10:06 | 36360 | 39.7727 | 0.23864 | 14.2499
| 2029-09-01 | 10:07 | 36420 | 288.757 | 1.7325 | 67.564 |  | 2029-09-01 | 10:07 | 36420 | 288.757 | 1.7325 | 67.564 |  | 2006-09-01 | 10:07 | 36420 | 278.661 | 1.672 | 65.6771 |  | 2029-09-01 | 10:07 | 36420 | 165.347 | 0.99208 | 44.2636 |  | 2006-09-01 | 10:07 | 36420 | 116.662 | 0.69997 | 36.3968 |  | 2028-01-01 | 10:07 | 36420 | 280.861 | 1.6852 | 66.1602 |  | 2007-01-01 | 10:07 | 36420 | 274.936 | 1.6496 | 65.232 |  | 2028-01-01 | 10:07 | 36420 | 81.598 | 0.48959 | 26.8224 |  | 2007-01-01 | 10:07 | 36420 | 89.3088 | 0.53585 | 28.6971 |  | 2029-09-01 | 10:07 | 36420 | 288.757 | 1.7325 | 67.564 |  | 2006-09-01 | 10:07 | 36420 | 278.661 | 1.672 | 65.6771 |  | 2029-09-01 | 10:07 | 36420 | 111.845 | 0.67107 | 32.1866 |  | 2006-09-01 | 10:07 | 36420 | 67.8699 | 0.40722 | 24.3021 |  | 2028-01-01 | 10:07 | 36420 | 280.861 | 1.6852 | 66.1602 |  | 2007-01-01 | 10:07 | 36420 | 274.936 | 1.6496 | 65.232 |  | 2028-01-01 | 10:07 | 36420 | 45.4074 | 0.27244 | 16.3387 |  | 2007-01-01 | 10:07 | 36420 | 50.7681 | 0.30461 | 17.8792 |  | 2029-09-01 | 10:07 | 36420 | 288.757 | 1.7325 | 67.564 |  | 2006-09-01 | 10:07 | 36420 | 278.661 | 1.672 | 65.6771 |  | 2029-09-01 | 10:07 | 36420 | 83.7188 | 0.50231 | 25.0525 |  | 2006-09-01 | 10:07 | 36420 | 47.2888 | 0.28373 | 18.1 |  | 2028-01-01 | 10:07 | 36420 | 280.861 | 1.6852 | 66.1602 |  | 2007-01-01 | 10:07 | 36420 | 274.936 | 1.6496 | 65.232 |  | 2028-01-01 | 10:07 | 36420 | 31.3922 | 0.18835 | 11.6937 |  | 2007-01-01 | 10:07 | 36420 | 35.3479 | 0.21209 | 12.9129 |  | 2029-09-01 | 10:07 | 36420 | 100.322 | 0.60193 | 31.669 |  | 2029-09-01 | 10:07 | 36420 | 66.0276 | 0.39617 | 22.6356 |  | 2029-09-01 | 10:07 | 36420 | 43.6831 | 0.2621 | 15.8404 |  | 2006-09-01 | 10:07 | 36420 | 43.3735 | 0.26024 | 15.7051 |  | 2028-01-01 | 10:07 | 36420 | 81.598 | 0.48959 | 26.8224 |  | 2007-01-01 | 10:07 | 36420 | 89.3088 | 0.53585 | 28.6971 |  | 2028-01-01 | 10:07 | 36420 | 38.1208 | 0.22872 | 13.9782 |  | 2007-01-01 | 10:07 | 36420 | 39.7697 | 0.23862 | 14.4885
| 2029-09-01 | 10:08 | 36480 | 291.36 | 1.7482 | 69.3121 |  | 2029-09-01 | 10:08 | 36480 | 291.36 | 1.7482 | 69.3121 |  | 2006-09-01 | 10:08 | 36480 | 281.068 | 1.6864 | 67.3635 |  | 2029-09-01 | 10:08 | 36480 | 166.385 | 0.99831 | 45.2619 |  | 2006-09-01 | 10:08 | 36480 | 116.668 | 0.70001 | 37.0969 |  | 2028-01-01 | 10:08 | 36480 | 283.367 | 1.7002 | 67.8604 |  | 2007-01-01 | 10:08 | 36480 | 277.283 | 1.6637 | 66.8957 |  | 2028-01-01 | 10:08 | 36480 | 81.6581 | 0.48995 | 27.3123 |  | 2007-01-01 | 10:08 | 36480 | 89.3636 | 0.53618 | 29.2333 |  | 2029-09-01 | 10:08 | 36480 | 291.36 | 1.7482 | 69.3121 |  | 2006-09-01 | 10:08 | 36480 | 281.068 | 1.6864 | 67.3635 |  | 2029-09-01 | 10:08 | 36480 | 112.508 | 0.67505 | 32.8616 |  | 2006-09-01 | 10:08 | 36480 | 67.7717 | 0.40663 | 24.7087 |  | 2028-01-01 | 10:08 | 36480 | 283.367 | 1.7002 | 67.8604 |  | 2007-01-01 | 10:08 | 36480 | 277.283 | 1.6637 | 66.8957 |  | 2028-01-01 | 10:08 | 36480 | 45.4256 | 0.27255 | 16.6113 |  | 2007-01-01 | 10:08 | 36480 | 50.771 | 0.30463 | 18.1839 |  | 2029-09-01 | 10:08 | 36480 | 291.36 | 1.7482 | 69.3121 |  | 2006-09-01 | 10:08 | 36480 | 281.068 | 1.6864 | 67.3635 |  | 2029-09-01 | 10:08 | 36480 | 84.2421 | 0.50545 | 25.558 |  | 2006-09-01 | 10:08 | 36480 | 47.2236 | 0.28334 | 18.3833 |  | 2028-01-01 | 10:08 | 36480 | 283.367 | 1.7002 | 67.8604 |  | 2007-01-01 | 10:08 | 36480 | 277.283 | 1.6637 | 66.8957 |  | 2028-01-01 | 10:08 | 36480 | 31.4059 | 0.18844 | 11.8822 |  | 2007-01-01 | 10:08 | 36480 | 35.3481 | 0.21209 | 13.125 |  | 2029-09-01 | 10:08 | 36480 | 100.405 | 0.60243 | 32.2715 |  | 2029-09-01 | 10:08 | 36480 | 66.0329 | 0.3962 | 23.0318 |  | 2029-09-01 | 10:08 | 36480 | 43.6812 | 0.26209 | 16.1025 |  | 2006-09-01 | 10:08 | 36480 | 43.368 | 0.26021 | 15.9653 |  | 2028-01-01 | 10:08 | 36480 | 81.6581 | 0.48995 | 27.3123 |  | 2007-01-01 | 10:08 | 36480 | 89.3636 | 0.53618 | 29.2333 |  | 2028-01-01 | 10:08 | 36480 | 38.1291 | 0.22877 | 14.207 |  | 2007-01-01 | 10:08 | 36480 | 39.7661 | 0.2386 | 14.7271
| 2029-09-01 | 10:09 | 36540 | 293.927 | 1.7636 | 71.0757 |  | 2029-09-01 | 10:09 | 36540 | 293.927 | 1.7636 | 71.0757 |  | 2006-09-01 | 10:09 | 36540 | 283.431 | 1.7006 | 69.0641 |  | 2029-09-01 | 10:09 | 36540 | 167.418 | 1.0045 | 46.2664 |  | 2006-09-01 | 10:09 | 36540 | 116.666 | 0.7 | 37.7968 |  | 2028-01-01 | 10:09 | 36540 | 285.842 | 1.7151 | 69.5754 |  | 2007-01-01 | 10:09 | 36540 | 279.596 | 1.6776 | 68.5732 |  | 2028-01-01 | 10:09 | 36540 | 81.7176 | 0.49031 | 27.8026 |  | 2007-01-01 | 10:09 | 36540 | 89.4119 | 0.53647 | 29.7698 |  | 2029-09-01 | 10:09 | 36540 | 293.927 | 1.7636 | 71.0757 |  | 2006-09-01 | 10:09 | 36540 | 283.431 | 1.7006 | 69.0641 |  | 2029-09-01 | 10:09 | 36540 | 113.178 | 0.67907 | 33.5407 |  | 2006-09-01 | 10:09 | 36540 | 67.678 | 0.40607 | 25.1148 |  | 2028-01-01 | 10:09 | 36540 | 285.842 | 1.7151 | 69.5754 |  | 2007-01-01 | 10:09 | 36540 | 279.596 | 1.6776 | 68.5732 |  | 2028-01-01 | 10:09 | 36540 | 45.4448 | 0.27267 | 16.8839 |  | 2007-01-01 | 10:09 | 36540 | 50.7721 | 0.30463 | 18.4885 |  | 2029-09-01 | 10:09 | 36540 | 293.927 | 1.7636 | 71.0757 |  | 2006-09-01 | 10:09 | 36540 | 283.431 | 1.7006 | 69.0641 |  | 2029-09-01 | 10:09 | 36540 | 84.7742 | 0.50865 | 26.0666 |  | 2006-09-01 | 10:09 | 36540 | 47.1635 | 0.28298 | 18.6663 |  | 2028-01-01 | 10:09 | 36540 | 285.842 | 1.7151 | 69.5754 |  | 2007-01-01 | 10:09 | 36540 | 279.596 | 1.6776 | 68.5732 |  | 2028-01-01 | 10:09 | 36540 | 31.4203 | 0.18852 | 12.0707 |  | 2007-01-01 | 10:09 | 36540 | 35.3473 | 0.21208 | 13.3371 |  | 2029-09-01 | 10:09 | 36540 | 100.483 | 0.6029 | 32.8744 |  | 2029-09-01 | 10:09 | 36540 | 66.0372 | 0.39622 | 23.428 |  | 2029-09-01 | 10:09 | 36540 | 43.6793 | 0.26208 | 16.3646 |  | 2006-09-01 | 10:09 | 36540 | 43.3619 | 0.26017 | 16.2254 |  | 2028-01-01 | 10:09 | 36540 | 81.7176 | 0.49031 | 27.8026 |  | 2007-01-01 | 10:09 | 36540 | 89.4119 | 0.53647 | 29.7698 |  | 2028-01-01 | 10:09 | 36540 | 38.1379 | 0.22883 | 14.4358 |  | 2007-01-01 | 10:09 | 36540 | 39.7618 | 0.23857 | 14.9657
| 2029-09-01 | 10:10 | 36600 | 296.457 | 1.7787 | 72.8544 |  | 2029-09-01 | 10:10 | 36600 | 296.457 | 1.7787 | 72.8544 |  | 2006-09-01 | 10:10 | 36600 | 285.749 | 1.7145 | 70.7786 |  | 2029-09-01 | 10:10 | 36600 | 168.448 | 1.0107 | 47.2771 |  | 2006-09-01 | 10:10 | 36600 | 116.656 | 0.69994 | 38.4968 |  | 2028-01-01 | 10:10 | 36600 | 288.286 | 1.7297 | 71.3052 |  | 2007-01-01 | 10:10 | 36600 | 281.874 | 1.6912 | 70.2645 |  | 2028-01-01 | 10:10 | 36600 | 81.7766 | 0.49066 | 28.2933 |  | 2007-01-01 | 10:10 | 36600 | 89.4542 | 0.53673 | 30.3065 |  | 2029-09-01 | 10:10 | 36600 | 296.457 | 1.7787 | 72.8544 |  | 2006-09-01 | 10:10 | 36600 | 285.749 | 1.7145 | 70.7786 |  | 2029-09-01 | 10:10 | 36600 | 113.854 | 0.68312 | 34.2238 |  | 2006-09-01 | 10:10 | 36600 | 67.5884 | 0.40553 | 25.5203 |  | 2028-01-01 | 10:10 | 36600 | 288.286 | 1.7297 | 71.3052 |  | 2007-01-01 | 10:10 | 36600 | 281.874 | 1.6912 | 70.2645 |  | 2028-01-01 | 10:10 | 36600 | 45.4649 | 0.27279 | 17.1567 |  | 2007-01-01 | 10:10 | 36600 | 50.7715 | 0.30463 | 18.7931 |  | 2029-09-01 | 10:10 | 36600 | 296.457 | 1.7787 | 72.8544 |  | 2006-09-01 | 10:10 | 36600 | 285.749 | 1.7145 | 70.7786 |  | 2029-09-01 | 10:10 | 36600 | 85.3155 | 0.51189 | 26.5785 |  | 2006-09-01 | 10:10 | 36600 | 47.108 | 0.28265 | 18.9489 |  | 2028-01-01 | 10:10 | 36600 | 288.286 | 1.7297 | 71.3052 |  | 2007-01-01 | 10:10 | 36600 | 281.874 | 1.6912 | 70.2645 |  | 2028-01-01 | 10:10 | 36600 | 31.4351 | 0.18861 | 12.2593 |  | 2007-01-01 | 10:10 | 36600 | 35.3456 | 0.21207 | 13.5492 |  | 2029-09-01 | 10:10 | 36600 | 100.555 | 0.60333 | 33.4777 |  | 2029-09-01 | 10:10 | 36600 | 66.0407 | 0.39624 | 23.8242 |  | 2029-09-01 | 10:10 | 36600 | 43.6773 | 0.26206 | 16.6266 |  | 2006-09-01 | 10:10 | 36600 | 43.3552 | 0.26013 | 16.4856 |  | 2028-01-01 | 10:10 | 36600 | 81.7766 | 0.49066 | 28.2933 |  | 2007-01-01 | 10:10 | 36600 | 89.4542 | 0.53673 | 30.3065 |  | 2028-01-01 | 10:10 | 36600 | 38.147 | 0.22888 | 14.6647 |  | 2007-01-01 | 10:10 | 36600 | 39.757 | 0.23854 | 15.2043
| 2029-09-01 | 10:11 | 36660 | 298.951 | 1.7937 | 74.6481 |  | 2029-09-01 | 10:11 | 36660 | 298.951 | 1.7937 | 74.6481 |  | 2006-09-01 | 10:11 | 36660 | 288.024 | 1.7281 | 72.5067 |  | 2029-09-01 | 10:11 | 36660 | 169.474 | 1.0168 | 48.2939 |  | 2006-09-01 | 10:11 | 36660 | 116.64 | 0.69984 | 39.1966 |  | 2028-01-01 | 10:11 | 36660 | 290.7 | 1.7442 | 73.0494 |  | 2007-01-01 | 10:11 | 36660 | 284.119 | 1.7047 | 71.9692 |  | 2028-01-01 | 10:11 | 36660 | 81.8351 | 0.49101 | 28.7843 |  | 2007-01-01 | 10:11 | 36660 | 89.491 | 0.53695 | 30.8435 |  | 2029-09-01 | 10:11 | 36660 | 298.951 | 1.7937 | 74.6481 |  | 2006-09-01 | 10:11 | 36660 | 288.024 | 1.7281 | 72.5067 |  | 2029-09-01 | 10:11 | 36660 | 114.538 | 0.68723 | 34.9111 |  | 2006-09-01 | 10:11 | 36660 | 67.5027 | 0.40502 | 25.9254 |  | 2028-01-01 | 10:11 | 36660 | 290.7 | 1.7442 | 73.0494 |  | 2007-01-01 | 10:11 | 36660 | 284.119 | 1.7047 | 71.9692 |  | 2028-01-01 | 10:11 | 36660 | 45.4858 | 0.27291 | 17.4296 |  | 2007-01-01 | 10:11 | 36660 | 50.7697 | 0.30462 | 19.0977 |  | 2029-09-01 | 10:11 | 36660 | 298.951 | 1.7937 | 74.6481 |  | 2006-09-01 | 10:11 | 36660 | 288.024 | 1.7281 | 72.5067 |  | 2029-09-01 | 10:11 | 36660 | 85.8665 | 0.5152 | 27.0937 |  | 2006-09-01 | 10:11 | 36660 | 47.0566 | 0.28234 | 19.2313 |  | 2028-01-01 | 10:11 | 36660 | 290.7 | 1.7442 | 73.0494 |  | 2007-01-01 | 10:11 | 36660 | 284.119 | 1.7047 | 71.9692 |  | 2028-01-01 | 10:11 | 36660 | 31.4505 | 0.1887 | 12.448 |  | 2007-01-01 | 10:11 | 36660 | 35.3433 | 0.21206 | 13.7612 |  | 2029-09-01 | 10:11 | 36660 | 100.621 | 0.60373 | 34.0814 |  | 2029-09-01 | 10:11 | 36660 | 66.0434 | 0.39626 | 24.2205 |  | 2029-09-01 | 10:11 | 36660 | 43.6752 | 0.26205 | 16.8887 |  | 2006-09-01 | 10:11 | 36660 | 43.348 | 0.26009 | 16.7457 |  | 2028-01-01 | 10:11 | 36660 | 81.8351 | 0.49101 | 28.7843 |  | 2007-01-01 | 10:11 | 36660 | 89.491 | 0.53695 | 30.8435 |  | 2028-01-01 | 10:11 | 36660 | 38.1564 | 0.22894 | 14.8936 |  | 2007-01-01 | 10:11 | 36660 | 39.7518 | 0.23851 | 15.4428
| 2029-09-01 | 10:12 | 36720 | 301.409 | 1.8085 | 76.4566 |  | 2029-09-01 | 10:12 | 36720 | 301.409 | 1.8085 | 76.4566 |  | 2006-09-01 | 10:12 | 36720 | 290.254 | 1.7415 | 74.2483 |  | 2029-09-01 | 10:12 | 36720 | 170.499 | 1.023 | 49.3169 |  | 2006-09-01 | 10:12 | 36720 | 116.617 | 0.6997 | 39.8963 |  | 2028-01-01 | 10:12 | 36720 | 293.085 | 1.7585 | 74.8079 |  | 2007-01-01 | 10:12 | 36720 | 286.332 | 1.718 | 73.6872 |  | 2028-01-01 | 10:12 | 36720 | 81.8931 | 0.49136 | 29.2757 |  | 2007-01-01 | 10:12 | 36720 | 89.5225 | 0.53713 | 31.3806 |  | 2029-09-01 | 10:12 | 36720 | 301.409 | 1.8085 | 76.4566 |  | 2006-09-01 | 10:12 | 36720 | 290.254 | 1.7415 | 74.2483 |  | 2029-09-01 | 10:12 | 36720 | 115.23 | 0.69138 | 35.6024 |  | 2006-09-01 | 10:12 | 36720 | 67.4205 | 0.40452 | 26.3299 |  | 2028-01-01 | 10:12 | 36720 | 293.085 | 1.7585 | 74.8079 |  | 2007-01-01 | 10:12 | 36720 | 286.332 | 1.718 | 73.6872 |  | 2028-01-01 | 10:12 | 36720 | 45.5073 | 0.27304 | 17.7027 |  | 2007-01-01 | 10:12 | 36720 | 50.7666 | 0.3046 | 19.4023 |  | 2029-09-01 | 10:12 | 36720 | 301.409 | 1.8085 | 76.4566 |  | 2006-09-01 | 10:12 | 36720 | 290.254 | 1.7415 | 74.2483 |  | 2029-09-01 | 10:12 | 36720 | 86.4274 | 0.51856 | 27.6123 |  | 2006-09-01 | 10:12 | 36720 | 47.0087 | 0.28205 | 19.5133 |  | 2028-01-01 | 10:12 | 36720 | 293.085 | 1.7585 | 74.8079 |  | 2007-01-01 | 10:12 | 36720 | 286.332 | 1.718 | 73.6872 |  | 2028-01-01 | 10:12 | 36720 | 31.4662 | 0.1888 | 12.6368 |  | 2007-01-01 | 10:12 | 36720 | 35.3404 | 0.21204 | 13.9733 |  | 2029-09-01 | 10:12 | 36720 | 100.683 | 0.6041 | 34.6855 |  | 2029-09-01 | 10:12 | 36720 | 66.0454 | 0.39627 | 24.6168 |  | 2029-09-01 | 10:12 | 36720 | 43.6732 | 0.26204 | 17.1507 |  | 2006-09-01 | 10:12 | 36720 | 43.3405 | 0.26004 | 17.0057 |  | 2028-01-01 | 10:12 | 36720 | 81.8931 | 0.49136 | 29.2757 |  | 2007-01-01 | 10:12 | 36720 | 89.5225 | 0.53713 | 31.3806 |  | 2028-01-01 | 10:12 | 36720 | 38.1661 | 0.229 | 15.1226 |  | 2007-01-01 | 10:12 | 36720 | 39.7462 | 0.23848 | 15.6812
| 2029-09-01 | 10:13 | 36780 | 303.832 | 1.823 | 78.2796 |  | 2029-09-01 | 10:13 | 36780 | 303.832 | 1.823 | 78.2796 |  | 2006-09-01 | 10:13 | 36780 | 292.442 | 1.7547 | 76.0029 |  | 2029-09-01 | 10:13 | 36780 | 171.522 | 1.0291 | 50.3461 |  | 2006-09-01 | 10:13 | 36780 | 116.588 | 0.69953 | 40.5959 |  | 2028-01-01 | 10:13 | 36780 | 295.441 | 1.7726 | 76.5805 |  | 2007-01-01 | 10:13 | 36780 | 288.518 | 1.7311 | 75.4183 |  | 2028-01-01 | 10:13 | 36780 | 81.9506 | 0.4917 | 29.7674 |  | 2007-01-01 | 10:13 | 36780 | 89.5494 | 0.5373 | 31.9179 |  | 2029-09-01 | 10:13 | 36780 | 303.832 | 1.823 | 78.2796 |  | 2006-09-01 | 10:13 | 36780 | 292.442 | 1.7547 | 76.0029 |  | 2029-09-01 | 10:13 | 36780 | 115.931 | 0.69559 | 36.298 |  | 2006-09-01 | 10:13 | 36780 | 67.3418 | 0.40405 | 26.7339 |  | 2028-01-01 | 10:13 | 36780 | 295.441 | 1.7726 | 76.5805 |  | 2007-01-01 | 10:13 | 36780 | 288.518 | 1.7311 | 75.4183 |  | 2028-01-01 | 10:13 | 36780 | 45.5295 | 0.27318 | 17.9759 |  | 2007-01-01 | 10:13 | 36780 | 50.7625 | 0.30457 | 19.7069 |  | 2029-09-01 | 10:13 | 36780 | 303.832 | 1.823 | 78.2796 |  | 2006-09-01 | 10:13 | 36780 | 292.442 | 1.7547 | 76.0029 |  | 2029-09-01 | 10:13 | 36780 | 86.9989 | 0.52199 | 28.1343 |  | 2006-09-01 | 10:13 | 36780 | 46.9641 | 0.28178 | 19.7951 |  | 2028-01-01 | 10:13 | 36780 | 295.441 | 1.7726 | 76.5805 |  | 2007-01-01 | 10:13 | 36780 | 288.518 | 1.7311 | 75.4183 |  | 2028-01-01 | 10:13 | 36780 | 31.4822 | 0.18889 | 12.8257 |  | 2007-01-01 | 10:13 | 36780 | 35.3371 | 0.21202 | 14.1853 |  | 2029-09-01 | 10:13 | 36780 | 100.741 | 0.60445 | 35.29 |  | 2029-09-01 | 10:13 | 36780 | 66.0468 | 0.39628 | 25.013 |  | 2029-09-01 | 10:13 | 36780 | 43.6711 | 0.26203 | 17.4127 |  | 2006-09-01 | 10:13 | 36780 | 43.3325 | 0.25999 | 17.2657 |  | 2028-01-01 | 10:13 | 36780 | 81.9506 | 0.4917 | 29.7674 |  | 2007-01-01 | 10:13 | 36780 | 89.5494 | 0.5373 | 31.9179 |  | 2028-01-01 | 10:13 | 36780 | 38.176 | 0.22906 | 15.3517 |  | 2007-01-01 | 10:13 | 36780 | 39.7403 | 0.23844 | 15.9197
| 2029-09-01 | 10:14 | 36840 | 306.22 | 1.8373 | 80.1169 |  | 2029-09-01 | 10:14 | 36840 | 306.22 | 1.8373 | 80.1169 |  | 2006-09-01 | 10:14 | 36840 | 294.587 | 1.7675 | 77.7704 |  | 2029-09-01 | 10:14 | 36840 | 172.545 | 1.0353 | 51.3813 |  | 2006-09-01 | 10:14 | 36840 | 116.553 | 0.69932 | 41.2952 |  | 2028-01-01 | 10:14 | 36840 | 297.768 | 1.7866 | 78.3671 |  | 2007-01-01 | 10:14 | 36840 | 290.658 | 1.7439 | 77.1622 |  | 2028-01-01 | 10:14 | 36840 | 82.0078 | 0.49205 | 30.2594 |  | 2007-01-01 | 10:14 | 36840 | 89.5718 | 0.53743 | 32.4553 |  | 2029-09-01 | 10:14 | 36840 | 306.22 | 1.8373 | 80.1169 |  | 2006-09-01 | 10:14 | 36840 | 294.587 | 1.7675 | 77.7704 |  | 2029-09-01 | 10:14 | 36840 | 116.64 | 0.69984 | 36.9979 |  | 2006-09-01 | 10:14 | 36840 | 67.2662 | 0.4036 | 27.1375 |  | 2028-01-01 | 10:14 | 36840 | 297.768 | 1.7866 | 78.3671 |  | 2007-01-01 | 10:14 | 36840 | 290.658 | 1.7439 | 77.1622 |  | 2028-01-01 | 10:14 | 36840 | 45.5522 | 0.27331 | 18.2492 |  | 2007-01-01 | 10:14 | 36840 | 50.7575 | 0.30455 | 20.0115 |  | 2029-09-01 | 10:14 | 36840 | 306.22 | 1.8373 | 80.1169 |  | 2006-09-01 | 10:14 | 36840 | 294.587 | 1.7675 | 77.7704 |  | 2029-09-01 | 10:14 | 36840 | 87.5812 | 0.52549 | 28.6598 |  | 2006-09-01 | 10:14 | 36840 | 46.9224 | 0.28153 | 20.0767 |  | 2028-01-01 | 10:14 | 36840 | 297.768 | 1.7866 | 78.3671 |  | 2007-01-01 | 10:14 | 36840 | 290.658 | 1.7439 | 77.1622 |  | 2028-01-01 | 10:14 | 36840 | 31.4985 | 0.18899 | 13.0147 |  | 2007-01-01 | 10:14 | 36840 | 35.3334 | 0.212 | 14.3973 |  | 2029-09-01 | 10:14 | 36840 | 100.794 | 0.60476 | 35.8947 |  | 2029-09-01 | 10:14 | 36840 | 66.0475 | 0.39628 | 25.4093 |  | 2029-09-01 | 10:14 | 36840 | 43.669 | 0.26201 | 17.6747 |  | 2006-09-01 | 10:14 | 36840 | 43.3242 | 0.25995 | 17.5256 |  | 2028-01-01 | 10:14 | 36840 | 82.0078 | 0.49205 | 30.2594 |  | 2007-01-01 | 10:14 | 36840 | 89.5718 | 0.53743 | 32.4553 |  | 2028-01-01 | 10:14 | 36840 | 38.1861 | 0.22912 | 15.5808 |  | 2007-01-01 | 10:14 | 36840 | 39.7343 | 0.23841 | 16.1581
| 2029-09-01 | 10:15 | 36900 | 308.575 | 1.8514 | 81.9684 |  | 2029-09-01 | 10:15 | 36900 | 308.575 | 1.8514 | 81.9684 |  | 2006-09-01 | 10:15 | 36900 | 296.69 | 1.7801 | 79.5506 |  | 2029-09-01 | 10:15 | 36900 | 173.568 | 1.0414 | 52.4227 |  | 2006-09-01 | 10:15 | 36900 | 116.513 | 0.69908 | 41.9943 |  | 2028-01-01 | 10:15 | 36900 | 300.067 | 1.8004 | 80.1675 |  | 2007-01-01 | 10:15 | 36900 | 292.756 | 1.7565 | 78.9188 |  | 2028-01-01 | 10:15 | 36900 | 82.0645 | 0.49239 | 30.7518 |  | 2007-01-01 | 10:15 | 36900 | 89.5901 | 0.53754 | 32.9929 |  | 2029-09-01 | 10:15 | 36900 | 308.575 | 1.8514 | 81.9684 |  | 2006-09-01 | 10:15 | 36900 | 296.69 | 1.7801 | 79.5506 |  | 2029-09-01 | 10:15 | 36900 | 117.359 | 0.70415 | 37.702 |  | 2006-09-01 | 10:15 | 36900 | 67.1935 | 0.40316 | 27.5407 |  | 2028-01-01 | 10:15 | 36900 | 300.067 | 1.8004 | 80.1675 |  | 2007-01-01 | 10:15 | 36900 | 292.756 | 1.7565 | 78.9188 |  | 2028-01-01 | 10:15 | 36900 | 45.5753 | 0.27345 | 18.5226 |  | 2007-01-01 | 10:15 | 36900 | 50.7517 | 0.30451 | 20.316 |  | 2029-09-01 | 10:15 | 36900 | 308.575 | 1.8514 | 81.9684 |  | 2006-09-01 | 10:15 | 36900 | 296.69 | 1.7801 | 79.5506 |  | 2029-09-01 | 10:15 | 36900 | 88.175 | 0.52905 | 29.1888 |  | 2006-09-01 | 10:15 | 36900 | 46.8832 | 0.2813 | 20.358 |  | 2028-01-01 | 10:15 | 36900 | 300.067 | 1.8004 | 80.1675 |  | 2007-01-01 | 10:15 | 36900 | 292.756 | 1.7565 | 78.9188 |  | 2028-01-01 | 10:15 | 36900 | 31.5149 | 0.18909 | 13.2038 |  | 2007-01-01 | 10:15 | 36900 | 35.3293 | 0.21198 | 14.6093 |  | 2029-09-01 | 10:15 | 36900 | 100.843 | 0.60506 | 36.4998 |  | 2029-09-01 | 10:15 | 36900 | 66.0477 | 0.39629 | 25.8056 |  | 2029-09-01 | 10:15 | 36900 | 43.6668 | 0.262 | 17.9367 |  | 2006-09-01 | 10:15 | 36900 | 43.3156 | 0.25989 | 17.7855 |  | 2028-01-01 | 10:15 | 36900 | 82.0645 | 0.49239 | 30.7518 |  | 2007-01-01 | 10:15 | 36900 | 89.5901 | 0.53754 | 32.9929 |  | 2028-01-01 | 10:15 | 36900 | 38.1964 | 0.22918 | 15.81 |  | 2007-01-01 | 10:15 | 36900 | 39.728 | 0.23837 | 16.3965
| 2029-09-01 | 10:16 | 36960 | 310.895 | 1.8654 | 83.8337 |  | 2029-09-01 | 10:16 | 36960 | 310.895 | 1.8654 | 83.8337 |  | 2006-09-01 | 10:16 | 36960 | 298.75 | 1.7925 | 81.3431 |  | 2029-09-01 | 10:16 | 36960 | 174.591 | 1.0475 | 53.4703 |  | 2006-09-01 | 10:16 | 36960 | 116.469 | 0.69881 | 42.6931 |  | 2028-01-01 | 10:16 | 36960 | 302.338 | 1.814 | 81.9815 |  | 2007-01-01 | 10:16 | 36960 | 294.81 | 1.7689 | 80.6876 |  | 2028-01-01 | 10:16 | 36960 | 82.121 | 0.49273 | 31.2445 |  | 2007-01-01 | 10:16 | 36960 | 89.6047 | 0.53763 | 33.5305 |  | 2029-09-01 | 10:16 | 36960 | 310.895 | 1.8654 | 83.8337 |  | 2006-09-01 | 10:16 | 36960 | 298.75 | 1.7925 | 81.3431 |  | 2029-09-01 | 10:16 | 36960 | 118.089 | 0.70853 | 38.4106 |  | 2006-09-01 | 10:16 | 36960 | 67.1235 | 0.40274 | 27.9434 |  | 2028-01-01 | 10:16 | 36960 | 302.338 | 1.814 | 81.9815 |  | 2007-01-01 | 10:16 | 36960 | 294.81 | 1.7689 | 80.6876 |  | 2028-01-01 | 10:16 | 36960 | 45.5988 | 0.27359 | 18.7962 |  | 2007-01-01 | 10:16 | 36960 | 50.7453 | 0.30447 | 20.6204 |  | 2029-09-01 | 10:16 | 36960 | 310.895 | 1.8654 | 83.8337 |  | 2006-09-01 | 10:16 | 36960 | 298.75 | 1.7925 | 81.3431 |  | 2029-09-01 | 10:16 | 36960 | 88.7806 | 0.53268 | 29.7215 |  | 2006-09-01 | 10:16 | 36960 | 46.8463 | 0.28108 | 20.639 |  | 2028-01-01 | 10:16 | 36960 | 302.338 | 1.814 | 81.9815 |  | 2007-01-01 | 10:16 | 36960 | 294.81 | 1.7689 | 80.6876 |  | 2028-01-01 | 10:16 | 36960 | 31.5316 | 0.18919 | 13.393 |  | 2007-01-01 | 10:16 | 36960 | 35.3251 | 0.21195 | 14.8212 |  | 2029-09-01 | 10:16 | 36960 | 100.889 | 0.60533 | 37.1051 |  | 2029-09-01 | 10:16 | 36960 | 66.0475 | 0.39628 | 26.2019 |  | 2029-09-01 | 10:16 | 36960 | 43.6646 | 0.26199 | 18.1987 |  | 2006-09-01 | 10:16 | 36960 | 43.3067 | 0.25984 | 18.0454 |  | 2028-01-01 | 10:16 | 36960 | 82.121 | 0.49273 | 31.2445 |  | 2007-01-01 | 10:16 | 36960 | 89.6047 | 0.53763 | 33.5305 |  | 2028-01-01 | 10:16 | 36960 | 38.2067 | 0.22924 | 16.0392 |  | 2007-01-01 | 10:16 | 36960 | 39.7215 | 0.23833 | 16.6348
| 2029-09-01 | 10:17 | 37020 | 313.181 | 1.8791 | 85.7128 |  | 2029-09-01 | 10:17 | 37020 | 313.181 | 1.8791 | 85.7128 |  | 2006-09-01 | 10:17 | 37020 | 300.768 | 1.8046 | 83.1477 |  | 2029-09-01 | 10:17 | 37020 | 175.617 | 1.0537 | 54.524 |  | 2006-09-01 | 10:17 | 37020 | 116.42 | 0.69852 | 43.3916 |  | 2028-01-01 | 10:17 | 37020 | 304.582 | 1.8275 | 83.809 |  | 2007-01-01 | 10:17 | 37020 | 296.823 | 1.7809 | 82.4686 |  | 2028-01-01 | 10:17 | 37020 | 82.1771 | 0.49306 | 31.7376 |  | 2007-01-01 | 10:17 | 37020 | 89.6158 | 0.53769 | 34.0682 |  | 2029-09-01 | 10:17 | 37020 | 313.181 | 1.8791 | 85.7128 |  | 2006-09-01 | 10:17 | 37020 | 300.768 | 1.8046 | 83.1477 |  | 2029-09-01 | 10:17 | 37020 | 118.829 | 0.71297 | 39.1235 |  | 2006-09-01 | 10:17 | 37020 | 67.0559 | 0.40234 | 28.3458 |  | 2028-01-01 | 10:17 | 37020 | 304.582 | 1.8275 | 83.809 |  | 2007-01-01 | 10:17 | 37020 | 296.823 | 1.7809 | 82.4686 |  | 2028-01-01 | 10:17 | 37020 | 45.6227 | 0.27374 | 19.07 |  | 2007-01-01 | 10:17 | 37020 | 50.7382 | 0.30443 | 20.9249 |  | 2029-09-01 | 10:17 | 37020 | 313.181 | 1.8791 | 85.7128 |  | 2006-09-01 | 10:17 | 37020 | 300.768 | 1.8046 | 83.1477 |  | 2029-09-01 | 10:17 | 37020 | 89.3986 | 0.53639 | 30.2579 |  | 2006-09-01 | 10:17 | 37020 | 46.8114 | 0.28087 | 20.9199 |  | 2028-01-01 | 10:17 | 37020 | 304.582 | 1.8275 | 83.809 |  | 2007-01-01 | 10:17 | 37020 | 296.823 | 1.7809 | 82.4686 |  | 2028-01-01 | 10:17 | 37020 | 31.5485 | 0.18929 | 13.5823 |  | 2007-01-01 | 10:17 | 37020 | 35.3206 | 0.21192 | 15.0331 |  | 2029-09-01 | 10:17 | 37020 | 100.931 | 0.60559 | 37.7107 |  | 2029-09-01 | 10:17 | 37020 | 66.0467 | 0.39628 | 26.5982 |  | 2029-09-01 | 10:17 | 37020 | 43.6624 | 0.26197 | 18.4607 |  | 2006-09-01 | 10:17 | 37020 | 43.2974 | 0.25978 | 18.3052 |  | 2028-01-01 | 10:17 | 37020 | 82.1771 | 0.49306 | 31.7376 |  | 2007-01-01 | 10:17 | 37020 | 89.6158 | 0.53769 | 34.0682 |  | 2028-01-01 | 10:17 | 37020 | 38.2172 | 0.2293 | 16.2685 |  | 2007-01-01 | 10:17 | 37020 | 39.715 | 0.23829 | 16.8731
| 2029-09-01 | 10:18 | 37080 | 315.435 | 1.8926 | 87.6054 |  | 2029-09-01 | 10:18 | 37080 | 315.435 | 1.8926 | 87.6054 |  | 2006-09-01 | 10:18 | 37080 | 302.745 | 1.8165 | 84.9642 |  | 2029-09-01 | 10:18 | 37080 | 176.644 | 1.0599 | 55.5838 |  | 2006-09-01 | 10:18 | 37080 | 116.366 | 0.6982 | 44.0898 |  | 2028-01-01 | 10:18 | 37080 | 306.799 | 1.8408 | 85.6498 |  | 2007-01-01 | 10:18 | 37080 | 298.796 | 1.7928 | 84.2614 |  | 2028-01-01 | 10:18 | 37080 | 82.2329 | 0.4934 | 32.231 |  | 2007-01-01 | 10:18 | 37080 | 89.6237 | 0.53774 | 34.6059 |  | 2029-09-01 | 10:18 | 37080 | 315.435 | 1.8926 | 87.6054 |  | 2006-09-01 | 10:18 | 37080 | 302.745 | 1.8165 | 84.9642 |  | 2029-09-01 | 10:18 | 37080 | 119.58 | 0.71748 | 39.841 |  | 2006-09-01 | 10:18 | 37080 | 66.9907 | 0.40194 | 28.7477 |  | 2028-01-01 | 10:18 | 37080 | 306.799 | 1.8408 | 85.6498 |  | 2007-01-01 | 10:18 | 37080 | 298.796 | 1.7928 | 84.2614 |  | 2028-01-01 | 10:18 | 37080 | 45.6469 | 0.27388 | 19.3438 |  | 2007-01-01 | 10:18 | 37080 | 50.7307 | 0.30438 | 21.2292 |  | 2029-09-01 | 10:18 | 37080 | 315.435 | 1.8926 | 87.6054 |  | 2006-09-01 | 10:18 | 37080 | 302.745 | 1.8165 | 84.9642 |  | 2029-09-01 | 10:18 | 37080 | 90.0294 | 0.54018 | 30.7981 |  | 2006-09-01 | 10:18 | 37080 | 46.7784 | 0.28067 | 21.2006 |  | 2028-01-01 | 10:18 | 37080 | 306.799 | 1.8408 | 85.6498 |  | 2007-01-01 | 10:18 | 37080 | 298.796 | 1.7928 | 84.2614 |  | 2028-01-01 | 10:18 | 37080 | 31.5654 | 0.18939 | 13.7717 |  | 2007-01-01 | 10:18 | 37080 | 35.316 | 0.2119 | 15.245 |  | 2029-09-01 | 10:18 | 37080 | 100.97 | 0.60582 | 38.3165 |  | 2029-09-01 | 10:18 | 37080 | 66.0456 | 0.39627 | 26.9944 |  | 2029-09-01 | 10:18 | 37080 | 43.6602 | 0.26196 | 18.7227 |  | 2006-09-01 | 10:18 | 37080 | 43.288 | 0.25973 | 18.5649 |  | 2028-01-01 | 10:18 | 37080 | 82.2329 | 0.4934 | 32.231 |  | 2007-01-01 | 10:18 | 37080 | 89.6237 | 0.53774 | 34.6059 |  | 2028-01-01 | 10:18 | 37080 | 38.2278 | 0.22937 | 16.4979 |  | 2007-01-01 | 10:18 | 37080 | 39.7084 | 0.23825 | 17.1113
| 2029-09-01 | 10:19 | 37140 | 317.656 | 1.9059 | 89.5114 |  | 2029-09-01 | 10:19 | 37140 | 317.656 | 1.9059 | 89.5114 |  | 2006-09-01 | 10:19 | 37140 | 304.681 | 1.8281 | 86.7923 |  | 2029-09-01 | 10:19 | 37140 | 177.675 | 1.066 | 56.6499 |  | 2006-09-01 | 10:19 | 37140 | 116.309 | 0.69785 | 44.7876 |  | 2028-01-01 | 10:19 | 37140 | 308.99 | 1.8539 | 87.5038 |  | 2007-01-01 | 10:19 | 37140 | 300.728 | 1.8044 | 86.0657 |  | 2028-01-01 | 10:19 | 37140 | 82.2885 | 0.49373 | 32.7247 |  | 2007-01-01 | 10:19 | 37140 | 89.6286 | 0.53777 | 35.1437 |  | 2029-09-01 | 10:19 | 37140 | 317.656 | 1.9059 | 89.5114 |  | 2006-09-01 | 10:19 | 37140 | 304.681 | 1.8281 | 86.7923 |  | 2029-09-01 | 10:19 | 37140 | 120.343 | 0.72206 | 40.5631 |  | 2006-09-01 | 10:19 | 37140 | 66.9277 | 0.40157 | 29.1493 |  | 2028-01-01 | 10:19 | 37140 | 308.99 | 1.8539 | 87.5038 |  | 2007-01-01 | 10:19 | 37140 | 300.728 | 1.8044 | 86.0657 |  | 2028-01-01 | 10:19 | 37140 | 45.6714 | 0.27403 | 19.6179 |  | 2007-01-01 | 10:19 | 37140 | 50.7227 | 0.30434 | 21.5336 |  | 2029-09-01 | 10:19 | 37140 | 317.656 | 1.9059 | 89.5114 |  | 2006-09-01 | 10:19 | 37140 | 304.681 | 1.8281 | 86.7923 |  | 2029-09-01 | 10:19 | 37140 | 90.6738 | 0.54404 | 31.3421 |  | 2006-09-01 | 10:19 | 37140 | 46.7469 | 0.28048 | 21.4811 |  | 2028-01-01 | 10:19 | 37140 | 308.99 | 1.8539 | 87.5038 |  | 2007-01-01 | 10:19 | 37140 | 300.728 | 1.8044 | 86.0657 |  | 2028-01-01 | 10:19 | 37140 | 31.5825 | 0.18949 | 13.9612 |  | 2007-01-01 | 10:19 | 37140 | 35.3112 | 0.21187 | 15.4569 |  | 2029-09-01 | 10:19 | 37140 | 101.005 | 0.60603 | 38.9225 |  | 2029-09-01 | 10:19 | 37140 | 66.0441 | 0.39626 | 27.3907 |  | 2029-09-01 | 10:19 | 37140 | 43.658 | 0.26195 | 18.9846 |  | 2006-09-01 | 10:19 | 37140 | 43.2782 | 0.25967 | 18.8246 |  | 2028-01-01 | 10:19 | 37140 | 82.2885 | 0.49373 | 32.7247 |  | 2007-01-01 | 10:19 | 37140 | 89.6286 | 0.53777 | 35.1437 |  | 2028-01-01 | 10:19 | 37140 | 38.2385 | 0.22943 | 16.7273 |  | 2007-01-01 | 10:19 | 37140 | 39.7017 | 0.23821 | 17.3495
| 2029-09-01 | 10:20 | 37200 | 319.845 | 1.9191 | 91.4304 |  | 2029-09-01 | 10:20 | 37200 | 319.845 | 1.9191 | 91.4304 |  | 2006-09-01 | 10:20 | 37200 | 306.576 | 1.8395 | 88.6317 |  | 2029-09-01 | 10:20 | 37200 | 178.709 | 1.0723 | 57.7221 |  | 2006-09-01 | 10:20 | 37200 | 116.248 | 0.69749 | 45.4851 |  | 2028-01-01 | 10:20 | 37200 | 311.155 | 1.8669 | 89.3707 |  | 2007-01-01 | 10:20 | 37200 | 302.62 | 1.8157 | 87.8814 |  | 2028-01-01 | 10:20 | 37200 | 82.3438 | 0.49406 | 33.2188 |  | 2007-01-01 | 10:20 | 37200 | 89.6308 | 0.53778 | 35.6815 |  | 2029-09-01 | 10:20 | 37200 | 319.845 | 1.9191 | 91.4304 |  | 2006-09-01 | 10:20 | 37200 | 306.576 | 1.8395 | 88.6317 |  | 2029-09-01 | 10:20 | 37200 | 121.119 | 0.72671 | 41.2898 |  | 2006-09-01 | 10:20 | 37200 | 66.8666 | 0.4012 | 29.5505 |  | 2028-01-01 | 10:20 | 37200 | 311.155 | 1.8669 | 89.3707 |  | 2007-01-01 | 10:20 | 37200 | 302.62 | 1.8157 | 87.8814 |  | 2028-01-01 | 10:20 | 37200 | 45.6961 | 0.27418 | 19.892 |  | 2007-01-01 | 10:20 | 37200 | 50.7144 | 0.30429 | 21.8379 |  | 2029-09-01 | 10:20 | 37200 | 319.845 | 1.9191 | 91.4304 |  | 2006-09-01 | 10:20 | 37200 | 306.576 | 1.8395 | 88.6317 |  | 2029-09-01 | 10:20 | 37200 | 91.3321 | 0.54799 | 31.8901 |  | 2006-09-01 | 10:20 | 37200 | 46.7168 | 0.2803 | 21.7614 |  | 2028-01-01 | 10:20 | 37200 | 311.155 | 1.8669 | 89.3707 |  | 2007-01-01 | 10:20 | 37200 | 302.62 | 1.8157 | 87.8814 |  | 2028-01-01 | 10:20 | 37200 | 31.5997 | 0.1896 | 14.1508 |  | 2007-01-01 | 10:20 | 37200 | 35.3064 | 0.21184 | 15.6687 |  | 2029-09-01 | 10:20 | 37200 | 101.038 | 0.60623 | 39.5288 |  | 2029-09-01 | 10:20 | 37200 | 66.0422 | 0.39625 | 27.787 |  | 2029-09-01 | 10:20 | 37200 | 43.6557 | 0.26193 | 19.2466 |  | 2006-09-01 | 10:20 | 37200 | 43.2683 | 0.25961 | 19.0842 |  | 2028-01-01 | 10:20 | 37200 | 82.3438 | 0.49406 | 33.2188 |  | 2007-01-01 | 10:20 | 37200 | 89.6308 | 0.53778 | 35.6815 |  | 2028-01-01 | 10:20 | 37200 | 38.2492 | 0.2295 | 16.9568 |  | 2007-01-01 | 10:20 | 37200 | 39.695 | 0.23817 | 17.5877
| 2029-09-01 | 10:21 | 37260 | 322.002 | 1.932 | 93.3624 |  | 2029-09-01 | 10:21 | 37260 | 322.002 | 1.932 | 93.3624 |  | 2006-09-01 | 10:21 | 37260 | 308.43 | 1.8506 | 90.4823 |  | 2029-09-01 | 10:21 | 37260 | 179.748 | 1.0785 | 58.8006 |  | 2006-09-01 | 10:21 | 37260 | 116.184 | 0.6971 | 46.1822 |  | 2028-01-01 | 10:21 | 37260 | 313.294 | 1.8798 | 91.2505 |  | 2007-01-01 | 10:21 | 37260 | 304.474 | 1.8268 | 89.7083 |  | 2028-01-01 | 10:21 | 37260 | 82.3989 | 0.49439 | 33.7132 |  | 2007-01-01 | 10:21 | 37260 | 89.6305 | 0.53778 | 36.2193 |  | 2029-09-01 | 10:21 | 37260 | 322.002 | 1.932 | 93.3624 |  | 2006-09-01 | 10:21 | 37260 | 308.43 | 1.8506 | 90.4823 |  | 2029-09-01 | 10:21 | 37260 | 121.909 | 0.73145 | 42.0212 |  | 2006-09-01 | 10:21 | 37260 | 66.8074 | 0.40084 | 29.9513 |  | 2028-01-01 | 10:21 | 37260 | 313.294 | 1.8798 | 91.2505 |  | 2007-01-01 | 10:21 | 37260 | 304.474 | 1.8268 | 89.7083 |  | 2028-01-01 | 10:21 | 37260 | 45.721 | 0.27433 | 20.1664 |  | 2007-01-01 | 10:21 | 37260 | 50.7058 | 0.30423 | 22.1421 |  | 2029-09-01 | 10:21 | 37260 | 322.002 | 1.932 | 93.3624 |  | 2006-09-01 | 10:21 | 37260 | 308.43 | 1.8506 | 90.4823 |  | 2029-09-01 | 10:21 | 37260 | 92.005 | 0.55203 | 32.4421 |  | 2006-09-01 | 10:21 | 37260 | 46.688 | 0.28013 | 22.0415 |  | 2028-01-01 | 10:21 | 37260 | 313.294 | 1.8798 | 91.2505 |  | 2007-01-01 | 10:21 | 37260 | 304.474 | 1.8268 | 89.7083 |  | 2028-01-01 | 10:21 | 37260 | 31.6169 | 0.1897 | 14.3405 |  | 2007-01-01 | 10:21 | 37260 | 35.3015 | 0.21181 | 15.8806 |  | 2029-09-01 | 10:21 | 37260 | 101.068 | 0.60641 | 40.1352 |  | 2029-09-01 | 10:21 | 37260 | 66.0401 | 0.39624 | 28.1832 |  | 2029-09-01 | 10:21 | 37260 | 43.6534 | 0.26192 | 19.5085 |  | 2006-09-01 | 10:21 | 37260 | 43.2582 | 0.25955 | 19.3437 |  | 2028-01-01 | 10:21 | 37260 | 82.3989 | 0.49439 | 33.7132 |  | 2007-01-01 | 10:21 | 37260 | 89.6305 | 0.53778 | 36.2193 |  | 2028-01-01 | 10:21 | 37260 | 38.26 | 0.22956 | 17.1864 |  | 2007-01-01 | 10:21 | 37260 | 39.6883 | 0.23813 | 17.8258
| 2029-09-01 | 10:22 | 37320 | 324.127 | 1.9448 | 95.3072 |  | 2029-09-01 | 10:22 | 37320 | 324.127 | 1.9448 | 95.3072 |  | 2006-09-01 | 10:22 | 37320 | 310.245 | 1.8615 | 92.3438 |  | 2029-09-01 | 10:22 | 37320 | 180.793 | 1.0848 | 59.8854 |  | 2006-09-01 | 10:22 | 37320 | 116.116 | 0.6967 | 46.8789 |  | 2028-01-01 | 10:22 | 37320 | 315.408 | 1.8924 | 93.1429 |  | 2007-01-01 | 10:22 | 37320 | 306.29 | 1.8377 | 91.546 |  | 2028-01-01 | 10:22 | 37320 | 82.4537 | 0.49472 | 34.2079 |  | 2007-01-01 | 10:22 | 37320 | 89.6278 | 0.53777 | 36.757 |  | 2029-09-01 | 10:22 | 37320 | 324.127 | 1.9448 | 95.3072 |  | 2006-09-01 | 10:22 | 37320 | 310.245 | 1.8615 | 92.3438 |  | 2029-09-01 | 10:22 | 37320 | 122.712 | 0.73627 | 42.7575 |  | 2006-09-01 | 10:22 | 37320 | 66.7499 | 0.4005 | 30.3518 |  | 2028-01-01 | 10:22 | 37320 | 315.408 | 1.8924 | 93.1429 |  | 2007-01-01 | 10:22 | 37320 | 306.29 | 1.8377 | 91.546 |  | 2028-01-01 | 10:22 | 37320 | 45.7461 | 0.27448 | 20.4408 |  | 2007-01-01 | 10:22 | 37320 | 50.6969 | 0.30418 | 22.4463 |  | 2029-09-01 | 10:22 | 37320 | 324.127 | 1.9448 | 95.3072 |  | 2006-09-01 | 10:22 | 37320 | 310.245 | 1.8615 | 92.3438 |  | 2029-09-01 | 10:22 | 37320 | 92.6933 | 0.55616 | 32.9983 |  | 2006-09-01 | 10:22 | 37320 | 46.6604 | 0.27996 | 22.3214 |  | 2028-01-01 | 10:22 | 37320 | 315.408 | 1.8924 | 93.1429 |  | 2007-01-01 | 10:22 | 37320 | 306.29 | 1.8377 | 91.546 |  | 2028-01-01 | 10:22 | 37320 | 31.6342 | 0.18981 | 14.5303 |  | 2007-01-01 | 10:22 | 37320 | 35.2966 | 0.21178 | 16.0923 |  | 2029-09-01 | 10:22 | 37320 | 101.095 | 0.60657 | 40.7417 |  | 2029-09-01 | 10:22 | 37320 | 66.0376 | 0.39623 | 28.5794 |  | 2029-09-01 | 10:22 | 37320 | 43.6512 | 0.26191 | 19.7704 |  | 2006-09-01 | 10:22 | 37320 | 43.2479 | 0.25949 | 19.6032 |  | 2028-01-01 | 10:22 | 37320 | 82.4537 | 0.49472 | 34.2079 |  | 2007-01-01 | 10:22 | 37320 | 89.6278 | 0.53777 | 36.757 |  | 2028-01-01 | 10:22 | 37320 | 38.2709 | 0.22963 | 17.416 |  | 2007-01-01 | 10:22 | 37320 | 39.6815 | 0.23809 | 18.0639
| 2029-09-01 | 10:23 | 37380 | 326.221 | 1.9573 | 97.2645 |  | 2029-09-01 | 10:23 | 37380 | 326.221 | 1.9573 | 97.2645 |  | 2006-09-01 | 10:23 | 37380 | 312.02 | 1.8721 | 94.2159 |  | 2029-09-01 | 10:23 | 37380 | 181.843 | 1.0911 | 60.9764 |  | 2006-09-01 | 10:23 | 37380 | 116.046 | 0.69628 | 47.5752 |  | 2028-01-01 | 10:23 | 37380 | 317.497 | 1.905 | 95.0479 |  | 2007-01-01 | 10:23 | 37380 | 308.069 | 1.8484 | 93.3944 |  | 2028-01-01 | 10:23 | 37380 | 82.5084 | 0.49505 | 34.703 |  | 2007-01-01 | 10:23 | 37380 | 89.6231 | 0.53774 | 37.2948 |  | 2029-09-01 | 10:23 | 37380 | 326.221 | 1.9573 | 97.2645 |  | 2006-09-01 | 10:23 | 37380 | 312.02 | 1.8721 | 94.2159 |  | 2029-09-01 | 10:23 | 37380 | 123.53 | 0.74118 | 43.4987 |  | 2006-09-01 | 10:23 | 37380 | 66.694 | 0.40016 | 30.752 |  | 2028-01-01 | 10:23 | 37380 | 317.497 | 1.905 | 95.0479 |  | 2007-01-01 | 10:23 | 37380 | 308.069 | 1.8484 | 93.3944 |  | 2028-01-01 | 10:23 | 37380 | 45.7714 | 0.27463 | 20.7155 |  | 2007-01-01 | 10:23 | 37380 | 50.6879 | 0.30413 | 22.7504 |  | 2029-09-01 | 10:23 | 37380 | 326.221 | 1.9573 | 97.2645 |  | 2006-09-01 | 10:23 | 37380 | 312.02 | 1.8721 | 94.2159 |  | 2029-09-01 | 10:23 | 37380 | 93.3974 | 0.56038 | 33.5587 |  | 2006-09-01 | 10:23 | 37380 | 46.6338 | 0.2798 | 22.6012 |  | 2028-01-01 | 10:23 | 37380 | 317.497 | 1.905 | 95.0479 |  | 2007-01-01 | 10:23 | 37380 | 308.069 | 1.8484 | 93.3944 |  | 2028-01-01 | 10:23 | 37380 | 31.6516 | 0.18991 | 14.7202 |  | 2007-01-01 | 10:23 | 37380 | 35.2915 | 0.21175 | 16.3041 |  | 2029-09-01 | 10:23 | 37380 | 101.12 | 0.60672 | 41.3485 |  | 2029-09-01 | 10:23 | 37380 | 66.0349 | 0.39621 | 28.9756 |  | 2029-09-01 | 10:23 | 37380 | 43.6489 | 0.26189 | 20.0323 |  | 2006-09-01 | 10:23 | 37380 | 43.2374 | 0.25942 | 19.8626 |  | 2028-01-01 | 10:23 | 37380 | 82.5084 | 0.49505 | 34.703 |  | 2007-01-01 | 10:23 | 37380 | 89.6231 | 0.53774 | 37.2948 |  | 2028-01-01 | 10:23 | 37380 | 38.2818 | 0.22969 | 17.6457 |  | 2007-01-01 | 10:23 | 37380 | 39.6748 | 0.23805 | 18.302
| 2029-09-01 | 10:24 | 37440 | 328.285 | 1.9697 | 99.2342 |  | 2029-09-01 | 10:24 | 37440 | 328.285 | 1.9697 | 99.2342 |  | 2006-09-01 | 10:24 | 37440 | 313.755 | 1.8825 | 96.0984 |  | 2029-09-01 | 10:24 | 37440 | 182.901 | 1.0974 | 62.0739 |  | 2006-09-01 | 10:24 | 37440 | 115.972 | 0.69583 | 48.271 |  | 2028-01-01 | 10:24 | 37440 | 319.562 | 1.9174 | 96.9653 |  | 2007-01-01 | 10:24 | 37440 | 309.812 | 1.8589 | 95.2533 |  | 2028-01-01 | 10:24 | 37440 | 82.5628 | 0.49538 | 35.1983 |  | 2007-01-01 | 10:24 | 37440 | 89.6163 | 0.5377 | 37.8325 |  | 2029-09-01 | 10:24 | 37440 | 328.285 | 1.9697 | 99.2342 |  | 2006-09-01 | 10:24 | 37440 | 313.755 | 1.8825 | 96.0984 |  | 2029-09-01 | 10:24 | 37440 | 124.363 | 0.74618 | 44.2449 |  | 2006-09-01 | 10:24 | 37440 | 66.6395 | 0.39984 | 31.1518 |  | 2028-01-01 | 10:24 | 37440 | 319.562 | 1.9174 | 96.9653 |  | 2007-01-01 | 10:24 | 37440 | 309.812 | 1.8589 | 95.2533 |  | 2028-01-01 | 10:24 | 37440 | 45.7968 | 0.27478 | 20.9903 |  | 2007-01-01 | 10:24 | 37440 | 50.6786 | 0.30407 | 23.0545 |  | 2029-09-01 | 10:24 | 37440 | 328.285 | 1.9697 | 99.2342 |  | 2006-09-01 | 10:24 | 37440 | 313.755 | 1.8825 | 96.0984 |  | 2029-09-01 | 10:24 | 37440 | 94.1181 | 0.56471 | 34.1234 |  | 2006-09-01 | 10:24 | 37440 | 46.608 | 0.27965 | 22.8809 |  | 2028-01-01 | 10:24 | 37440 | 319.562 | 1.9174 | 96.9653 |  | 2007-01-01 | 10:24 | 37440 | 309.812 | 1.8589 | 95.2533 |  | 2028-01-01 | 10:24 | 37440 | 31.669 | 0.19001 | 14.9102 |  | 2007-01-01 | 10:24 | 37440 | 35.2865 | 0.21172 | 16.5158 |  | 2029-09-01 | 10:24 | 37440 | 101.143 | 0.60686 | 41.9553 |  | 2029-09-01 | 10:24 | 37440 | 66.032 | 0.39619 | 29.3718 |  | 2029-09-01 | 10:24 | 37440 | 43.6466 | 0.26188 | 20.2942 |  | 2006-09-01 | 10:24 | 37440 | 43.2268 | 0.25936 | 20.122 |  | 2028-01-01 | 10:24 | 37440 | 82.5628 | 0.49538 | 35.1983 |  | 2007-01-01 | 10:24 | 37440 | 89.6163 | 0.5377 | 37.8325 |  | 2028-01-01 | 10:24 | 37440 | 38.2927 | 0.22976 | 17.8755 |  | 2007-01-01 | 10:24 | 37440 | 39.6681 | 0.23801 | 18.54
| 2029-09-01 | 10:25 | 37500 | 330.318 | 1.9819 | 101.2162 |  | 2029-09-01 | 10:25 | 37500 | 330.318 | 1.9819 | 101.2162 |  | 2006-09-01 | 10:25 | 37500 | 315.451 | 1.8927 | 97.9911 |  | 2029-09-01 | 10:25 | 37500 | 183.965 | 1.1038 | 63.1776 |  | 2006-09-01 | 10:25 | 37500 | 115.896 | 0.69538 | 48.9664 |  | 2028-01-01 | 10:25 | 37500 | 321.603 | 1.9296 | 98.8949 |  | 2007-01-01 | 10:25 | 37500 | 311.521 | 1.8691 | 97.1224 |  | 2028-01-01 | 10:25 | 37500 | 82.6172 | 0.4957 | 35.694 |  | 2007-01-01 | 10:25 | 37500 | 89.6078 | 0.53765 | 38.3701 |  | 2029-09-01 | 10:25 | 37500 | 330.318 | 1.9819 | 101.2162 |  | 2006-09-01 | 10:25 | 37500 | 315.451 | 1.8927 | 97.9911 |  | 2029-09-01 | 10:25 | 37500 | 125.212 | 0.75127 | 44.9961 |  | 2006-09-01 | 10:25 | 37500 | 66.5863 | 0.39952 | 31.5513 |  | 2028-01-01 | 10:25 | 37500 | 321.603 | 1.9296 | 98.8949 |  | 2007-01-01 | 10:25 | 37500 | 311.521 | 1.8691 | 97.1224 |  | 2028-01-01 | 10:25 | 37500 | 45.8224 | 0.27493 | 21.2652 |  | 2007-01-01 | 10:25 | 37500 | 50.6693 | 0.30402 | 23.3585 |  | 2029-09-01 | 10:25 | 37500 | 330.318 | 1.9819 | 101.2162 |  | 2006-09-01 | 10:25 | 37500 | 315.451 | 1.8927 | 97.9911 |  | 2029-09-01 | 10:25 | 37500 | 94.8563 | 0.56914 | 34.6925 |  | 2006-09-01 | 10:25 | 37500 | 46.5831 | 0.2795 | 23.1604 |  | 2028-01-01 | 10:25 | 37500 | 321.603 | 1.9296 | 98.8949 |  | 2007-01-01 | 10:25 | 37500 | 311.521 | 1.8691 | 97.1224 |  | 2028-01-01 | 10:25 | 37500 | 31.6865 | 0.19012 | 15.1003 |  | 2007-01-01 | 10:25 | 37500 | 35.2815 | 0.21169 | 16.7275 |  | 2029-09-01 | 10:25 | 37500 | 101.163 | 0.60698 | 42.5623 |  | 2029-09-01 | 10:25 | 37500 | 66.0288 | 0.39617 | 29.768 |  | 2029-09-01 | 10:25 | 37500 | 43.6443 | 0.26187 | 20.556 |  | 2006-09-01 | 10:25 | 37500 | 43.216 | 0.2593 | 20.3813 |  | 2028-01-01 | 10:25 | 37500 | 82.6172 | 0.4957 | 35.694 |  | 2007-01-01 | 10:25 | 37500 | 89.6078 | 0.53765 | 38.3701 |  | 2028-01-01 | 10:25 | 37500 | 38.3036 | 0.22982 | 18.1053 |  | 2007-01-01 | 10:25 | 37500 | 39.6615 | 0.23797 | 18.778
| 2029-09-01 | 10:26 | 37560 | 332.321 | 1.9939 | 103.2101 |  | 2029-09-01 | 10:26 | 37560 | 332.321 | 1.9939 | 103.2101 |  | 2006-09-01 | 10:26 | 37560 | 317.108 | 1.9026 | 99.8938 |  | 2029-09-01 | 10:26 | 37560 | 185.039 | 1.1102 | 64.2879 |  | 2006-09-01 | 10:26 | 37560 | 115.818 | 0.69491 | 49.6613 |  | 2028-01-01 | 10:26 | 37560 | 323.62 | 1.9417 | 100.8366 |  | 2007-01-01 | 10:26 | 37560 | 313.195 | 1.8792 | 99.0016 |  | 2028-01-01 | 10:26 | 37560 | 82.6713 | 0.49603 | 36.1901 |  | 2007-01-01 | 10:26 | 37560 | 89.5977 | 0.53759 | 38.9077 |  | 2029-09-01 | 10:26 | 37560 | 332.321 | 1.9939 | 103.2101 |  | 2006-09-01 | 10:26 | 37560 | 317.108 | 1.9026 | 99.8938 |  | 2029-09-01 | 10:26 | 37560 | 126.078 | 0.75647 | 45.7526 |  | 2006-09-01 | 10:26 | 37560 | 66.5344 | 0.39921 | 31.9505 |  | 2028-01-01 | 10:26 | 37560 | 323.62 | 1.9417 | 100.8366 |  | 2007-01-01 | 10:26 | 37560 | 313.195 | 1.8792 | 99.0016 |  | 2028-01-01 | 10:26 | 37560 | 45.8481 | 0.27509 | 21.5403 |  | 2007-01-01 | 10:26 | 37560 | 50.6598 | 0.30396 | 23.6625 |  | 2029-09-01 | 10:26 | 37560 | 332.321 | 1.9939 | 103.2101 |  | 2006-09-01 | 10:26 | 37560 | 317.108 | 1.9026 | 99.8938 |  | 2029-09-01 | 10:26 | 37560 | 95.6126 | 0.57368 | 35.2662 |  | 2006-09-01 | 10:26 | 37560 | 46.5589 | 0.27935 | 23.4397 |  | 2028-01-01 | 10:26 | 37560 | 323.62 | 1.9417 | 100.8366 |  | 2007-01-01 | 10:26 | 37560 | 313.195 | 1.8792 | 99.0016 |  | 2028-01-01 | 10:26 | 37560 | 31.704 | 0.19022 | 15.2905 |  | 2007-01-01 | 10:26 | 37560 | 35.2765 | 0.21166 | 16.9392 |  | 2029-09-01 | 10:26 | 37560 | 101.182 | 0.60709 | 43.1694 |  | 2029-09-01 | 10:26 | 37560 | 66.0255 | 0.39615 | 30.1642 |  | 2029-09-01 | 10:26 | 37560 | 43.642 | 0.26185 | 20.8179 |  | 2006-09-01 | 10:26 | 37560 | 43.2049 | 0.25923 | 20.6405 |  | 2028-01-01 | 10:26 | 37560 | 82.6713 | 0.49603 | 36.1901 |  | 2007-01-01 | 10:26 | 37560 | 89.5977 | 0.53759 | 38.9077 |  | 2028-01-01 | 10:26 | 37560 | 38.3146 | 0.22989 | 18.3352 |  | 2007-01-01 | 10:26 | 37560 | 39.6549 | 0.23793 | 19.0159
| 2029-09-01 | 10:27 | 37620 | 334.295 | 2.0058 | 105.2158 |  | 2029-09-01 | 10:27 | 37620 | 334.295 | 2.0058 | 105.2158 |  | 2006-09-01 | 10:27 | 37620 | 318.726 | 1.9124 | 101.8061 |  | 2029-09-01 | 10:27 | 37620 | 186.121 | 1.1167 | 65.4046 |  | 2006-09-01 | 10:27 | 37620 | 115.738 | 0.69443 | 50.3557 |  | 2028-01-01 | 10:27 | 37620 | 325.614 | 1.9537 | 102.7903 |  | 2007-01-01 | 10:27 | 37620 | 314.835 | 1.889 | 100.8906 |  | 2028-01-01 | 10:27 | 37620 | 82.7253 | 0.49635 | 36.6864 |  | 2007-01-01 | 10:27 | 37620 | 89.586 | 0.53752 | 39.4452 |  | 2029-09-01 | 10:27 | 37620 | 334.295 | 2.0058 | 105.2158 |  | 2006-09-01 | 10:27 | 37620 | 318.726 | 1.9124 | 101.8061 |  | 2029-09-01 | 10:27 | 37620 | 126.962 | 0.76177 | 46.5144 |  | 2006-09-01 | 10:27 | 37620 | 66.4837 | 0.3989 | 32.3494 |  | 2028-01-01 | 10:27 | 37620 | 325.614 | 1.9537 | 102.7903 |  | 2007-01-01 | 10:27 | 37620 | 314.835 | 1.889 | 100.8906 |  | 2028-01-01 | 10:27 | 37620 | 45.8738 | 0.27524 | 21.8155 |  | 2007-01-01 | 10:27 | 37620 | 50.6503 | 0.3039 | 23.9664 |  | 2029-09-01 | 10:27 | 37620 | 334.295 | 2.0058 | 105.2158 |  | 2006-09-01 | 10:27 | 37620 | 318.726 | 1.9124 | 101.8061 |  | 2029-09-01 | 10:27 | 37620 | 96.3879 | 0.57833 | 35.8445 |  | 2006-09-01 | 10:27 | 37620 | 46.5353 | 0.27921 | 23.719 |  | 2028-01-01 | 10:27 | 37620 | 325.614 | 1.9537 | 102.7903 |  | 2007-01-01 | 10:27 | 37620 | 314.835 | 1.889 | 100.8906 |  | 2028-01-01 | 10:27 | 37620 | 31.7215 | 0.19033 | 15.4809 |  | 2007-01-01 | 10:27 | 37620 | 35.2715 | 0.21163 | 17.1508 |  | 2029-09-01 | 10:27 | 37620 | 101.199 | 0.60719 | 43.7766 |  | 2029-09-01 | 10:27 | 37620 | 66.0219 | 0.39613 | 30.5603 |  | 2029-09-01 | 10:27 | 37620 | 43.6396 | 0.26184 | 21.0797 |  | 2006-09-01 | 10:27 | 37620 | 43.1937 | 0.25916 | 20.8997 |  | 2028-01-01 | 10:27 | 37620 | 82.7253 | 0.49635 | 36.6864 |  | 2007-01-01 | 10:27 | 37620 | 89.586 | 0.53752 | 39.4452 |  | 2028-01-01 | 10:27 | 37620 | 38.3256 | 0.22995 | 18.5651 |  | 2007-01-01 | 10:27 | 37620 | 39.6483 | 0.23789 | 19.2538
| 2029-09-01 | 10:28 | 37680 | 336.239 | 2.0174 | 107.2333 |  | 2029-09-01 | 10:28 | 37680 | 336.239 | 2.0174 | 107.2333 |  | 2006-09-01 | 10:28 | 37680 | 320.306 | 1.9218 | 103.728 |  | 2029-09-01 | 10:28 | 37680 | 187.214 | 1.1233 | 66.5279 |  | 2006-09-01 | 10:28 | 37680 | 115.655 | 0.69393 | 51.0497 |  | 2028-01-01 | 10:28 | 37680 | 327.585 | 1.9655 | 104.7558 |  | 2007-01-01 | 10:28 | 37680 | 316.443 | 1.8987 | 102.7893 |  | 2028-01-01 | 10:28 | 37680 | 82.7792 | 0.49668 | 37.1831 |  | 2007-01-01 | 10:28 | 37680 | 89.573 | 0.53744 | 39.9827 |  | 2029-09-01 | 10:28 | 37680 | 336.239 | 2.0174 | 107.2333 |  | 2006-09-01 | 10:28 | 37680 | 320.306 | 1.9218 | 103.728 |  | 2029-09-01 | 10:28 | 37680 | 127.865 | 0.76719 | 47.2816 |  | 2006-09-01 | 10:28 | 37680 | 66.434 | 0.3986 | 32.748 |  | 2028-01-01 | 10:28 | 37680 | 327.585 | 1.9655 | 104.7558 |  | 2007-01-01 | 10:28 | 37680 | 316.443 | 1.8987 | 102.7893 |  | 2028-01-01 | 10:28 | 37680 | 45.8997 | 0.2754 | 22.0909 |  | 2007-01-01 | 10:28 | 37680 | 50.6407 | 0.30384 | 24.2702 |  | 2029-09-01 | 10:28 | 37680 | 336.239 | 2.0174 | 107.2333 |  | 2006-09-01 | 10:28 | 37680 | 320.306 | 1.9218 | 103.728 |  | 2029-09-01 | 10:28 | 37680 | 97.1831 | 0.5831 | 36.4276 |  | 2006-09-01 | 10:28 | 37680 | 46.5123 | 0.27907 | 23.998 |  | 2028-01-01 | 10:28 | 37680 | 327.585 | 1.9655 | 104.7558 |  | 2007-01-01 | 10:28 | 37680 | 316.443 | 1.8987 | 102.7893 |  | 2028-01-01 | 10:28 | 37680 | 31.7391 | 0.19043 | 15.6713 |  | 2007-01-01 | 10:28 | 37680 | 35.2665 | 0.2116 | 17.3624 |  | 2029-09-01 | 10:28 | 37680 | 101.213 | 0.60728 | 44.3839 |  | 2029-09-01 | 10:28 | 37680 | 66.0182 | 0.39611 | 30.9564 |  | 2029-09-01 | 10:28 | 37680 | 43.6373 | 0.26182 | 21.3415 |  | 2006-09-01 | 10:28 | 37680 | 43.1824 | 0.25909 | 21.1588 |  | 2028-01-01 | 10:28 | 37680 | 82.7792 | 0.49668 | 37.1831 |  | 2007-01-01 | 10:28 | 37680 | 89.573 | 0.53744 | 39.9827 |  | 2028-01-01 | 10:28 | 37680 | 38.3366 | 0.23002 | 18.7951 |  | 2007-01-01 | 10:28 | 37680 | 39.6418 | 0.23785 | 19.4916
| 2029-09-01 | 10:29 | 37740 | 338.155 | 2.0289 | 109.2622 |  | 2029-09-01 | 10:29 | 37740 | 338.155 | 2.0289 | 109.2622 |  | 2006-09-01 | 10:29 | 37740 | 321.848 | 1.9311 | 105.659 |  | 2029-09-01 | 10:29 | 37740 | 188.318 | 1.1299 | 67.6578 |  | 2006-09-01 | 10:29 | 37740 | 115.57 | 0.69342 | 51.7431 |  | 2028-01-01 | 10:29 | 37740 | 329.533 | 1.9772 | 106.733 |  | 2007-01-01 | 10:29 | 37740 | 318.018 | 1.9081 | 104.6974 |  | 2028-01-01 | 10:29 | 37740 | 82.8329 | 0.497 | 37.6801 |  | 2007-01-01 | 10:29 | 37740 | 89.5587 | 0.53735 | 40.52 |  | 2029-09-01 | 10:29 | 37740 | 338.155 | 2.0289 | 109.2622 |  | 2006-09-01 | 10:29 | 37740 | 321.848 | 1.9311 | 105.659 |  | 2029-09-01 | 10:29 | 37740 | 128.786 | 0.77272 | 48.0543 |  | 2006-09-01 | 10:29 | 37740 | 66.3854 | 0.39831 | 33.1464 |  | 2028-01-01 | 10:29 | 37740 | 329.533 | 1.9772 | 106.733 |  | 2007-01-01 | 10:29 | 37740 | 318.018 | 1.9081 | 104.6974 |  | 2028-01-01 | 10:29 | 37740 | 45.9257 | 0.27555 | 22.3665 |  | 2007-01-01 | 10:29 | 37740 | 50.6311 | 0.30379 | 24.574 |  | 2029-09-01 | 10:29 | 37740 | 338.155 | 2.0289 | 109.2622 |  | 2006-09-01 | 10:29 | 37740 | 321.848 | 1.9311 | 105.659 |  | 2029-09-01 | 10:29 | 37740 | 97.9992 | 0.588 | 37.0156 |  | 2006-09-01 | 10:29 | 37740 | 46.4898 | 0.27894 | 24.277 |  | 2028-01-01 | 10:29 | 37740 | 329.533 | 1.9772 | 106.733 |  | 2007-01-01 | 10:29 | 37740 | 318.018 | 1.9081 | 104.6974 |  | 2028-01-01 | 10:29 | 37740 | 31.7567 | 0.19054 | 15.8618 |  | 2007-01-01 | 10:29 | 37740 | 35.2616 | 0.21157 | 17.574 |  | 2029-09-01 | 10:29 | 37740 | 101.227 | 0.60736 | 44.9912 |  | 2029-09-01 | 10:29 | 37740 | 66.0144 | 0.39609 | 31.3525 |  | 2029-09-01 | 10:29 | 37740 | 43.635 | 0.26181 | 21.6033 |  | 2006-09-01 | 10:29 | 37740 | 43.1708 | 0.25902 | 21.4178 |  | 2028-01-01 | 10:29 | 37740 | 82.8329 | 0.497 | 37.6801 |  | 2007-01-01 | 10:29 | 37740 | 89.5587 | 0.53735 | 40.52 |  | 2028-01-01 | 10:29 | 37740 | 38.3476 | 0.23009 | 19.0252 |  | 2007-01-01 | 10:29 | 37740 | 39.6353 | 0.23781 | 19.7294
| 2029-09-01 | 10:30 | 37800 | 340.042 | 2.0403 | 111.3025 |  | 2029-09-01 | 10:30 | 37800 | 340.042 | 2.0403 | 111.3025 |  | 2006-09-01 | 10:30 | 37800 | 323.351 | 1.9401 | 107.5991 |  | 2029-09-01 | 10:30 | 37800 | 189.433 | 1.1366 | 68.7944 |  | 2006-09-01 | 10:30 | 37800 | 115.484 | 0.6929 | 52.436 |  | 2028-01-01 | 10:30 | 37800 | 331.459 | 1.9888 | 108.7218 |  | 2007-01-01 | 10:30 | 37800 | 319.562 | 1.9174 | 106.6148 |  | 2028-01-01 | 10:30 | 37800 | 82.8865 | 0.49732 | 38.1774 |  | 2007-01-01 | 10:30 | 37800 | 89.5433 | 0.53726 | 41.0573 |  | 2029-09-01 | 10:30 | 37800 | 340.042 | 2.0403 | 111.3025 |  | 2006-09-01 | 10:30 | 37800 | 323.351 | 1.9401 | 107.5991 |  | 2029-09-01 | 10:30 | 37800 | 129.729 | 0.77837 | 48.8327 |  | 2006-09-01 | 10:30 | 37800 | 66.3376 | 0.39803 | 33.5444 |  | 2028-01-01 | 10:30 | 37800 | 331.459 | 1.9888 | 108.7218 |  | 2007-01-01 | 10:30 | 37800 | 319.562 | 1.9174 | 106.6148 |  | 2028-01-01 | 10:30 | 37800 | 45.9517 | 0.27571 | 22.6422 |  | 2007-01-01 | 10:30 | 37800 | 50.6214 | 0.30373 | 24.8777 |  | 2029-09-01 | 10:30 | 37800 | 340.042 | 2.0403 | 111.3025 |  | 2006-09-01 | 10:30 | 37800 | 323.351 | 1.9401 | 107.5991 |  | 2029-09-01 | 10:30 | 37800 | 98.8372 | 0.59302 | 37.6086 |  | 2006-09-01 | 10:30 | 37800 | 46.4677 | 0.27881 | 24.5558 |  | 2028-01-01 | 10:30 | 37800 | 331.459 | 1.9888 | 108.7218 |  | 2007-01-01 | 10:30 | 37800 | 319.562 | 1.9174 | 106.6148 |  | 2028-01-01 | 10:30 | 37800 | 31.7744 | 0.19065 | 16.0525 |  | 2007-01-01 | 10:30 | 37800 | 35.2567 | 0.21154 | 17.7855 |  | 2029-09-01 | 10:30 | 37800 | 101.238 | 0.60743 | 45.5987 |  | 2029-09-01 | 10:30 | 37800 | 66.0104 | 0.39606 | 31.7485 |  | 2029-09-01 | 10:30 | 37800 | 43.6326 | 0.2618 | 21.8651 |  | 2006-09-01 | 10:30 | 37800 | 43.1591 | 0.25895 | 21.6767 |  | 2028-01-01 | 10:30 | 37800 | 82.8865 | 0.49732 | 38.1774 |  | 2007-01-01 | 10:30 | 37800 | 89.5433 | 0.53726 | 41.0573 |  | 2028-01-01 | 10:30 | 37800 | 38.3586 | 0.23015 | 19.2554 |  | 2007-01-01 | 10:30 | 37800 | 39.6289 | 0.23777 | 19.9672
| 2029-09-01 | 10:31 | 37860 | 335.647 | 0 | 111.3025 |  | 2029-09-01 | 10:31 | 37860 | 296.196 | 0 | 111.3025 |  | 2006-09-01 | 10:31 | 37860 | 259.77 | 0 | 107.5991 |  | 2029-09-01 | 10:31 | 37860 | 165.007 | 0 | 68.7944 |  | 2006-09-01 | 10:31 | 37860 | 92.7761 | 0 | 52.436 |  | 2028-01-01 | 10:31 | 37860 | 291.259 | 0 | 108.7218 |  | 2007-01-01 | 10:31 | 37860 | 242.311 | 0 | 106.6148 |  | 2028-01-01 | 10:31 | 37860 | 72.8339 | 0 | 38.1774 |  | 2007-01-01 | 10:31 | 37860 | 67.8971 | 0 | 41.0573 |  | 2029-09-01 | 10:31 | 37860 | 272.666 | 0 | 111.3025 |  | 2006-09-01 | 10:31 | 37860 | 229.042 | 0 | 107.5991 |  | 2029-09-01 | 10:31 | 37860 | 104.024 | 0 | 48.8327 |  | 2006-09-01 | 10:31 | 37860 | 46.9895 | 0 | 33.5444 |  | 2028-01-01 | 10:31 | 37860 | 266.426 | 0 | 108.7218 |  | 2007-01-01 | 10:31 | 37860 | 207.277 | 0 | 106.6148 |  | 2028-01-01 | 10:31 | 37860 | 36.9359 | 0 | 22.6422 |  | 2007-01-01 | 10:31 | 37860 | 32.8345 | 0 | 24.8777 |  | 2029-09-01 | 10:31 | 37860 | 259.902 | 0 | 111.3025 |  | 2006-09-01 | 10:31 | 37860 | 213.59 | 0 | 107.5991 |  | 2029-09-01 | 10:31 | 37860 | 75.5436 | 0 | 37.6086 |  | 2006-09-01 | 10:31 | 37860 | 30.6942 | 0 | 24.5558 |  | 2028-01-01 | 10:31 | 37860 | 248.489 | 0 | 108.7218 |  | 2007-01-01 | 10:31 | 37860 | 190.473 | 0 | 106.6148 |  | 2028-01-01 | 10:31 | 37860 | 23.8207 | 0 | 16.0525 |  | 2007-01-01 | 10:31 | 37860 | 21.0146 | 0 | 17.7855 |  | 2029-09-01 | 10:31 | 37860 | 95.1605 | 0 | 45.5987 |  | 2029-09-01 | 10:31 | 37860 | 60.0917 | 0 | 31.7485 |  | 2029-09-01 | 10:31 | 37860 | 37.9657 | 0 | 21.8651 |  | 2006-09-01 | 10:31 | 37860 | 37.464 | 0 | 21.6767 |  | 2028-01-01 | 10:31 | 37860 | 72.8339 | 0 | 38.1774 |  | 2007-01-01 | 10:31 | 37860 | 67.8971 | 0 | 41.0573 |  | 2028-01-01 | 10:31 | 37860 | 31.1851 | 0 | 19.2554 |  | 2007-01-01 | 10:31 | 37860 | 28.0893 | 0 | 19.9672
| 2029-09-01 | 10:32 | 37920 | 331.307 | 0 | 111.3025 |  | 2029-09-01 | 10:32 | 37920 | 257.842 | 0 | 111.3025 |  | 2006-09-01 | 10:32 | 37920 | 207.953 | 0 | 107.5991 |  | 2029-09-01 | 10:32 | 37920 | 143.641 | 0 | 68.7944 |  | 2006-09-01 | 10:32 | 37920 | 74.2698 | 0 | 52.436 |  | 2028-01-01 | 10:32 | 37920 | 256.1 | 0 | 108.7218 |  | 2007-01-01 | 10:32 | 37920 | 183.568 | 0 | 106.6148 |  | 2028-01-01 | 10:32 | 37920 | 64.0417 | 0 | 38.1774 |  | 2007-01-01 | 10:32 | 37920 | 51.437 | 0 | 41.0573 |  | 2029-09-01 | 10:32 | 37920 | 218.421 | 0 | 111.3025 |  | 2006-09-01 | 10:32 | 37920 | 161.361 | 0 | 107.5991 |  | 2029-09-01 | 10:32 | 37920 | 83.3295 | 0 | 48.8327 |  | 2006-09-01 | 10:32 | 37920 | 33.1042 | 0 | 33.5444 |  | 2028-01-01 | 10:32 | 37920 | 214.346 | 0 | 108.7218 |  | 2007-01-01 | 10:32 | 37920 | 134.267 | 0 | 106.6148 |  | 2028-01-01 | 10:32 | 37920 | 29.7157 | 0 | 22.6422 |  | 2007-01-01 | 10:32 | 37920 | 21.2691 | 0 | 24.8777 |  | 2029-09-01 | 10:32 | 37920 | 198.409 | 0 | 111.3025 |  | 2006-09-01 | 10:32 | 37920 | 140.183 | 0 | 107.5991 |  | 2029-09-01 | 10:32 | 37920 | 57.67 | 0 | 37.6086 |  | 2006-09-01 | 10:32 | 37920 | 20.1452 | 0 | 24.5558 |  | 2028-01-01 | 10:32 | 37920 | 186.468 | 0 | 108.7218 |  | 2007-01-01 | 10:32 | 37920 | 113.355 | 0 | 106.6148 |  | 2028-01-01 | 10:32 | 37920 | 17.8752 | 0 | 16.0525 |  | 2007-01-01 | 10:32 | 37920 | 12.5063 | 0 | 17.7855 |  | 2029-09-01 | 10:32 | 37920 | 89.4473 | 0 | 45.5987 |  | 2029-09-01 | 10:32 | 37920 | 54.7036 | 0 | 31.7485 |  | 2029-09-01 | 10:32 | 37920 | 33.0346 | 0 | 21.8651 |  | 2006-09-01 | 10:32 | 37920 | 32.5185 | 0 | 21.6767 |  | 2028-01-01 | 10:32 | 37920 | 64.0417 | 0 | 38.1774 |  | 2007-01-01 | 10:32 | 37920 | 51.437 | 0 | 41.0573 |  | 2028-01-01 | 10:32 | 37920 | 25.3683 | 0 | 19.2554 |  | 2007-01-01 | 10:32 | 37920 | 19.8931 | 0 | 19.9672
| 2029-09-01 | 10:33 | 37980 | 327.022 | 0 | 111.3025 |  | 2029-09-01 | 10:33 | 37980 | 224.314 | 0 | 111.3025 |  | 2006-09-01 | 10:33 | 37980 | 165.889 | 0 | 107.5991 |  | 2029-09-01 | 10:33 | 37980 | 124.963 | 0 | 68.7944 |  | 2006-09-01 | 10:33 | 37980 | 59.2467 | 0 | 52.436 |  | 2028-01-01 | 10:33 | 37980 | 225.329 | 0 | 108.7218 |  | 2007-01-01 | 10:33 | 37980 | 138.942 | 0 | 106.6148 |  | 2028-01-01 | 10:33 | 37980 | 56.347 | 0 | 38.1774 |  | 2007-01-01 | 10:33 | 37980 | 38.9326 | 0 | 41.0573 |  | 2029-09-01 | 10:33 | 37980 | 174.793 | 0 | 111.3025 |  | 2006-09-01 | 10:33 | 37980 | 113.072 | 0 | 107.5991 |  | 2029-09-01 | 10:33 | 37980 | 66.6849 | 0 | 48.8327 |  | 2006-09-01 | 10:33 | 37980 | 23.1975 | 0 | 33.5444 |  | 2028-01-01 | 10:33 | 37980 | 172.6 | 0 | 108.7218 |  | 2007-01-01 | 10:33 | 37980 | 86.8597 | 0 | 106.6148 |  | 2028-01-01 | 10:33 | 37980 | 23.9283 | 0 | 22.6422 |  | 2007-01-01 | 10:33 | 37980 | 13.7593 | 0 | 24.8777 |  | 2029-09-01 | 10:33 | 37980 | 151.283 | 0 | 111.3025 |  | 2006-09-01 | 10:33 | 37980 | 91.4249 | 0 | 107.5991 |  | 2029-09-01 | 10:33 | 37980 | 43.9721 | 0 | 37.6086 |  | 2006-09-01 | 10:33 | 37980 | 13.1384 | 0 | 24.5558 |  | 2028-01-01 | 10:33 | 37980 | 140.06 | 0 | 108.7218 |  | 2007-01-01 | 10:33 | 37980 | 67.3575 | 0 | 106.6148 |  | 2028-01-01 | 10:33 | 37980 | 13.4265 | 0 | 16.0525 |  | 2007-01-01 | 10:33 | 37980 | 7.4314 | 0 | 17.7855 |  | 2029-09-01 | 10:33 | 37980 | 84.0769 | 0 | 45.5987 |  | 2029-09-01 | 10:33 | 37980 | 49.7983 | 0 | 31.7485 |  | 2029-09-01 | 10:33 | 37980 | 28.7439 | 0 | 21.8651 |  | 2006-09-01 | 10:33 | 37980 | 28.2242 | 0 | 21.6767 |  | 2028-01-01 | 10:33 | 37980 | 56.347 | 0 | 38.1774 |  | 2007-01-01 | 10:33 | 37980 | 38.9326 | 0 | 41.0573 |  | 2028-01-01 | 10:33 | 37980 | 20.6487 | 0 | 19.2554 |  | 2007-01-01 | 10:33 | 37980 | 14.0767 | 0 | 19.9672
| 2029-09-01 | 10:34 | 38040 | 322.791 | 0 | 111.3025 |  | 2029-09-01 | 10:34 | 38040 | 195.023 | 0 | 111.3025 |  | 2006-09-01 | 10:34 | 38040 | 131.875 | 0 | 107.5991 |  | 2029-09-01 | 10:34 | 38040 | 108.645 | 0 | 68.7944 |  | 2006-09-01 | 10:34 | 38040 | 47.0989 | 0 | 52.436 |  | 2028-01-01 | 10:34 | 38040 | 198.382 | 0 | 108.7218 |  | 2007-01-01 | 10:34 | 38040 | 105.073 | 0 | 106.6148 |  | 2028-01-01 | 10:34 | 38040 | 49.6084 | 0 | 38.1774 |  | 2007-01-01 | 10:34 | 38040 | 29.4421 | 0 | 41.0573 |  | 2029-09-01 | 10:34 | 38040 | 139.739 | 0 | 111.3025 |  | 2006-09-01 | 10:34 | 38040 | 78.8171 | 0 | 107.5991 |  | 2029-09-01 | 10:34 | 38040 | 53.3117 | 0 | 48.8327 |  | 2006-09-01 | 10:34 | 38040 | 16.1698 | 0 | 33.5444 |  | 2028-01-01 | 10:34 | 38040 | 139.109 | 0 | 108.7218 |  | 2007-01-01 | 10:34 | 38040 | 56.1185 | 0 | 106.6148 |  | 2028-01-01 | 10:34 | 38040 | 19.2853 | 0 | 22.6422 |  | 2007-01-01 | 10:34 | 38040 | 8.8897 | 0 | 24.8777 |  | 2029-09-01 | 10:34 | 38040 | 115.211 | 0 | 111.3025 |  | 2006-09-01 | 10:34 | 38040 | 59.2557 | 0 | 107.5991 |  | 2029-09-01 | 10:34 | 38040 | 33.4874 | 0 | 37.6086 |  | 2006-09-01 | 10:34 | 38040 | 8.5154 | 0 | 24.5558 |  | 2028-01-01 | 10:34 | 38040 | 105.303 | 0 | 108.7218 |  | 2007-01-01 | 10:34 | 38040 | 39.965 | 0 | 106.6148 |  | 2028-01-01 | 10:34 | 38040 | 10.0946 | 0 | 16.0525 |  | 2007-01-01 | 10:34 | 38040 | 4.4093 | 0 | 17.7855 |  | 2029-09-01 | 10:34 | 38040 | 79.0285 | 0 | 45.5987 |  | 2029-09-01 | 10:34 | 38040 | 45.3328 | 0 | 31.7485 |  | 2029-09-01 | 10:34 | 38040 | 25.0104 | 0 | 21.8651 |  | 2006-09-01 | 10:34 | 38040 | 24.4951 | 0 | 21.6767 |  | 2028-01-01 | 10:34 | 38040 | 49.6084 | 0 | 38.1774 |  | 2007-01-01 | 10:34 | 38040 | 29.4421 | 0 | 41.0573 |  | 2028-01-01 | 10:34 | 38040 | 16.8171 | 0 | 19.2554 |  | 2007-01-01 | 10:34 | 38040 | 9.9527 | 0 | 19.9672
| 2029-09-01 | 10:35 | 38100 | 318.613 | 0 | 111.3025 |  | 2029-09-01 | 10:35 | 38100 | 169.452 | 0 | 111.3025 |  | 2006-09-01 | 10:35 | 38100 | 104.477 | 0 | 107.5991 |  | 2029-09-01 | 10:35 | 38100 | 94.3994 | 0 | 68.7944 |  | 2006-09-01 | 10:35 | 38100 | 37.3136 | 0 | 52.436 |  | 2028-01-01 | 10:35 | 38100 | 174.769 | 0 | 108.7218 |  | 2007-01-01 | 10:35 | 38100 | 79.3904 | 0 | 106.6148 |  | 2028-01-01 | 10:35 | 38100 | 43.7036 | 0 | 38.1774 |  | 2007-01-01 | 10:35 | 38100 | 22.2457 | 0 | 41.0573 |  | 2029-09-01 | 10:35 | 38100 | 111.604 | 0 | 111.3025 |  | 2006-09-01 | 10:35 | 38100 | 54.6542 | 0 | 107.5991 |  | 2029-09-01 | 10:35 | 38100 | 42.5779 | 0 | 48.8327 |  | 2006-09-01 | 10:35 | 38100 | 11.2127 | 0 | 33.5444 |  | 2028-01-01 | 10:35 | 38100 | 112.216 | 0 | 108.7218 |  | 2007-01-01 | 10:35 | 38100 | 36.211 | 0 | 106.6148 |  | 2028-01-01 | 10:35 | 38100 | 15.557 | 0 | 22.6422 |  | 2007-01-01 | 10:35 | 38100 | 5.7362 | 0 | 24.8777 |  | 2029-09-01 | 10:35 | 38100 | 87.6347 | 0 | 111.3025 |  | 2006-09-01 | 10:35 | 38100 | 38.1708 | 0 | 107.5991 |  | 2029-09-01 | 10:35 | 38100 | 25.4721 | 0 | 37.6086 |  | 2006-09-01 | 10:35 | 38100 | 5.4854 | 0 | 24.5558 |  | 2028-01-01 | 10:35 | 38100 | 79.2469 | 0 | 108.7218 |  | 2007-01-01 | 10:35 | 38100 | 23.6772 | 0 | 106.6148 |  | 2028-01-01 | 10:35 | 38100 | 7.5968 | 0 | 16.0525 |  | 2007-01-01 | 10:35 | 38100 | 2.6123 | 0 | 17.7855 |  | 2029-09-01 | 10:35 | 38100 | 74.283 | 0 | 45.5987 |  | 2029-09-01 | 10:35 | 38100 | 41.2675 | 0 | 31.7485 |  | 2029-09-01 | 10:35 | 38100 | 21.7617 | 0 | 21.8651 |  | 2006-09-01 | 10:35 | 38100 | 21.2572 | 0 | 21.6767 |  | 2028-01-01 | 10:35 | 38100 | 43.7036 | 0 | 38.1774 |  | 2007-01-01 | 10:35 | 38100 | 22.2457 | 0 | 41.0573 |  | 2028-01-01 | 10:35 | 38100 | 13.7046 | 0 | 19.2554 |  | 2007-01-01 | 10:35 | 38100 | 7.0312 | 0 | 19.9672
| 2029-09-01 | 10:36 | 38160 | 314.488 | 0 | 111.3025 |  | 2029-09-01 | 10:36 | 38160 | 147.141 | 0 | 111.3025 |  | 2006-09-01 | 10:36 | 38160 | 82.4905 | 0 | 107.5991 |  | 2029-09-01 | 10:36 | 38160 | 81.9704 | 0 | 68.7944 |  | 2006-09-01 | 10:36 | 38160 | 29.4612 | 0 | 52.436 |  | 2028-01-01 | 10:36 | 38160 | 154.063 | 0 | 108.7218 |  | 2007-01-01 | 10:36 | 38160 | 59.9342 | 0 | 106.6148 |  | 2028-01-01 | 10:36 | 38160 | 38.5259 | 0 | 38.1774 |  | 2007-01-01 | 10:36 | 38160 | 16.7939 | 0 | 41.0573 |  | 2029-09-01 | 10:36 | 38160 | 89.0451 | 0 | 111.3025 |  | 2006-09-01 | 10:36 | 38160 | 37.7045 | 0 | 107.5991 |  | 2029-09-01 | 10:36 | 38160 | 33.9715 | 0 | 48.8327 |  | 2006-09-01 | 10:36 | 38160 | 7.7353 | 0 | 33.5444 |  | 2028-01-01 | 10:36 | 38160 | 90.6028 | 0 | 108.7218 |  | 2007-01-01 | 10:36 | 38160 | 23.3362 | 0 | 106.6148 |  | 2028-01-01 | 10:36 | 38160 | 12.5607 | 0 | 22.6422 |  | 2007-01-01 | 10:36 | 38160 | 3.6967 | 0 | 24.8777 |  | 2029-09-01 | 10:36 | 38160 | 66.5789 | 0 | 111.3025 |  | 2006-09-01 | 10:36 | 38160 | 24.4403 | 0 | 107.5991 |  | 2029-09-01 | 10:36 | 38160 | 19.3519 | 0 | 37.6086 |  | 2006-09-01 | 10:36 | 38160 | 3.5122 | 0 | 24.5558 |  | 2028-01-01 | 10:36 | 38160 | 59.6949 | 0 | 108.7218 |  | 2007-01-01 | 10:36 | 38160 | 14.0071 | 0 | 106.6148 |  | 2028-01-01 | 10:36 | 38160 | 5.7225 | 0 | 16.0525 |  | 2007-01-01 | 10:36 | 38160 | 1.5454 | 0 | 17.7855 |  | 2029-09-01 | 10:36 | 38160 | 69.8222 | 0 | 45.5987 |  | 2029-09-01 | 10:36 | 38160 | 37.5667 | 0 | 31.7485 |  | 2029-09-01 | 10:36 | 38160 | 18.935 | 0 | 21.8651 |  | 2006-09-01 | 10:36 | 38160 | 18.4461 | 0 | 21.6767 |  | 2028-01-01 | 10:36 | 38160 | 38.5259 | 0 | 38.1774 |  | 2007-01-01 | 10:36 | 38160 | 16.7939 | 0 | 41.0573 |  | 2028-01-01 | 10:36 | 38160 | 11.1746 | 0 | 19.2554 |  | 2007-01-01 | 10:36 | 38160 | 4.9633 | 0 | 19.9672
| 2029-09-01 | 10:37 | 38220 | 310.416 | 0 | 111.3025 |  | 2029-09-01 | 10:37 | 38220 | 127.688 | 0 | 111.3025 |  | 2006-09-01 | 10:37 | 38220 | 64.9128 | 0 | 107.5991 |  | 2029-09-01 | 10:37 | 38220 | 71.1333 | 0 | 68.7944 |  | 2006-09-01 | 10:37 | 38220 | 23.1834 | 0 | 52.436 |  | 2028-01-01 | 10:37 | 38220 | 135.897 | 0 | 108.7218 |  | 2007-01-01 | 10:37 | 38220 | 45.2079 | 0 | 106.6148 |  | 2028-01-01 | 10:37 | 38220 | 33.9831 | 0 | 38.1774 |  | 2007-01-01 | 10:37 | 38220 | 12.6675 | 0 | 41.0573 |  | 2029-09-01 | 10:37 | 38220 | 70.9754 | 0 | 111.3025 |  | 2006-09-01 | 10:37 | 38220 | 25.8796 | 0 | 107.5991 |  | 2029-09-01 | 10:37 | 38220 | 27.0777 | 0 | 48.8327 |  | 2006-09-01 | 10:37 | 38220 | 5.3094 | 0 | 33.5444 |  | 2028-01-01 | 10:37 | 38220 | 73.2169 | 0 | 108.7218 |  | 2007-01-01 | 10:37 | 38220 | 15.0204 | 0 | 106.6148 |  | 2028-01-01 | 10:37 | 38220 | 10.1504 | 0 | 22.6422 |  | 2007-01-01 | 10:37 | 38220 | 2.3794 | 0 | 24.8777 |  | 2029-09-01 | 10:37 | 38220 | 50.5216 | 0 | 111.3025 |  | 2006-09-01 | 10:37 | 38220 | 15.5557 | 0 | 107.5991 |  | 2029-09-01 | 10:37 | 38220 | 14.6847 | 0 | 37.6086 |  | 2006-09-01 | 10:37 | 38220 | 2.2355 | 0 | 24.5558 |  | 2028-01-01 | 10:37 | 38220 | 45.0096 | 0 | 108.7218 |  | 2007-01-01 | 10:37 | 38220 | 8.2745 | 0 | 106.6148 |  | 2028-01-01 | 10:37 | 38220 | 4.3147 | 0 | 16.0525 |  | 2007-01-01 | 10:37 | 38220 | 0.91292 | 0 | 17.7855 |  | 2029-09-01 | 10:37 | 38220 | 65.629 | 0 | 45.5987 |  | 2029-09-01 | 10:37 | 38220 | 34.1976 | 0 | 31.7485 |  | 2029-09-01 | 10:37 | 38220 | 16.4754 | 0 | 21.8651 |  | 2006-09-01 | 10:37 | 38220 | 16.0057 | 0 | 21.6767 |  | 2028-01-01 | 10:37 | 38220 | 33.9831 | 0 | 38.1774 |  | 2007-01-01 | 10:37 | 38220 | 12.6675 | 0 | 41.0573 |  | 2028-01-01 | 10:37 | 38220 | 9.117 | 0 | 19.2554 |  | 2007-01-01 | 10:37 | 38220 | 3.5008 | 0 | 19.9672
| 2029-09-01 | 10:38 | 38280 | 306.394 | 0 | 111.3025 |  | 2029-09-01 | 10:38 | 38280 | 110.738 | 0 | 111.3025 |  | 2006-09-01 | 10:38 | 38280 | 50.9113 | 0 | 107.5991 |  | 2029-09-01 | 10:38 | 38280 | 61.6906 | 0 | 68.7944 |  | 2006-09-01 | 10:38 | 38280 | 18.1828 | 0 | 52.436 |  | 2028-01-01 | 10:38 | 38280 | 119.947 | 0 | 108.7218 |  | 2007-01-01 | 10:38 | 38280 | 34.0716 | 0 | 106.6148 |  | 2028-01-01 | 10:38 | 38280 | 29.9947 | 0 | 38.1774 |  | 2007-01-01 | 10:38 | 38280 | 9.5471 | 0 | 41.0573 |  | 2029-09-01 | 10:38 | 38280 | 56.5164 | 0 | 111.3025 |  | 2006-09-01 | 10:38 | 38280 | 17.6743 | 0 | 107.5991 |  | 2029-09-01 | 10:38 | 38280 | 21.5615 | 0 | 48.8327 |  | 2006-09-01 | 10:38 | 38280 | 3.626 | 0 | 33.5444 |  | 2028-01-01 | 10:38 | 38280 | 59.2194 | 0 | 108.7218 |  | 2007-01-01 | 10:38 | 38280 | 9.6561 | 0 | 106.6148 |  | 2028-01-01 | 10:38 | 38280 | 8.2099 | 0 | 22.6422 |  | 2007-01-01 | 10:38 | 38280 | 1.5296 | 0 | 24.8777 |  | 2029-09-01 | 10:38 | 38280 | 38.2911 | 0 | 111.3025 |  | 2006-09-01 | 10:38 | 38280 | 9.8428 | 0 | 107.5991 |  | 2029-09-01 | 10:38 | 38280 | 11.1298 | 0 | 37.6086 |  | 2006-09-01 | 10:38 | 38280 | 1.4145 | 0 | 24.5558 |  | 2028-01-01 | 10:38 | 38280 | 33.9692 | 0 | 108.7218 |  | 2007-01-01 | 10:38 | 38280 | 4.8812 | 0 | 106.6148 |  | 2028-01-01 | 10:38 | 38280 | 3.2564 | 0 | 16.0525 |  | 2007-01-01 | 10:38 | 38280 | 0.53853 | 0 | 17.7855 |  | 2029-09-01 | 10:38 | 38280 | 61.6874 | 0 | 45.5987 |  | 2029-09-01 | 10:38 | 38280 | 31.1305 | 0 | 31.7485 |  | 2029-09-01 | 10:38 | 38280 | 14.3352 | 0 | 21.8651 |  | 2006-09-01 | 10:38 | 38280 | 13.8875 | 0 | 21.6767 |  | 2028-01-01 | 10:38 | 38280 | 29.9947 | 0 | 38.1774 |  | 2007-01-01 | 10:38 | 38280 | 9.5471 | 0 | 41.0573 |  | 2028-01-01 | 10:38 | 38280 | 7.4426 | 0 | 19.2554 |  | 2007-01-01 | 10:38 | 38280 | 2.4674 | 0 | 19.9672
| 2029-09-01 | 10:39 | 38340 | 302.424 | 0 | 111.3025 |  | 2029-09-01 | 10:39 | 38340 | 95.9777 | 0 | 111.3025 |  | 2006-09-01 | 10:39 | 38340 | 39.7988 | 0 | 107.5991 |  | 2029-09-01 | 10:39 | 38340 | 53.468 | 0 | 68.7944 |  | 2006-09-01 | 10:39 | 38340 | 14.214 | 0 | 52.436 |  | 2028-01-01 | 10:39 | 38340 | 105.936 | 0 | 108.7218 |  | 2007-01-01 | 10:39 | 38340 | 25.6575 | 0 | 106.6148 |  | 2028-01-01 | 10:39 | 38340 | 26.4908 | 0 | 38.1774 |  | 2007-01-01 | 10:39 | 38340 | 7.1894 | 0 | 41.0573 |  | 2029-09-01 | 10:39 | 38340 | 44.9584 | 0 | 111.3025 |  | 2006-09-01 | 10:39 | 38340 | 12.0109 | 0 | 107.5991 |  | 2029-09-01 | 10:39 | 38340 | 17.152 | 0 | 48.8327 |  | 2006-09-01 | 10:39 | 38340 | 2.4641 | 0 | 33.5444 |  | 2028-01-01 | 10:39 | 38340 | 47.9401 | 0 | 108.7218 |  | 2007-01-01 | 10:39 | 38340 | 6.2001 | 0 | 106.6148 |  | 2028-01-01 | 10:39 | 38340 | 6.6461 | 0 | 22.6422 |  | 2007-01-01 | 10:39 | 38340 | 0.98216 | 0 | 24.8777 |  | 2029-09-01 | 10:39 | 38340 | 28.9868 | 0 | 111.3025 |  | 2006-09-01 | 10:39 | 38340 | 6.1919 | 0 | 107.5991 |  | 2029-09-01 | 10:39 | 38340 | 8.4253 | 0 | 37.6086 |  | 2006-09-01 | 10:39 | 38340 | 0.88982 | 0 | 24.5558 |  | 2028-01-01 | 10:39 | 38340 | 25.6613 | 0 | 108.7218 |  | 2007-01-01 | 10:39 | 38340 | 2.8754 | 0 | 106.6148 |  | 2028-01-01 | 10:39 | 38340 | 2.4599 | 0 | 16.0525 |  | 2007-01-01 | 10:39 | 38340 | 0.31724 | 0 | 17.7855 |  | 2029-09-01 | 10:39 | 38340 | 57.9822 | 0 | 45.5987 |  | 2029-09-01 | 10:39 | 38340 | 28.3384 | 0 | 31.7485 |  | 2029-09-01 | 10:39 | 38340 | 12.473 | 0 | 21.8651 |  | 2006-09-01 | 10:39 | 38340 | 12.0489 | 0 | 21.6767 |  | 2028-01-01 | 10:39 | 38340 | 26.4908 | 0 | 38.1774 |  | 2007-01-01 | 10:39 | 38340 | 7.1894 | 0 | 41.0573 |  | 2028-01-01 | 10:39 | 38340 | 6.0792 | 0 | 19.2554 |  | 2007-01-01 | 10:39 | 38340 | 1.7376 | 0 | 19.9672
| 2029-09-01 | 10:40 | 38400 | 298.504 | 0 | 111.3025 |  | 2029-09-01 | 10:40 | 38400 | 83.1334 | 0 | 111.3025 |  | 2006-09-01 | 10:40 | 38400 | 31.0106 | 0 | 107.5991 |  | 2029-09-01 | 10:40 | 38400 | 46.3126 | 0 | 68.7944 |  | 2006-09-01 | 10:40 | 38400 | 11.0753 | 0 | 52.436 |  | 2028-01-01 | 10:40 | 38400 | 93.6184 | 0 | 108.7218 |  | 2007-01-01 | 10:40 | 38400 | 19.3056 | 0 | 106.6148 |  | 2028-01-01 | 10:40 | 38400 | 23.4107 | 0 | 38.1774 |  | 2007-01-01 | 10:40 | 38400 | 5.4096 | 0 | 41.0573 |  | 2029-09-01 | 10:40 | 38400 | 35.7286 | 0 | 111.3025 |  | 2006-09-01 | 10:40 | 38400 | 8.1222 | 0 | 107.5991 |  | 2029-09-01 | 10:40 | 38400 | 13.6308 | 0 | 48.8327 |  | 2006-09-01 | 10:40 | 38400 | 1.6663 | 0 | 33.5444 |  | 2028-01-01 | 10:40 | 38400 | 38.8431 | 0 | 108.7218 |  | 2007-01-01 | 10:40 | 38400 | 3.9764 | 0 | 106.6148 |  | 2028-01-01 | 10:40 | 38400 | 5.385 | 0 | 22.6422 |  | 2007-01-01 | 10:40 | 38400 | 0.62989 | 0 | 24.8777 |  | 2029-09-01 | 10:40 | 38400 | 21.9172 | 0 | 111.3025 |  | 2006-09-01 | 10:40 | 38400 | 3.8729 | 0 | 107.5991 |  | 2029-09-01 | 10:40 | 38400 | 6.3705 | 0 | 37.6086 |  | 2006-09-01 | 10:40 | 38400 | 0.55656 | 0 | 24.5558 |  | 2028-01-01 | 10:40 | 38400 | 19.4036 | 0 | 108.7218 |  | 2007-01-01 | 10:40 | 38400 | 1.6915 | 0 | 106.6148 |  | 2028-01-01 | 10:40 | 38400 | 1.8601 | 0 | 16.0525 |  | 2007-01-01 | 10:40 | 38400 | 0.18662 | 0 | 17.7855 |  | 2029-09-01 | 10:40 | 38400 | 54.4994 | 0 | 45.5987 |  | 2029-09-01 | 10:40 | 38400 | 25.7967 | 0 | 31.7485 |  | 2029-09-01 | 10:40 | 38400 | 10.8526 | 0 | 21.8651 |  | 2006-09-01 | 10:40 | 38400 | 10.4532 | 0 | 21.6767 |  | 2028-01-01 | 10:40 | 38400 | 23.4107 | 0 | 38.1774 |  | 2007-01-01 | 10:40 | 38400 | 5.4096 | 0 | 41.0573 |  | 2028-01-01 | 10:40 | 38400 | 4.9684 | 0 | 19.2554 |  | 2007-01-01 | 10:40 | 38400 | 1.2228 | 0 | 19.9672
| 2029-09-01 | 10:41 | 38460 | 294.634 | 0 | 111.3025 |  | 2029-09-01 | 10:41 | 38460 | 71.9632 | 0 | 111.3025 |  | 2006-09-01 | 10:41 | 38460 | 24.085 | 0 | 107.5991 |  | 2029-09-01 | 10:41 | 38460 | 40.0898 | 0 | 68.7944 |  | 2006-09-01 | 10:41 | 38460 | 8.6019 | 0 | 52.436 |  | 2028-01-01 | 10:41 | 38460 | 82.7843 | 0 | 108.7218 |  | 2007-01-01 | 10:41 | 38460 | 14.5147 | 0 | 106.6148 |  | 2028-01-01 | 10:41 | 38460 | 20.7015 | 0 | 38.1774 |  | 2007-01-01 | 10:41 | 38460 | 4.0671 | 0 | 41.0573 |  | 2029-09-01 | 10:41 | 38460 | 28.3657 | 0 | 111.3025 |  | 2006-09-01 | 10:41 | 38460 | 5.466 | 0 | 107.5991 |  | 2029-09-01 | 10:41 | 38460 | 10.8217 | 0 | 48.8327 |  | 2006-09-01 | 10:41 | 38460 | 1.1214 | 0 | 33.5444 |  | 2028-01-01 | 10:41 | 38460 | 31.4998 | 0 | 108.7218 |  | 2007-01-01 | 10:41 | 38460 | 2.5472 | 0 | 106.6148 |  | 2028-01-01 | 10:41 | 38460 | 4.367 | 0 | 22.6422 |  | 2007-01-01 | 10:41 | 38460 | 0.4035 | 0 | 24.8777 |  | 2029-09-01 | 10:41 | 38460 | 16.5521 | 0 | 111.3025 |  | 2006-09-01 | 10:41 | 38460 | 2.4087 | 0 | 107.5991 |  | 2029-09-01 | 10:41 | 38460 | 4.8111 | 0 | 37.6086 |  | 2006-09-01 | 10:41 | 38460 | 0.34614 | 0 | 24.5558 |  | 2028-01-01 | 10:41 | 38460 | 14.6857 | 0 | 108.7218 |  | 2007-01-01 | 10:41 | 38460 | 0.99372 | 0 | 106.6148 |  | 2028-01-01 | 10:41 | 38460 | 1.4078 | 0 | 16.0525 |  | 2007-01-01 | 10:41 | 38460 | 0.10963 | 0 | 17.7855 |  | 2029-09-01 | 10:41 | 38460 | 51.2256 | 0 | 45.5987 |  | 2029-09-01 | 10:41 | 38460 | 23.4828 | 0 | 31.7485 |  | 2029-09-01 | 10:41 | 38460 | 9.4428 | 0 | 21.8651 |  | 2006-09-01 | 10:41 | 38460 | 9.0683 | 0 | 21.6767 |  | 2028-01-01 | 10:41 | 38460 | 20.7015 | 0 | 38.1774 |  | 2007-01-01 | 10:41 | 38460 | 4.0671 | 0 | 41.0573 |  | 2028-01-01 | 10:41 | 38460 | 4.0629 | 0 | 19.2554 |  | 2007-01-01 | 10:41 | 38460 | 0.85987 | 0 | 19.9672
| 2029-09-01 | 10:42 | 38520 | 290.812 | 0 | 111.3025 |  | 2029-09-01 | 10:42 | 38520 | 62.2552 | 0 | 111.3025 |  | 2006-09-01 | 10:42 | 38520 | 18.6463 | 0 | 107.5991 |  | 2029-09-01 | 10:42 | 38520 | 34.6816 | 0 | 68.7944 |  | 2006-09-01 | 10:42 | 38520 | 6.6595 | 0 | 52.436 |  | 2028-01-01 | 10:42 | 38520 | 73.2488 | 0 | 108.7218 |  | 2007-01-01 | 10:42 | 38520 | 10.9041 | 0 | 106.6148 |  | 2028-01-01 | 10:42 | 38520 | 18.317 | 0 | 38.1774 |  | 2007-01-01 | 10:42 | 38520 | 3.0554 | 0 | 41.0573 |  | 2029-09-01 | 10:42 | 38520 | 22.4979 | 0 | 111.3025 |  | 2006-09-01 | 10:42 | 38520 | 3.6608 | 0 | 107.5991 |  | 2029-09-01 | 10:42 | 38520 | 8.5831 | 0 | 48.8327 |  | 2006-09-01 | 10:42 | 38520 | 0.75103 | 0 | 33.5444 |  | 2028-01-01 | 10:42 | 38520 | 25.567 | 0 | 108.7218 |  | 2007-01-01 | 10:42 | 38520 | 1.6298 | 0 | 106.6148 |  | 2028-01-01 | 10:42 | 38520 | 3.5445 | 0 | 22.6422 |  | 2007-01-01 | 10:42 | 38520 | 0.25818 | 0 | 24.8777 |  | 2029-09-01 | 10:42 | 38520 | 12.4855 | 0 | 111.3025 |  | 2006-09-01 | 10:42 | 38520 | 1.4897 | 0 | 107.5991 |  | 2029-09-01 | 10:42 | 38520 | 3.629 | 0 | 37.6086 |  | 2006-09-01 | 10:42 | 38520 | 0.21408 | 0 | 24.5558 |  | 2028-01-01 | 10:42 | 38520 | 11.1255 | 0 | 108.7218 |  | 2007-01-01 | 10:42 | 38520 | 0.583 | 0 | 106.6148 |  | 2028-01-01 | 10:42 | 38520 | 1.0665 | 0 | 16.0525 |  | 2007-01-01 | 10:42 | 38520 | 0.064322 | 0 | 17.7855 |  | 2029-09-01 | 10:42 | 38520 | 48.1483 | 0 | 45.5987 |  | 2029-09-01 | 10:42 | 38520 | 21.3764 | 0 | 31.7485 |  | 2029-09-01 | 10:42 | 38520 | 8.216 | 0 | 21.8651 |  | 2006-09-01 | 10:42 | 38520 | 7.8665 | 0 | 21.6767 |  | 2028-01-01 | 10:42 | 38520 | 18.317 | 0 | 38.1774 |  | 2007-01-01 | 10:42 | 38520 | 3.0554 | 0 | 41.0573 |  | 2028-01-01 | 10:42 | 38520 | 3.3243 | 0 | 19.2554 |  | 2007-01-01 | 10:42 | 38520 | 0.60421 | 0 | 19.9672
| 2029-09-01 | 10:43 | 38580 | 287.039 | 0 | 111.3025 |  | 2029-09-01 | 10:43 | 38580 | 53.8235 | 0 | 111.3025 |  | 2006-09-01 | 10:43 | 38580 | 14.39 | 0 | 107.5991 |  | 2029-09-01 | 10:43 | 38580 | 29.9844 | 0 | 68.7944 |  | 2006-09-01 | 10:43 | 38580 | 5.1393 | 0 | 52.436 |  | 2028-01-01 | 10:43 | 38580 | 64.851 | 0 | 108.7218 |  | 2007-01-01 | 10:43 | 38580 | 8.1853 | 0 | 106.6148 |  | 2028-01-01 | 10:43 | 38580 | 16.217 | 0 | 38.1774 |  | 2007-01-01 | 10:43 | 38580 | 2.2936 | 0 | 41.0573 |  | 2029-09-01 | 10:43 | 38580 | 17.8263 | 0 | 111.3025 |  | 2006-09-01 | 10:43 | 38580 | 2.4401 | 0 | 107.5991 |  | 2029-09-01 | 10:43 | 38580 | 6.8009 | 0 | 48.8327 |  | 2006-09-01 | 10:43 | 38580 | 0.50061 | 0 | 33.5444 |  | 2028-01-01 | 10:43 | 38580 | 20.7696 | 0 | 108.7218 |  | 2007-01-01 | 10:43 | 38580 | 1.0416 | 0 | 106.6148 |  | 2028-01-01 | 10:43 | 38580 | 2.8794 | 0 | 22.6422 |  | 2007-01-01 | 10:43 | 38580 | 0.16501 | 0 | 24.8777 |  | 2029-09-01 | 10:43 | 38580 | 9.4068 | 0 | 111.3025 |  | 2006-09-01 | 10:43 | 38580 | 0.9162 | 0 | 107.5991 |  | 2029-09-01 | 10:43 | 38580 | 2.7342 | 0 | 37.6086 |  | 2006-09-01 | 10:43 | 38580 | 0.13167 | 0 | 24.5558 |  | 2028-01-01 | 10:43 | 38580 | 8.4362 | 0 | 108.7218 |  | 2007-01-01 | 10:43 | 38580 | 0.34159 | 0 | 106.6148 |  | 2028-01-01 | 10:43 | 38580 | 0.80871 | 0 | 16.0525 |  | 2007-01-01 | 10:43 | 38580 | 0.037687 | 0 | 17.7855 |  | 2029-09-01 | 10:43 | 38580 | 45.2556 | 0 | 45.5987 |  | 2029-09-01 | 10:43 | 38580 | 19.4589 | 0 | 31.7485 |  | 2029-09-01 | 10:43 | 38580 | 7.1486 | 0 | 21.8651 |  | 2006-09-01 | 10:43 | 38580 | 6.8236 | 0 | 21.6767 |  | 2028-01-01 | 10:43 | 38580 | 16.217 | 0 | 38.1774 |  | 2007-01-01 | 10:43 | 38580 | 2.2936 | 0 | 41.0573 |  | 2028-01-01 | 10:43 | 38580 | 2.7215 | 0 | 19.2554 |  | 2007-01-01 | 10:43 | 38580 | 0.42425 | 0 | 19.9672
| 2029-09-01 | 10:44 | 38640 | 283.314 | 0 | 111.3025 |  | 2029-09-01 | 10:44 | 38640 | 46.5049 | 0 | 111.3025 |  | 2006-09-01 | 10:44 | 38640 | 11.0703 | 0 | 107.5991 |  | 2029-09-01 | 10:44 | 38640 | 25.9073 | 0 | 68.7944 |  | 2006-09-01 | 10:44 | 38640 | 3.9537 | 0 | 52.436 |  | 2028-01-01 | 10:44 | 38640 | 57.4508 | 0 | 108.7218 |  | 2007-01-01 | 10:44 | 38640 | 6.1396 | 0 | 106.6148 |  | 2028-01-01 | 10:44 | 38640 | 14.3665 | 0 | 38.1774 |  | 2007-01-01 | 10:44 | 38640 | 1.7204 | 0 | 41.0573 |  | 2029-09-01 | 10:44 | 38640 | 14.1109 | 0 | 111.3025 |  | 2006-09-01 | 10:44 | 38640 | 1.6189 | 0 | 107.5991 |  | 2029-09-01 | 10:44 | 38640 | 5.3834 | 0 | 48.8327 |  | 2006-09-01 | 10:44 | 38640 | 0.33212 | 0 | 33.5444 |  | 2028-01-01 | 10:44 | 38640 | 16.887 | 0 | 108.7218 |  | 2007-01-01 | 10:44 | 38640 | 0.66499 | 0 | 106.6148 |  | 2028-01-01 | 10:44 | 38640 | 2.3411 | 0 | 22.6422 |  | 2007-01-01 | 10:44 | 38640 | 0.10534 | 0 | 24.8777 |  | 2029-09-01 | 10:44 | 38640 | 7.0789 | 0 | 111.3025 |  | 2006-09-01 | 10:44 | 38640 | 0.56041 | 0 | 107.5991 |  | 2029-09-01 | 10:44 | 38640 | 2.0576 | 0 | 37.6086 |  | 2006-09-01 | 10:44 | 38640 | 0.080535 | 0 | 24.5558 |  | 2028-01-01 | 10:44 | 38640 | 6.4031 | 0 | 108.7218 |  | 2007-01-01 | 10:44 | 38640 | 0.19989 | 0 | 106.6148 |  | 2028-01-01 | 10:44 | 38640 | 0.61381 | 0 | 16.0525 |  | 2007-01-01 | 10:44 | 38640 | 0.022053 | 0 | 17.7855 |  | 2029-09-01 | 10:44 | 38640 | 42.5365 | 0 | 45.5987 |  | 2029-09-01 | 10:44 | 38640 | 17.7133 | 0 | 31.7485 |  | 2029-09-01 | 10:44 | 38640 | 6.2199 | 0 | 21.8651 |  | 2006-09-01 | 10:44 | 38640 | 5.9188 | 0 | 21.6767 |  | 2028-01-01 | 10:44 | 38640 | 14.3665 | 0 | 38.1774 |  | 2007-01-01 | 10:44 | 38640 | 1.7204 | 0 | 41.0573 |  | 2028-01-01 | 10:44 | 38640 | 2.2292 | 0 | 19.2554 |  | 2007-01-01 | 10:44 | 38640 | 0.29768 | 0 | 19.9672
| 2029-09-01 | 10:45 | 38700 | 279.636 | 1.6778 | 112.9803 |  | 2029-09-01 | 10:45 | 38700 | 40.1566 | 0.24094 | 111.5434 |  | 2006-09-01 | 10:45 | 38700 | 8.4899 | 0.05094 | 107.6501 |  | 2029-09-01 | 10:45 | 38700 | 22.3707 | 0.13422 | 68.9286 |  | 2006-09-01 | 10:45 | 38700 | 3.0322 | 0.018193 | 52.4542 |  | 2028-01-01 | 10:45 | 38700 | 50.9257 | 0.30555 | 109.0273 |  | 2007-01-01 | 10:45 | 38700 | 4.6018 | 0.027611 | 106.6424 |  | 2028-01-01 | 10:45 | 38700 | 12.7348 | 0.076409 | 38.2538 |  | 2007-01-01 | 10:45 | 38700 | 1.2894 | 0.0077367 | 41.065 |  | 2029-09-01 | 10:45 | 38700 | 11.1589 | 0.066953 | 111.3694 |  | 2006-09-01 | 10:45 | 38700 | 1.069 | 0.006414 | 107.6056 |  | 2029-09-01 | 10:45 | 38700 | 4.2572 | 0.025543 | 48.8582 |  | 2006-09-01 | 10:45 | 38700 | 0.21931 | 0.0013159 | 33.5457 |  | 2028-01-01 | 10:45 | 38700 | 13.742 | 0.082452 | 108.8042 |  | 2007-01-01 | 10:45 | 38700 | 0.42406 | 0.0025444 | 106.6173 |  | 2028-01-01 | 10:45 | 38700 | 1.9051 | 0.011431 | 22.6536 |  | 2007-01-01 | 10:45 | 38700 | 0.067176 | 0.00040305 | 24.8781 |  | 2029-09-01 | 10:45 | 38700 | 5.3208 | 0.031925 | 111.3344 |  | 2006-09-01 | 10:45 | 38700 | 0.34093 | 0.0020456 | 107.6012 |  | 2029-09-01 | 10:45 | 38700 | 1.5466 | 0.0092793 | 37.6179 |  | 2006-09-01 | 10:45 | 38700 | 0.048994 | 0.00029397 | 24.5561 |  | 2028-01-01 | 10:45 | 38700 | 4.8644 | 0.029187 | 108.7509 |  | 2007-01-01 | 10:45 | 38700 | 0.11682 | 0.00070089 | 106.6155 |  | 2028-01-01 | 10:45 | 38700 | 0.46632 | 0.0027979 | 16.0553 |  | 2007-01-01 | 10:45 | 38700 | 0.012888 | 7.7329e-05 | 17.7856 |  | 2029-09-01 | 10:45 | 38700 | 39.9807 | 0.23988 | 45.8385 |  | 2029-09-01 | 10:45 | 38700 | 16.1242 | 0.096745 | 31.8453 |  | 2029-09-01 | 10:45 | 38700 | 5.4117 | 0.03247 | 21.8976 |  | 2006-09-01 | 10:45 | 38700 | 5.1336 | 0.030802 | 21.7076 |  | 2028-01-01 | 10:45 | 38700 | 12.7348 | 0.076409 | 38.2538 |  | 2007-01-01 | 10:45 | 38700 | 1.2894 | 0.0077367 | 41.065 |  | 2028-01-01 | 10:45 | 38700 | 1.827 | 0.010962 | 19.2663 |  | 2007-01-01 | 10:45 | 38700 | 0.20872 | 0.0012523 | 19.9685
| 2029-09-01 | 10:46 | 38760 | 282.276 | 1.6937 | 114.6739 |  | 2029-09-01 | 10:46 | 38760 | 46.0566 | 0.27634 | 111.8197 |  | 2006-09-01 | 10:46 | 38760 | 14.7834 | 0.0887 | 107.7388 |  | 2029-09-01 | 10:46 | 38760 | 28.2251 | 0.16935 | 69.098 |  | 2006-09-01 | 10:46 | 38760 | 9.0414 | 0.054248 | 52.5084 |  | 2028-01-01 | 10:46 | 38760 | 56.692 | 0.34015 | 109.3675 |  | 2007-01-01 | 10:46 | 38760 | 10.9687 | 0.065812 | 106.7082 |  | 2028-01-01 | 10:46 | 38760 | 17.8916 | 0.10735 | 38.3612 |  | 2007-01-01 | 10:46 | 38760 | 7.2945 | 0.043767 | 41.1088 |  | 2029-09-01 | 10:46 | 38760 | 17.4536 | 0.10472 | 111.4741 |  | 2006-09-01 | 10:46 | 38760 | 7.4823 | 0.044894 | 107.6505 |  | 2029-09-01 | 10:46 | 38760 | 10.4378 | 0.062627 | 48.9208 |  | 2006-09-01 | 10:46 | 38760 | 6.1405 | 0.036843 | 33.5825 |  | 2028-01-01 | 10:46 | 38760 | 20.0114 | 0.12007 | 108.9243 |  | 2007-01-01 | 10:46 | 38760 | 6.8566 | 0.04114 | 106.6584 |  | 2028-01-01 | 10:46 | 38760 | 7.4078 | 0.044447 | 22.6981 |  | 2007-01-01 | 10:46 | 38760 | 5.8498 | 0.035099 | 24.9132 |  | 2029-09-01 | 10:46 | 38760 | 11.695 | 0.07017 | 111.4046 |  | 2006-09-01 | 10:46 | 38760 | 6.766 | 0.040596 | 107.6418 |  | 2029-09-01 | 10:46 | 38760 | 7.7421 | 0.046453 | 37.6644 |  | 2006-09-01 | 10:46 | 38760 | 5.7661 | 0.034597 | 24.5907 |  | 2028-01-01 | 10:46 | 38760 | 11.2539 | 0.067523 | 108.8185 |  | 2007-01-01 | 10:46 | 38760 | 6.5542 | 0.039325 | 106.6548 |  | 2028-01-01 | 10:46 | 38760 | 5.8245 | 0.034947 | 16.0902 |  | 2007-01-01 | 10:46 | 38760 | 5.5266 | 0.033159 | 17.8187 |  | 2029-09-01 | 10:46 | 38760 | 43.6947 | 0.26217 | 46.1007 |  | 2029-09-01 | 10:46 | 38760 | 20.6148 | 0.12369 | 31.969 |  | 2029-09-01 | 10:46 | 38760 | 10.3892 | 0.062335 | 21.9599 |  | 2006-09-01 | 10:46 | 38760 | 10.1251 | 0.060751 | 21.7683 |  | 2028-01-01 | 10:46 | 38760 | 17.8916 | 0.10735 | 38.3612 |  | 2007-01-01 | 10:46 | 38760 | 7.2945 | 0.043767 | 41.1088 |  | 2028-01-01 | 10:46 | 38760 | 7.1574 | 0.042944 | 19.3093 |  | 2007-01-01 | 10:46 | 38760 | 5.7915 | 0.034749 | 20.0032
| 2029-09-01 | 10:47 | 38820 | 284.878 | 1.7093 | 116.3832 |  | 2029-09-01 | 10:47 | 38820 | 51.8758 | 0.31125 | 112.131 |  | 2006-09-01 | 10:47 | 38820 | 20.9744 | 0.12585 | 107.8646 |  | 2029-09-01 | 10:47 | 38820 | 33.9531 | 0.20372 | 69.3017 |  | 2006-09-01 | 10:47 | 38820 | 14.719 | 0.088314 | 52.5968 |  | 2028-01-01 | 10:47 | 38820 | 62.3811 | 0.37429 | 109.7417 |  | 2007-01-01 | 10:47 | 38820 | 17.2355 | 0.10341 | 106.8116 |  | 2028-01-01 | 10:47 | 38820 | 22.6784 | 0.13607 | 38.4972 |  | 2007-01-01 | 10:47 | 38820 | 12.8876 | 0.077326 | 41.1861 |  | 2029-09-01 | 10:47 | 38820 | 23.6624 | 0.14197 | 111.6161 |  | 2006-09-01 | 10:47 | 38820 | 13.7915 | 0.082749 | 107.7332 |  | 2029-09-01 | 10:47 | 38820 | 16.4265 | 0.098559 | 49.0194 |  | 2006-09-01 | 10:47 | 38820 | 11.522 | 0.069132 | 33.6517 |  | 2028-01-01 | 10:47 | 38820 | 26.1962 | 0.15718 | 109.0814 |  | 2007-01-01 | 10:47 | 38820 | 13.1879 | 0.079127 | 106.7376 |  | 2028-01-01 | 10:47 | 38820 | 12.2334 | 0.0734 | 22.7715 |  | 2007-01-01 | 10:47 | 38820 | 10.968 | 0.065808 | 24.979 |  | 2029-09-01 | 10:47 | 38820 | 17.9823 | 0.10789 | 111.5125 |  | 2006-09-01 | 10:47 | 38820 | 13.0868 | 0.078521 | 107.7203 |  | 2029-09-01 | 10:47 | 38820 | 13.6912 | 0.082147 | 37.7465 |  | 2006-09-01 | 10:47 | 38820 | 10.7717 | 0.06463 | 24.6553 |  | 2028-01-01 | 10:47 | 38820 | 17.5571 | 0.10534 | 108.9238 |  | 2007-01-01 | 10:47 | 38820 | 12.8903 | 0.077342 | 106.7321 |  | 2028-01-01 | 10:47 | 38820 | 10.2774 | 0.061664 | 16.1519 |  | 2007-01-01 | 10:47 | 38820 | 10.1752 | 0.061051 | 17.8798 |  | 2029-09-01 | 10:47 | 38820 | 47.1831 | 0.2831 | 46.3838 |  | 2029-09-01 | 10:47 | 38820 | 24.7 | 0.1482 | 32.1172 |  | 2029-09-01 | 10:47 | 38820 | 14.7175 | 0.088305 | 22.0483 |  | 2006-09-01 | 10:47 | 38820 | 14.4552 | 0.086731 | 21.855 |  | 2028-01-01 | 10:47 | 38820 | 22.6784 | 0.13607 | 38.4972 |  | 2007-01-01 | 10:47 | 38820 | 12.8876 | 0.077326 | 41.1861 |  | 2028-01-01 | 10:47 | 38820 | 11.7156 | 0.070294 | 19.3796 |  | 2007-01-01 | 10:47 | 38820 | 10.5809 | 0.063485 | 20.0667
| 2029-09-01 | 10:48 | 38880 | 287.441 | 1.7246 | 118.1078 |  | 2029-09-01 | 10:48 | 38880 | 57.6153 | 0.34569 | 112.4767 |  | 2006-09-01 | 10:48 | 38880 | 27.0639 | 0.16238 | 108.027 |  | 2029-09-01 | 10:48 | 38880 | 39.5622 | 0.23737 | 69.5391 |  | 2006-09-01 | 10:48 | 38880 | 20.0825 | 0.12049 | 52.7172 |  | 2028-01-01 | 10:48 | 38880 | 67.9943 | 0.40797 | 110.1497 |  | 2007-01-01 | 10:48 | 38880 | 23.4034 | 0.14042 | 106.952 |  | 2028-01-01 | 10:48 | 38880 | 27.1222 | 0.16273 | 38.66 |  | 2007-01-01 | 10:48 | 38880 | 18.0969 | 0.10858 | 41.2947 |  | 2029-09-01 | 10:48 | 38880 | 29.7865 | 0.17872 | 111.7948 |  | 2006-09-01 | 10:48 | 38880 | 19.9976 | 0.11999 | 107.8532 |  | 2029-09-01 | 10:48 | 38880 | 22.2381 | 0.13343 | 49.1528 |  | 2006-09-01 | 10:48 | 38880 | 16.4124 | 0.098474 | 33.7501 |  | 2028-01-01 | 10:48 | 38880 | 32.2979 | 0.19379 | 109.2752 |  | 2007-01-01 | 10:48 | 38880 | 19.4195 | 0.11652 | 106.8541 |  | 2028-01-01 | 10:48 | 38880 | 16.4658 | 0.098795 | 22.8703 |  | 2007-01-01 | 10:48 | 38880 | 15.4979 | 0.092987 | 25.072 |  | 2029-09-01 | 10:48 | 38880 | 24.1837 | 0.1451 | 111.6576 |  | 2006-09-01 | 10:48 | 38880 | 19.3044 | 0.11583 | 107.8361 |  | 2029-09-01 | 10:48 | 38880 | 19.4167 | 0.1165 | 37.863 |  | 2006-09-01 | 10:48 | 38880 | 15.1538 | 0.090923 | 24.7462 |  | 2028-01-01 | 10:48 | 38880 | 23.7754 | 0.14265 | 109.0665 |  | 2007-01-01 | 10:48 | 38880 | 19.1265 | 0.11476 | 106.8469 |  | 2028-01-01 | 10:48 | 38880 | 13.9788 | 0.083873 | 16.2358 |  | 2007-01-01 | 10:48 | 38880 | 14.0943 | 0.084566 | 17.9643 |  | 2029-09-01 | 10:48 | 38880 | 50.4595 | 0.30276 | 46.6866 |  | 2029-09-01 | 10:48 | 38880 | 28.4163 | 0.1705 | 32.2877 |  | 2029-09-01 | 10:48 | 38880 | 18.4811 | 0.11089 | 22.1591 |  | 2006-09-01 | 10:48 | 38880 | 18.2113 | 0.10927 | 21.9643 |  | 2028-01-01 | 10:48 | 38880 | 27.1222 | 0.16273 | 38.66 |  | 2007-01-01 | 10:48 | 38880 | 18.0969 | 0.10858 | 41.2947 |  | 2028-01-01 | 10:48 | 38880 | 15.6138 | 0.093683 | 19.4733 |  | 2007-01-01 | 10:48 | 38880 | 14.6895 | 0.088137 | 20.1548
| 2029-09-01 | 10:49 | 38940 | 289.968 | 1.7398 | 119.8477 |  | 2029-09-01 | 10:49 | 38940 | 63.2761 | 0.37966 | 112.8563 |  | 2006-09-01 | 10:49 | 38940 | 33.0531 | 0.19832 | 108.2253 |  | 2029-09-01 | 10:49 | 38940 | 45.0598 | 0.27036 | 69.8094 |  | 2006-09-01 | 10:49 | 38940 | 25.1487 | 0.15089 | 52.8681 |  | 2028-01-01 | 10:49 | 38940 | 73.5326 | 0.4412 | 110.5909 |  | 2007-01-01 | 10:49 | 38940 | 29.4738 | 0.17684 | 107.1289 |  | 2028-01-01 | 10:49 | 38940 | 31.2481 | 0.18749 | 38.8475 |  | 2007-01-01 | 10:49 | 38940 | 22.9484 | 0.13769 | 41.4324 |  | 2029-09-01 | 10:49 | 38940 | 35.8268 | 0.21496 | 112.0098 |  | 2006-09-01 | 10:49 | 38940 | 26.1018 | 0.15661 | 108.0098 |  | 2029-09-01 | 10:49 | 38940 | 27.8875 | 0.16732 | 49.3201 |  | 2006-09-01 | 10:49 | 38940 | 20.8562 | 0.12514 | 33.8753 |  | 2028-01-01 | 10:49 | 38940 | 38.3177 | 0.22991 | 109.5051 |  | 2007-01-01 | 10:49 | 38940 | 25.5527 | 0.15332 | 107.0074 |  | 2028-01-01 | 10:49 | 38940 | 20.1787 | 0.12107 | 22.9913 |  | 2007-01-01 | 10:49 | 38940 | 19.507 | 0.11704 | 25.1891 |  | 2029-09-01 | 10:49 | 38940 | 30.3004 | 0.1818 | 111.8394 |  | 2006-09-01 | 10:49 | 38940 | 25.4198 | 0.15252 | 107.9887 |  | 2029-09-01 | 10:49 | 38940 | 24.9408 | 0.14964 | 38.0127 |  | 2006-09-01 | 10:49 | 38940 | 18.9896 | 0.11394 | 24.8602 |  | 2028-01-01 | 10:49 | 38940 | 29.9102 | 0.17946 | 109.2459 |  | 2007-01-01 | 10:49 | 38940 | 25.2643 | 0.15159 | 106.9985 |  | 2028-01-01 | 10:49 | 38940 | 17.0565 | 0.10234 | 16.3381 |  | 2007-01-01 | 10:49 | 38940 | 17.3983 | 0.10439 | 18.0687 |  | 2029-09-01 | 10:49 | 38940 | 53.5366 | 0.32122 | 47.0078 |  | 2029-09-01 | 10:49 | 38940 | 31.7969 | 0.19078 | 32.4785 |  | 2029-09-01 | 10:49 | 38940 | 21.7537 | 0.13052 | 22.2897 |  | 2006-09-01 | 10:49 | 38940 | 21.4691 | 0.12881 | 22.0931 |  | 2028-01-01 | 10:49 | 38940 | 31.2481 | 0.18749 | 38.8475 |  | 2007-01-01 | 10:49 | 38940 | 22.9484 | 0.13769 | 41.4324 |  | 2028-01-01 | 10:49 | 38940 | 18.9481 | 0.11369 | 19.5869 |  | 2007-01-01 | 10:49 | 38940 | 18.2139 | 0.10928 | 20.2641
| 2029-09-01 | 10:50 | 39000 | 292.458 | 1.7547 | 121.6024 |  | 2029-09-01 | 10:50 | 39000 | 68.8591 | 0.41315 | 113.2695 |  | 2006-09-01 | 10:50 | 39000 | 38.9431 | 0.23366 | 108.459 |  | 2029-09-01 | 10:50 | 39000 | 50.4534 | 0.30272 | 70.1121 |  | 2006-09-01 | 10:50 | 39000 | 29.9335 | 0.1796 | 53.0477 |  | 2028-01-01 | 10:50 | 39000 | 78.9972 | 0.47398 | 111.0649 |  | 2007-01-01 | 10:50 | 39000 | 35.4482 | 0.21269 | 107.3415 |  | 2028-01-01 | 10:50 | 39000 | 35.0793 | 0.21048 | 39.0579 |  | 2007-01-01 | 10:50 | 39000 | 27.4666 | 0.1648 | 41.5972 |  | 2029-09-01 | 10:50 | 39000 | 41.7843 | 0.25071 | 112.2605 |  | 2006-09-01 | 10:50 | 39000 | 32.1053 | 0.19263 | 108.2024 |  | 2029-09-01 | 10:50 | 39000 | 33.3892 | 0.20034 | 49.5205 |  | 2006-09-01 | 10:50 | 39000 | 24.8935 | 0.14936 | 34.0246 |  | 2028-01-01 | 10:50 | 39000 | 44.2569 | 0.26554 | 109.7707 |  | 2007-01-01 | 10:50 | 39000 | 31.5888 | 0.18953 | 107.1969 |  | 2028-01-01 | 10:50 | 39000 | 23.4365 | 0.14062 | 23.132 |  | 2007-01-01 | 10:50 | 39000 | 23.0549 | 0.13833 | 25.3274 |  | 2029-09-01 | 10:50 | 39000 | 36.3334 | 0.218 | 112.0574 |  | 2006-09-01 | 10:50 | 39000 | 31.4344 | 0.18861 | 108.1773 |  | 2029-09-01 | 10:50 | 39000 | 30.2852 | 0.18171 | 38.1944 |  | 2006-09-01 | 10:50 | 39000 | 22.3467 | 0.13408 | 24.9942 |  | 2028-01-01 | 10:50 | 39000 | 35.9626 | 0.21578 | 109.4617 |  | 2007-01-01 | 10:50 | 39000 | 31.305 | 0.18783 | 107.1863 |  | 2028-01-01 | 10:50 | 39000 | 19.6162 | 0.1177 | 16.4558 |  | 2007-01-01 | 10:50 | 39000 | 20.1835 | 0.1211 | 18.1898 |  | 2029-09-01 | 10:50 | 39000 | 56.4266 | 0.33856 | 47.3463 |  | 2029-09-01 | 10:50 | 39000 | 34.872 | 0.20923 | 32.6877 |  | 2029-09-01 | 10:50 | 39000 | 24.5992 | 0.1476 | 22.4373 |  | 2006-09-01 | 10:50 | 39000 | 24.2945 | 0.14577 | 22.2389 |  | 2028-01-01 | 10:50 | 39000 | 35.0793 | 0.21048 | 39.0579 |  | 2007-01-01 | 10:50 | 39000 | 27.4666 | 0.1648 | 41.5972 |  | 2028-01-01 | 10:50 | 39000 | 21.8003 | 0.1308 | 19.7177 |  | 2007-01-01 | 10:50 | 39000 | 21.2371 | 0.12742 | 20.3915
| 2029-09-01 | 10:51 | 39060 | 294.912 | 1.7695 | 123.3719 |  | 2029-09-01 | 10:51 | 39060 | 74.3654 | 0.44619 | 113.7157 |  | 2006-09-01 | 10:51 | 39060 | 44.735 | 0.26841 | 108.7274 |  | 2029-09-01 | 10:51 | 39060 | 55.7506 | 0.3345 | 70.4466 |  | 2006-09-01 | 10:51 | 39060 | 34.452 | 0.20671 | 53.2545 |  | 2028-01-01 | 10:51 | 39060 | 84.3892 | 0.50634 | 111.5712 |  | 2007-01-01 | 10:51 | 39060 | 41.3278 | 0.24797 | 107.5895 |  | 2028-01-01 | 10:51 | 39060 | 38.6372 | 0.23182 | 39.2898 |  | 2007-01-01 | 10:51 | 39060 | 31.6742 | 0.19005 | 41.7872 |  | 2029-09-01 | 10:51 | 39060 | 47.6602 | 0.28596 | 112.5465 |  | 2006-09-01 | 10:51 | 39060 | 38.0091 | 0.22805 | 108.4305 |  | 2029-09-01 | 10:51 | 39060 | 38.7577 | 0.23255 | 49.753 |  | 2006-09-01 | 10:51 | 39060 | 28.561 | 0.17137 | 34.196 |  | 2028-01-01 | 10:51 | 39060 | 50.1166 | 0.3007 | 110.0714 |  | 2007-01-01 | 10:51 | 39060 | 37.5293 | 0.22518 | 107.4221 |  | 2028-01-01 | 10:51 | 39060 | 26.2956 | 0.15777 | 23.2897 |  | 2007-01-01 | 10:51 | 39060 | 26.1945 | 0.15717 | 25.4846 |  | 2029-09-01 | 10:51 | 39060 | 42.2837 | 0.2537 | 112.3111 |  | 2006-09-01 | 10:51 | 39060 | 37.3492 | 0.2241 | 108.4014 |  | 2029-09-01 | 10:51 | 39060 | 35.4712 | 0.21283 | 38.4072 |  | 2006-09-01 | 10:51 | 39060 | 25.2845 | 0.15171 | 25.1459 |  | 2028-01-01 | 10:51 | 39060 | 41.9341 | 0.2516 | 109.7133 |  | 2007-01-01 | 10:51 | 39060 | 37.25 | 0.2235 | 107.4098 |  | 2028-01-01 | 10:51 | 39060 | 21.7459 | 0.13048 | 16.5863 |  | 2007-01-01 | 10:51 | 39060 | 22.5314 | 0.13519 | 18.325 |  | 2029-09-01 | 10:51 | 39060 | 59.1407 | 0.35484 | 47.7012 |  | 2029-09-01 | 10:51 | 39060 | 37.6693 | 0.22602 | 32.9137 |  | 2029-09-01 | 10:51 | 39060 | 27.0734 | 0.16244 | 22.5997 |  | 2006-09-01 | 10:51 | 39060 | 26.7444 | 0.16047 | 22.3993 |  | 2028-01-01 | 10:51 | 39060 | 38.6372 | 0.23182 | 39.2898 |  | 2007-01-01 | 10:51 | 39060 | 31.6742 | 0.19005 | 41.7872 |  | 2028-01-01 | 10:51 | 39060 | 24.2404 | 0.14544 | 19.8632 |  | 2007-01-01 | 10:51 | 39060 | 23.8301 | 0.14298 | 20.5345
| 2029-09-01 | 10:52 | 39120 | 297.329 | 1.784 | 125.1559 |  | 2029-09-01 | 10:52 | 39120 | 79.7958 | 0.47877 | 114.1945 |  | 2006-09-01 | 10:52 | 39120 | 50.4299 | 0.30258 | 109.03 |  | 2029-09-01 | 10:52 | 39120 | 60.9593 | 0.36576 | 70.8124 |  | 2006-09-01 | 10:52 | 39120 | 38.7184 | 0.23231 | 53.4868 |  | 2028-01-01 | 10:52 | 39120 | 89.7098 | 0.53826 | 112.1095 |  | 2007-01-01 | 10:52 | 39120 | 47.1141 | 0.28268 | 107.8722 |  | 2028-01-01 | 10:52 | 39120 | 41.9417 | 0.25165 | 39.5414 |  | 2007-01-01 | 10:52 | 39120 | 35.5923 | 0.21355 | 42.0008 |  | 2029-09-01 | 10:52 | 39120 | 53.4554 | 0.32073 | 112.8672 |  | 2006-09-01 | 10:52 | 39120 | 43.8144 | 0.26289 | 108.6934 |  | 2029-09-01 | 10:52 | 39120 | 44.0079 | 0.26405 | 50.0171 |  | 2006-09-01 | 10:52 | 39120 | 31.8921 | 0.19135 | 34.3874 |  | 2028-01-01 | 10:52 | 39120 | 55.8982 | 0.33539 | 110.4068 |  | 2007-01-01 | 10:52 | 39120 | 43.3755 | 0.26025 | 107.6824 |  | 2028-01-01 | 10:52 | 39120 | 28.8053 | 0.17283 | 23.4626 |  | 2007-01-01 | 10:52 | 39120 | 28.9728 | 0.17384 | 25.6584 |  | 2029-09-01 | 10:52 | 39120 | 48.1523 | 0.28891 | 112.6 |  | 2006-09-01 | 10:52 | 39120 | 43.1653 | 0.25899 | 108.6603 |  | 2029-09-01 | 10:52 | 39120 | 40.5202 | 0.24312 | 38.6503 |  | 2006-09-01 | 10:52 | 39120 | 27.8549 | 0.16713 | 25.3131 |  | 2028-01-01 | 10:52 | 39120 | 47.8257 | 0.28695 | 110.0003 |  | 2007-01-01 | 10:52 | 39120 | 43.1006 | 0.2586 | 107.6684 |  | 2028-01-01 | 10:52 | 39120 | 23.5184 | 0.14111 | 16.7274 |  | 2007-01-01 | 10:52 | 39120 | 24.5103 | 0.14706 | 18.4721 |  | 2029-09-01 | 10:52 | 39120 | 61.6897 | 0.37014 | 48.0713 |  | 2029-09-01 | 10:52 | 39120 | 40.2138 | 0.24128 | 33.155 |  | 2029-09-01 | 10:52 | 39120 | 29.2246 | 0.17535 | 22.775 |  | 2006-09-01 | 10:52 | 39120 | 28.8685 | 0.17321 | 22.5726 |  | 2028-01-01 | 10:52 | 39120 | 41.9417 | 0.25165 | 39.5414 |  | 2007-01-01 | 10:52 | 39120 | 35.5923 | 0.21355 | 42.0008 |  | 2028-01-01 | 10:52 | 39120 | 26.3283 | 0.15797 | 20.0212 |  | 2007-01-01 | 10:52 | 39120 | 26.0541 | 0.15632 | 20.6908
| 2029-09-01 | 10:53 | 39180 | 299.711 | 1.7983 | 126.9541 |  | 2029-09-01 | 10:53 | 39180 | 85.1513 | 0.51091 | 114.7054 |  | 2006-09-01 | 10:53 | 39180 | 56.029 | 0.33617 | 109.3662 |  | 2029-09-01 | 10:53 | 39180 | 66.0877 | 0.39653 | 71.2089 |  | 2006-09-01 | 10:53 | 39180 | 42.7461 | 0.25648 | 53.7432 |  | 2028-01-01 | 10:53 | 39180 | 94.96 | 0.56976 | 112.6792 |  | 2007-01-01 | 10:53 | 39180 | 52.8082 | 0.31685 | 108.189 |  | 2028-01-01 | 10:53 | 39180 | 45.0113 | 0.27007 | 39.8115 |  | 2007-01-01 | 10:53 | 39180 | 39.2407 | 0.23544 | 42.2362 |  | 2029-09-01 | 10:53 | 39180 | 59.171 | 0.35503 | 113.2222 |  | 2006-09-01 | 10:53 | 39180 | 49.5223 | 0.29713 | 108.9905 |  | 2029-09-01 | 10:53 | 39180 | 49.1549 | 0.29493 | 50.312 |  | 2006-09-01 | 10:53 | 39180 | 34.9172 | 0.2095 | 34.5969 |  | 2028-01-01 | 10:53 | 39180 | 61.6028 | 0.36962 | 110.7764 |  | 2007-01-01 | 10:53 | 39180 | 49.1288 | 0.29477 | 107.9771 |  | 2028-01-01 | 10:53 | 39180 | 31.0089 | 0.18605 | 23.6486 |  | 2007-01-01 | 10:53 | 39180 | 31.4312 | 0.18859 | 25.847 |  | 2029-09-01 | 10:53 | 39180 | 53.9404 | 0.32364 | 112.9236 |  | 2006-09-01 | 10:53 | 39180 | 48.8839 | 0.2933 | 108.9537 |  | 2029-09-01 | 10:53 | 39180 | 45.4539 | 0.27272 | 38.923 |  | 2006-09-01 | 10:53 | 39180 | 30.1035 | 0.18062 | 25.4937 |  | 2028-01-01 | 10:53 | 39180 | 53.6388 | 0.32183 | 110.3221 |  | 2007-01-01 | 10:53 | 39180 | 48.8581 | 0.29315 | 107.9616 |  | 2028-01-01 | 10:53 | 39180 | 24.9944 | 0.14997 | 16.8774 |  | 2007-01-01 | 10:53 | 39180 | 26.1783 | 0.15707 | 18.6292 |  | 2029-09-01 | 10:53 | 39180 | 64.0833 | 0.3845 | 48.4558 |  | 2029-09-01 | 10:53 | 39180 | 42.5282 | 0.25517 | 33.4102 |  | 2029-09-01 | 10:53 | 39180 | 31.095 | 0.18657 | 22.9616 |  | 2006-09-01 | 10:53 | 39180 | 30.7099 | 0.18426 | 22.7568 |  | 2028-01-01 | 10:53 | 39180 | 45.0113 | 0.27007 | 39.8115 |  | 2007-01-01 | 10:53 | 39180 | 39.2407 | 0.23544 | 42.2362 |  | 2028-01-01 | 10:53 | 39180 | 28.1152 | 0.16869 | 20.1898 |  | 2007-01-01 | 10:53 | 39180 | 27.9615 | 0.16777 | 20.8586
| 2029-09-01 | 10:54 | 39240 | 302.058 | 1.8123 | 128.7665 |  | 2029-09-01 | 10:54 | 39240 | 90.4329 | 0.5426 | 115.248 |  | 2006-09-01 | 10:54 | 39240 | 61.5334 | 0.3692 | 109.7354 |  | 2029-09-01 | 10:54 | 39240 | 71.1449 | 0.42687 | 71.6358 |  | 2006-09-01 | 10:54 | 39240 | 46.548 | 0.27929 | 54.0225 |  | 2028-01-01 | 10:54 | 39240 | 100.141 | 0.60085 | 113.2801 |  | 2007-01-01 | 10:54 | 39240 | 58.4116 | 0.35047 | 108.5395 |  | 2028-01-01 | 10:54 | 39240 | 47.8631 | 0.28718 | 40.0987 |  | 2007-01-01 | 10:54 | 39240 | 42.6379 | 0.25583 | 42.492 |  | 2029-09-01 | 10:54 | 39240 | 64.8079 | 0.38885 | 113.6111 |  | 2006-09-01 | 10:54 | 39240 | 55.134 | 0.3308 | 109.3213 |  | 2029-09-01 | 10:54 | 39240 | 54.215 | 0.32529 | 50.6373 |  | 2006-09-01 | 10:54 | 39240 | 37.664 | 0.22598 | 34.8229 |  | 2028-01-01 | 10:54 | 39240 | 67.2316 | 0.40339 | 111.1798 |  | 2007-01-01 | 10:54 | 39240 | 54.7903 | 0.32874 | 108.3059 |  | 2028-01-01 | 10:54 | 39240 | 32.9442 | 0.19767 | 23.8463 |  | 2007-01-01 | 10:54 | 39240 | 33.6063 | 0.20164 | 26.0486 |  | 2029-09-01 | 10:54 | 39240 | 59.6489 | 0.35789 | 113.2815 |  | 2006-09-01 | 10:54 | 39240 | 54.5061 | 0.32704 | 109.2807 |  | 2029-09-01 | 10:54 | 39240 | 50.2951 | 0.30177 | 39.2248 |  | 2006-09-01 | 10:54 | 39240 | 32.0701 | 0.19242 | 25.6861 |  | 2028-01-01 | 10:54 | 39240 | 59.3745 | 0.35625 | 110.6783 |  | 2007-01-01 | 10:54 | 39240 | 54.524 | 0.32714 | 108.2887 |  | 2028-01-01 | 10:54 | 39240 | 26.2241 | 0.15734 | 17.0347 |  | 2007-01-01 | 10:54 | 39240 | 27.5841 | 0.1655 | 18.7947 |  | 2029-09-01 | 10:54 | 39240 | 66.3312 | 0.39799 | 48.8538 |  | 2029-09-01 | 10:54 | 39240 | 44.6332 | 0.2678 | 33.678 |  | 2029-09-01 | 10:54 | 39240 | 32.7211 | 0.19633 | 23.1579 |  | 2006-09-01 | 10:54 | 39240 | 32.3059 | 0.19384 | 22.9507 |  | 2028-01-01 | 10:54 | 39240 | 47.8631 | 0.28718 | 40.0987 |  | 2007-01-01 | 10:54 | 39240 | 42.6379 | 0.25583 | 42.492 |  | 2028-01-01 | 10:54 | 39240 | 29.6447 | 0.17787 | 20.3677 |  | 2007-01-01 | 10:54 | 39240 | 29.5972 | 0.17758 | 21.0362
| 2029-09-01 | 10:55 | 39300 | 304.371 | 1.8262 | 130.5927 |  | 2029-09-01 | 10:55 | 39300 | 95.6414 | 0.57385 | 115.8218 |  | 2006-09-01 | 10:55 | 39300 | 66.9442 | 0.40167 | 110.137 |  | 2029-09-01 | 10:55 | 39300 | 76.1404 | 0.45684 | 72.0926 |  | 2006-09-01 | 10:55 | 39300 | 50.1362 | 0.30082 | 54.3233 |  | 2028-01-01 | 10:55 | 39300 | 105.254 | 0.63152 | 113.9116 |  | 2007-01-01 | 10:55 | 39300 | 63.9256 | 0.38355 | 108.9231 |  | 2028-01-01 | 10:55 | 39300 | 50.5129 | 0.30308 | 40.4017 |  | 2007-01-01 | 10:55 | 39300 | 45.8008 | 0.2748 | 42.7668 |  | 2029-09-01 | 10:55 | 39300 | 70.3671 | 0.4222 | 114.0333 |  | 2006-09-01 | 10:55 | 39300 | 60.6506 | 0.3639 | 109.6852 |  | 2029-09-01 | 10:55 | 39300 | 59.2059 | 0.35524 | 50.9925 |  | 2006-09-01 | 10:55 | 39300 | 40.1576 | 0.24095 | 35.0638 |  | 2028-01-01 | 10:55 | 39300 | 72.7857 | 0.43671 | 111.6165 |  | 2007-01-01 | 10:55 | 39300 | 60.3616 | 0.36217 | 108.668 |  | 2028-01-01 | 10:55 | 39300 | 34.6446 | 0.20787 | 24.0541 |  | 2007-01-01 | 10:55 | 39300 | 35.5307 | 0.21318 | 26.2618 |  | 2029-09-01 | 10:55 | 39300 | 65.2787 | 0.39167 | 113.6732 |  | 2006-09-01 | 10:55 | 39300 | 60.0331 | 0.3602 | 109.6409 |  | 2029-09-01 | 10:55 | 39300 | 55.0687 | 0.33041 | 39.5552 |  | 2006-09-01 | 10:55 | 39300 | 33.7898 | 0.20274 | 25.8889 |  | 2028-01-01 | 10:55 | 39300 | 65.034 | 0.3902 | 111.0685 |  | 2007-01-01 | 10:55 | 39300 | 60.0995 | 0.3606 | 108.6493 |  | 2028-01-01 | 10:55 | 39300 | 27.2491 | 0.16349 | 17.1982 |  | 2007-01-01 | 10:55 | 39300 | 28.7687 | 0.17261 | 18.9673 |  | 2029-09-01 | 10:55 | 39300 | 68.442 | 0.41065 | 49.2645 |  | 2029-09-01 | 10:55 | 39300 | 46.5479 | 0.27929 | 33.9572 |  | 2029-09-01 | 10:55 | 39300 | 34.1348 | 0.20481 | 23.3627 |  | 2006-09-01 | 10:55 | 39300 | 33.6889 | 0.20213 | 23.1528 |  | 2028-01-01 | 10:55 | 39300 | 50.5129 | 0.30308 | 40.4017 |  | 2007-01-01 | 10:55 | 39300 | 45.8008 | 0.2748 | 42.7668 |  | 2028-01-01 | 10:55 | 39300 | 30.9541 | 0.18572 | 20.5534 |  | 2007-01-01 | 10:55 | 39300 | 30.9998 | 0.186 | 21.2222
| 2029-09-01 | 10:56 | 39360 | 306.649 | 1.8399 | 132.4326 |  | 2029-09-01 | 10:56 | 39360 | 100.778 | 0.60467 | 116.4265 |  | 2006-09-01 | 10:56 | 39360 | 72.2625 | 0.43358 | 110.5706 |  | 2029-09-01 | 10:56 | 39360 | 81.0857 | 0.48651 | 72.5792 |  | 2006-09-01 | 10:56 | 39360 | 53.5221 | 0.32113 | 54.6445 |  | 2028-01-01 | 10:56 | 39360 | 110.299 | 0.66179 | 114.5734 |  | 2007-01-01 | 10:56 | 39360 | 69.3513 | 0.41611 | 109.3392 |  | 2028-01-01 | 10:56 | 39360 | 52.9754 | 0.31785 | 40.7196 |  | 2007-01-01 | 10:56 | 39360 | 48.7457 | 0.29247 | 43.0593 |  | 2029-09-01 | 10:56 | 39360 | 75.8497 | 0.4551 | 114.4884 |  | 2006-09-01 | 10:56 | 39360 | 66.0732 | 0.39644 | 110.0817 |  | 2029-09-01 | 10:56 | 39360 | 64.1474 | 0.38488 | 51.3774 |  | 2006-09-01 | 10:56 | 39360 | 42.4209 | 0.25453 | 35.3183 |  | 2028-01-01 | 10:56 | 39360 | 78.2663 | 0.4696 | 112.0861 |  | 2007-01-01 | 10:56 | 39360 | 65.8438 | 0.39506 | 109.0631 |  | 2028-01-01 | 10:56 | 39360 | 36.1389 | 0.21683 | 24.271 |  | 2007-01-01 | 10:56 | 39360 | 37.2332 | 0.2234 | 26.4852 |  | 2029-09-01 | 10:56 | 39360 | 70.8309 | 0.42499 | 114.0982 |  | 2006-09-01 | 10:56 | 39360 | 65.466 | 0.3928 | 110.0337 |  | 2029-09-01 | 10:56 | 39360 | 59.8025 | 0.35881 | 39.914 |  | 2006-09-01 | 10:56 | 39360 | 35.2932 | 0.21176 | 26.1006 |  | 2028-01-01 | 10:56 | 39360 | 70.6185 | 0.42371 | 111.4922 |  | 2007-01-01 | 10:56 | 39360 | 65.5858 | 0.39351 | 109.0428 |  | 2028-01-01 | 10:56 | 39360 | 28.1041 | 0.16862 | 17.3668 |  | 2007-01-01 | 10:56 | 39360 | 29.7669 | 0.1786 | 19.1459 |  | 2029-09-01 | 10:56 | 39360 | 70.4241 | 0.42254 | 49.687 |  | 2029-09-01 | 10:56 | 39360 | 48.2892 | 0.28974 | 34.247 |  | 2029-09-01 | 10:56 | 39360 | 35.3638 | 0.21218 | 23.5749 |  | 2006-09-01 | 10:56 | 39360 | 34.8872 | 0.20932 | 23.3621 |  | 2028-01-01 | 10:56 | 39360 | 52.9754 | 0.31785 | 40.7196 |  | 2007-01-01 | 10:56 | 39360 | 48.7457 | 0.29247 | 43.0593 |  | 2028-01-01 | 10:56 | 39360 | 32.0755 | 0.19245 | 20.7459 |  | 2007-01-01 | 10:56 | 39360 | 32.2025 | 0.19321 | 21.4154
| 2029-09-01 | 10:57 | 39420 | 308.894 | 1.8534 | 134.2859 |  | 2029-09-01 | 10:57 | 39420 | 105.843 | 0.63506 | 117.0615 |  | 2006-09-01 | 10:57 | 39420 | 77.4895 | 0.46494 | 111.0355 |  | 2029-09-01 | 10:57 | 39420 | 85.9943 | 0.51597 | 73.0951 |  | 2006-09-01 | 10:57 | 39420 | 56.7167 | 0.3403 | 54.9848 |  | 2028-01-01 | 10:57 | 39420 | 115.278 | 0.69167 | 115.2651 |  | 2007-01-01 | 10:57 | 39420 | 74.6902 | 0.44814 | 109.7873 |  | 2028-01-01 | 10:57 | 39420 | 55.2641 | 0.33158 | 41.0512 |  | 2007-01-01 | 10:57 | 39420 | 51.4873 | 0.30892 | 43.3682 |  | 2029-09-01 | 10:57 | 39420 | 81.2565 | 0.48754 | 114.9759 |  | 2006-09-01 | 10:57 | 39420 | 71.4029 | 0.42842 | 110.5101 |  | 2029-09-01 | 10:57 | 39420 | 69.0641 | 0.41438 | 51.7918 |  | 2006-09-01 | 10:57 | 39420 | 44.4748 | 0.26685 | 35.5852 |  | 2028-01-01 | 10:57 | 39420 | 83.6745 | 0.50205 | 112.5881 |  | 2007-01-01 | 10:57 | 39420 | 71.2383 | 0.42743 | 109.4905 |  | 2028-01-01 | 10:57 | 39420 | 37.4527 | 0.22472 | 24.4957 |  | 2007-01-01 | 10:57 | 39420 | 38.7392 | 0.23244 | 26.7176 |  | 2029-09-01 | 10:57 | 39420 | 76.3065 | 0.45784 | 114.556 |  | 2006-09-01 | 10:57 | 39420 | 70.8058 | 0.42483 | 110.4585 |  | 2029-09-01 | 10:57 | 39420 | 64.5308 | 0.38718 | 40.3012 |  | 2006-09-01 | 10:57 | 39420 | 36.6072 | 0.21964 | 26.3203 |  | 2028-01-01 | 10:57 | 39420 | 76.1291 | 0.45677 | 111.949 |  | 2007-01-01 | 10:57 | 39420 | 70.9844 | 0.42591 | 109.4687 |  | 2028-01-01 | 10:57 | 39420 | 28.818 | 0.17291 | 17.5397 |  | 2007-01-01 | 10:57 | 39420 | 30.608 | 0.18365 | 19.3295 |  | 2029-09-01 | 10:57 | 39420 | 72.2852 | 0.43371 | 50.1207 |  | 2029-09-01 | 10:57 | 39420 | 49.8729 | 0.29924 | 34.5462 |  | 2029-09-01 | 10:57 | 39420 | 36.4322 | 0.21859 | 23.7935 |  | 2006-09-01 | 10:57 | 39420 | 35.9251 | 0.21555 | 23.5777 |  | 2028-01-01 | 10:57 | 39420 | 55.2641 | 0.33158 | 41.0512 |  | 2007-01-01 | 10:57 | 39420 | 51.4873 | 0.30892 | 43.3682 |  | 2028-01-01 | 10:57 | 39420 | 33.036 | 0.19822 | 20.9441 |  | 2007-01-01 | 10:57 | 39420 | 33.2336 | 0.1994 | 21.6148
| 2029-09-01 | 10:58 | 39480 | 311.105 | 1.8666 | 136.1526 |  | 2029-09-01 | 10:58 | 39480 | 110.838 | 0.66503 | 117.7266 |  | 2006-09-01 | 10:58 | 39480 | 82.6261 | 0.49576 | 111.5313 |  | 2029-09-01 | 10:58 | 39480 | 90.8848 | 0.54531 | 73.6404 |  | 2006-09-01 | 10:58 | 39480 | 59.7302 | 0.35838 | 55.3432 |  | 2028-01-01 | 10:58 | 39480 | 120.193 | 0.72116 | 115.9862 |  | 2007-01-01 | 10:58 | 39480 | 79.9434 | 0.47966 | 110.267 |  | 2028-01-01 | 10:58 | 39480 | 57.3918 | 0.34435 | 41.3955 |  | 2007-01-01 | 10:58 | 39480 | 54.0395 | 0.32424 | 43.6925 |  | 2029-09-01 | 10:58 | 39480 | 86.5885 | 0.51953 | 115.4954 |  | 2006-09-01 | 10:58 | 39480 | 76.6409 | 0.45985 | 110.9699 |  | 2029-09-01 | 10:58 | 39480 | 73.989 | 0.44393 | 52.2357 |  | 2006-09-01 | 10:58 | 39480 | 46.3382 | 0.27803 | 35.8632 |  | 2028-01-01 | 10:58 | 39480 | 89.0114 | 0.53407 | 113.1222 |  | 2007-01-01 | 10:58 | 39480 | 76.5463 | 0.45928 | 109.9498 |  | 2028-01-01 | 10:58 | 39480 | 38.6082 | 0.23165 | 24.7273 |  | 2007-01-01 | 10:58 | 39480 | 40.0714 | 0.24043 | 26.9581 |  | 2029-09-01 | 10:58 | 39480 | 81.7063 | 0.49024 | 115.0462 |  | 2006-09-01 | 10:58 | 39480 | 76.0537 | 0.45632 | 110.9148 |  | 2029-09-01 | 10:58 | 39480 | 69.2999 | 0.4158 | 40.717 |  | 2006-09-01 | 10:58 | 39480 | 37.7552 | 0.22653 | 26.5468 |  | 2028-01-01 | 10:58 | 39480 | 81.5669 | 0.4894 | 112.4384 |  | 2007-01-01 | 10:58 | 39480 | 76.2964 | 0.45778 | 109.9265 |  | 2028-01-01 | 10:58 | 39480 | 29.4145 | 0.17649 | 17.7162 |  | 2007-01-01 | 10:58 | 39480 | 31.3165 | 0.1879 | 19.5174 |  | 2029-09-01 | 10:58 | 39480 | 74.0327 | 0.4442 | 50.5649 |  | 2029-09-01 | 10:58 | 39480 | 51.3132 | 0.30788 | 34.8541 |  | 2029-09-01 | 10:58 | 39480 | 37.3609 | 0.22417 | 24.0177 |  | 2006-09-01 | 10:58 | 39480 | 36.8239 | 0.22094 | 23.7986 |  | 2028-01-01 | 10:58 | 39480 | 57.3918 | 0.34435 | 41.3955 |  | 2007-01-01 | 10:58 | 39480 | 54.0395 | 0.32424 | 43.6925 |  | 2028-01-01 | 10:58 | 39480 | 33.8591 | 0.20315 | 21.1473 |  | 2007-01-01 | 10:58 | 39480 | 34.1175 | 0.2047 | 21.8195
| 2029-09-01 | 10:59 | 39540 | 313.283 | 1.8797 | 138.0323 |  | 2029-09-01 | 10:59 | 39540 | 115.764 | 0.69458 | 118.4212 |  | 2006-09-01 | 10:59 | 39540 | 87.6735 | 0.52604 | 112.0573 |  | 2029-09-01 | 10:59 | 39540 | 95.7865 | 0.57472 | 74.2151 |  | 2006-09-01 | 10:59 | 39540 | 62.5724 | 0.37543 | 55.7186 |  | 2028-01-01 | 10:59 | 39540 | 125.042 | 0.75025 | 116.7365 |  | 2007-01-01 | 10:59 | 39540 | 85.1123 | 0.51067 | 110.7777 |  | 2028-01-01 | 10:59 | 39540 | 59.3701 | 0.35622 | 41.7517 |  | 2007-01-01 | 10:59 | 39540 | 56.4153 | 0.33849 | 44.031 |  | 2029-09-01 | 10:59 | 39540 | 91.8466 | 0.55108 | 116.0465 |  | 2006-09-01 | 10:59 | 39540 | 81.7883 | 0.49073 | 111.4606 |  | 2029-09-01 | 10:59 | 39540 | 78.9764 | 0.47386 | 52.7096 |  | 2006-09-01 | 10:59 | 39540 | 48.0284 | 0.28817 | 36.1514 |  | 2028-01-01 | 10:59 | 39540 | 94.2781 | 0.56567 | 113.6879 |  | 2007-01-01 | 10:59 | 39540 | 81.769 | 0.49061 | 110.4404 |  | 2028-01-01 | 10:59 | 39540 | 39.625 | 0.23775 | 24.9651 |  | 2007-01-01 | 10:59 | 39540 | 41.2496 | 0.2475 | 27.2056 |  | 2029-09-01 | 10:59 | 39540 | 87.0315 | 0.52219 | 115.5684 |  | 2006-09-01 | 10:59 | 39540 | 81.2109 | 0.48727 | 111.4021 |  | 2029-09-01 | 10:59 | 39540 | 74.1871 | 0.44512 | 41.1621 |  | 2006-09-01 | 10:59 | 39540 | 38.7579 | 0.23255 | 26.7793 |  | 2028-01-01 | 10:59 | 39540 | 86.9331 | 0.5216 | 112.96 |  | 2007-01-01 | 10:59 | 39540 | 81.5232 | 0.48914 | 110.4156 |  | 2028-01-01 | 10:59 | 39540 | 29.9135 | 0.17948 | 17.8957 |  | 2007-01-01 | 10:59 | 39540 | 31.9133 | 0.19148 | 19.7089 |  | 2029-09-01 | 10:59 | 39540 | 75.6734 | 0.45404 | 51.019 |  | 2029-09-01 | 10:59 | 39540 | 52.623 | 0.31574 | 35.1698 |  | 2029-09-01 | 10:59 | 39540 | 38.1681 | 0.22901 | 24.2467 |  | 2006-09-01 | 10:59 | 39540 | 37.602 | 0.22561 | 24.0242 |  | 2028-01-01 | 10:59 | 39540 | 59.3701 | 0.35622 | 41.7517 |  | 2007-01-01 | 10:59 | 39540 | 56.4153 | 0.33849 | 44.031 |  | 2028-01-01 | 10:59 | 39540 | 34.5646 | 0.20739 | 21.3547 |  | 2007-01-01 | 10:59 | 39540 | 34.8751 | 0.20925 | 22.0288
2 | 2029-09-01 | 11:00 | 39600 | 315.429 | 1.8926 | 139.9249 |  | 2029-09-01 | 11:00 | 39600 | 120.62 | 0.72372 | 119.1449 |  | 2006-09-01 | 11:00 | 39600 | 92.6329 | 0.5558 | 112.6131 |  | 2029-09-01 | 11:00 | 39600 | 100.72 | 0.60432 | 74.8195 |  | 2006-09-01 | 11:00 | 39600 | 65.2525 | 0.39152 | 56.1101 |  | 2028-01-01 | 11:00 | 39600 | 129.829 | 0.77897 | 117.5155 |  | 2007-01-01 | 11:00 | 39600 | 90.198 | 0.54119 | 111.3188 |  | 2028-01-01 | 11:00 | 39600 | 61.2097 | 0.36726 | 42.119 |  | 2007-01-01 | 11:00 | 39600 | 58.6267 | 0.35176 | 44.3827 |  | 2029-09-01 | 11:00 | 39600 | 97.0319 | 0.58219 | 116.6287 |  | 2006-09-01 | 11:00 | 39600 | 86.8462 | 0.52108 | 111.9817 |  | 2029-09-01 | 11:00 | 39600 | 84.1731 | 0.50504 | 53.2146 |  | 2006-09-01 | 11:00 | 39600 | 49.5611 | 0.29737 | 36.4487 |  | 2028-01-01 | 11:00 | 39600 | 99.4756 | 0.59685 | 114.2847 |  | 2007-01-01 | 11:00 | 39600 | 86.9079 | 0.52145 | 110.9619 |  | 2028-01-01 | 11:00 | 39600 | 40.5202 | 0.24312 | 25.2082 |  | 2007-01-01 | 11:00 | 39600 | 42.2917 | 0.25375 | 27.4593 |  | 2029-09-01 | 11:00 | 39600 | 92.2828 | 0.5537 | 116.1221 |  | 2006-09-01 | 11:00 | 39600 | 86.2785 | 0.51767 | 111.9198 |  | 2029-09-01 | 11:00 | 39600 | 79.4588 | 0.47675 | 41.6389 |  | 2006-09-01 | 11:00 | 39600 | 39.6334 | 0.2378 | 27.0171 |  | 2028-01-01 | 11:00 | 39600 | 92.2287 | 0.55337 | 113.5134 |  | 2007-01-01 | 11:00 | 39600 | 86.6659 | 0.52 | 110.9356 |  | 2028-01-01 | 11:00 | 39600 | 30.3315 | 0.18199 | 18.0777 |  | 2007-01-01 | 11:00 | 39600 | 32.4159 | 0.1945 | 19.9034 |  | 2029-09-01 | 11:00 | 39600 | 77.2138 | 0.46328 | 51.4822 |  | 2029-09-01 | 11:00 | 39600 | 53.814 | 0.32288 | 35.4927 |  | 2029-09-01 | 11:00 | 39600 | 38.8697 | 0.23322 | 24.4799 |  | 2006-09-01 | 11:00 | 39600 | 38.2754 | 0.22965 | 24.2539 |  | 2028-01-01 | 11:00 | 39600 | 61.2097 | 0.36726 | 42.119 |  | 2007-01-01 | 11:00 | 39600 | 58.6267 | 0.35176 | 44.3827 |  | 2028-01-01 | 11:00 | 39600 | 35.1695 | 0.21102 | 21.5657 |  | 2007-01-01 | 11:00 | 39600 | 35.5244 | 0.21315 | 22.2419
| 2029-09-01 | 11:01 | 39660 | 317.55 | 1.9053 | 141.8302 |  | 2029-09-01 | 11:01 | 39660 | 125.413 | 0.75248 | 119.8974 |  | 2006-09-01 | 11:01 | 39660 | 97.5093 | 0.58506 | 113.1982 |  | 2029-09-01 | 11:01 | 39660 | 105.458 | 0.63275 | 75.4522 |  | 2006-09-01 | 11:01 | 39660 | 67.786 | 0.40672 | 56.5168 |  | 2028-01-01 | 11:01 | 39660 | 134.552 | 0.80731 | 118.3228 |  | 2007-01-01 | 11:01 | 39660 | 95.2076 | 0.57125 | 111.8901 |  | 2028-01-01 | 11:01 | 39660 | 62.918 | 0.37751 | 42.4965 |  | 2007-01-01 | 11:01 | 39660 | 60.6899 | 0.36414 | 44.7469 |  | 2029-09-01 | 11:01 | 39660 | 102.148 | 0.61289 | 117.2416 |  | 2006-09-01 | 11:01 | 39660 | 91.8194 | 0.55092 | 112.5326 |  | 2029-09-01 | 11:01 | 39660 | 88.9655 | 0.53379 | 53.7484 |  | 2006-09-01 | 11:01 | 39660 | 50.9575 | 0.30574 | 36.7545 |  | 2028-01-01 | 11:01 | 39660 | 104.604 | 0.62762 | 114.9124 |  | 2007-01-01 | 11:01 | 39660 | 91.9696 | 0.55182 | 111.5137 |  | 2028-01-01 | 11:01 | 39660 | 41.3058 | 0.24783 | 25.456 |  | 2007-01-01 | 11:01 | 39660 | 43.2163 | 0.2593 | 27.7186 |  | 2029-09-01 | 11:01 | 39660 | 97.4636 | 0.58478 | 116.7069 |  | 2006-09-01 | 11:01 | 39660 | 91.2612 | 0.54757 | 112.4673 |  | 2029-09-01 | 11:01 | 39660 | 84.126 | 0.50476 | 42.1437 |  | 2006-09-01 | 11:01 | 39660 | 40.4043 | 0.24243 | 27.2596 |  | 2028-01-01 | 11:01 | 39660 | 97.4535 | 0.58472 | 114.0981 |  | 2007-01-01 | 11:01 | 39660 | 91.7315 | 0.55039 | 111.486 |  | 2028-01-01 | 11:01 | 39660 | 30.6792 | 0.18408 | 18.2618 |  | 2007-01-01 | 11:01 | 39660 | 32.8414 | 0.19705 | 20.1004 |  | 2029-09-01 | 11:01 | 39660 | 78.6619 | 0.47197 | 51.9542 |  | 2029-09-01 | 11:01 | 39660 | 54.8983 | 0.32939 | 35.8221 |  | 2029-09-01 | 11:01 | 39660 | 39.4803 | 0.23688 | 24.7168 |  | 2006-09-01 | 11:01 | 39660 | 38.8594 | 0.23316 | 24.487 |  | 2028-01-01 | 11:01 | 39660 | 62.918 | 0.37751 | 42.4965 |  | 2007-01-01 | 11:01 | 39660 | 60.6899 | 0.36414 | 44.7469 |  | 2028-01-01 | 11:01 | 39660 | 35.687 | 0.21412 | 21.7798 |  | 2007-01-01 | 11:01 | 39660 | 36.0835 | 0.2165 | 22.4584
| 2029-09-01 | 11:02 | 39720 | 319.648 | 1.9179 | 143.748 |  | 2029-09-01 | 11:02 | 39720 | 130.141 | 0.78085 | 120.6782 |  | 2006-09-01 | 11:02 | 39720 | 102.304 | 0.61382 | 113.812 |  | 2029-09-01 | 11:02 | 39720 | 110.005 | 0.66003 | 76.1122 |  | 2006-09-01 | 11:02 | 39720 | 70.1813 | 0.42109 | 56.9379 |  | 2028-01-01 | 11:02 | 39720 | 139.211 | 0.83527 | 119.158 |  | 2007-01-01 | 11:02 | 39720 | 100.143 | 0.60086 | 112.4909 |  | 2028-01-01 | 11:02 | 39720 | 64.5042 | 0.38703 | 42.8835 |  | 2007-01-01 | 11:02 | 39720 | 62.6151 | 0.37569 | 45.1226 |  | 2029-09-01 | 11:02 | 39720 | 107.195 | 0.64317 | 117.8848 |  | 2006-09-01 | 11:02 | 39720 | 96.7094 | 0.58026 | 113.1129 |  | 2029-09-01 | 11:02 | 39720 | 93.4681 | 0.56081 | 54.3092 |  | 2006-09-01 | 11:02 | 39720 | 52.2302 | 0.31338 | 37.0679 |  | 2028-01-01 | 11:02 | 39720 | 109.663 | 0.65798 | 115.5703 |  | 2007-01-01 | 11:02 | 39720 | 96.9561 | 0.58174 | 112.0954 |  | 2028-01-01 | 11:02 | 39720 | 41.9952 | 0.25197 | 25.708 |  | 2007-01-01 | 11:02 | 39720 | 44.037 | 0.26422 | 27.9828 |  | 2029-09-01 | 11:02 | 39720 | 102.575 | 0.61545 | 117.3224 |  | 2006-09-01 | 11:02 | 39720 | 96.1605 | 0.57696 | 113.0443 |  | 2029-09-01 | 11:02 | 39720 | 88.4096 | 0.53046 | 42.6741 |  | 2006-09-01 | 11:02 | 39720 | 41.0838 | 0.2465 | 27.5061 |  | 2028-01-01 | 11:02 | 39720 | 102.608 | 0.61565 | 114.7138 |  | 2007-01-01 | 11:02 | 39720 | 96.7217 | 0.58033 | 112.0663 |  | 2028-01-01 | 11:02 | 39720 | 30.9684 | 0.18581 | 18.4476 |  | 2007-01-01 | 11:02 | 39720 | 33.2018 | 0.19921 | 20.2997 |  | 2029-09-01 | 11:02 | 39720 | 80.0231 | 0.48014 | 52.4344 |  | 2029-09-01 | 11:02 | 39720 | 55.8854 | 0.33531 | 36.1574 |  | 2029-09-01 | 11:02 | 39720 | 40.0118 | 0.24007 | 24.9569 |  | 2006-09-01 | 11:02 | 39720 | 39.3657 | 0.23619 | 24.7232 |  | 2028-01-01 | 11:02 | 39720 | 64.5042 | 0.38703 | 42.8835 |  | 2007-01-01 | 11:02 | 39720 | 62.6151 | 0.37569 | 45.1226 |  | 2028-01-01 | 11:02 | 39720 | 36.1297 | 0.21678 | 21.9966 |  | 2007-01-01 | 11:02 | 39720 | 36.565 | 0.21939 | 22.6778
| 2029-09-01 | 11:03 | 39780 | 321.722 | 1.9303 | 145.6784 |  | 2029-09-01 | 11:03 | 39780 | 134.807 | 0.80884 | 121.487 |  | 2006-09-01 | 11:03 | 39780 | 107.019 | 0.64211 | 114.4541 |  | 2029-09-01 | 11:03 | 39780 | 114.38 | 0.68628 | 76.7985 |  | 2006-09-01 | 11:03 | 39780 | 72.4462 | 0.43468 | 57.3726 |  | 2028-01-01 | 11:03 | 39780 | 143.809 | 0.86285 | 120.0209 |  | 2007-01-01 | 11:03 | 39780 | 105.006 | 0.63004 | 113.121 |  | 2028-01-01 | 11:03 | 39780 | 65.9771 | 0.39586 | 43.2794 |  | 2007-01-01 | 11:03 | 39780 | 64.412 | 0.38647 | 45.509 |  | 2029-09-01 | 11:03 | 39780 | 112.175 | 0.67305 | 118.5578 |  | 2006-09-01 | 11:03 | 39780 | 101.518 | 0.60911 | 113.722 |  | 2029-09-01 | 11:03 | 39780 | 97.7161 | 0.5863 | 54.8955 |  | 2006-09-01 | 11:03 | 39780 | 53.3909 | 0.32035 | 37.3882 |  | 2028-01-01 | 11:03 | 39780 | 114.655 | 0.68793 | 116.2583 |  | 2007-01-01 | 11:03 | 39780 | 101.869 | 0.61121 | 112.7066 |  | 2028-01-01 | 11:03 | 39780 | 42.6002 | 0.2556 | 25.9636 |  | 2007-01-01 | 11:03 | 39780 | 44.766 | 0.2686 | 28.2514 |  | 2029-09-01 | 11:03 | 39780 | 107.618 | 0.64571 | 117.9681 |  | 2006-09-01 | 11:03 | 39780 | 100.978 | 0.60587 | 113.6502 |  | 2029-09-01 | 11:03 | 39780 | 92.3612 | 0.55417 | 43.2283 |  | 2006-09-01 | 11:03 | 39780 | 41.6836 | 0.2501 | 27.7562 |  | 2028-01-01 | 11:03 | 39780 | 107.695 | 0.64617 | 115.3599 |  | 2007-01-01 | 11:03 | 39780 | 101.638 | 0.60983 | 112.6762 |  | 2028-01-01 | 11:03 | 39780 | 31.209 | 0.18725 | 18.6348 |  | 2007-01-01 | 11:03 | 39780 | 33.5075 | 0.20105 | 20.5007 |  | 2029-09-01 | 11:03 | 39780 | 81.303 | 0.48782 | 52.9222 |  | 2029-09-01 | 11:03 | 39780 | 56.7843 | 0.34071 | 36.4981 |  | 2029-09-01 | 11:03 | 39780 | 40.4745 | 0.24285 | 25.1997 |  | 2006-09-01 | 11:03 | 39780 | 39.8049 | 0.23883 | 24.962 |  | 2028-01-01 | 11:03 | 39780 | 65.9771 | 0.39586 | 43.2794 |  | 2007-01-01 | 11:03 | 39780 | 64.412 | 0.38647 | 45.509 |  | 2028-01-01 | 11:03 | 39780 | 36.5084 | 0.21905 | 22.2156 |  | 2007-01-01 | 11:03 | 39780 | 36.9802 | 0.22188 | 22.8997
| 2029-09-01 | 11:04 | 39840 | 323.773 | 1.9426 | 147.621 |  | 2029-09-01 | 11:04 | 39840 | 139.412 | 0.83647 | 122.3235 |  | 2006-09-01 | 11:04 | 39840 | 111.654 | 0.66992 | 115.124 |  | 2029-09-01 | 11:04 | 39840 | 118.594 | 0.71156 | 77.5101 |  | 2006-09-01 | 11:04 | 39840 | 74.5882 | 0.44753 | 57.8201 |  | 2028-01-01 | 11:04 | 39840 | 148.345 | 0.89007 | 120.911 |  | 2007-01-01 | 11:04 | 39840 | 109.797 | 0.65878 | 113.7798 |  | 2028-01-01 | 11:04 | 39840 | 67.3448 | 0.40407 | 43.6835 |  | 2007-01-01 | 11:04 | 39840 | 66.0897 | 0.39654 | 45.9056 |  | 2029-09-01 | 11:04 | 39840 | 117.088 | 0.70253 | 119.2603 |  | 2006-09-01 | 11:04 | 39840 | 106.245 | 0.63747 | 114.3595 |  | 2029-09-01 | 11:04 | 39840 | 101.728 | 0.61037 | 55.5059 |  | 2006-09-01 | 11:04 | 39840 | 54.4499 | 0.3267 | 37.7149 |  | 2028-01-01 | 11:04 | 39840 | 119.58 | 0.71748 | 116.9757 |  | 2007-01-01 | 11:04 | 39840 | 106.71 | 0.64026 | 113.3469 |  | 2028-01-01 | 11:04 | 39840 | 43.1311 | 0.25879 | 26.2224 |  | 2007-01-01 | 11:04 | 39840 | 45.4137 | 0.27248 | 28.5239 |  | 2029-09-01 | 11:04 | 39840 | 112.594 | 0.67556 | 118.6436 |  | 2006-09-01 | 11:04 | 39840 | 105.715 | 0.63429 | 114.2845 |  | 2029-09-01 | 11:04 | 39840 | 96.0082 | 0.57605 | 43.8043 |  | 2006-09-01 | 11:04 | 39840 | 42.2136 | 0.25328 | 28.0095 |  | 2028-01-01 | 11:04 | 39840 | 112.713 | 0.67628 | 116.0362 |  | 2007-01-01 | 11:04 | 39840 | 106.483 | 0.6389 | 113.3151 |  | 2028-01-01 | 11:04 | 39840 | 31.4092 | 0.18846 | 18.8233 |  | 2007-01-01 | 11:04 | 39840 | 33.767 | 0.2026 | 20.7033 |  | 2029-09-01 | 11:04 | 39840 | 82.5063 | 0.49504 | 53.4172 |  | 2029-09-01 | 11:04 | 39840 | 57.6028 | 0.34562 | 36.8437 |  | 2029-09-01 | 11:04 | 39840 | 40.8774 | 0.24526 | 25.445 |  | 2006-09-01 | 11:04 | 39840 | 40.1857 | 0.24111 | 25.2032 |  | 2028-01-01 | 11:04 | 39840 | 67.3448 | 0.40407 | 43.6835 |  | 2007-01-01 | 11:04 | 39840 | 66.0897 | 0.39654 | 45.9056 |  | 2028-01-01 | 11:04 | 39840 | 36.8322 | 0.22099 | 22.4366 |  | 2007-01-01 | 11:04 | 39840 | 37.3385 | 0.22403 | 23.1237
| 2029-09-01 | 11:05 | 39900 | 325.8 | 1.9548 | 149.5758 |  | 2029-09-01 | 11:05 | 39900 | 143.956 | 0.86374 | 123.1873 |  | 2006-09-01 | 11:05 | 39900 | 116.212 | 0.69727 | 115.8213 |  | 2029-09-01 | 11:05 | 39900 | 122.655 | 0.73593 | 78.246 |  | 2006-09-01 | 11:05 | 39900 | 76.6144 | 0.45969 | 58.2798 |  | 2028-01-01 | 11:05 | 39900 | 152.82 | 0.91692 | 121.8279 |  | 2007-01-01 | 11:05 | 39900 | 114.519 | 0.68711 | 114.4669 |  | 2028-01-01 | 11:05 | 39900 | 68.6147 | 0.41169 | 44.0951 |  | 2007-01-01 | 11:05 | 39900 | 67.6564 | 0.40594 | 46.3115 |  | 2029-09-01 | 11:05 | 39900 | 121.937 | 0.73162 | 119.992 |  | 2006-09-01 | 11:05 | 39900 | 110.894 | 0.66536 | 115.0248 |  | 2029-09-01 | 11:05 | 39900 | 105.516 | 0.6331 | 56.139 |  | 2006-09-01 | 11:05 | 39900 | 55.4168 | 0.3325 | 38.0474 |  | 2028-01-01 | 11:05 | 39900 | 124.44 | 0.74664 | 117.7224 |  | 2007-01-01 | 11:05 | 39900 | 111.48 | 0.66888 | 114.0158 |  | 2028-01-01 | 11:05 | 39900 | 43.597 | 0.26158 | 26.484 |  | 2007-01-01 | 11:05 | 39900 | 45.9895 | 0.27594 | 28.7999 |  | 2029-09-01 | 11:05 | 39900 | 117.504 | 0.70502 | 119.3487 |  | 2006-09-01 | 11:05 | 39900 | 110.372 | 0.66223 | 114.9467 |  | 2029-09-01 | 11:05 | 39900 | 99.3694 | 0.59622 | 44.4005 |  | 2006-09-01 | 11:05 | 39900 | 42.6828 | 0.2561 | 28.2655 |  | 2028-01-01 | 11:05 | 39900 | 117.664 | 0.70598 | 116.7422 |  | 2007-01-01 | 11:05 | 39900 | 111.257 | 0.66754 | 113.9826 |  | 2028-01-01 | 11:05 | 39900 | 31.5756 | 0.18945 | 19.0127 |  | 2007-01-01 | 11:05 | 39900 | 33.9875 | 0.20392 | 20.9072 |  | 2029-09-01 | 11:05 | 39900 | 83.6378 | 0.50183 | 53.919 |  | 2029-09-01 | 11:05 | 39900 | 58.3482 | 0.35009 | 37.1938 |  | 2029-09-01 | 11:05 | 39900 | 41.2283 | 0.24737 | 25.6924 |  | 2006-09-01 | 11:05 | 39900 | 40.5159 | 0.2431 | 25.4463 |  | 2028-01-01 | 11:05 | 39900 | 68.6147 | 0.41169 | 44.0951 |  | 2007-01-01 | 11:05 | 39900 | 67.6564 | 0.40594 | 46.3115 |  | 2028-01-01 | 11:05 | 39900 | 37.1093 | 0.22266 | 22.6593 |  | 2007-01-01 | 11:05 | 39900 | 37.6479 | 0.22589 | 23.3496
| 2029-09-01 | 11:06 | 39960 | 327.806 | 1.9668 | 151.5426 |  | 2029-09-01 | 11:06 | 39960 | 148.44 | 0.89064 | 124.0779 |  | 2006-09-01 | 11:06 | 39960 | 120.694 | 0.72416 | 116.5455 |  | 2029-09-01 | 11:06 | 39960 | 126.568 | 0.75941 | 79.0054 |  | 2006-09-01 | 11:06 | 39960 | 78.5314 | 0.47119 | 58.751 |  | 2028-01-01 | 11:06 | 39960 | 157.235 | 0.94341 | 122.7713 |  | 2007-01-01 | 11:06 | 39960 | 119.173 | 0.71504 | 115.1819 |  | 2028-01-01 | 11:06 | 39960 | 69.7939 | 0.41876 | 44.5139 |  | 2007-01-01 | 11:06 | 39960 | 69.1199 | 0.41472 | 46.7262 |  | 2029-09-01 | 11:06 | 39960 | 126.721 | 0.76033 | 120.7523 |  | 2006-09-01 | 11:06 | 39960 | 115.465 | 0.69279 | 115.7176 |  | 2029-09-01 | 11:06 | 39960 | 109.089 | 0.65453 | 56.7935 |  | 2006-09-01 | 11:06 | 39960 | 56.3 | 0.3378 | 38.3852 |  | 2028-01-01 | 11:06 | 39960 | 129.234 | 0.7754 | 118.4978 |  | 2007-01-01 | 11:06 | 39960 | 116.181 | 0.69709 | 114.7129 |  | 2028-01-01 | 11:06 | 39960 | 44.0058 | 0.26403 | 26.748 |  | 2007-01-01 | 11:06 | 39960 | 46.5018 | 0.27901 | 29.0789 |  | 2029-09-01 | 11:06 | 39960 | 122.349 | 0.73409 | 120.0828 |  | 2006-09-01 | 11:06 | 39960 | 114.952 | 0.68971 | 115.6364 |  | 2029-09-01 | 11:06 | 39960 | 102.46 | 0.61476 | 45.0153 |  | 2006-09-01 | 11:06 | 39960 | 43.0987 | 0.25859 | 28.5241 |  | 2028-01-01 | 11:06 | 39960 | 122.549 | 0.73529 | 117.4775 |  | 2007-01-01 | 11:06 | 39960 | 115.961 | 0.69577 | 114.6784 |  | 2028-01-01 | 11:06 | 39960 | 31.714 | 0.19028 | 19.203 |  | 2007-01-01 | 11:06 | 39960 | 34.1753 | 0.20505 | 21.1123 |  | 2029-09-01 | 11:06 | 39960 | 84.7019 | 0.50821 | 54.4272 |  | 2029-09-01 | 11:06 | 39960 | 59.0272 | 0.35416 | 37.548 |  | 2029-09-01 | 11:06 | 39960 | 41.534 | 0.2492 | 25.9416 |  | 2006-09-01 | 11:06 | 39960 | 40.8023 | 0.24481 | 25.6911 |  | 2028-01-01 | 11:06 | 39960 | 69.7939 | 0.41876 | 44.5139 |  | 2007-01-01 | 11:06 | 39960 | 69.1199 | 0.41472 | 46.7262 |  | 2028-01-01 | 11:06 | 39960 | 37.3462 | 0.22408 | 22.8833 |  | 2007-01-01 | 11:06 | 39960 | 37.9155 | 0.22749 | 23.5771
| 2029-09-01 | 11:07 | 40020 | 329.789 | 1.9787 | 153.5214 |  | 2029-09-01 | 11:07 | 40020 | 152.865 | 0.91719 | 124.9951 |  | 2006-09-01 | 11:07 | 40020 | 125.101 | 0.75061 | 117.2961 |  | 2029-09-01 | 11:07 | 40020 | 130.338 | 0.78203 | 79.7875 |  | 2006-09-01 | 11:07 | 40020 | 80.3453 | 0.48207 | 59.2331 |  | 2028-01-01 | 11:07 | 40020 | 161.592 | 0.96955 | 123.7408 |  | 2007-01-01 | 11:07 | 40020 | 123.761 | 0.74257 | 115.9245 |  | 2028-01-01 | 11:07 | 40020 | 70.8887 | 0.42533 | 44.9392 |  | 2007-01-01 | 11:07 | 40020 | 70.4875 | 0.42292 | 47.1492 |  | 2029-09-01 | 11:07 | 40020 | 131.442 | 0.78865 | 121.5409 |  | 2006-09-01 | 11:07 | 40020 | 119.959 | 0.71975 | 116.4374 |  | 2029-09-01 | 11:07 | 40020 | 112.456 | 0.67474 | 57.4683 |  | 2006-09-01 | 11:07 | 40020 | 57.1074 | 0.34264 | 38.7279 |  | 2028-01-01 | 11:07 | 40020 | 133.964 | 0.80378 | 119.3016 |  | 2007-01-01 | 11:07 | 40020 | 120.815 | 0.72489 | 115.4378 |  | 2028-01-01 | 11:07 | 40020 | 44.3645 | 0.26619 | 27.0142 |  | 2007-01-01 | 11:07 | 40020 | 46.9579 | 0.28175 | 29.3606 |  | 2029-09-01 | 11:07 | 40020 | 127.129 | 0.76277 | 120.8455 |  | 2006-09-01 | 11:07 | 40020 | 119.455 | 0.71673 | 116.3531 |  | 2029-09-01 | 11:07 | 40020 | 105.293 | 0.63176 | 45.6471 |  | 2006-09-01 | 11:07 | 40020 | 43.4682 | 0.26081 | 28.7849 |  | 2028-01-01 | 11:07 | 40020 | 127.368 | 0.76421 | 118.2417 |  | 2007-01-01 | 11:07 | 40020 | 120.599 | 0.72359 | 115.402 |  | 2028-01-01 | 11:07 | 40020 | 31.8292 | 0.19098 | 19.394 |  | 2007-01-01 | 11:07 | 40020 | 34.3354 | 0.20601 | 21.3183 |  | 2029-09-01 | 11:07 | 40020 | 85.7027 | 0.51422 | 54.9415 |  | 2029-09-01 | 11:07 | 40020 | 59.6458 | 0.35787 | 37.9059 |  | 2029-09-01 | 11:07 | 40020 | 41.8004 | 0.2508 | 26.1924 |  | 2006-09-01 | 11:07 | 40020 | 41.0507 | 0.2463 | 25.9374 |  | 2028-01-01 | 11:07 | 40020 | 70.8887 | 0.42533 | 44.9392 |  | 2007-01-01 | 11:07 | 40020 | 70.4875 | 0.42292 | 47.1492 |  | 2028-01-01 | 11:07 | 40020 | 37.5489 | 0.22529 | 23.1086 |  | 2007-01-01 | 11:07 | 40020 | 38.1472 | 0.22888 | 23.806
| 2029-09-01 | 11:08 | 40080 | 331.75 | 1.9905 | 155.5119 |  | 2029-09-01 | 11:08 | 40080 | 157.233 | 0.9434 | 125.9385 |  | 2006-09-01 | 11:08 | 40080 | 129.434 | 0.7766 | 118.0727 |  | 2029-09-01 | 11:08 | 40080 | 133.968 | 0.80381 | 80.5913 |  | 2006-09-01 | 11:08 | 40080 | 82.0621 | 0.49237 | 59.7254 |  | 2028-01-01 | 11:08 | 40080 | 165.89 | 0.99534 | 124.7362 |  | 2007-01-01 | 11:08 | 40080 | 128.283 | 0.7697 | 116.6942 |  | 2028-01-01 | 11:08 | 40080 | 71.9053 | 0.43143 | 45.3707 |  | 2007-01-01 | 11:08 | 40080 | 71.7657 | 0.43059 | 47.5798 |  | 2029-09-01 | 11:08 | 40080 | 136.101 | 0.81661 | 122.3575 |  | 2006-09-01 | 11:08 | 40080 | 124.379 | 0.74627 | 117.1837 |  | 2029-09-01 | 11:08 | 40080 | 115.624 | 0.69374 | 58.162 |  | 2006-09-01 | 11:08 | 40080 | 57.846 | 0.34708 | 39.0749 |  | 2028-01-01 | 11:08 | 40080 | 138.632 | 0.83179 | 120.1334 |  | 2007-01-01 | 11:08 | 40080 | 125.383 | 0.7523 | 116.1901 |  | 2028-01-01 | 11:08 | 40080 | 44.6793 | 0.26808 | 27.2823 |  | 2007-01-01 | 11:08 | 40080 | 47.3642 | 0.28419 | 29.6448 |  | 2029-09-01 | 11:08 | 40080 | 131.847 | 0.79108 | 121.6366 |  | 2006-09-01 | 11:08 | 40080 | 123.883 | 0.7433 | 117.0964 |  | 2029-09-01 | 11:08 | 40080 | 107.88 | 0.64728 | 46.2943 |  | 2006-09-01 | 11:08 | 40080 | 43.797 | 0.26278 | 29.0477 |  | 2028-01-01 | 11:08 | 40080 | 132.124 | 0.79274 | 119.0344 |  | 2007-01-01 | 11:08 | 40080 | 125.17 | 0.75102 | 116.153 |  | 2028-01-01 | 11:08 | 40080 | 31.9249 | 0.19155 | 19.5855 |  | 2007-01-01 | 11:08 | 40080 | 34.4721 | 0.20683 | 21.5251 |  | 2029-09-01 | 11:08 | 40080 | 86.6441 | 0.51986 | 55.4613 |  | 2029-09-01 | 11:08 | 40080 | 60.2094 | 0.36126 | 38.2671 |  | 2029-09-01 | 11:08 | 40080 | 42.0326 | 0.2522 | 26.4446 |  | 2006-09-01 | 11:08 | 40080 | 41.266 | 0.2476 | 26.185 |  | 2028-01-01 | 11:08 | 40080 | 71.9053 | 0.43143 | 45.3707 |  | 2007-01-01 | 11:08 | 40080 | 71.7657 | 0.43059 | 47.5798 |  | 2028-01-01 | 11:08 | 40080 | 37.7222 | 0.22633 | 23.335 |  | 2007-01-01 | 11:08 | 40080 | 38.3481 | 0.23009 | 24.0361
| 2029-09-01 | 11:09 | 40140 | 333.689 | 2.0021 | 157.514 |  | 2029-09-01 | 11:09 | 40140 | 161.543 | 0.96926 | 126.9077 |  | 2006-09-01 | 11:09 | 40140 | 133.695 | 0.80217 | 118.8749 |  | 2029-09-01 | 11:09 | 40140 | 137.462 | 0.82477 | 81.416 |  | 2006-09-01 | 11:09 | 40140 | 83.6873 | 0.50212 | 60.2276 |  | 2028-01-01 | 11:09 | 40140 | 170.131 | 1.0208 | 125.757 |  | 2007-01-01 | 11:09 | 40140 | 132.742 | 0.79645 | 117.4906 |  | 2028-01-01 | 11:09 | 40140 | 72.8492 | 0.4371 | 45.8078 |  | 2007-01-01 | 11:09 | 40140 | 72.9609 | 0.43777 | 48.0175 |  | 2029-09-01 | 11:09 | 40140 | 140.699 | 0.84419 | 123.2017 |  | 2006-09-01 | 11:09 | 40140 | 128.724 | 0.77234 | 117.956 |  | 2029-09-01 | 11:09 | 40140 | 118.599 | 0.71159 | 58.8736 |  | 2006-09-01 | 11:09 | 40140 | 58.5222 | 0.35113 | 39.4261 |  | 2028-01-01 | 11:09 | 40140 | 143.237 | 0.85942 | 120.9928 |  | 2007-01-01 | 11:09 | 40140 | 129.887 | 0.77932 | 116.9694 |  | 2028-01-01 | 11:09 | 40140 | 44.9555 | 0.26973 | 27.552 |  | 2007-01-01 | 11:09 | 40140 | 47.7265 | 0.28636 | 29.9312 |  | 2029-09-01 | 11:09 | 40140 | 136.502 | 0.81901 | 122.4556 |  | 2006-09-01 | 11:09 | 40140 | 128.236 | 0.76942 | 117.8659 |  | 2029-09-01 | 11:09 | 40140 | 110.233 | 0.6614 | 46.9557 |  | 2006-09-01 | 11:09 | 40140 | 44.0903 | 0.26454 | 29.3123 |  | 2028-01-01 | 11:09 | 40140 | 136.816 | 0.8209 | 119.8553 |  | 2007-01-01 | 11:09 | 40140 | 129.677 | 0.77806 | 116.9311 |  | 2028-01-01 | 11:09 | 40140 | 32.0045 | 0.19203 | 19.7776 |  | 2007-01-01 | 11:09 | 40140 | 34.5892 | 0.20754 | 21.7327 |  | 2029-09-01 | 11:09 | 40140 | 87.5296 | 0.52518 | 55.9865 |  | 2029-09-01 | 11:09 | 40140 | 60.723 | 0.36434 | 38.6315 |  | 2029-09-01 | 11:09 | 40140 | 42.2351 | 0.25341 | 26.698 |  | 2006-09-01 | 11:09 | 40140 | 41.4528 | 0.24872 | 26.4337 |  | 2028-01-01 | 11:09 | 40140 | 72.8492 | 0.4371 | 45.8078 |  | 2007-01-01 | 11:09 | 40140 | 72.9609 | 0.43777 | 48.0175 |  | 2028-01-01 | 11:09 | 40140 | 37.8704 | 0.22722 | 23.5622 |  | 2007-01-01 | 11:09 | 40140 | 38.5225 | 0.23114 | 24.2672
| 2029-09-01 | 11:10 | 40200 | 335.608 | 2.0136 | 159.5277 |  | 2029-09-01 | 11:10 | 40200 | 165.798 | 0.99479 | 127.9025 |  | 2006-09-01 | 11:10 | 40200 | 137.885 | 0.82731 | 119.7022 |  | 2029-09-01 | 11:10 | 40200 | 140.824 | 0.84494 | 82.261 |  | 2006-09-01 | 11:10 | 40200 | 85.2262 | 0.51136 | 60.7389 |  | 2028-01-01 | 11:10 | 40200 | 174.315 | 1.0459 | 126.8029 |  | 2007-01-01 | 11:10 | 40200 | 137.138 | 0.82283 | 118.3135 |  | 2028-01-01 | 11:10 | 40200 | 73.7255 | 0.44235 | 46.2501 |  | 2007-01-01 | 11:10 | 40200 | 74.0787 | 0.44447 | 48.462 |  | 2029-09-01 | 11:10 | 40200 | 145.236 | 0.87142 | 124.0732 |  | 2006-09-01 | 11:10 | 40200 | 132.997 | 0.79798 | 118.754 |  | 2029-09-01 | 11:10 | 40200 | 121.388 | 0.72833 | 59.6019 |  | 2006-09-01 | 11:10 | 40200 | 59.1418 | 0.35485 | 39.7809 |  | 2028-01-01 | 11:10 | 40200 | 147.78 | 0.88668 | 121.8795 |  | 2007-01-01 | 11:10 | 40200 | 134.327 | 0.80596 | 117.7753 |  | 2028-01-01 | 11:10 | 40200 | 45.1978 | 0.27119 | 27.8232 |  | 2007-01-01 | 11:10 | 40200 | 48.0499 | 0.2883 | 30.2195 |  | 2029-09-01 | 11:10 | 40200 | 141.097 | 0.84658 | 123.3022 |  | 2006-09-01 | 11:10 | 40200 | 132.517 | 0.7951 | 118.661 |  | 2029-09-01 | 11:10 | 40200 | 112.362 | 0.67417 | 47.6299 |  | 2006-09-01 | 11:10 | 40200 | 44.3526 | 0.26612 | 29.5784 |  | 2028-01-01 | 11:10 | 40200 | 141.445 | 0.84867 | 120.704 |  | 2007-01-01 | 11:10 | 40200 | 134.12 | 0.80472 | 117.7358 |  | 2028-01-01 | 11:10 | 40200 | 32.0707 | 0.19242 | 19.97 |  | 2007-01-01 | 11:10 | 40200 | 34.6897 | 0.20814 | 21.9408 |  | 2029-09-01 | 11:10 | 40200 | 88.3628 | 0.53018 | 56.5167 |  | 2029-09-01 | 11:10 | 40200 | 61.1911 | 0.36715 | 38.9986 |  | 2029-09-01 | 11:10 | 40200 | 42.4118 | 0.25447 | 26.9524 |  | 2006-09-01 | 11:10 | 40200 | 41.6148 | 0.24969 | 26.6834 |  | 2028-01-01 | 11:10 | 40200 | 73.7255 | 0.44235 | 46.2501 |  | 2007-01-01 | 11:10 | 40200 | 74.0787 | 0.44447 | 48.462 |  | 2028-01-01 | 11:10 | 40200 | 37.9971 | 0.22798 | 23.7902 |  | 2007-01-01 | 11:10 | 40200 | 38.6743 | 0.23205 | 24.4993
| 2029-09-01 | 11:11 | 40260 | 337.505 | 2.025 | 161.5527 |  | 2029-09-01 | 11:11 | 40260 | 169.997 | 1.02 | 128.9225 |  | 2006-09-01 | 11:11 | 40260 | 142.004 | 0.85202 | 120.5542 |  | 2029-09-01 | 11:11 | 40260 | 144.056 | 0.86434 | 83.1253 |  | 2006-09-01 | 11:11 | 40260 | 86.6835 | 0.5201 | 61.259 |  | 2028-01-01 | 11:11 | 40260 | 178.443 | 1.0707 | 127.8735 |  | 2007-01-01 | 11:11 | 40260 | 141.473 | 0.84884 | 119.1623 |  | 2028-01-01 | 11:11 | 40260 | 74.5392 | 0.44724 | 46.6974 |  | 2007-01-01 | 11:11 | 40260 | 75.1246 | 0.45075 | 48.9127 |  | 2029-09-01 | 11:11 | 40260 | 149.715 | 0.89829 | 124.9714 |  | 2006-09-01 | 11:11 | 40260 | 137.198 | 0.82319 | 119.5772 |  | 2029-09-01 | 11:11 | 40260 | 123.998 | 0.74399 | 60.3459 |  | 2006-09-01 | 11:11 | 40260 | 59.7101 | 0.35826 | 40.1392 |  | 2028-01-01 | 11:11 | 40260 | 152.263 | 0.91358 | 122.793 |  | 2007-01-01 | 11:11 | 40260 | 138.706 | 0.83224 | 118.6076 |  | 2028-01-01 | 11:11 | 40260 | 45.4104 | 0.27246 | 28.0957 |  | 2007-01-01 | 11:11 | 40260 | 48.3388 | 0.29003 | 30.5095 |  | 2029-09-01 | 11:11 | 40260 | 145.631 | 0.87379 | 124.176 |  | 2006-09-01 | 11:11 | 40260 | 136.726 | 0.82036 | 119.4813 |  | 2029-09-01 | 11:11 | 40260 | 114.278 | 0.68567 | 48.3156 |  | 2006-09-01 | 11:11 | 40260 | 44.5877 | 0.26753 | 29.8459 |  | 2028-01-01 | 11:11 | 40260 | 146.012 | 0.87607 | 121.5801 |  | 2007-01-01 | 11:11 | 40260 | 138.502 | 0.83101 | 118.5668 |  | 2028-01-01 | 11:11 | 40260 | 32.1257 | 0.19275 | 20.1627 |  | 2007-01-01 | 11:11 | 40260 | 34.7762 | 0.20866 | 22.1495 |  | 2029-09-01 | 11:11 | 40260 | 89.1467 | 0.53488 | 57.0516 |  | 2029-09-01 | 11:11 | 40260 | 61.6179 | 0.36971 | 39.3683 |  | 2029-09-01 | 11:11 | 40260 | 42.566 | 0.2554 | 27.2078 |  | 2006-09-01 | 11:11 | 40260 | 41.7552 | 0.25053 | 26.9339 |  | 2028-01-01 | 11:11 | 40260 | 74.5392 | 0.44724 | 46.6974 |  | 2007-01-01 | 11:11 | 40260 | 75.1246 | 0.45075 | 48.9127 |  | 2028-01-01 | 11:11 | 40260 | 38.1055 | 0.22863 | 24.0188 |  | 2007-01-01 | 11:11 | 40260 | 38.8066 | 0.23284 | 24.7321
| 2029-09-01 | 11:12 | 40320 | 339.382 | 2.0363 | 163.589 |  | 2029-09-01 | 11:12 | 40320 | 174.143 | 1.0449 | 129.9674 |  | 2006-09-01 | 11:12 | 40320 | 146.055 | 0.87633 | 121.4305 |  | 2029-09-01 | 11:12 | 40320 | 147.163 | 0.88298 | 84.0083 |  | 2006-09-01 | 11:12 | 40320 | 88.064 | 0.52838 | 61.7874 |  | 2028-01-01 | 11:12 | 40320 | 182.516 | 1.0951 | 128.9686 |  | 2007-01-01 | 11:12 | 40320 | 145.749 | 0.87449 | 120.0368 |  | 2028-01-01 | 11:12 | 40320 | 75.2947 | 0.45177 | 47.1491 |  | 2007-01-01 | 11:12 | 40320 | 76.1036 | 0.45662 | 49.3694 |  | 2029-09-01 | 11:12 | 40320 | 154.134 | 0.9248 | 125.8963 |  | 2006-09-01 | 11:12 | 40320 | 141.329 | 0.84797 | 120.4251 |  | 2029-09-01 | 11:12 | 40320 | 126.433 | 0.7586 | 61.1045 |  | 2006-09-01 | 11:12 | 40320 | 60.2317 | 0.36139 | 40.5006 |  | 2028-01-01 | 11:12 | 40320 | 156.685 | 0.94011 | 123.7332 |  | 2007-01-01 | 11:12 | 40320 | 143.024 | 0.85814 | 119.4657 |  | 2028-01-01 | 11:12 | 40320 | 45.5969 | 0.27358 | 28.3692 |  | 2007-01-01 | 11:12 | 40320 | 48.5971 | 0.29158 | 30.8011 |  | 2029-09-01 | 11:12 | 40320 | 150.106 | 0.90064 | 125.0766 |  | 2006-09-01 | 11:12 | 40320 | 140.865 | 0.84519 | 120.3265 |  | 2029-09-01 | 11:12 | 40320 | 115.99 | 0.69594 | 49.0115 |  | 2006-09-01 | 11:12 | 40320 | 44.7992 | 0.2688 | 30.1147 |  | 2028-01-01 | 11:12 | 40320 | 150.518 | 0.90311 | 122.4832 |  | 2007-01-01 | 11:12 | 40320 | 142.823 | 0.85694 | 119.4237 |  | 2028-01-01 | 11:12 | 40320 | 32.1714 | 0.19303 | 20.3558 |  | 2007-01-01 | 11:12 | 40320 | 34.8509 | 0.20911 | 22.3586 |  | 2029-09-01 | 11:12 | 40320 | 89.8843 | 0.53931 | 57.5909 |  | 2029-09-01 | 11:12 | 40320 | 62.007 | 0.37204 | 39.7404 |  | 2029-09-01 | 11:12 | 40320 | 42.7006 | 0.2562 | 27.464 |  | 2006-09-01 | 11:12 | 40320 | 41.877 | 0.25126 | 27.1852 |  | 2028-01-01 | 11:12 | 40320 | 75.2947 | 0.45177 | 47.1491 |  | 2007-01-01 | 11:12 | 40320 | 76.1036 | 0.45662 | 49.3694 |  | 2028-01-01 | 11:12 | 40320 | 38.1981 | 0.22919 | 24.248 |  | 2007-01-01 | 11:12 | 40320 | 38.9222 | 0.23353 | 24.9656
| 2029-09-01 | 11:13 | 40380 | 341.239 | 2.0474 | 165.6364 |  | 2029-09-01 | 11:13 | 40380 | 178.234 | 1.0694 | 131.0368 |  | 2006-09-01 | 11:13 | 40380 | 150.037 | 0.90022 | 122.3307 |  | 2029-09-01 | 11:13 | 40380 | 150.146 | 0.90088 | 84.9092 |  | 2006-09-01 | 11:13 | 40380 | 89.3721 | 0.53623 | 62.3236 |  | 2028-01-01 | 11:13 | 40380 | 186.535 | 1.1192 | 130.0878 |  | 2007-01-01 | 11:13 | 40380 | 149.967 | 0.8998 | 120.9366 |  | 2028-01-01 | 11:13 | 40380 | 75.9961 | 0.45598 | 47.6051 |  | 2007-01-01 | 11:13 | 40380 | 77.0203 | 0.46212 | 49.8315 |  | 2029-09-01 | 11:13 | 40380 | 158.497 | 0.95098 | 126.8472 |  | 2006-09-01 | 11:13 | 40380 | 145.391 | 0.87235 | 121.2975 |  | 2029-09-01 | 11:13 | 40380 | 128.701 | 0.77221 | 61.8767 |  | 2006-09-01 | 11:13 | 40380 | 60.7111 | 0.36427 | 40.8648 |  | 2028-01-01 | 11:13 | 40380 | 161.049 | 0.96629 | 124.6994 |  | 2007-01-01 | 11:13 | 40380 | 147.283 | 0.8837 | 120.3494 |  | 2028-01-01 | 11:13 | 40380 | 45.7605 | 0.27456 | 28.6438 |  | 2007-01-01 | 11:13 | 40380 | 48.8285 | 0.29297 | 31.094 |  | 2029-09-01 | 11:13 | 40380 | 154.523 | 0.92714 | 126.0038 |  | 2006-09-01 | 11:13 | 40380 | 144.935 | 0.86961 | 121.1961 |  | 2029-09-01 | 11:13 | 40380 | 117.51 | 0.70506 | 49.7166 |  | 2006-09-01 | 11:13 | 40380 | 44.99 | 0.26994 | 30.3846 |  | 2028-01-01 | 11:13 | 40380 | 154.964 | 0.92978 | 123.413 |  | 2007-01-01 | 11:13 | 40380 | 147.086 | 0.88252 | 120.3062 |  | 2028-01-01 | 11:13 | 40380 | 32.2094 | 0.19326 | 20.549 |  | 2007-01-01 | 11:13 | 40380 | 34.9157 | 0.20949 | 22.5681 |  | 2029-09-01 | 11:13 | 40380 | 90.5786 | 0.54347 | 58.1343 |  | 2029-09-01 | 11:13 | 40380 | 62.3619 | 0.37417 | 40.1145 |  | 2029-09-01 | 11:13 | 40380 | 42.8183 | 0.25691 | 27.7209 |  | 2006-09-01 | 11:13 | 40380 | 41.9827 | 0.2519 | 27.4371 |  | 2028-01-01 | 11:13 | 40380 | 75.9961 | 0.45598 | 47.6051 |  | 2007-01-01 | 11:13 | 40380 | 77.0203 | 0.46212 | 49.8315 |  | 2028-01-01 | 11:13 | 40380 | 38.2773 | 0.22966 | 24.4777 |  | 2007-01-01 | 11:13 | 40380 | 39.0235 | 0.23414 | 25.1998
| 2029-09-01 | 11:14 | 40440 | 343.076 | 2.0585 | 167.6949 |  | 2029-09-01 | 11:14 | 40440 | 182.273 | 1.0936 | 132.1304 |  | 2006-09-01 | 11:14 | 40440 | 153.953 | 0.92372 | 123.2545 |  | 2029-09-01 | 11:14 | 40440 | 153.008 | 0.91805 | 85.8272 |  | 2006-09-01 | 11:14 | 40440 | 90.6118 | 0.54367 | 62.8673 |  | 2028-01-01 | 11:14 | 40440 | 190.5 | 1.143 | 131.2308 |  | 2007-01-01 | 11:14 | 40440 | 154.127 | 0.92476 | 121.8614 |  | 2028-01-01 | 11:14 | 40440 | 76.6473 | 0.45988 | 48.065 |  | 2007-01-01 | 11:14 | 40440 | 77.8789 | 0.46727 | 50.2988 |  | 2029-09-01 | 11:14 | 40440 | 162.802 | 0.97681 | 127.824 |  | 2006-09-01 | 11:14 | 40440 | 149.384 | 0.8963 | 122.1938 |  | 2029-09-01 | 11:14 | 40440 | 130.807 | 0.78484 | 62.6616 |  | 2006-09-01 | 11:14 | 40440 | 61.1521 | 0.36691 | 41.2317 |  | 2028-01-01 | 11:14 | 40440 | 165.355 | 0.99213 | 125.6916 |  | 2007-01-01 | 11:14 | 40440 | 151.484 | 0.9089 | 121.2583 |  | 2028-01-01 | 11:14 | 40440 | 45.9041 | 0.27542 | 28.9192 |  | 2007-01-01 | 11:14 | 40440 | 49.0359 | 0.29422 | 31.3883 |  | 2029-09-01 | 11:14 | 40440 | 158.882 | 0.95329 | 126.9571 |  | 2006-09-01 | 11:14 | 40440 | 148.936 | 0.89362 | 122.0897 |  | 2029-09-01 | 11:14 | 40440 | 118.846 | 0.71308 | 50.4297 |  | 2006-09-01 | 11:14 | 40440 | 45.1626 | 0.27098 | 30.6556 |  | 2028-01-01 | 11:14 | 40440 | 159.351 | 0.95611 | 124.3691 |  | 2007-01-01 | 11:14 | 40440 | 151.29 | 0.90774 | 121.214 |  | 2028-01-01 | 11:14 | 40440 | 32.241 | 0.19345 | 20.7425 |  | 2007-01-01 | 11:14 | 40440 | 34.972 | 0.20983 | 22.7779 |  | 2029-09-01 | 11:14 | 40440 | 91.2321 | 0.54739 | 58.6817 |  | 2029-09-01 | 11:14 | 40440 | 62.6857 | 0.37611 | 40.4906 |  | 2029-09-01 | 11:14 | 40440 | 42.9212 | 0.25753 | 27.9785 |  | 2006-09-01 | 11:14 | 40440 | 42.0743 | 0.25245 | 27.6895 |  | 2028-01-01 | 11:14 | 40440 | 76.6473 | 0.45988 | 48.065 |  | 2007-01-01 | 11:14 | 40440 | 77.8789 | 0.46727 | 50.2988 |  | 2028-01-01 | 11:14 | 40440 | 38.345 | 0.23007 | 24.7077 |  | 2007-01-01 | 11:14 | 40440 | 39.1124 | 0.23467 | 25.4344
| 2029-09-01 | 11:15 | 40500 | 344.893 | 2.0694 | 169.7642 |  | 2029-09-01 | 11:15 | 40500 | 186.261 | 1.1176 | 133.248 |  | 2006-09-01 | 11:15 | 40500 | 157.804 | 0.94682 | 124.2013 |  | 2029-09-01 | 11:15 | 40500 | 155.753 | 0.93452 | 86.7617 |  | 2006-09-01 | 11:15 | 40500 | 91.7871 | 0.55072 | 63.418 |  | 2028-01-01 | 11:15 | 40500 | 194.413 | 1.1665 | 132.3973 |  | 2007-01-01 | 11:15 | 40500 | 158.231 | 0.94939 | 122.8107 |  | 2028-01-01 | 11:15 | 40500 | 77.2519 | 0.46351 | 48.5285 |  | 2007-01-01 | 11:15 | 40500 | 78.6835 | 0.4721 | 50.7709 |  | 2029-09-01 | 11:15 | 40500 | 167.053 | 1.0023 | 128.8264 |  | 2006-09-01 | 11:15 | 40500 | 153.312 | 0.91987 | 123.1137 |  | 2029-09-01 | 11:15 | 40500 | 132.757 | 0.79654 | 63.4581 |  | 2006-09-01 | 11:15 | 40500 | 61.5583 | 0.36935 | 41.6011 |  | 2028-01-01 | 11:15 | 40500 | 169.603 | 1.0176 | 126.7092 |  | 2007-01-01 | 11:15 | 40500 | 155.628 | 0.93377 | 122.1921 |  | 2028-01-01 | 11:15 | 40500 | 46.03 | 0.27618 | 29.1954 |  | 2007-01-01 | 11:15 | 40500 | 49.2221 | 0.29533 | 31.6836 |  | 2029-09-01 | 11:15 | 40500 | 163.185 | 0.97911 | 127.9362 |  | 2006-09-01 | 11:15 | 40500 | 152.871 | 0.91723 | 123.007 |  | 2029-09-01 | 11:15 | 40500 | 120.008 | 0.72005 | 51.1497 |  | 2006-09-01 | 11:15 | 40500 | 45.3194 | 0.27192 | 30.9275 |  | 2028-01-01 | 11:15 | 40500 | 163.679 | 0.98207 | 125.3512 |  | 2007-01-01 | 11:15 | 40500 | 155.437 | 0.93262 | 122.1466 |  | 2028-01-01 | 11:15 | 40500 | 32.2672 | 0.1936 | 20.9361 |  | 2007-01-01 | 11:15 | 40500 | 35.0212 | 0.21013 | 22.988 |  | 2029-09-01 | 11:15 | 40500 | 91.8473 | 0.55108 | 59.2328 |  | 2029-09-01 | 11:15 | 40500 | 62.9812 | 0.37789 | 40.8685 |  | 2029-09-01 | 11:15 | 40500 | 43.0112 | 0.25807 | 28.2365 |  | 2006-09-01 | 11:15 | 40500 | 42.1537 | 0.25292 | 27.9424 |  | 2028-01-01 | 11:15 | 40500 | 77.2519 | 0.46351 | 48.5285 |  | 2007-01-01 | 11:15 | 40500 | 78.6835 | 0.4721 | 50.7709 |  | 2028-01-01 | 11:15 | 40500 | 38.4029 | 0.23042 | 24.9381 |  | 2007-01-01 | 11:15 | 40500 | 39.1908 | 0.23514 | 25.6696
| 2029-09-01 | 11:16 | 40560 | 346.691 | 2.0801 | 171.8444 |  | 2029-09-01 | 11:16 | 40560 | 190.197 | 1.1412 | 134.3892 |  | 2006-09-01 | 11:16 | 40560 | 161.59 | 0.96954 | 125.1708 |  | 2029-09-01 | 11:16 | 40560 | 158.384 | 0.9503 | 87.712 |  | 2006-09-01 | 11:16 | 40560 | 92.9016 | 0.55741 | 63.9754 |  | 2028-01-01 | 11:16 | 40560 | 198.273 | 1.1896 | 133.5869 |  | 2007-01-01 | 11:16 | 40560 | 162.281 | 0.97369 | 123.7844 |  | 2028-01-01 | 11:16 | 40560 | 77.8132 | 0.46688 | 48.9954 |  | 2007-01-01 | 11:16 | 40560 | 79.4379 | 0.47663 | 51.2475 |  | 2029-09-01 | 11:16 | 40560 | 171.248 | 1.0275 | 129.8539 |  | 2006-09-01 | 11:16 | 40560 | 157.173 | 0.94304 | 124.0567 |  | 2029-09-01 | 11:16 | 40560 | 134.557 | 0.80734 | 64.2654 |  | 2006-09-01 | 11:16 | 40560 | 61.933 | 0.3716 | 41.9727 |  | 2028-01-01 | 11:16 | 40560 | 173.794 | 1.0428 | 127.752 |  | 2007-01-01 | 11:16 | 40560 | 159.718 | 0.95831 | 123.1504 |  | 2028-01-01 | 11:16 | 40560 | 46.1404 | 0.27684 | 29.4723 |  | 2007-01-01 | 11:16 | 40560 | 49.3896 | 0.29634 | 31.9799 |  | 2029-09-01 | 11:16 | 40560 | 167.433 | 1.0046 | 128.9408 |  | 2006-09-01 | 11:16 | 40560 | 156.74 | 0.94044 | 123.9474 |  | 2029-09-01 | 11:16 | 40560 | 121.006 | 0.72604 | 51.8757 |  | 2006-09-01 | 11:16 | 40560 | 45.4624 | 0.27277 | 31.2003 |  | 2028-01-01 | 11:16 | 40560 | 167.95 | 1.0077 | 126.3589 |  | 2007-01-01 | 11:16 | 40560 | 159.529 | 0.95717 | 123.1038 |  | 2028-01-01 | 11:16 | 40560 | 32.289 | 0.19373 | 21.1298 |  | 2007-01-01 | 11:16 | 40560 | 35.0644 | 0.21039 | 23.1984 |  | 2029-09-01 | 11:16 | 40560 | 92.4265 | 0.55456 | 59.7874 |  | 2029-09-01 | 11:16 | 40560 | 63.2508 | 0.3795 | 41.248 |  | 2029-09-01 | 11:16 | 40560 | 43.0901 | 0.25854 | 28.4951 |  | 2006-09-01 | 11:16 | 40560 | 42.2226 | 0.25334 | 28.1958 |  | 2028-01-01 | 11:16 | 40560 | 77.8132 | 0.46688 | 48.9954 |  | 2007-01-01 | 11:16 | 40560 | 79.4379 | 0.47663 | 51.2475 |  | 2028-01-01 | 11:16 | 40560 | 38.4523 | 0.23071 | 25.1689 |  | 2007-01-01 | 11:16 | 40560 | 39.26 | 0.23556 | 25.9051
| 2029-09-01 | 11:17 | 40620 | 348.469 | 2.0908 | 173.9352 |  | 2029-09-01 | 11:17 | 40620 | 194.083 | 1.1645 | 135.5537 |  | 2006-09-01 | 11:17 | 40620 | 165.313 | 0.99188 | 126.1627 |  | 2029-09-01 | 11:17 | 40620 | 160.903 | 0.96542 | 88.6775 |  | 2006-09-01 | 11:17 | 40620 | 93.9587 | 0.56375 | 64.5392 |  | 2028-01-01 | 11:17 | 40620 | 202.081 | 1.2125 | 134.7994 |  | 2007-01-01 | 11:17 | 40620 | 166.277 | 0.99766 | 124.7821 |  | 2028-01-01 | 11:17 | 40620 | 78.3343 | 0.47001 | 49.4654 |  | 2007-01-01 | 11:17 | 40620 | 80.1454 | 0.48087 | 51.7284 |  | 2029-09-01 | 11:17 | 40620 | 175.389 | 1.0523 | 130.9062 |  | 2006-09-01 | 11:17 | 40620 | 160.97 | 0.96582 | 125.0225 |  | 2029-09-01 | 11:17 | 40620 | 136.212 | 0.81727 | 65.0827 |  | 2006-09-01 | 11:17 | 40620 | 62.2789 | 0.37367 | 42.3464 |  | 2028-01-01 | 11:17 | 40620 | 177.93 | 1.0676 | 128.8195 |  | 2007-01-01 | 11:17 | 40620 | 163.752 | 0.98251 | 124.1329 |  | 2028-01-01 | 11:17 | 40620 | 46.2373 | 0.27742 | 29.7497 |  | 2007-01-01 | 11:17 | 40620 | 49.5404 | 0.29724 | 32.2772 |  | 2029-09-01 | 11:17 | 40620 | 171.626 | 1.0298 | 129.9705 |  | 2006-09-01 | 11:17 | 40620 | 160.544 | 0.96326 | 124.9107 |  | 2029-09-01 | 11:17 | 40620 | 121.848 | 0.73109 | 52.6068 |  | 2006-09-01 | 11:17 | 40620 | 45.5933 | 0.27356 | 31.4739 |  | 2028-01-01 | 11:17 | 40620 | 172.163 | 1.033 | 127.3918 |  | 2007-01-01 | 11:17 | 40620 | 163.567 | 0.9814 | 124.0852 |  | 2028-01-01 | 11:17 | 40620 | 32.3071 | 0.19384 | 21.3237 |  | 2007-01-01 | 11:17 | 40620 | 35.1025 | 0.21061 | 23.409 |  | 2029-09-01 | 11:17 | 40620 | 92.972 | 0.55783 | 60.3452 |  | 2029-09-01 | 11:17 | 40620 | 63.4971 | 0.38098 | 41.629 |  | 2029-09-01 | 11:17 | 40620 | 43.1592 | 0.25896 | 28.754 |  | 2006-09-01 | 11:17 | 40620 | 42.2824 | 0.25369 | 28.4495 |  | 2028-01-01 | 11:17 | 40620 | 78.3343 | 0.47001 | 49.4654 |  | 2007-01-01 | 11:17 | 40620 | 80.1454 | 0.48087 | 51.7284 |  | 2028-01-01 | 11:17 | 40620 | 38.4946 | 0.23097 | 25.3998 |  | 2007-01-01 | 11:17 | 40620 | 39.3215 | 0.23593 | 26.1411
| 2029-09-01 | 11:18 | 40680 | 350.229 | 2.1014 | 176.0366 |  | 2029-09-01 | 11:18 | 40680 | 197.92 | 1.1875 | 136.7412 |  | 2006-09-01 | 11:18 | 40680 | 168.974 | 1.0138 | 127.1766 |  | 2029-09-01 | 11:18 | 40680 | 163.312 | 0.97987 | 89.6573 |  | 2006-09-01 | 11:18 | 40680 | 94.9617 | 0.56977 | 65.109 |  | 2028-01-01 | 11:18 | 40680 | 205.839 | 1.235 | 136.0345 |  | 2007-01-01 | 11:18 | 40680 | 170.221 | 1.0213 | 125.8034 |  | 2028-01-01 | 11:18 | 40680 | 78.8181 | 0.47291 | 49.9383 |  | 2007-01-01 | 11:18 | 40680 | 80.8093 | 0.48486 | 52.2132 |  | 2029-09-01 | 11:18 | 40680 | 179.477 | 1.0769 | 131.983 |  | 2006-09-01 | 11:18 | 40680 | 164.703 | 0.98822 | 126.0107 |  | 2029-09-01 | 11:18 | 40680 | 137.728 | 0.82637 | 65.9091 |  | 2006-09-01 | 11:18 | 40680 | 62.5989 | 0.37559 | 42.722 |  | 2028-01-01 | 11:18 | 40680 | 182.01 | 1.0921 | 129.9116 |  | 2007-01-01 | 11:18 | 40680 | 167.734 | 1.0064 | 125.1393 |  | 2028-01-01 | 11:18 | 40680 | 46.3222 | 0.27793 | 30.0276 |  | 2007-01-01 | 11:18 | 40680 | 49.6766 | 0.29806 | 32.5752 |  | 2029-09-01 | 11:18 | 40680 | 175.764 | 1.0546 | 131.0251 |  | 2006-09-01 | 11:18 | 40680 | 164.284 | 0.9857 | 125.8964 |  | 2029-09-01 | 11:18 | 40680 | 122.543 | 0.73526 | 53.3421 |  | 2006-09-01 | 11:18 | 40680 | 45.7136 | 0.27428 | 31.7482 |  | 2028-01-01 | 11:18 | 40680 | 176.321 | 1.0579 | 128.4498 |  | 2007-01-01 | 11:18 | 40680 | 167.551 | 1.0053 | 125.0905 |  | 2028-01-01 | 11:18 | 40680 | 32.3221 | 0.19393 | 21.5176 |  | 2007-01-01 | 11:18 | 40680 | 35.1364 | 0.21082 | 23.6198 |  | 2029-09-01 | 11:18 | 40680 | 93.4858 | 0.56091 | 60.9061 |  | 2029-09-01 | 11:18 | 40680 | 63.722 | 0.38233 | 42.0114 |  | 2029-09-01 | 11:18 | 40680 | 43.2199 | 0.25932 | 29.0134 |  | 2006-09-01 | 11:18 | 40680 | 42.3342 | 0.25401 | 28.7035 |  | 2028-01-01 | 11:18 | 40680 | 78.8181 | 0.47291 | 49.9383 |  | 2007-01-01 | 11:18 | 40680 | 80.8093 | 0.48486 | 52.2132 |  | 2028-01-01 | 11:18 | 40680 | 38.5306 | 0.23118 | 25.631 |  | 2007-01-01 | 11:18 | 40680 | 39.3762 | 0.23626 | 26.3773
| 2029-09-01 | 11:19 | 40740 | 351.97 | 2.1118 | 178.1484 |  | 2029-09-01 | 11:19 | 40740 | 201.708 | 1.2102 | 137.9514 |  | 2006-09-01 | 11:19 | 40740 | 172.574 | 1.0354 | 128.212 |  | 2029-09-01 | 11:19 | 40740 | 165.616 | 0.9937 | 90.651 |  | 2006-09-01 | 11:19 | 40740 | 95.9138 | 0.57548 | 65.6844 |  | 2028-01-01 | 11:19 | 40740 | 209.547 | 1.2573 | 137.2917 |  | 2007-01-01 | 11:19 | 40740 | 174.113 | 1.0447 | 126.8481 |  | 2028-01-01 | 11:19 | 40740 | 79.2672 | 0.4756 | 50.4139 |  | 2007-01-01 | 11:19 | 40740 | 81.4326 | 0.4886 | 52.7018 |  | 2029-09-01 | 11:19 | 40740 | 183.513 | 1.1011 | 133.0841 |  | 2006-09-01 | 11:19 | 40740 | 168.374 | 1.0102 | 127.021 |  | 2029-09-01 | 11:19 | 40740 | 139.11 | 0.83466 | 66.7437 |  | 2006-09-01 | 11:19 | 40740 | 62.8953 | 0.37737 | 43.0993 |  | 2028-01-01 | 11:19 | 40740 | 186.036 | 1.1162 | 131.0278 |  | 2007-01-01 | 11:19 | 40740 | 171.664 | 1.03 | 126.1693 |  | 2028-01-01 | 11:19 | 40740 | 46.3967 | 0.27838 | 30.306 |  | 2007-01-01 | 11:19 | 40740 | 49.7996 | 0.2988 | 32.874 |  | 2029-09-01 | 11:19 | 40740 | 179.85 | 1.0791 | 132.1042 |  | 2006-09-01 | 11:19 | 40740 | 167.962 | 1.0078 | 126.9041 |  | 2029-09-01 | 11:19 | 40740 | 123.101 | 0.73861 | 54.0807 |  | 2006-09-01 | 11:19 | 40740 | 45.8248 | 0.27495 | 32.0231 |  | 2028-01-01 | 11:19 | 40740 | 180.423 | 1.0825 | 129.5323 |  | 2007-01-01 | 11:19 | 40740 | 171.483 | 1.0289 | 126.1194 |  | 2028-01-01 | 11:19 | 40740 | 32.3345 | 0.19401 | 21.7116 |  | 2007-01-01 | 11:19 | 40740 | 35.1666 | 0.211 | 23.8308 |  | 2029-09-01 | 11:19 | 40740 | 93.9697 | 0.56382 | 61.4699 |  | 2029-09-01 | 11:19 | 40740 | 63.9275 | 0.38356 | 42.3949 |  | 2029-09-01 | 11:19 | 40740 | 43.2733 | 0.25964 | 29.273 |  | 2006-09-01 | 11:19 | 40740 | 42.3792 | 0.25428 | 28.9577 |  | 2028-01-01 | 11:19 | 40740 | 79.2672 | 0.4756 | 50.4139 |  | 2007-01-01 | 11:19 | 40740 | 81.4326 | 0.4886 | 52.7018 |  | 2028-01-01 | 11:19 | 40740 | 38.5614 | 0.23137 | 25.8624 |  | 2007-01-01 | 11:19 | 40740 | 39.4252 | 0.23655 | 26.6139
| 2029-09-01 | 11:20 | 40800 | 353.693 | 2.1222 | 180.2705 |  | 2029-09-01 | 11:20 | 40800 | 205.448 | 1.2327 | 139.1841 |  | 2006-09-01 | 11:20 | 40800 | 176.113 | 1.0567 | 129.2687 |  | 2029-09-01 | 11:20 | 40800 | 167.815 | 1.0069 | 91.6579 |  | 2006-09-01 | 11:20 | 40800 | 96.8176 | 0.58091 | 66.2654 |  | 2028-01-01 | 11:20 | 40800 | 213.205 | 1.2792 | 138.571 |  | 2007-01-01 | 11:20 | 40800 | 177.955 | 1.0677 | 127.9158 |  | 2028-01-01 | 11:20 | 40800 | 79.6841 | 0.4781 | 50.892 |  | 2007-01-01 | 11:20 | 40800 | 82.0181 | 0.49211 | 53.1939 |  | 2029-09-01 | 11:20 | 40800 | 187.498 | 1.125 | 134.2091 |  | 2006-09-01 | 11:20 | 40800 | 171.984 | 1.0319 | 128.0529 |  | 2029-09-01 | 11:20 | 40800 | 140.364 | 0.84218 | 67.5859 |  | 2006-09-01 | 11:20 | 40800 | 63.1702 | 0.37902 | 43.4784 |  | 2028-01-01 | 11:20 | 40800 | 190.008 | 1.14 | 132.1679 |  | 2007-01-01 | 11:20 | 40800 | 175.542 | 1.0533 | 127.2226 |  | 2028-01-01 | 11:20 | 40800 | 46.462 | 0.27877 | 30.5848 |  | 2007-01-01 | 11:20 | 40800 | 49.9111 | 0.29947 | 33.1735 |  | 2029-09-01 | 11:20 | 40800 | 183.884 | 1.1033 | 133.2075 |  | 2006-09-01 | 11:20 | 40800 | 171.579 | 1.0295 | 127.9336 |  | 2029-09-01 | 11:20 | 40800 | 123.529 | 0.74117 | 54.8219 |  | 2006-09-01 | 11:20 | 40800 | 45.9278 | 0.27557 | 32.2987 |  | 2028-01-01 | 11:20 | 40800 | 184.47 | 1.1068 | 130.6391 |  | 2007-01-01 | 11:20 | 40800 | 175.365 | 1.0522 | 127.1716 |  | 2028-01-01 | 11:20 | 40800 | 32.3448 | 0.19407 | 21.9057 |  | 2007-01-01 | 11:20 | 40800 | 35.1937 | 0.21116 | 24.042 |  | 2029-09-01 | 11:20 | 40800 | 94.4257 | 0.56655 | 62.0365 |  | 2029-09-01 | 11:20 | 40800 | 64.1153 | 0.38469 | 42.7796 |  | 2029-09-01 | 11:20 | 40800 | 43.3202 | 0.25992 | 29.5329 |  | 2006-09-01 | 11:20 | 40800 | 42.4182 | 0.25451 | 29.2123 |  | 2028-01-01 | 11:20 | 40800 | 79.6841 | 0.4781 | 50.892 |  | 2007-01-01 | 11:20 | 40800 | 82.0181 | 0.49211 | 53.1939 |  | 2028-01-01 | 11:20 | 40800 | 38.5877 | 0.23153 | 26.0939 |  | 2007-01-01 | 11:20 | 40800 | 39.4691 | 0.23681 | 26.8507
| 2029-09-01 | 11:21 | 40860 | 355.398 | 2.1324 | 182.4029 |  | 2029-09-01 | 11:21 | 40860 | 209.141 | 1.2548 | 140.439 |  | 2006-09-01 | 11:21 | 40860 | 179.593 | 1.0776 | 130.3462 |  | 2029-09-01 | 11:21 | 40860 | 169.914 | 1.0195 | 92.6774 |  | 2006-09-01 | 11:21 | 40860 | 97.6761 | 0.58606 | 66.8514 |  | 2028-01-01 | 11:21 | 40860 | 216.815 | 1.3009 | 139.8719 |  | 2007-01-01 | 11:21 | 40860 | 181.748 | 1.0905 | 129.0063 |  | 2028-01-01 | 11:21 | 40860 | 80.0711 | 0.48043 | 51.3724 |  | 2007-01-01 | 11:21 | 40860 | 82.5683 | 0.49541 | 53.6893 |  | 2029-09-01 | 11:21 | 40860 | 191.431 | 1.1486 | 135.3577 |  | 2006-09-01 | 11:21 | 40860 | 175.533 | 1.0532 | 129.1061 |  | 2029-09-01 | 11:21 | 40860 | 141.496 | 0.84898 | 68.4349 |  | 2006-09-01 | 11:21 | 40860 | 63.4257 | 0.38055 | 43.8589 |  | 2028-01-01 | 11:21 | 40860 | 193.927 | 1.1636 | 133.3314 |  | 2007-01-01 | 11:21 | 40860 | 179.371 | 1.0762 | 128.2988 |  | 2028-01-01 | 11:21 | 40860 | 46.5192 | 0.27912 | 30.8639 |  | 2007-01-01 | 11:21 | 40860 | 50.0123 | 0.30007 | 33.4736 |  | 2029-09-01 | 11:21 | 40860 | 187.866 | 1.1272 | 134.3347 |  | 2006-09-01 | 11:21 | 40860 | 175.135 | 1.0508 | 128.9844 |  | 2029-09-01 | 11:21 | 40860 | 123.836 | 0.74302 | 55.5649 |  | 2006-09-01 | 11:21 | 40860 | 46.0238 | 0.27614 | 32.5748 |  | 2028-01-01 | 11:21 | 40860 | 188.463 | 1.1308 | 131.7699 |  | 2007-01-01 | 11:21 | 40860 | 179.197 | 1.0752 | 128.2468 |  | 2028-01-01 | 11:21 | 40860 | 32.3534 | 0.19412 | 22.0998 |  | 2007-01-01 | 11:21 | 40860 | 35.2182 | 0.21131 | 24.2533 |  | 2029-09-01 | 11:21 | 40860 | 94.8553 | 0.56913 | 62.6056 |  | 2029-09-01 | 11:21 | 40860 | 64.2871 | 0.38572 | 43.1653 |  | 2029-09-01 | 11:21 | 40860 | 43.3616 | 0.26017 | 29.7931 |  | 2006-09-01 | 11:21 | 40860 | 42.452 | 0.25471 | 29.467 |  | 2028-01-01 | 11:21 | 40860 | 80.0711 | 0.48043 | 51.3724 |  | 2007-01-01 | 11:21 | 40860 | 82.5683 | 0.49541 | 53.6893 |  | 2028-01-01 | 11:21 | 40860 | 38.6102 | 0.23166 | 26.3256 |  | 2007-01-01 | 11:21 | 40860 | 39.5089 | 0.23705 | 27.0878
| 2029-09-01 | 11:22 | 40920 | 357.085 | 2.1425 | 184.5454 |  | 2029-09-01 | 11:22 | 40920 | 212.787 | 1.2767 | 141.7157 |  | 2006-09-01 | 11:22 | 40920 | 183.015 | 1.0981 | 131.4443 |  | 2029-09-01 | 11:22 | 40920 | 171.914 | 1.0315 | 93.7089 |  | 2006-09-01 | 11:22 | 40920 | 98.4918 | 0.59095 | 67.4424 |  | 2028-01-01 | 11:22 | 40920 | 220.376 | 1.3223 | 141.1941 |  | 2007-01-01 | 11:22 | 40920 | 185.493 | 1.113 | 130.1193 |  | 2028-01-01 | 11:22 | 40920 | 80.4303 | 0.48258 | 51.855 |  | 2007-01-01 | 11:22 | 40920 | 83.0857 | 0.49851 | 54.1878 |  | 2029-09-01 | 11:22 | 40920 | 195.315 | 1.1719 | 136.5296 |  | 2006-09-01 | 11:22 | 40920 | 179.023 | 1.0741 | 130.1802 |  | 2029-09-01 | 11:22 | 40920 | 142.509 | 0.85505 | 69.29 |  | 2006-09-01 | 11:22 | 40920 | 63.6636 | 0.38198 | 44.2409 |  | 2028-01-01 | 11:22 | 40920 | 197.794 | 1.1868 | 134.5182 |  | 2007-01-01 | 11:22 | 40920 | 183.152 | 1.0989 | 129.3977 |  | 2028-01-01 | 11:22 | 40920 | 46.5694 | 0.27942 | 31.1433 |  | 2007-01-01 | 11:22 | 40920 | 50.1045 | 0.30063 | 33.7742 |  | 2029-09-01 | 11:22 | 40920 | 191.797 | 1.1508 | 135.4855 |  | 2006-09-01 | 11:22 | 40920 | 178.631 | 1.0718 | 130.0562 |  | 2029-09-01 | 11:22 | 40920 | 124.029 | 0.74417 | 56.3091 |  | 2006-09-01 | 11:22 | 40920 | 46.1137 | 0.27668 | 32.8515 |  | 2028-01-01 | 11:22 | 40920 | 192.403 | 1.1544 | 132.9243 |  | 2007-01-01 | 11:22 | 40920 | 182.979 | 1.0979 | 129.3446 |  | 2028-01-01 | 11:22 | 40920 | 32.3604 | 0.19416 | 22.2939 |  | 2007-01-01 | 11:22 | 40920 | 35.2405 | 0.21144 | 24.4647 |  | 2029-09-01 | 11:22 | 40920 | 95.2603 | 0.57156 | 63.1772 |  | 2029-09-01 | 11:22 | 40920 | 64.4443 | 0.38667 | 43.552 |  | 2029-09-01 | 11:22 | 40920 | 43.3981 | 0.26039 | 30.0535 |  | 2006-09-01 | 11:22 | 40920 | 42.4813 | 0.25489 | 29.7219 |  | 2028-01-01 | 11:22 | 40920 | 80.4303 | 0.48258 | 51.855 |  | 2007-01-01 | 11:22 | 40920 | 83.0857 | 0.49851 | 54.1878 |  | 2028-01-01 | 11:22 | 40920 | 38.6293 | 0.23178 | 26.5573 |  | 2007-01-01 | 11:22 | 40920 | 39.5449 | 0.23727 | 27.325
| 2029-09-01 | 11:23 | 40980 | 358.755 | 2.1525 | 186.698 |  | 2029-09-01 | 11:23 | 40980 | 216.388 | 1.2983 | 143.014 |  | 2006-09-01 | 11:23 | 40980 | 186.38 | 1.1183 | 132.5626 |  | 2029-09-01 | 11:23 | 40980 | 173.819 | 1.0429 | 94.7518 |  | 2006-09-01 | 11:23 | 40980 | 99.267 | 0.5956 | 68.038 |  | 2028-01-01 | 11:23 | 40980 | 223.89 | 1.3433 | 142.5375 |  | 2007-01-01 | 11:23 | 40980 | 189.191 | 1.1351 | 131.2544 |  | 2028-01-01 | 11:23 | 40980 | 80.7638 | 0.48458 | 52.3396 |  | 2007-01-01 | 11:23 | 40980 | 83.5725 | 0.50143 | 54.6893 |  | 2029-09-01 | 11:23 | 40980 | 199.149 | 1.1949 | 137.7245 |  | 2006-09-01 | 11:23 | 40980 | 182.454 | 1.0947 | 131.2749 |  | 2029-09-01 | 11:23 | 40980 | 143.411 | 0.86047 | 70.1504 |  | 2006-09-01 | 11:23 | 40980 | 63.8855 | 0.38331 | 44.6242 |  | 2028-01-01 | 11:23 | 40980 | 201.61 | 1.2097 | 135.7278 |  | 2007-01-01 | 11:23 | 40980 | 186.884 | 1.1213 | 130.519 |  | 2028-01-01 | 11:23 | 40980 | 46.6134 | 0.27968 | 31.423 |  | 2007-01-01 | 11:23 | 40980 | 50.1885 | 0.30113 | 34.0753 |  | 2029-09-01 | 11:23 | 40980 | 195.679 | 1.1741 | 136.6596 |  | 2006-09-01 | 11:23 | 40980 | 182.069 | 1.0924 | 131.1486 |  | 2029-09-01 | 11:23 | 40980 | 124.116 | 0.7447 | 57.0538 |  | 2006-09-01 | 11:23 | 40980 | 46.1982 | 0.27719 | 33.1287 |  | 2028-01-01 | 11:23 | 40980 | 196.291 | 1.1777 | 134.1021 |  | 2007-01-01 | 11:23 | 40980 | 186.714 | 1.1203 | 130.4649 |  | 2028-01-01 | 11:23 | 40980 | 32.3663 | 0.1942 | 22.4881 |  | 2007-01-01 | 11:23 | 40980 | 35.261 | 0.21157 | 24.6763 |  | 2029-09-01 | 11:23 | 40980 | 95.6421 | 0.57385 | 63.751 |  | 2029-09-01 | 11:23 | 40980 | 64.5881 | 0.38753 | 43.9395 |  | 2029-09-01 | 11:23 | 40980 | 43.4304 | 0.26058 | 30.3141 |  | 2006-09-01 | 11:23 | 40980 | 42.5068 | 0.25504 | 29.9769 |  | 2028-01-01 | 11:23 | 40980 | 80.7638 | 0.48458 | 52.3396 |  | 2007-01-01 | 11:23 | 40980 | 83.5725 | 0.50143 | 54.6893 |  | 2028-01-01 | 11:23 | 40980 | 38.6456 | 0.23187 | 26.7892 |  | 2007-01-01 | 11:23 | 40980 | 39.5777 | 0.23747 | 27.5625
| 2029-09-01 | 11:24 | 41040 | 360.407 | 2.1624 | 188.8604 |  | 2029-09-01 | 11:24 | 41040 | 219.943 | 1.3197 | 144.3337 |  | 2006-09-01 | 11:24 | 41040 | 189.688 | 1.1381 | 133.7007 |  | 2029-09-01 | 11:24 | 41040 | 175.63 | 1.0538 | 95.8056 |  | 2006-09-01 | 11:24 | 41040 | 100.004 | 0.60002 | 68.638 |  | 2028-01-01 | 11:24 | 41040 | 227.358 | 1.3641 | 143.9016 |  | 2007-01-01 | 11:24 | 41040 | 192.843 | 1.1571 | 132.4115 |  | 2028-01-01 | 11:24 | 41040 | 81.0733 | 0.48644 | 52.826 |  | 2007-01-01 | 11:24 | 41040 | 84.0307 | 0.50418 | 55.1935 |  | 2029-09-01 | 11:24 | 41040 | 202.935 | 1.2176 | 138.9421 |  | 2006-09-01 | 11:24 | 41040 | 185.829 | 1.115 | 132.3899 |  | 2029-09-01 | 11:24 | 41040 | 144.204 | 0.86522 | 71.0156 |  | 2006-09-01 | 11:24 | 41040 | 64.0928 | 0.38456 | 45.0088 |  | 2028-01-01 | 11:24 | 41040 | 205.375 | 1.2322 | 136.9601 |  | 2007-01-01 | 11:24 | 41040 | 190.57 | 1.1434 | 131.6624 |  | 2028-01-01 | 11:24 | 41040 | 46.652 | 0.27991 | 31.7029 |  | 2007-01-01 | 11:24 | 41040 | 50.2654 | 0.30159 | 34.3769 |  | 2029-09-01 | 11:24 | 41040 | 199.511 | 1.1971 | 137.8566 |  | 2006-09-01 | 11:24 | 41040 | 185.45 | 1.1127 | 132.2613 |  | 2029-09-01 | 11:24 | 41040 | 124.104 | 0.74462 | 57.7984 |  | 2006-09-01 | 11:24 | 41040 | 46.278 | 0.27767 | 33.4064 |  | 2028-01-01 | 11:24 | 41040 | 200.126 | 1.2008 | 135.3028 |  | 2007-01-01 | 11:24 | 41040 | 190.403 | 1.1424 | 131.6073 |  | 2028-01-01 | 11:24 | 41040 | 32.3711 | 0.19423 | 22.6824 |  | 2007-01-01 | 11:24 | 41040 | 35.2798 | 0.21168 | 24.888 |  | 2029-09-01 | 11:24 | 41040 | 96.002 | 0.57601 | 64.3271 |  | 2029-09-01 | 11:24 | 41040 | 64.7198 | 0.38832 | 44.3278 |  | 2029-09-01 | 11:24 | 41040 | 43.459 | 0.26075 | 30.5748 |  | 2006-09-01 | 11:24 | 41040 | 42.5288 | 0.25517 | 30.2321 |  | 2028-01-01 | 11:24 | 41040 | 81.0733 | 0.48644 | 52.826 |  | 2007-01-01 | 11:24 | 41040 | 84.0307 | 0.50418 | 55.1935 |  | 2028-01-01 | 11:24 | 41040 | 38.6595 | 0.23196 | 27.0212 |  | 2007-01-01 | 11:24 | 41040 | 39.6078 | 0.23765 | 27.8001
| 2029-09-01 | 11:25 | 41100 | 362.043 | 2.1723 | 191.0327 |  | 2029-09-01 | 11:25 | 41100 | 223.455 | 1.3407 | 145.6744 |  | 2006-09-01 | 11:25 | 41100 | 192.941 | 1.1576 | 134.8584 |  | 2029-09-01 | 11:25 | 41100 | 177.35 | 1.0641 | 96.8697 |  | 2006-09-01 | 11:25 | 41100 | 100.705 | 0.60423 | 69.2422 |  | 2028-01-01 | 11:25 | 41100 | 230.779 | 1.3847 | 145.2863 |  | 2007-01-01 | 11:25 | 41100 | 196.449 | 1.1787 | 133.5902 |  | 2028-01-01 | 11:25 | 41100 | 81.3606 | 0.48816 | 53.3142 |  | 2007-01-01 | 11:25 | 41100 | 84.4624 | 0.50677 | 55.7002 |  | 2029-09-01 | 11:25 | 41100 | 206.674 | 1.24 | 140.1821 |  | 2006-09-01 | 11:25 | 41100 | 189.146 | 1.1349 | 133.5248 |  | 2029-09-01 | 11:25 | 41100 | 144.896 | 0.86938 | 71.885 |  | 2006-09-01 | 11:25 | 41100 | 64.287 | 0.38572 | 45.3945 |  | 2028-01-01 | 11:25 | 41100 | 209.09 | 1.2545 | 138.2146 |  | 2007-01-01 | 11:25 | 41100 | 194.21 | 1.1653 | 132.8277 |  | 2028-01-01 | 11:25 | 41100 | 46.6857 | 0.28011 | 31.983 |  | 2007-01-01 | 11:25 | 41100 | 50.3359 | 0.30202 | 34.6789 |  | 2029-09-01 | 11:25 | 41100 | 203.295 | 1.2198 | 139.0764 |  | 2006-09-01 | 11:25 | 41100 | 188.774 | 1.1326 | 133.394 |  | 2029-09-01 | 11:25 | 41100 | 124 | 0.744 | 58.5424 |  | 2006-09-01 | 11:25 | 41100 | 46.3537 | 0.27812 | 33.6845 |  | 2028-01-01 | 11:25 | 41100 | 203.911 | 1.2235 | 136.5263 |  | 2007-01-01 | 11:25 | 41100 | 194.045 | 1.1643 | 132.7716 |  | 2028-01-01 | 11:25 | 41100 | 32.3751 | 0.19425 | 22.8766 |  | 2007-01-01 | 11:25 | 41100 | 35.2973 | 0.21178 | 25.0998 |  | 2029-09-01 | 11:25 | 41100 | 96.3415 | 0.57805 | 64.9051 |  | 2029-09-01 | 11:25 | 41100 | 64.8406 | 0.38904 | 44.7169 |  | 2029-09-01 | 11:25 | 41100 | 43.4845 | 0.26091 | 30.8357 |  | 2006-09-01 | 11:25 | 41100 | 42.548 | 0.25529 | 30.4874 |  | 2028-01-01 | 11:25 | 41100 | 81.3606 | 0.48816 | 53.3142 |  | 2007-01-01 | 11:25 | 41100 | 84.4624 | 0.50677 | 55.7002 |  | 2028-01-01 | 11:25 | 41100 | 38.6714 | 0.23203 | 27.2532 |  | 2007-01-01 | 11:25 | 41100 | 39.6355 | 0.23781 | 28.0379
| 2029-09-01 | 11:26 | 41160 | 363.661 | 2.182 | 193.2146 |  | 2029-09-01 | 11:26 | 41160 | 226.922 | 1.3615 | 147.0359 |  | 2006-09-01 | 11:26 | 41160 | 196.14 | 1.1768 | 136.0352 |  | 2029-09-01 | 11:26 | 41160 | 178.982 | 1.0739 | 97.9436 |  | 2006-09-01 | 11:26 | 41160 | 101.373 | 0.60824 | 69.8505 |  | 2028-01-01 | 11:26 | 41160 | 234.155 | 1.4049 | 146.6912 |  | 2007-01-01 | 11:26 | 41160 | 200.011 | 1.2001 | 134.7902 |  | 2028-01-01 | 11:26 | 41160 | 81.6273 | 0.48976 | 53.804 |  | 2007-01-01 | 11:26 | 41160 | 84.8692 | 0.50922 | 56.2094 |  | 2029-09-01 | 11:26 | 41160 | 210.365 | 1.2622 | 141.4443 |  | 2006-09-01 | 11:26 | 41160 | 192.409 | 1.1545 | 134.6793 |  | 2029-09-01 | 11:26 | 41160 | 145.49 | 0.87294 | 72.758 |  | 2006-09-01 | 11:26 | 41160 | 64.4692 | 0.38682 | 45.7813 |  | 2028-01-01 | 11:26 | 41160 | 212.755 | 1.2765 | 139.4912 |  | 2007-01-01 | 11:26 | 41160 | 197.805 | 1.1868 | 134.0145 |  | 2028-01-01 | 11:26 | 41160 | 46.7153 | 0.28029 | 32.2633 |  | 2007-01-01 | 11:26 | 41160 | 50.4008 | 0.3024 | 34.9813 |  | 2029-09-01 | 11:26 | 41160 | 207.031 | 1.2422 | 140.3186 |  | 2006-09-01 | 11:26 | 41160 | 192.043 | 1.1523 | 134.5462 |  | 2029-09-01 | 11:26 | 41160 | 123.812 | 0.74287 | 59.2853 |  | 2006-09-01 | 11:26 | 41160 | 46.4258 | 0.27855 | 33.963 |  | 2028-01-01 | 11:26 | 41160 | 207.646 | 1.2459 | 137.7722 |  | 2007-01-01 | 11:26 | 41160 | 197.643 | 1.1859 | 133.9575 |  | 2028-01-01 | 11:26 | 41160 | 32.3784 | 0.19427 | 23.0709 |  | 2007-01-01 | 11:26 | 41160 | 35.3136 | 0.21188 | 25.3117 |  | 2029-09-01 | 11:26 | 41160 | 96.6618 | 0.57997 | 65.4851 |  | 2029-09-01 | 11:26 | 41160 | 64.9513 | 0.38971 | 45.1066 |  | 2029-09-01 | 11:26 | 41160 | 43.5071 | 0.26104 | 31.0968 |  | 2006-09-01 | 11:26 | 41160 | 42.5646 | 0.25539 | 30.7427 |  | 2028-01-01 | 11:26 | 41160 | 81.6273 | 0.48976 | 53.804 |  | 2007-01-01 | 11:26 | 41160 | 84.8692 | 0.50922 | 56.2094 |  | 2028-01-01 | 11:26 | 41160 | 38.6814 | 0.23209 | 27.4853 |  | 2007-01-01 | 11:26 | 41160 | 39.6612 | 0.23797 | 28.2759
| 2029-09-01 | 11:27 | 41220 | 365.264 | 2.1916 | 195.4062 |  | 2029-09-01 | 11:27 | 41220 | 230.347 | 1.3821 | 148.418 |  | 2006-09-01 | 11:27 | 41220 | 199.286 | 1.1957 | 137.2309 |  | 2029-09-01 | 11:27 | 41220 | 180.529 | 1.0832 | 99.0267 |  | 2006-09-01 | 11:27 | 41220 | 102.008 | 0.61205 | 70.4625 |  | 2028-01-01 | 11:27 | 41220 | 237.486 | 1.4249 | 148.1161 |  | 2007-01-01 | 11:27 | 41220 | 203.53 | 1.2212 | 136.0114 |  | 2028-01-01 | 11:27 | 41220 | 81.8747 | 0.49125 | 54.2952 |  | 2007-01-01 | 11:27 | 41220 | 85.253 | 0.51152 | 56.721 |  | 2029-09-01 | 11:27 | 41220 | 214.01 | 1.2841 | 142.7284 |  | 2006-09-01 | 11:27 | 41220 | 195.617 | 1.1737 | 135.853 |  | 2029-09-01 | 11:27 | 41220 | 145.99 | 0.87594 | 73.6339 |  | 2006-09-01 | 11:27 | 41220 | 64.6405 | 0.38784 | 46.1691 |  | 2028-01-01 | 11:27 | 41220 | 216.372 | 1.2982 | 140.7894 |  | 2007-01-01 | 11:27 | 41220 | 201.356 | 1.2081 | 135.2226 |  | 2028-01-01 | 11:27 | 41220 | 46.7412 | 0.28045 | 32.5437 |  | 2007-01-01 | 11:27 | 41220 | 50.4606 | 0.30276 | 35.2841 |  | 2029-09-01 | 11:27 | 41220 | 210.721 | 1.2643 | 141.5829 |  | 2006-09-01 | 11:27 | 41220 | 195.257 | 1.1715 | 135.7178 |  | 2029-09-01 | 11:27 | 41220 | 123.545 | 0.74127 | 60.0265 |  | 2006-09-01 | 11:27 | 41220 | 46.4949 | 0.27897 | 34.242 |  | 2028-01-01 | 11:27 | 41220 | 211.331 | 1.268 | 139.0401 |  | 2007-01-01 | 11:27 | 41220 | 201.196 | 1.2072 | 135.1646 |  | 2028-01-01 | 11:27 | 41220 | 32.3811 | 0.19429 | 23.2652 |  | 2007-01-01 | 11:27 | 41220 | 35.329 | 0.21197 | 25.5236 |  | 2029-09-01 | 11:27 | 41220 | 96.964 | 0.58178 | 66.0669 |  | 2029-09-01 | 11:27 | 41220 | 65.0528 | 0.39032 | 45.4969 |  | 2029-09-01 | 11:27 | 41220 | 43.5273 | 0.26116 | 31.3579 |  | 2006-09-01 | 11:27 | 41220 | 42.579 | 0.25547 | 30.9982 |  | 2028-01-01 | 11:27 | 41220 | 81.8747 | 0.49125 | 54.2952 |  | 2007-01-01 | 11:27 | 41220 | 85.253 | 0.51152 | 56.721 |  | 2028-01-01 | 11:27 | 41220 | 38.69 | 0.23214 | 27.7174 |  | 2007-01-01 | 11:27 | 41220 | 39.6851 | 0.23811 | 28.514
| 2029-09-01 | 11:28 | 41280 | 366.85 | 2.2011 | 197.6073 |  | 2029-09-01 | 11:28 | 41280 | 233.729 | 1.4024 | 149.8204 |  | 2006-09-01 | 11:28 | 41280 | 202.378 | 1.2143 | 138.4452 |  | 2029-09-01 | 11:28 | 41280 | 181.992 | 1.092 | 100.1187 |  | 2006-09-01 | 11:28 | 41280 | 102.613 | 0.61568 | 71.0782 |  | 2028-01-01 | 11:28 | 41280 | 240.772 | 1.4446 | 149.5608 |  | 2007-01-01 | 11:28 | 41280 | 207.007 | 1.242 | 137.2535 |  | 2028-01-01 | 11:28 | 41280 | 82.1044 | 0.49263 | 54.7878 |  | 2007-01-01 | 11:28 | 41280 | 85.6152 | 0.51369 | 57.2347 |  | 2029-09-01 | 11:28 | 41280 | 217.609 | 1.3057 | 144.034 |  | 2006-09-01 | 11:28 | 41280 | 198.771 | 1.1926 | 137.0456 |  | 2029-09-01 | 11:28 | 41280 | 146.403 | 0.87842 | 74.5123 |  | 2006-09-01 | 11:28 | 41280 | 64.802 | 0.38881 | 46.5579 |  | 2028-01-01 | 11:28 | 41280 | 219.94 | 1.3196 | 142.109 |  | 2007-01-01 | 11:28 | 41280 | 204.864 | 1.2292 | 136.4518 |  | 2028-01-01 | 11:28 | 41280 | 46.7639 | 0.28058 | 32.8243 |  | 2007-01-01 | 11:28 | 41280 | 50.516 | 0.3031 | 35.5872 |  | 2029-09-01 | 11:28 | 41280 | 214.364 | 1.2862 | 142.8691 |  | 2006-09-01 | 11:28 | 41280 | 198.417 | 1.1905 | 136.9083 |  | 2029-09-01 | 11:28 | 41280 | 123.206 | 0.73924 | 60.7658 |  | 2006-09-01 | 11:28 | 41280 | 46.5612 | 0.27937 | 34.5214 |  | 2028-01-01 | 11:28 | 41280 | 214.966 | 1.2898 | 140.3299 |  | 2007-01-01 | 11:28 | 41280 | 204.707 | 1.2282 | 136.3929 |  | 2028-01-01 | 11:28 | 41280 | 32.3833 | 0.1943 | 23.4595 |  | 2007-01-01 | 11:28 | 41280 | 35.3435 | 0.21206 | 25.7357 |  | 2029-09-01 | 11:28 | 41280 | 97.2491 | 0.58349 | 66.6504 |  | 2029-09-01 | 11:28 | 41280 | 65.1461 | 0.39088 | 45.8878 |  | 2029-09-01 | 11:28 | 41280 | 43.5455 | 0.26127 | 31.6192 |  | 2006-09-01 | 11:28 | 41280 | 42.5915 | 0.25555 | 31.2538 |  | 2028-01-01 | 11:28 | 41280 | 82.1044 | 0.49263 | 54.7878 |  | 2007-01-01 | 11:28 | 41280 | 85.6152 | 0.51369 | 57.2347 |  | 2028-01-01 | 11:28 | 41280 | 38.6973 | 0.23218 | 27.9496 |  | 2007-01-01 | 11:28 | 41280 | 39.7074 | 0.23824 | 28.7523
| 2029-09-01 | 11:29 | 41340 | 368.419 | 2.2105 | 199.8178 |  | 2029-09-01 | 11:29 | 41340 | 237.069 | 1.4224 | 151.2428 |  | 2006-09-01 | 11:29 | 41340 | 205.42 | 1.2325 | 139.6777 |  | 2029-09-01 | 11:29 | 41340 | 183.374 | 1.1002 | 101.2189 |  | 2006-09-01 | 11:29 | 41340 | 103.189 | 0.61913 | 71.6973 |  | 2028-01-01 | 11:29 | 41340 | 244.016 | 1.4641 | 151.0249 |  | 2007-01-01 | 11:29 | 41340 | 210.442 | 1.2627 | 138.5161 |  | 2028-01-01 | 11:29 | 41340 | 82.3176 | 0.49391 | 55.2817 |  | 2007-01-01 | 11:29 | 41340 | 85.9572 | 0.51574 | 57.7504 |  | 2029-09-01 | 11:29 | 41340 | 221.164 | 1.327 | 145.361 |  | 2006-09-01 | 11:29 | 41340 | 201.872 | 1.2112 | 138.2568 |  | 2029-09-01 | 11:29 | 41340 | 146.731 | 0.88039 | 75.3927 |  | 2006-09-01 | 11:29 | 41340 | 64.9546 | 0.38973 | 46.9477 |  | 2028-01-01 | 11:29 | 41340 | 223.461 | 1.3408 | 143.4498 |  | 2007-01-01 | 11:29 | 41340 | 208.331 | 1.25 | 137.7018 |  | 2028-01-01 | 11:29 | 41340 | 46.7837 | 0.2807 | 33.105 |  | 2007-01-01 | 11:29 | 41340 | 50.5674 | 0.3034 | 35.8906 |  | 2029-09-01 | 11:29 | 41340 | 217.962 | 1.3078 | 144.1769 |  | 2006-09-01 | 11:29 | 41340 | 201.524 | 1.2091 | 138.1174 |  | 2029-09-01 | 11:29 | 41340 | 122.8 | 0.7368 | 61.5026 |  | 2006-09-01 | 11:29 | 41340 | 46.6252 | 0.27975 | 34.8011 |  | 2028-01-01 | 11:29 | 41340 | 218.554 | 1.3113 | 141.6413 |  | 2007-01-01 | 11:29 | 41340 | 208.175 | 1.249 | 137.6419 |  | 2028-01-01 | 11:29 | 41340 | 32.3851 | 0.19431 | 23.6538 |  | 2007-01-01 | 11:29 | 41340 | 35.3572 | 0.21214 | 25.9478 |  | 2029-09-01 | 11:29 | 41340 | 97.5184 | 0.58511 | 67.2355 |  | 2029-09-01 | 11:29 | 41340 | 65.2318 | 0.39139 | 46.2792 |  | 2029-09-01 | 11:29 | 41340 | 43.5618 | 0.26137 | 31.8806 |  | 2006-09-01 | 11:29 | 41340 | 42.6023 | 0.25561 | 31.5094 |  | 2028-01-01 | 11:29 | 41340 | 82.3176 | 0.49391 | 55.2817 |  | 2007-01-01 | 11:29 | 41340 | 85.9572 | 0.51574 | 57.7504 |  | 2028-01-01 | 11:29 | 41340 | 38.7034 | 0.23222 | 28.1818 |  | 2007-01-01 | 11:29 | 41340 | 39.7284 | 0.23837 | 28.9906
| 2029-09-01 | 11:30 | 41400 | 369.973 | 2.2198 | 202.0377 |  | 2029-09-01 | 11:30 | 41400 | 240.368 | 1.4422 | 152.685 |  | 2006-09-01 | 11:30 | 41400 | 208.41 | 1.2505 | 140.9282 |  | 2029-09-01 | 11:30 | 41400 | 184.677 | 1.1081 | 102.327 |  | 2006-09-01 | 11:30 | 41400 | 103.739 | 0.62243 | 72.3197 |  | 2028-01-01 | 11:30 | 41400 | 247.216 | 1.4833 | 152.5081 |  | 2007-01-01 | 11:30 | 41400 | 213.837 | 1.283 | 139.7991 |  | 2028-01-01 | 11:30 | 41400 | 82.5154 | 0.49509 | 55.7768 |  | 2007-01-01 | 11:30 | 41400 | 86.2805 | 0.51768 | 58.2681 |  | 2029-09-01 | 11:30 | 41400 | 224.675 | 1.348 | 146.7091 |  | 2006-09-01 | 11:30 | 41400 | 204.922 | 1.2295 | 139.4863 |  | 2029-09-01 | 11:30 | 41400 | 146.98 | 0.88188 | 76.2746 |  | 2006-09-01 | 11:30 | 41400 | 65.0991 | 0.39059 | 47.3383 |  | 2028-01-01 | 11:30 | 41400 | 226.936 | 1.3616 | 144.8114 |  | 2007-01-01 | 11:30 | 41400 | 211.756 | 1.2705 | 138.9723 |  | 2028-01-01 | 11:30 | 41400 | 46.8011 | 0.28081 | 33.3858 |  | 2007-01-01 | 11:30 | 41400 | 50.6152 | 0.30369 | 36.1943 |  | 2029-09-01 | 11:30 | 41400 | 221.515 | 1.3291 | 145.506 |  | 2006-09-01 | 11:30 | 41400 | 204.58 | 1.2275 | 139.3449 |  | 2029-09-01 | 11:30 | 41400 | 122.334 | 0.734 | 62.2366 |  | 2006-09-01 | 11:30 | 41400 | 46.6871 | 0.28012 | 35.0812 |  | 2028-01-01 | 11:30 | 41400 | 222.094 | 1.3326 | 142.9738 |  | 2007-01-01 | 11:30 | 41400 | 211.603 | 1.2696 | 138.9115 |  | 2028-01-01 | 11:30 | 41400 | 32.3865 | 0.19432 | 23.8481 |  | 2007-01-01 | 11:30 | 41400 | 35.3703 | 0.21222 | 26.1601 |  | 2029-09-01 | 11:30 | 41400 | 97.7726 | 0.58664 | 67.8221 |  | 2029-09-01 | 11:30 | 41400 | 65.3106 | 0.39186 | 46.671 |  | 2029-09-01 | 11:30 | 41400 | 43.5764 | 0.26146 | 32.142 |  | 2006-09-01 | 11:30 | 41400 | 42.6118 | 0.25567 | 31.7651 |  | 2028-01-01 | 11:30 | 41400 | 82.5154 | 0.49509 | 55.7768 |  | 2007-01-01 | 11:30 | 41400 | 86.2805 | 0.51768 | 58.2681 |  | 2028-01-01 | 11:30 | 41400 | 38.7086 | 0.23225 | 28.4141 |  | 2007-01-01 | 11:30 | 41400 | 39.7483 | 0.23849 | 29.2291
| 2029-09-01 | 11:31 | 41460 | 371.512 | 2.2291 | 204.2667 |  | 2029-09-01 | 11:31 | 41460 | 243.626 | 1.4618 | 154.1468 |  | 2006-09-01 | 11:31 | 41460 | 211.35 | 1.2681 | 142.1963 |  | 2029-09-01 | 11:31 | 41460 | 185.905 | 1.1154 | 103.4424 |  | 2006-09-01 | 11:31 | 41460 | 104.263 | 0.62558 | 72.9453 |  | 2028-01-01 | 11:31 | 41460 | 250.374 | 1.5022 | 154.0104 |  | 2007-01-01 | 11:31 | 41460 | 217.191 | 1.3031 | 141.1023 |  | 2028-01-01 | 11:31 | 41460 | 82.6993 | 0.4962 | 56.273 |  | 2007-01-01 | 11:31 | 41460 | 86.5863 | 0.51952 | 58.7876 |  | 2029-09-01 | 11:31 | 41460 | 228.141 | 1.3688 | 148.0779 |  | 2006-09-01 | 11:31 | 41460 | 207.92 | 1.2475 | 140.7339 |  | 2029-09-01 | 11:31 | 41460 | 147.154 | 0.88292 | 77.1575 |  | 2006-09-01 | 11:31 | 41460 | 65.2362 | 0.39142 | 47.7297 |  | 2028-01-01 | 11:31 | 41460 | 230.364 | 1.3822 | 146.1936 |  | 2007-01-01 | 11:31 | 41460 | 215.141 | 1.2908 | 140.2632 |  | 2028-01-01 | 11:31 | 41460 | 46.8165 | 0.2809 | 33.6667 |  | 2007-01-01 | 11:31 | 41460 | 50.6599 | 0.30396 | 36.4982 |  | 2029-09-01 | 11:31 | 41460 | 225.024 | 1.3501 | 146.8561 |  | 2006-09-01 | 11:31 | 41460 | 207.584 | 1.2455 | 140.5904 |  | 2029-09-01 | 11:31 | 41460 | 121.812 | 0.73087 | 62.9674 |  | 2006-09-01 | 11:31 | 41460 | 46.7473 | 0.28048 | 35.3617 |  | 2028-01-01 | 11:31 | 41460 | 225.587 | 1.3535 | 144.3273 |  | 2007-01-01 | 11:31 | 41460 | 214.99 | 1.2899 | 140.2015 |  | 2028-01-01 | 11:31 | 41460 | 32.3879 | 0.19433 | 24.0424 |  | 2007-01-01 | 11:31 | 41460 | 35.3829 | 0.2123 | 26.3724 |  | 2029-09-01 | 11:31 | 41460 | 98.0127 | 0.58808 | 68.4102 |  | 2029-09-01 | 11:31 | 41460 | 65.3831 | 0.3923 | 47.0633 |  | 2029-09-01 | 11:31 | 41460 | 43.5897 | 0.26154 | 32.4036 |  | 2006-09-01 | 11:31 | 41460 | 42.6199 | 0.25572 | 32.0208 |  | 2028-01-01 | 11:31 | 41460 | 82.6993 | 0.4962 | 56.273 |  | 2007-01-01 | 11:31 | 41460 | 86.5863 | 0.51952 | 58.7876 |  | 2028-01-01 | 11:31 | 41460 | 38.7132 | 0.23228 | 28.6464 |  | 2007-01-01 | 11:31 | 41460 | 39.7671 | 0.2386 | 29.4677
| 2029-09-01 | 11:32 | 41520 | 373.035 | 2.2382 | 206.505 |  | 2029-09-01 | 11:32 | 41520 | 246.845 | 1.4811 | 155.6278 |  | 2006-09-01 | 11:32 | 41520 | 214.241 | 1.2854 | 143.4817 |  | 2029-09-01 | 11:32 | 41520 | 187.058 | 1.1223 | 104.5648 |  | 2006-09-01 | 11:32 | 41520 | 104.764 | 0.62858 | 73.5739 |  | 2028-01-01 | 11:32 | 41520 | 253.491 | 1.5209 | 155.5313 |  | 2007-01-01 | 11:32 | 41520 | 220.507 | 1.323 | 142.4253 |  | 2028-01-01 | 11:32 | 41520 | 82.8705 | 0.49722 | 56.7703 |  | 2007-01-01 | 11:32 | 41520 | 86.8757 | 0.52125 | 59.3089 |  | 2029-09-01 | 11:32 | 41520 | 231.565 | 1.3894 | 149.4673 |  | 2006-09-01 | 11:32 | 41520 | 210.869 | 1.2652 | 141.9991 |  | 2029-09-01 | 11:32 | 41520 | 147.256 | 0.88354 | 78.041 |  | 2006-09-01 | 11:32 | 41520 | 65.3667 | 0.3922 | 48.1219 |  | 2028-01-01 | 11:32 | 41520 | 233.748 | 1.4025 | 147.5961 |  | 2007-01-01 | 11:32 | 41520 | 218.486 | 1.3109 | 141.5741 |  | 2028-01-01 | 11:32 | 41520 | 46.8302 | 0.28098 | 33.9477 |  | 2007-01-01 | 11:32 | 41520 | 50.7018 | 0.30421 | 36.8025 |  | 2029-09-01 | 11:32 | 41520 | 228.489 | 1.3709 | 148.227 |  | 2006-09-01 | 11:32 | 41520 | 210.538 | 1.2632 | 141.8536 |  | 2029-09-01 | 11:32 | 41520 | 121.24 | 0.72744 | 63.6949 |  | 2006-09-01 | 11:32 | 41520 | 46.8059 | 0.28084 | 35.6426 |  | 2028-01-01 | 11:32 | 41520 | 229.035 | 1.3742 | 145.7016 |  | 2007-01-01 | 11:32 | 41520 | 218.337 | 1.31 | 141.5115 |  | 2028-01-01 | 11:32 | 41520 | 32.3891 | 0.19433 | 24.2368 |  | 2007-01-01 | 11:32 | 41520 | 35.395 | 0.21237 | 26.5847 |  | 2029-09-01 | 11:32 | 41520 | 98.2396 | 0.58944 | 68.9996 |  | 2029-09-01 | 11:32 | 41520 | 65.4499 | 0.3927 | 47.456 |  | 2029-09-01 | 11:32 | 41520 | 43.6018 | 0.26161 | 32.6652 |  | 2006-09-01 | 11:32 | 41520 | 42.627 | 0.25576 | 32.2765 |  | 2028-01-01 | 11:32 | 41520 | 82.8705 | 0.49722 | 56.7703 |  | 2007-01-01 | 11:32 | 41520 | 86.8757 | 0.52125 | 59.3089 |  | 2028-01-01 | 11:32 | 41520 | 38.7173 | 0.2323 | 28.8787 |  | 2007-01-01 | 11:32 | 41520 | 39.7851 | 0.23871 | 29.7064
| 2029-09-01 | 11:33 | 41580 | 374.543 | 2.2473 | 208.7522 |  | 2029-09-01 | 11:33 | 41580 | 250.024 | 1.5001 | 157.128 |  | 2006-09-01 | 11:33 | 41580 | 217.084 | 1.3025 | 144.7842 |  | 2029-09-01 | 11:33 | 41580 | 188.14 | 1.1288 | 105.6936 |  | 2006-09-01 | 11:33 | 41580 | 105.241 | 0.63145 | 74.2054 |  | 2028-01-01 | 11:33 | 41580 | 256.567 | 1.5394 | 157.0707 |  | 2007-01-01 | 11:33 | 41580 | 223.785 | 1.3427 | 143.768 |  | 2028-01-01 | 11:33 | 41580 | 83.0297 | 0.49818 | 57.2684 |  | 2007-01-01 | 11:33 | 41580 | 87.1499 | 0.5229 | 59.8318 |  | 2029-09-01 | 11:33 | 41580 | 234.947 | 1.4097 | 150.877 |  | 2006-09-01 | 11:33 | 41580 | 213.768 | 1.2826 | 143.2817 |  | 2029-09-01 | 11:33 | 41580 | 147.291 | 0.88375 | 78.9248 |  | 2006-09-01 | 11:33 | 41580 | 65.4911 | 0.39295 | 48.5148 |  | 2028-01-01 | 11:33 | 41580 | 237.088 | 1.4225 | 149.0186 |  | 2007-01-01 | 11:33 | 41580 | 221.793 | 1.3308 | 142.9049 |  | 2028-01-01 | 11:33 | 41580 | 46.8425 | 0.28105 | 34.2288 |  | 2007-01-01 | 11:33 | 41580 | 50.7412 | 0.30445 | 37.1069 |  | 2029-09-01 | 11:33 | 41580 | 231.912 | 1.3915 | 149.6185 |  | 2006-09-01 | 11:33 | 41580 | 213.443 | 1.2807 | 143.1343 |  | 2029-09-01 | 11:33 | 41580 | 120.622 | 0.72373 | 64.4186 |  | 2006-09-01 | 11:33 | 41580 | 46.8632 | 0.28118 | 35.9237 |  | 2028-01-01 | 11:33 | 41580 | 232.437 | 1.3946 | 147.0962 |  | 2007-01-01 | 11:33 | 41580 | 221.646 | 1.3299 | 142.8414 |  | 2028-01-01 | 11:33 | 41580 | 32.3903 | 0.19434 | 24.4311 |  | 2007-01-01 | 11:33 | 41580 | 35.4068 | 0.21244 | 26.7972 |  | 2029-09-01 | 11:33 | 41580 | 98.4541 | 0.59072 | 69.5903 |  | 2029-09-01 | 11:33 | 41580 | 65.5115 | 0.39307 | 47.8491 |  | 2029-09-01 | 11:33 | 41580 | 43.6128 | 0.26168 | 32.9268 |  | 2006-09-01 | 11:33 | 41580 | 42.6332 | 0.2558 | 32.5323 |  | 2028-01-01 | 11:33 | 41580 | 83.0297 | 0.49818 | 57.2684 |  | 2007-01-01 | 11:33 | 41580 | 87.1499 | 0.5229 | 59.8318 |  | 2028-01-01 | 11:33 | 41580 | 38.7209 | 0.23233 | 29.111 |  | 2007-01-01 | 11:33 | 41580 | 39.8023 | 0.23881 | 29.9453
| 2029-09-01 | 11:34 | 41640 | 376.036 | 2.2562 | 211.0084 |  | 2029-09-01 | 11:34 | 41640 | 253.165 | 1.519 | 158.647 |  | 2006-09-01 | 11:34 | 41640 | 219.88 | 1.3193 | 146.1035 |  | 2029-09-01 | 11:34 | 41640 | 189.152 | 1.1349 | 106.8285 |  | 2006-09-01 | 11:34 | 41640 | 105.698 | 0.63419 | 74.8395 |  | 2028-01-01 | 11:34 | 41640 | 259.603 | 1.5576 | 158.6284 |  | 2007-01-01 | 11:34 | 41640 | 227.025 | 1.3622 | 145.1302 |  | 2028-01-01 | 11:34 | 41640 | 83.1778 | 0.49907 | 57.7675 |  | 2007-01-01 | 11:34 | 41640 | 87.4099 | 0.52446 | 60.3562 |  | 2029-09-01 | 11:34 | 41640 | 238.287 | 1.4297 | 152.3067 |  | 2006-09-01 | 11:34 | 41640 | 216.619 | 1.2997 | 144.5814 |  | 2029-09-01 | 11:34 | 41640 | 147.263 | 0.88358 | 79.8084 |  | 2006-09-01 | 11:34 | 41640 | 65.61 | 0.39366 | 48.9085 |  | 2028-01-01 | 11:34 | 41640 | 240.383 | 1.4423 | 150.4609 |  | 2007-01-01 | 11:34 | 41640 | 225.062 | 1.3504 | 144.2552 |  | 2028-01-01 | 11:34 | 41640 | 46.8534 | 0.28112 | 34.5099 |  | 2007-01-01 | 11:34 | 41640 | 50.7783 | 0.30467 | 37.4116 |  | 2029-09-01 | 11:34 | 41640 | 235.292 | 1.4118 | 151.0303 |  | 2006-09-01 | 11:34 | 41640 | 216.299 | 1.2978 | 144.4321 |  | 2029-09-01 | 11:34 | 41640 | 119.964 | 0.71978 | 65.1384 |  | 2006-09-01 | 11:34 | 41640 | 46.9194 | 0.28152 | 36.2053 |  | 2028-01-01 | 11:34 | 41640 | 235.794 | 1.4148 | 148.5109 |  | 2007-01-01 | 11:34 | 41640 | 224.917 | 1.3495 | 144.1909 |  | 2028-01-01 | 11:34 | 41640 | 32.3914 | 0.19435 | 24.6255 |  | 2007-01-01 | 11:34 | 41640 | 35.4181 | 0.21251 | 27.0097 |  | 2029-09-01 | 11:34 | 41640 | 98.6568 | 0.59194 | 70.1823 |  | 2029-09-01 | 11:34 | 41640 | 65.5684 | 0.39341 | 48.2425 |  | 2029-09-01 | 11:34 | 41640 | 43.6229 | 0.26174 | 33.1886 |  | 2006-09-01 | 11:34 | 41640 | 42.6385 | 0.25583 | 32.7882 |  | 2028-01-01 | 11:34 | 41640 | 83.1778 | 0.49907 | 57.7675 |  | 2007-01-01 | 11:34 | 41640 | 87.4099 | 0.52446 | 60.3562 |  | 2028-01-01 | 11:34 | 41640 | 38.7241 | 0.23234 | 29.3433 |  | 2007-01-01 | 11:34 | 41640 | 39.8188 | 0.23891 | 30.1842
| 2029-09-01 | 11:35 | 41700 | 377.514 | 2.2651 | 213.2735 |  | 2029-09-01 | 11:35 | 41700 | 256.268 | 1.5376 | 160.1846 |  | 2006-09-01 | 11:35 | 41700 | 222.628 | 1.3358 | 147.4393 |  | 2029-09-01 | 11:35 | 41700 | 190.097 | 1.1406 | 107.9691 |  | 2006-09-01 | 11:35 | 41700 | 106.134 | 0.6368 | 75.4763 |  | 2028-01-01 | 11:35 | 41700 | 262.599 | 1.5756 | 160.204 |  | 2007-01-01 | 11:35 | 41700 | 230.229 | 1.3814 | 146.5115 |  | 2028-01-01 | 11:35 | 41700 | 83.3154 | 0.49989 | 58.2674 |  | 2007-01-01 | 11:35 | 41700 | 87.6565 | 0.52594 | 60.8822 |  | 2029-09-01 | 11:35 | 41700 | 241.586 | 1.4495 | 153.7562 |  | 2006-09-01 | 11:35 | 41700 | 219.422 | 1.3165 | 145.8979 |  | 2029-09-01 | 11:35 | 41700 | 147.175 | 0.88305 | 80.6914 |  | 2006-09-01 | 11:35 | 41700 | 65.724 | 0.39434 | 49.3028 |  | 2028-01-01 | 11:35 | 41700 | 243.636 | 1.4618 | 151.9227 |  | 2007-01-01 | 11:35 | 41700 | 228.294 | 1.3698 | 145.625 |  | 2028-01-01 | 11:35 | 41700 | 46.8631 | 0.28118 | 34.7911 |  | 2007-01-01 | 11:35 | 41700 | 50.8134 | 0.30488 | 37.7165 |  | 2029-09-01 | 11:35 | 41700 | 238.631 | 1.4318 | 152.462 |  | 2006-09-01 | 11:35 | 41700 | 219.108 | 1.3146 | 145.7467 |  | 2029-09-01 | 11:35 | 41700 | 119.269 | 0.71561 | 65.854 |  | 2006-09-01 | 11:35 | 41700 | 46.9746 | 0.28185 | 36.4871 |  | 2028-01-01 | 11:35 | 41700 | 239.108 | 1.4346 | 149.9456 |  | 2007-01-01 | 11:35 | 41700 | 228.151 | 1.3689 | 145.5598 |  | 2028-01-01 | 11:35 | 41700 | 32.3924 | 0.19435 | 24.8198 |  | 2007-01-01 | 11:35 | 41700 | 35.4291 | 0.21257 | 27.2223 |  | 2029-09-01 | 11:35 | 41700 | 98.8486 | 0.59309 | 70.7754 |  | 2029-09-01 | 11:35 | 41700 | 65.6209 | 0.39373 | 48.6362 |  | 2029-09-01 | 11:35 | 41700 | 43.6322 | 0.26179 | 33.4504 |  | 2006-09-01 | 11:35 | 41700 | 42.6432 | 0.25586 | 33.044 |  | 2028-01-01 | 11:35 | 41700 | 83.3154 | 0.49989 | 58.2674 |  | 2007-01-01 | 11:35 | 41700 | 87.6565 | 0.52594 | 60.8822 |  | 2028-01-01 | 11:35 | 41700 | 38.7269 | 0.23236 | 29.5757 |  | 2007-01-01 | 11:35 | 41700 | 39.8347 | 0.23901 | 30.4232
| 2029-09-01 | 11:36 | 41760 | 378.977 | 2.2739 | 215.5474 |  | 2029-09-01 | 11:36 | 41760 | 259.332 | 1.556 | 161.7406 |  | 2006-09-01 | 11:36 | 41760 | 225.331 | 1.352 | 148.7913 |  | 2029-09-01 | 11:36 | 41760 | 190.977 | 1.1459 | 109.115 |  | 2006-09-01 | 11:36 | 41760 | 106.552 | 0.63931 | 76.1157 |  | 2028-01-01 | 11:36 | 41760 | 265.556 | 1.5933 | 161.7973 |  | 2007-01-01 | 11:36 | 41760 | 233.398 | 1.4004 | 147.9119 |  | 2028-01-01 | 11:36 | 41760 | 83.4435 | 0.50066 | 58.768 |  | 2007-01-01 | 11:36 | 41760 | 87.8906 | 0.52734 | 61.4095 |  | 2029-09-01 | 11:36 | 41760 | 244.845 | 1.4691 | 155.2253 |  | 2006-09-01 | 11:36 | 41760 | 222.179 | 1.3331 | 147.231 |  | 2029-09-01 | 11:36 | 41760 | 147.03 | 0.88218 | 81.5736 |  | 2006-09-01 | 11:36 | 41760 | 65.8335 | 0.395 | 49.6978 |  | 2028-01-01 | 11:36 | 41760 | 246.846 | 1.4811 | 153.4038 |  | 2007-01-01 | 11:36 | 41760 | 231.49 | 1.3889 | 147.0139 |  | 2028-01-01 | 11:36 | 41760 | 46.8718 | 0.28123 | 35.0723 |  | 2007-01-01 | 11:36 | 41760 | 50.8468 | 0.30508 | 38.0215 |  | 2029-09-01 | 11:36 | 41760 | 241.928 | 1.4516 | 153.9136 |  | 2006-09-01 | 11:36 | 41760 | 221.869 | 1.3312 | 147.0779 |  | 2029-09-01 | 11:36 | 41760 | 118.541 | 0.71125 | 66.5653 |  | 2006-09-01 | 11:36 | 41760 | 47.0289 | 0.28217 | 36.7693 |  | 2028-01-01 | 11:36 | 41760 | 242.378 | 1.4543 | 151.3999 |  | 2007-01-01 | 11:36 | 41760 | 231.349 | 1.3881 | 146.9479 |  | 2028-01-01 | 11:36 | 41760 | 32.3934 | 0.19436 | 25.0142 |  | 2007-01-01 | 11:36 | 41760 | 35.4399 | 0.21264 | 27.4349 |  | 2029-09-01 | 11:36 | 41760 | 99.03 | 0.59418 | 71.3695 |  | 2029-09-01 | 11:36 | 41760 | 65.6696 | 0.39402 | 49.0303 |  | 2029-09-01 | 11:36 | 41760 | 43.6408 | 0.26184 | 33.7122 |  | 2006-09-01 | 11:36 | 41760 | 42.6472 | 0.25588 | 33.2999 |  | 2028-01-01 | 11:36 | 41760 | 83.4435 | 0.50066 | 58.768 |  | 2007-01-01 | 11:36 | 41760 | 87.8906 | 0.52734 | 61.4095 |  | 2028-01-01 | 11:36 | 41760 | 38.7294 | 0.23238 | 29.8081 |  | 2007-01-01 | 11:36 | 41760 | 39.85 | 0.2391 | 30.6623
| 2029-09-01 | 11:37 | 41820 | 380.427 | 2.2826 | 217.8299 |  | 2029-09-01 | 11:37 | 41820 | 262.36 | 1.5742 | 163.3147 |  | 2006-09-01 | 11:37 | 41820 | 227.989 | 1.3679 | 150.1592 |  | 2029-09-01 | 11:37 | 41820 | 191.794 | 1.1508 | 110.2657 |  | 2006-09-01 | 11:37 | 41820 | 106.951 | 0.64171 | 76.7574 |  | 2028-01-01 | 11:37 | 41820 | 268.475 | 1.6109 | 163.4081 |  | 2007-01-01 | 11:37 | 41820 | 236.531 | 1.4192 | 149.3311 |  | 2028-01-01 | 11:37 | 41820 | 83.5629 | 0.50138 | 59.2694 |  | 2007-01-01 | 11:37 | 41820 | 88.1132 | 0.52868 | 61.9382 |  | 2029-09-01 | 11:37 | 41820 | 248.064 | 1.4884 | 156.7137 |  | 2006-09-01 | 11:37 | 41820 | 224.889 | 1.3493 | 148.5803 |  | 2029-09-01 | 11:37 | 41820 | 146.833 | 0.881 | 82.4546 |  | 2006-09-01 | 11:37 | 41820 | 65.9389 | 0.39563 | 50.0935 |  | 2028-01-01 | 11:37 | 41820 | 250.014 | 1.5001 | 154.9039 |  | 2007-01-01 | 11:37 | 41820 | 234.65 | 1.4079 | 148.4218 |  | 2028-01-01 | 11:37 | 41820 | 46.8796 | 0.28128 | 35.3536 |  | 2007-01-01 | 11:37 | 41820 | 50.8785 | 0.30527 | 38.3268 |  | 2029-09-01 | 11:37 | 41820 | 245.186 | 1.4711 | 155.3847 |  | 2006-09-01 | 11:37 | 41820 | 224.585 | 1.3475 | 148.4254 |  | 2029-09-01 | 11:37 | 41820 | 117.784 | 0.7067 | 67.272 |  | 2006-09-01 | 11:37 | 41820 | 47.0824 | 0.28249 | 37.0518 |  | 2028-01-01 | 11:37 | 41820 | 245.606 | 1.4736 | 152.8735 |  | 2007-01-01 | 11:37 | 41820 | 234.512 | 1.4071 | 148.355 |  | 2028-01-01 | 11:37 | 41820 | 32.3943 | 0.19437 | 25.2085 |  | 2007-01-01 | 11:37 | 41820 | 35.4504 | 0.2127 | 27.6476 |  | 2029-09-01 | 11:37 | 41820 | 99.2017 | 0.59521 | 71.9648 |  | 2029-09-01 | 11:37 | 41820 | 65.7146 | 0.39429 | 49.4246 |  | 2029-09-01 | 11:37 | 41820 | 43.6487 | 0.26189 | 33.9741 |  | 2006-09-01 | 11:37 | 41820 | 42.6507 | 0.2559 | 33.5558 |  | 2028-01-01 | 11:37 | 41820 | 83.5629 | 0.50138 | 59.2694 |  | 2007-01-01 | 11:37 | 41820 | 88.1132 | 0.52868 | 61.9382 |  | 2028-01-01 | 11:37 | 41820 | 38.7316 | 0.23239 | 30.0405 |  | 2007-01-01 | 11:37 | 41820 | 39.8649 | 0.23919 | 30.9015
| 2029-09-01 | 11:38 | 41880 | 381.862 | 2.2912 | 220.1211 |  | 2029-09-01 | 11:38 | 41880 | 265.351 | 1.5921 | 164.9068 |  | 2006-09-01 | 11:38 | 41880 | 230.602 | 1.3836 | 151.5428 |  | 2029-09-01 | 11:38 | 41880 | 192.55 | 1.1553 | 111.421 |  | 2006-09-01 | 11:38 | 41880 | 107.334 | 0.644 | 77.4014 |  | 2028-01-01 | 11:38 | 41880 | 271.356 | 1.6281 | 165.0363 |  | 2007-01-01 | 11:38 | 41880 | 239.63 | 1.4378 | 150.7689 |  | 2028-01-01 | 11:38 | 41880 | 83.674 | 0.50204 | 59.7715 |  | 2007-01-01 | 11:38 | 41880 | 88.3249 | 0.52995 | 62.4681 |  | 2029-09-01 | 11:38 | 41880 | 251.244 | 1.5075 | 158.2212 |  | 2006-09-01 | 11:38 | 41880 | 227.554 | 1.3653 | 149.9457 |  | 2029-09-01 | 11:38 | 41880 | 146.586 | 0.87952 | 83.3341 |  | 2006-09-01 | 11:38 | 41880 | 66.0407 | 0.39624 | 50.4897 |  | 2028-01-01 | 11:38 | 41880 | 253.141 | 1.5188 | 156.4227 |  | 2007-01-01 | 11:38 | 41880 | 237.776 | 1.4267 | 149.8485 |  | 2028-01-01 | 11:38 | 41880 | 46.8867 | 0.28132 | 35.6349 |  | 2007-01-01 | 11:38 | 41880 | 50.9087 | 0.30545 | 38.6323 |  | 2029-09-01 | 11:38 | 41880 | 248.403 | 1.4904 | 156.8751 |  | 2006-09-01 | 11:38 | 41880 | 227.255 | 1.3635 | 149.789 |  | 2029-09-01 | 11:38 | 41880 | 117.003 | 0.70202 | 67.974 |  | 2006-09-01 | 11:38 | 41880 | 47.1354 | 0.28281 | 37.3346 |  | 2028-01-01 | 11:38 | 41880 | 248.792 | 1.4928 | 154.3662 |  | 2007-01-01 | 11:38 | 41880 | 237.64 | 1.4258 | 149.7808 |  | 2028-01-01 | 11:38 | 41880 | 32.3953 | 0.19437 | 25.4029 |  | 2007-01-01 | 11:38 | 41880 | 35.4607 | 0.21276 | 27.8604 |  | 2029-09-01 | 11:38 | 41880 | 99.3643 | 0.59619 | 72.5609 |  | 2029-09-01 | 11:38 | 41880 | 65.7564 | 0.39454 | 49.8191 |  | 2029-09-01 | 11:38 | 41880 | 43.6561 | 0.26194 | 34.2361 |  | 2006-09-01 | 11:38 | 41880 | 42.6538 | 0.25592 | 33.8117 |  | 2028-01-01 | 11:38 | 41880 | 83.674 | 0.50204 | 59.7715 |  | 2007-01-01 | 11:38 | 41880 | 88.3249 | 0.52995 | 62.4681 |  | 2028-01-01 | 11:38 | 41880 | 38.7338 | 0.2324 | 30.2729 |  | 2007-01-01 | 11:38 | 41880 | 39.8794 | 0.23928 | 31.1407
| 2029-09-01 | 11:39 | 41940 | 383.283 | 2.2997 | 222.4208 |  | 2029-09-01 | 11:39 | 41940 | 268.307 | 1.6098 | 166.5167 |  | 2006-09-01 | 11:39 | 41940 | 233.171 | 1.399 | 152.9418 |  | 2029-09-01 | 11:39 | 41940 | 193.246 | 1.1595 | 112.5805 |  | 2006-09-01 | 11:39 | 41940 | 107.7 | 0.6462 | 78.0476 |  | 2028-01-01 | 11:39 | 41940 | 274.2 | 1.6452 | 166.6815 |  | 2007-01-01 | 11:39 | 41940 | 242.696 | 1.4562 | 152.2251 |  | 2028-01-01 | 11:39 | 41940 | 83.7776 | 0.50267 | 60.2741 |  | 2007-01-01 | 11:39 | 41940 | 88.5265 | 0.53116 | 62.9993 |  | 2029-09-01 | 11:39 | 41940 | 254.385 | 1.5263 | 159.7475 |  | 2006-09-01 | 11:39 | 41940 | 230.175 | 1.3811 | 151.3267 |  | 2029-09-01 | 11:39 | 41940 | 146.293 | 0.87776 | 84.2119 |  | 2006-09-01 | 11:39 | 41940 | 66.1391 | 0.39683 | 50.8866 |  | 2028-01-01 | 11:39 | 41940 | 256.227 | 1.5374 | 157.9601 |  | 2007-01-01 | 11:39 | 41940 | 240.868 | 1.4452 | 151.2937 |  | 2028-01-01 | 11:39 | 41940 | 46.8932 | 0.28136 | 35.9163 |  | 2007-01-01 | 11:39 | 41940 | 50.9377 | 0.30563 | 38.9379 |  | 2029-09-01 | 11:39 | 41940 | 251.582 | 1.5095 | 158.3846 |  | 2006-09-01 | 11:39 | 41940 | 229.881 | 1.3793 | 151.1683 |  | 2029-09-01 | 11:39 | 41940 | 116.199 | 0.69719 | 68.6712 |  | 2006-09-01 | 11:39 | 41940 | 47.1878 | 0.28313 | 37.6177 |  | 2028-01-01 | 11:39 | 41940 | 251.936 | 1.5116 | 155.8779 |  | 2007-01-01 | 11:39 | 41940 | 240.734 | 1.4444 | 151.2252 |  | 2028-01-01 | 11:39 | 41940 | 32.3962 | 0.19438 | 25.5973 |  | 2007-01-01 | 11:39 | 41940 | 35.4707 | 0.21282 | 28.0732 |  | 2029-09-01 | 11:39 | 41940 | 99.5182 | 0.59711 | 73.1581 |  | 2029-09-01 | 11:39 | 41940 | 65.7952 | 0.39477 | 50.2139 |  | 2029-09-01 | 11:39 | 41940 | 43.6631 | 0.26198 | 34.498 |  | 2006-09-01 | 11:39 | 41940 | 42.6564 | 0.25594 | 34.0677 |  | 2028-01-01 | 11:39 | 41940 | 83.7776 | 0.50267 | 60.2741 |  | 2007-01-01 | 11:39 | 41940 | 88.5265 | 0.53116 | 62.9993 |  | 2028-01-01 | 11:39 | 41940 | 38.7357 | 0.23241 | 30.5053 |  | 2007-01-01 | 11:39 | 41940 | 39.8935 | 0.23936 | 31.3801
| 2029-09-01 | 11:40 | 42000 | 384.69 | 2.3081 | 224.7289 |  | 2029-09-01 | 11:40 | 42000 | 271.226 | 1.6274 | 168.144 |  | 2006-09-01 | 11:40 | 42000 | 235.698 | 1.4142 | 154.356 |  | 2029-09-01 | 11:40 | 42000 | 193.886 | 1.1633 | 113.7438 |  | 2006-09-01 | 11:40 | 42000 | 108.052 | 0.64831 | 78.6959 |  | 2028-01-01 | 11:40 | 42000 | 277.007 | 1.662 | 168.3435 |  | 2007-01-01 | 11:40 | 42000 | 245.73 | 1.4744 | 153.6995 |  | 2028-01-01 | 11:40 | 42000 | 83.8742 | 0.50325 | 60.7774 |  | 2007-01-01 | 11:40 | 42000 | 88.7185 | 0.53231 | 63.5316 |  | 2029-09-01 | 11:40 | 42000 | 257.488 | 1.5449 | 161.2924 |  | 2006-09-01 | 11:40 | 42000 | 232.751 | 1.3965 | 152.7232 |  | 2029-09-01 | 11:40 | 42000 | 145.957 | 0.87574 | 85.0876 |  | 2006-09-01 | 11:40 | 42000 | 66.2344 | 0.39741 | 51.284 |  | 2028-01-01 | 11:40 | 42000 | 259.273 | 1.5556 | 159.5157 |  | 2007-01-01 | 11:40 | 42000 | 243.928 | 1.4636 | 152.7573 |  | 2028-01-01 | 11:40 | 42000 | 46.899 | 0.28139 | 36.1977 |  | 2007-01-01 | 11:40 | 42000 | 50.9655 | 0.30579 | 39.2437 |  | 2029-09-01 | 11:40 | 42000 | 254.722 | 1.5283 | 159.913 |  | 2006-09-01 | 11:40 | 42000 | 232.462 | 1.3948 | 152.563 |  | 2029-09-01 | 11:40 | 42000 | 115.377 | 0.69226 | 69.3634 |  | 2006-09-01 | 11:40 | 42000 | 47.2398 | 0.28344 | 37.9012 |  | 2028-01-01 | 11:40 | 42000 | 255.039 | 1.5302 | 157.4081 |  | 2007-01-01 | 11:40 | 42000 | 243.795 | 1.4628 | 152.688 |  | 2028-01-01 | 11:40 | 42000 | 32.3971 | 0.19438 | 25.7917 |  | 2007-01-01 | 11:40 | 42000 | 35.4806 | 0.21288 | 28.2861 |  | 2029-09-01 | 11:40 | 42000 | 99.6641 | 0.59798 | 73.756 |  | 2029-09-01 | 11:40 | 42000 | 65.8313 | 0.39499 | 50.6089 |  | 2029-09-01 | 11:40 | 42000 | 43.6696 | 0.26202 | 34.7601 |  | 2006-09-01 | 11:40 | 42000 | 42.6587 | 0.25595 | 34.3236 |  | 2028-01-01 | 11:40 | 42000 | 83.8742 | 0.50325 | 60.7774 |  | 2007-01-01 | 11:40 | 42000 | 88.7185 | 0.53231 | 63.5316 |  | 2028-01-01 | 11:40 | 42000 | 38.7376 | 0.23243 | 30.7377 |  | 2007-01-01 | 11:40 | 42000 | 39.9073 | 0.23944 | 31.6195
| 2029-09-01 | 11:41 | 42060 | 386.084 | 2.3165 | 227.0455 |  | 2029-09-01 | 11:41 | 42060 | 274.111 | 1.6447 | 169.7887 |  | 2006-09-01 | 11:41 | 42060 | 238.182 | 1.4291 | 155.7851 |  | 2029-09-01 | 11:41 | 42060 | 194.471 | 1.1668 | 114.9107 |  | 2006-09-01 | 11:41 | 42060 | 108.39 | 0.65034 | 79.3462 |  | 2028-01-01 | 11:41 | 42060 | 279.777 | 1.6787 | 170.0222 |  | 2007-01-01 | 11:41 | 42060 | 248.732 | 1.4924 | 155.1919 |  | 2028-01-01 | 11:41 | 42060 | 83.9644 | 0.50379 | 61.2812 |  | 2007-01-01 | 11:41 | 42060 | 88.9016 | 0.53341 | 64.065 |  | 2029-09-01 | 11:41 | 42060 | 260.553 | 1.5633 | 162.8557 |  | 2006-09-01 | 11:41 | 42060 | 235.285 | 1.4117 | 154.1349 |  | 2029-09-01 | 11:41 | 42060 | 145.581 | 0.87349 | 85.9611 |  | 2006-09-01 | 11:41 | 42060 | 66.3271 | 0.39796 | 51.6819 |  | 2028-01-01 | 11:41 | 42060 | 262.279 | 1.5737 | 161.0894 |  | 2007-01-01 | 11:41 | 42060 | 246.955 | 1.4817 | 154.239 |  | 2028-01-01 | 11:41 | 42060 | 46.9044 | 0.28143 | 36.4791 |  | 2007-01-01 | 11:41 | 42060 | 50.9922 | 0.30595 | 39.5496 |  | 2029-09-01 | 11:41 | 42060 | 257.824 | 1.5469 | 161.4599 |  | 2006-09-01 | 11:41 | 42060 | 235.001 | 1.41 | 153.973 |  | 2029-09-01 | 11:41 | 42060 | 114.538 | 0.68723 | 70.0507 |  | 2006-09-01 | 11:41 | 42060 | 47.2914 | 0.28375 | 38.1849 |  | 2028-01-01 | 11:41 | 42060 | 258.102 | 1.5486 | 158.9567 |  | 2007-01-01 | 11:41 | 42060 | 246.825 | 1.4809 | 154.1689 |  | 2028-01-01 | 11:41 | 42060 | 32.398 | 0.19439 | 25.9861 |  | 2007-01-01 | 11:41 | 42060 | 35.4903 | 0.21294 | 28.499 |  | 2029-09-01 | 11:41 | 42060 | 99.8024 | 0.59881 | 74.3549 |  | 2029-09-01 | 11:41 | 42060 | 65.865 | 0.39519 | 51.004 |  | 2029-09-01 | 11:41 | 42060 | 43.6757 | 0.26205 | 35.0221 |  | 2006-09-01 | 11:41 | 42060 | 42.6607 | 0.25596 | 34.5796 |  | 2028-01-01 | 11:41 | 42060 | 83.9644 | 0.50379 | 61.2812 |  | 2007-01-01 | 11:41 | 42060 | 88.9016 | 0.53341 | 64.065 |  | 2028-01-01 | 11:41 | 42060 | 38.7394 | 0.23244 | 30.9701 |  | 2007-01-01 | 11:41 | 42060 | 39.9207 | 0.23952 | 31.8591
| 2029-09-01 | 11:42 | 42120 | 387.464 | 2.3248 | 229.3702 |  | 2029-09-01 | 11:42 | 42120 | 276.962 | 1.6618 | 171.4505 |  | 2006-09-01 | 11:42 | 42120 | 240.625 | 1.4437 | 157.2289 |  | 2029-09-01 | 11:42 | 42120 | 195.002 | 1.17 | 116.0807 |  | 2006-09-01 | 11:42 | 42120 | 108.714 | 0.65228 | 79.9985 |  | 2028-01-01 | 11:42 | 42120 | 282.512 | 1.6951 | 171.7173 |  | 2007-01-01 | 11:42 | 42120 | 251.704 | 1.5102 | 156.7021 |  | 2028-01-01 | 11:42 | 42120 | 84.0485 | 0.50429 | 61.7855 |  | 2007-01-01 | 11:42 | 42120 | 89.0765 | 0.53446 | 64.5995 |  | 2029-09-01 | 11:42 | 42120 | 263.582 | 1.5815 | 164.4372 |  | 2006-09-01 | 11:42 | 42120 | 237.777 | 1.4267 | 155.5616 |  | 2029-09-01 | 11:42 | 42120 | 145.167 | 0.871 | 86.8321 |  | 2006-09-01 | 11:42 | 42120 | 66.4173 | 0.3985 | 52.0804 |  | 2028-01-01 | 11:42 | 42120 | 265.247 | 1.5915 | 162.6809 |  | 2007-01-01 | 11:42 | 42120 | 249.952 | 1.4997 | 155.7387 |  | 2028-01-01 | 11:42 | 42120 | 46.9094 | 0.28146 | 36.7605 |  | 2007-01-01 | 11:42 | 42120 | 51.018 | 0.30611 | 39.8557 |  | 2029-09-01 | 11:42 | 42120 | 260.888 | 1.5653 | 163.0252 |  | 2006-09-01 | 11:42 | 42120 | 237.497 | 1.425 | 155.398 |  | 2029-09-01 | 11:42 | 42120 | 113.687 | 0.68212 | 70.7328 |  | 2006-09-01 | 11:42 | 42120 | 47.3428 | 0.28406 | 38.469 |  | 2028-01-01 | 11:42 | 42120 | 261.125 | 1.5668 | 160.5235 |  | 2007-01-01 | 11:42 | 42120 | 249.823 | 1.4989 | 155.6679 |  | 2028-01-01 | 11:42 | 42120 | 32.399 | 0.19439 | 26.1805 |  | 2007-01-01 | 11:42 | 42120 | 35.4999 | 0.213 | 28.712 |  | 2029-09-01 | 11:42 | 42120 | 99.9336 | 0.5996 | 74.9545 |  | 2029-09-01 | 11:42 | 42120 | 65.8964 | 0.39538 | 51.3994 |  | 2029-09-01 | 11:42 | 42120 | 43.6816 | 0.26209 | 35.2842 |  | 2006-09-01 | 11:42 | 42120 | 42.6624 | 0.25597 | 34.8356 |  | 2028-01-01 | 11:42 | 42120 | 84.0485 | 0.50429 | 61.7855 |  | 2007-01-01 | 11:42 | 42120 | 89.0765 | 0.53446 | 64.5995 |  | 2028-01-01 | 11:42 | 42120 | 38.7411 | 0.23245 | 31.2026 |  | 2007-01-01 | 11:42 | 42120 | 39.9339 | 0.2396 | 32.0987
| 2029-09-01 | 11:43 | 42180 | 388.831 | 2.333 | 231.7032 |  | 2029-09-01 | 11:43 | 42180 | 279.778 | 1.6787 | 173.1291 |  | 2006-09-01 | 11:43 | 42180 | 243.027 | 1.4582 | 158.687 |  | 2029-09-01 | 11:43 | 42180 | 195.483 | 1.1729 | 117.2536 |  | 2006-09-01 | 11:43 | 42180 | 109.025 | 0.65415 | 80.6527 |  | 2028-01-01 | 11:43 | 42180 | 285.212 | 1.7113 | 173.4285 |  | 2007-01-01 | 11:43 | 42180 | 254.644 | 1.5279 | 158.2299 |  | 2028-01-01 | 11:43 | 42180 | 84.1271 | 0.50476 | 62.2902 |  | 2007-01-01 | 11:43 | 42180 | 89.2435 | 0.53546 | 65.1349 |  | 2029-09-01 | 11:43 | 42180 | 266.574 | 1.5994 | 166.0366 |  | 2006-09-01 | 11:43 | 42180 | 240.226 | 1.4414 | 157.0029 |  | 2029-09-01 | 11:43 | 42180 | 144.718 | 0.86831 | 87.7004 |  | 2006-09-01 | 11:43 | 42180 | 66.5052 | 0.39903 | 52.4795 |  | 2028-01-01 | 11:43 | 42180 | 268.176 | 1.6091 | 164.29 |  | 2007-01-01 | 11:43 | 42180 | 252.917 | 1.5175 | 157.2562 |  | 2028-01-01 | 11:43 | 42180 | 46.914 | 0.28148 | 37.042 |  | 2007-01-01 | 11:43 | 42180 | 51.0429 | 0.30626 | 40.162 |  | 2029-09-01 | 11:43 | 42180 | 263.915 | 1.5835 | 164.6087 |  | 2006-09-01 | 11:43 | 42180 | 239.951 | 1.4397 | 156.8377 |  | 2029-09-01 | 11:43 | 42180 | 112.825 | 0.67695 | 71.4097 |  | 2006-09-01 | 11:43 | 42180 | 47.3938 | 0.28436 | 38.7533 |  | 2028-01-01 | 11:43 | 42180 | 264.109 | 1.5847 | 162.1081 |  | 2007-01-01 | 11:43 | 42180 | 252.79 | 1.5167 | 157.1846 |  | 2028-01-01 | 11:43 | 42180 | 32.3999 | 0.1944 | 26.3749 |  | 2007-01-01 | 11:43 | 42180 | 35.5093 | 0.21306 | 28.9251 |  | 2029-09-01 | 11:43 | 42180 | 100.058 | 0.60035 | 75.5548 |  | 2029-09-01 | 11:43 | 42180 | 65.9257 | 0.39555 | 51.795 |  | 2029-09-01 | 11:43 | 42180 | 43.6871 | 0.26212 | 35.5463 |  | 2006-09-01 | 11:43 | 42180 | 42.664 | 0.25598 | 35.0915 |  | 2028-01-01 | 11:43 | 42180 | 84.1271 | 0.50476 | 62.2902 |  | 2007-01-01 | 11:43 | 42180 | 89.2435 | 0.53546 | 65.1349 |  | 2028-01-01 | 11:43 | 42180 | 38.7427 | 0.23246 | 31.4351 |  | 2007-01-01 | 11:43 | 42180 | 39.9468 | 0.23968 | 32.3384
| 2029-09-01 | 11:44 | 42240 | 390.185 | 2.3411 | 234.0443 |  | 2029-09-01 | 11:44 | 42240 | 282.562 | 1.6954 | 174.8245 |  | 2006-09-01 | 11:44 | 42240 | 245.389 | 1.4723 | 160.1594 |  | 2029-09-01 | 11:44 | 42240 | 195.914 | 1.1755 | 118.429 |  | 2006-09-01 | 11:44 | 42240 | 109.325 | 0.65595 | 81.3086 |  | 2028-01-01 | 11:44 | 42240 | 287.877 | 1.7273 | 175.1558 |  | 2007-01-01 | 11:44 | 42240 | 257.555 | 1.5453 | 159.7753 |  | 2028-01-01 | 11:44 | 42240 | 84.2006 | 0.5052 | 62.7954 |  | 2007-01-01 | 11:44 | 42240 | 89.4032 | 0.53642 | 65.6713 |  | 2029-09-01 | 11:44 | 42240 | 269.53 | 1.6172 | 167.6538 |  | 2006-09-01 | 11:44 | 42240 | 242.635 | 1.4558 | 158.4588 |  | 2029-09-01 | 11:44 | 42240 | 144.237 | 0.86542 | 88.5658 |  | 2006-09-01 | 11:44 | 42240 | 66.5912 | 0.39955 | 52.879 |  | 2028-01-01 | 11:44 | 42240 | 271.068 | 1.6264 | 165.9164 |  | 2007-01-01 | 11:44 | 42240 | 255.852 | 1.5351 | 158.7913 |  | 2028-01-01 | 11:44 | 42240 | 46.9183 | 0.28151 | 37.3235 |  | 2007-01-01 | 11:44 | 42240 | 51.067 | 0.3064 | 40.4684 |  | 2029-09-01 | 11:44 | 42240 | 266.906 | 1.6014 | 166.2102 |  | 2006-09-01 | 11:44 | 42240 | 242.365 | 1.4542 | 158.2919 |  | 2029-09-01 | 11:44 | 42240 | 111.955 | 0.67173 | 72.0815 |  | 2006-09-01 | 11:44 | 42240 | 47.4447 | 0.28467 | 39.038 |  | 2028-01-01 | 11:44 | 42240 | 267.055 | 1.6023 | 163.7104 |  | 2007-01-01 | 11:44 | 42240 | 255.726 | 1.5344 | 158.719 |  | 2028-01-01 | 11:44 | 42240 | 32.4009 | 0.19441 | 26.5693 |  | 2007-01-01 | 11:44 | 42240 | 35.5186 | 0.21311 | 29.1382 |  | 2029-09-01 | 11:44 | 42240 | 100.176 | 0.60106 | 76.1559 |  | 2029-09-01 | 11:44 | 42240 | 65.9531 | 0.39572 | 52.1907 |  | 2029-09-01 | 11:44 | 42240 | 43.6925 | 0.26215 | 35.8085 |  | 2006-09-01 | 11:44 | 42240 | 42.6653 | 0.25599 | 35.3475 |  | 2028-01-01 | 11:44 | 42240 | 84.2006 | 0.5052 | 62.7954 |  | 2007-01-01 | 11:44 | 42240 | 89.4032 | 0.53642 | 65.6713 |  | 2028-01-01 | 11:44 | 42240 | 38.7443 | 0.23247 | 31.6675 |  | 2007-01-01 | 11:44 | 42240 | 39.9595 | 0.23976 | 32.5781
| 2029-09-01 | 11:45 | 42300 | 391.526 | 2.3492 | 236.3935 |  | 2029-09-01 | 11:45 | 42300 | 285.312 | 1.7119 | 176.5364 |  | 2006-09-01 | 11:45 | 42300 | 247.712 | 1.4863 | 161.6456 |  | 2029-09-01 | 11:45 | 42300 | 196.297 | 1.1778 | 119.6068 |  | 2006-09-01 | 11:45 | 42300 | 109.613 | 0.65768 | 81.9663 |  | 2028-01-01 | 11:45 | 42300 | 290.508 | 1.743 | 176.8988 |  | 2007-01-01 | 11:45 | 42300 | 260.437 | 1.5626 | 161.3379 |  | 2028-01-01 | 11:45 | 42300 | 84.2693 | 0.50562 | 63.301 |  | 2007-01-01 | 11:45 | 42300 | 89.5561 | 0.53734 | 66.2087 |  | 2029-09-01 | 11:45 | 42300 | 272.451 | 1.6347 | 169.2885 |  | 2006-09-01 | 11:45 | 42300 | 245.004 | 1.47 | 159.9288 |  | 2029-09-01 | 11:45 | 42300 | 143.727 | 0.86236 | 89.4282 |  | 2006-09-01 | 11:45 | 42300 | 66.6753 | 0.40005 | 53.2791 |  | 2028-01-01 | 11:45 | 42300 | 273.922 | 1.6435 | 167.5599 |  | 2007-01-01 | 11:45 | 42300 | 258.757 | 1.5525 | 160.3439 |  | 2028-01-01 | 11:45 | 42300 | 46.9223 | 0.28153 | 37.6051 |  | 2007-01-01 | 11:45 | 42300 | 51.0904 | 0.30654 | 40.7749 |  | 2029-09-01 | 11:45 | 42300 | 269.862 | 1.6192 | 167.8293 |  | 2006-09-01 | 11:45 | 42300 | 244.738 | 1.4684 | 159.7603 |  | 2029-09-01 | 11:45 | 42300 | 111.079 | 0.66647 | 72.7479 |  | 2006-09-01 | 11:45 | 42300 | 47.4953 | 0.28497 | 39.323 |  | 2028-01-01 | 11:45 | 42300 | 269.962 | 1.6198 | 165.3302 |  | 2007-01-01 | 11:45 | 42300 | 258.634 | 1.5518 | 160.2708 |  | 2028-01-01 | 11:45 | 42300 | 32.4018 | 0.19441 | 26.7637 |  | 2007-01-01 | 11:45 | 42300 | 35.5277 | 0.21317 | 29.3513 |  | 2029-09-01 | 11:45 | 42300 | 100.288 | 0.60173 | 76.7576 |  | 2029-09-01 | 11:45 | 42300 | 65.9788 | 0.39587 | 52.5866 |  | 2029-09-01 | 11:45 | 42300 | 43.6975 | 0.26219 | 36.0707 |  | 2006-09-01 | 11:45 | 42300 | 42.6665 | 0.256 | 35.6035 |  | 2028-01-01 | 11:45 | 42300 | 84.2693 | 0.50562 | 63.301 |  | 2007-01-01 | 11:45 | 42300 | 89.5561 | 0.53734 | 66.2087 |  | 2028-01-01 | 11:45 | 42300 | 38.7459 | 0.23248 | 31.9 |  | 2007-01-01 | 11:45 | 42300 | 39.972 | 0.23983 | 32.8179
| 2029-09-01 | 11:46 | 42360 | 392.854 | 2.3571 | 238.7506 |  | 2029-09-01 | 11:46 | 42360 | 288.029 | 1.7282 | 178.2646 |  | 2006-09-01 | 11:46 | 42360 | 249.996 | 1.5 | 163.1456 |  | 2029-09-01 | 11:46 | 42360 | 196.634 | 1.1798 | 120.7866 |  | 2006-09-01 | 11:46 | 42360 | 109.891 | 0.65935 | 82.6256 |  | 2028-01-01 | 11:46 | 42360 | 293.105 | 1.7586 | 178.6575 |  | 2007-01-01 | 11:46 | 42360 | 263.291 | 1.5797 | 162.9176 |  | 2028-01-01 | 11:46 | 42360 | 84.3336 | 0.506 | 63.807 |  | 2007-01-01 | 11:46 | 42360 | 89.7026 | 0.53822 | 66.7469 |  | 2029-09-01 | 11:46 | 42360 | 275.337 | 1.652 | 170.9406 |  | 2006-09-01 | 11:46 | 42360 | 247.333 | 1.484 | 161.4128 |  | 2029-09-01 | 11:46 | 42360 | 143.189 | 0.85913 | 90.2873 |  | 2006-09-01 | 11:46 | 42360 | 66.7578 | 0.40055 | 53.6796 |  | 2028-01-01 | 11:46 | 42360 | 276.74 | 1.6604 | 169.2203 |  | 2007-01-01 | 11:46 | 42360 | 261.634 | 1.5698 | 161.9137 |  | 2028-01-01 | 11:46 | 42360 | 46.9261 | 0.28156 | 37.8866 |  | 2007-01-01 | 11:46 | 42360 | 51.1132 | 0.30668 | 41.0816 |  | 2029-09-01 | 11:46 | 42360 | 272.781 | 1.6367 | 169.466 |  | 2006-09-01 | 11:46 | 42360 | 247.072 | 1.4824 | 161.2428 |  | 2029-09-01 | 11:46 | 42360 | 110.199 | 0.66119 | 73.4091 |  | 2006-09-01 | 11:46 | 42360 | 47.5459 | 0.28528 | 39.6082 |  | 2028-01-01 | 11:46 | 42360 | 272.833 | 1.637 | 166.9672 |  | 2007-01-01 | 11:46 | 42360 | 261.512 | 1.5691 | 161.8398 |  | 2028-01-01 | 11:46 | 42360 | 32.4028 | 0.19442 | 26.9581 |  | 2007-01-01 | 11:46 | 42360 | 35.5368 | 0.21322 | 29.5646 |  | 2029-09-01 | 11:46 | 42360 | 100.395 | 0.60237 | 77.36 |  | 2029-09-01 | 11:46 | 42360 | 66.003 | 0.39602 | 52.9826 |  | 2029-09-01 | 11:46 | 42360 | 43.7024 | 0.26221 | 36.3329 |  | 2006-09-01 | 11:46 | 42360 | 42.6675 | 0.256 | 35.8595 |  | 2028-01-01 | 11:46 | 42360 | 84.3336 | 0.506 | 63.807 |  | 2007-01-01 | 11:46 | 42360 | 89.7026 | 0.53822 | 66.7469 |  | 2028-01-01 | 11:46 | 42360 | 38.7475 | 0.23248 | 32.1325 |  | 2007-01-01 | 11:46 | 42360 | 39.9842 | 0.23991 | 33.0579
| 2029-09-01 | 11:47 | 42420 | 394.17 | 2.365 | 241.1156 |  | 2029-09-01 | 11:47 | 42420 | 290.715 | 1.7443 | 180.0088 |  | 2006-09-01 | 11:47 | 42420 | 252.242 | 1.5135 | 164.6591 |  | 2029-09-01 | 11:47 | 42420 | 196.926 | 1.1816 | 121.9682 |  | 2006-09-01 | 11:47 | 42420 | 110.158 | 0.66095 | 83.2866 |  | 2028-01-01 | 11:47 | 42420 | 295.669 | 1.774 | 180.4315 |  | 2007-01-01 | 11:47 | 42420 | 266.117 | 1.5967 | 164.5143 |  | 2028-01-01 | 11:47 | 42420 | 84.3938 | 0.50636 | 64.3134 |  | 2007-01-01 | 11:47 | 42420 | 89.8431 | 0.53906 | 67.286 |  | 2029-09-01 | 11:47 | 42420 | 278.188 | 1.6691 | 172.6097 |  | 2006-09-01 | 11:47 | 42420 | 249.623 | 1.4977 | 162.9105 |  | 2029-09-01 | 11:47 | 42420 | 142.626 | 0.85576 | 91.1431 |  | 2006-09-01 | 11:47 | 42420 | 66.8389 | 0.40103 | 54.0806 |  | 2028-01-01 | 11:47 | 42420 | 279.521 | 1.6771 | 170.8975 |  | 2007-01-01 | 11:47 | 42420 | 264.483 | 1.5869 | 163.5006 |  | 2028-01-01 | 11:47 | 42420 | 46.9297 | 0.28158 | 38.1682 |  | 2007-01-01 | 11:47 | 42420 | 51.1353 | 0.30681 | 41.3884 |  | 2029-09-01 | 11:47 | 42420 | 275.666 | 1.654 | 171.12 |  | 2006-09-01 | 11:47 | 42420 | 249.366 | 1.4962 | 162.739 |  | 2029-09-01 | 11:47 | 42420 | 109.317 | 0.6559 | 74.065 |  | 2006-09-01 | 11:47 | 42420 | 47.5964 | 0.28558 | 39.8938 |  | 2028-01-01 | 11:47 | 42420 | 275.666 | 1.654 | 168.6212 |  | 2007-01-01 | 11:47 | 42420 | 264.363 | 1.5862 | 163.426 |  | 2028-01-01 | 11:47 | 42420 | 32.4038 | 0.19442 | 27.1525 |  | 2007-01-01 | 11:47 | 42420 | 35.5457 | 0.21327 | 29.7778 |  | 2029-09-01 | 11:47 | 42420 | 100.496 | 0.60298 | 77.9629 |  | 2029-09-01 | 11:47 | 42420 | 66.0257 | 0.39615 | 53.3787 |  | 2029-09-01 | 11:47 | 42420 | 43.7072 | 0.26224 | 36.5951 |  | 2006-09-01 | 11:47 | 42420 | 42.6683 | 0.25601 | 36.1156 |  | 2028-01-01 | 11:47 | 42420 | 84.3938 | 0.50636 | 64.3134 |  | 2007-01-01 | 11:47 | 42420 | 89.8431 | 0.53906 | 67.286 |  | 2028-01-01 | 11:47 | 42420 | 38.749 | 0.23249 | 32.365 |  | 2007-01-01 | 11:47 | 42420 | 39.9963 | 0.23998 | 33.2978
| 2029-09-01 | 11:48 | 42480 | 395.473 | 2.3728 | 243.4885 |  | 2029-09-01 | 11:48 | 42480 | 293.369 | 1.7602 | 181.7691 |  | 2006-09-01 | 11:48 | 42480 | 254.45 | 1.5267 | 166.1858 |  | 2029-09-01 | 11:48 | 42480 | 197.177 | 1.1831 | 123.1513 |  | 2006-09-01 | 11:48 | 42480 | 110.417 | 0.6625 | 83.9491 |  | 2028-01-01 | 11:48 | 42480 | 298.201 | 1.7892 | 182.2207 |  | 2007-01-01 | 11:48 | 42480 | 268.907 | 1.6134 | 166.1278 |  | 2028-01-01 | 11:48 | 42480 | 84.4502 | 0.5067 | 64.8201 |  | 2007-01-01 | 11:48 | 42480 | 89.9779 | 0.53987 | 67.8258 |  | 2029-09-01 | 11:48 | 42480 | 281.006 | 1.686 | 174.2957 |  | 2006-09-01 | 11:48 | 42480 | 251.875 | 1.5113 | 164.4218 |  | 2029-09-01 | 11:48 | 42480 | 142.04 | 0.85224 | 91.9953 |  | 2006-09-01 | 11:48 | 42480 | 66.9186 | 0.40151 | 54.4821 |  | 2028-01-01 | 11:48 | 42480 | 282.267 | 1.6936 | 172.5911 |  | 2007-01-01 | 11:48 | 42480 | 267.296 | 1.6038 | 165.1044 |  | 2028-01-01 | 11:48 | 42480 | 46.9332 | 0.2816 | 38.4498 |  | 2007-01-01 | 11:48 | 42480 | 51.1569 | 0.30694 | 41.6954 |  | 2029-09-01 | 11:48 | 42480 | 278.517 | 1.6711 | 172.7911 |  | 2006-09-01 | 11:48 | 42480 | 251.622 | 1.5097 | 164.2487 |  | 2029-09-01 | 11:48 | 42480 | 108.435 | 0.65061 | 74.7156 |  | 2006-09-01 | 11:48 | 42480 | 47.6468 | 0.28588 | 40.1797 |  | 2028-01-01 | 11:48 | 42480 | 278.463 | 1.6708 | 170.292 |  | 2007-01-01 | 11:48 | 42480 | 267.177 | 1.6031 | 165.0291 |  | 2028-01-01 | 11:48 | 42480 | 32.4048 | 0.19443 | 27.3469 |  | 2007-01-01 | 11:48 | 42480 | 35.5545 | 0.21333 | 29.9912 |  | 2029-09-01 | 11:48 | 42480 | 100.593 | 0.60356 | 78.5665 |  | 2029-09-01 | 11:48 | 42480 | 66.0472 | 0.39628 | 53.775 |  | 2029-09-01 | 11:48 | 42480 | 43.7117 | 0.26227 | 36.8574 |  | 2006-09-01 | 11:48 | 42480 | 42.6691 | 0.25601 | 36.3716 |  | 2028-01-01 | 11:48 | 42480 | 84.4502 | 0.5067 | 64.8201 |  | 2007-01-01 | 11:48 | 42480 | 89.9779 | 0.53987 | 67.8258 |  | 2028-01-01 | 11:48 | 42480 | 38.7506 | 0.2325 | 32.5975 |  | 2007-01-01 | 11:48 | 42480 | 40.0082 | 0.24005 | 33.5379
| 2029-09-01 | 11:49 | 42540 | 396.764 | 2.3806 | 245.8691 |  | 2029-09-01 | 11:49 | 42540 | 295.992 | 1.776 | 183.545 |  | 2006-09-01 | 11:49 | 42540 | 256.621 | 1.5397 | 167.7255 |  | 2029-09-01 | 11:49 | 42540 | 197.386 | 1.1843 | 124.3356 |  | 2006-09-01 | 11:49 | 42540 | 110.666 | 0.664 | 84.6131 |  | 2028-01-01 | 11:49 | 42540 | 300.7 | 1.8042 | 184.0249 |  | 2007-01-01 | 11:49 | 42540 | 271.663 | 1.63 | 167.7578 |  | 2028-01-01 | 11:49 | 42540 | 84.5032 | 0.50702 | 65.3271 |  | 2007-01-01 | 11:49 | 42540 | 90.1074 | 0.54064 | 68.3665 |  | 2029-09-01 | 11:49 | 42540 | 283.79 | 1.7027 | 175.9985 |  | 2006-09-01 | 11:49 | 42540 | 254.089 | 1.5245 | 165.9463 |  | 2029-09-01 | 11:49 | 42540 | 141.434 | 0.8486 | 92.8439 |  | 2006-09-01 | 11:49 | 42540 | 66.9971 | 0.40198 | 54.8841 |  | 2028-01-01 | 11:49 | 42540 | 284.978 | 1.7099 | 174.3009 |  | 2007-01-01 | 11:49 | 42540 | 270.074 | 1.6204 | 166.7248 |  | 2028-01-01 | 11:49 | 42540 | 46.9365 | 0.28162 | 38.7314 |  | 2007-01-01 | 11:49 | 42540 | 51.1779 | 0.30707 | 42.0024 |  | 2029-09-01 | 11:49 | 42540 | 281.334 | 1.688 | 174.4791 |  | 2006-09-01 | 11:49 | 42540 | 253.841 | 1.523 | 165.7717 |  | 2029-09-01 | 11:49 | 42540 | 107.553 | 0.64532 | 75.361 |  | 2006-09-01 | 11:49 | 42540 | 47.6972 | 0.28618 | 40.4659 |  | 2028-01-01 | 11:49 | 42540 | 281.225 | 1.6874 | 171.9793 |  | 2007-01-01 | 11:49 | 42540 | 269.957 | 1.6197 | 166.6488 |  | 2028-01-01 | 11:49 | 42540 | 32.4058 | 0.19443 | 27.5414 |  | 2007-01-01 | 11:49 | 42540 | 35.5632 | 0.21338 | 30.2045 |  | 2029-09-01 | 11:49 | 42540 | 100.684 | 0.6041 | 79.1706 |  | 2029-09-01 | 11:49 | 42540 | 66.0674 | 0.3964 | 54.1714 |  | 2029-09-01 | 11:49 | 42540 | 43.7162 | 0.2623 | 37.1197 |  | 2006-09-01 | 11:49 | 42540 | 42.6698 | 0.25602 | 36.6276 |  | 2028-01-01 | 11:49 | 42540 | 84.5032 | 0.50702 | 65.3271 |  | 2007-01-01 | 11:49 | 42540 | 90.1074 | 0.54064 | 68.3665 |  | 2028-01-01 | 11:49 | 42540 | 38.7521 | 0.23251 | 32.83 |  | 2007-01-01 | 11:49 | 42540 | 40.0199 | 0.24012 | 33.778
| 2029-09-01 | 11:50 | 42600 | 398.043 | 2.3883 | 248.2573 |  | 2029-09-01 | 11:50 | 42600 | 298.585 | 1.7915 | 185.3365 |  | 2006-09-01 | 11:50 | 42600 | 258.756 | 1.5525 | 169.278 |  | 2029-09-01 | 11:50 | 42600 | 197.555 | 1.1853 | 125.5209 |  | 2006-09-01 | 11:50 | 42600 | 110.907 | 0.66544 | 85.2785 |  | 2028-01-01 | 11:50 | 42600 | 303.168 | 1.819 | 185.8439 |  | 2007-01-01 | 11:50 | 42600 | 274.387 | 1.6463 | 169.4041 |  | 2028-01-01 | 11:50 | 42600 | 84.5529 | 0.50732 | 65.8344 |  | 2007-01-01 | 11:50 | 42600 | 90.232 | 0.54139 | 68.9079 |  | 2029-09-01 | 11:50 | 42600 | 286.542 | 1.7193 | 177.7177 |  | 2006-09-01 | 11:50 | 42600 | 256.267 | 1.5376 | 167.4839 |  | 2029-09-01 | 11:50 | 42600 | 140.808 | 0.84485 | 93.6888 |  | 2006-09-01 | 11:50 | 42600 | 67.0746 | 0.40245 | 55.2866 |  | 2028-01-01 | 11:50 | 42600 | 287.655 | 1.7259 | 176.0269 |  | 2007-01-01 | 11:50 | 42600 | 272.819 | 1.6369 | 168.3617 |  | 2028-01-01 | 11:50 | 42600 | 46.9396 | 0.28164 | 39.0131 |  | 2007-01-01 | 11:50 | 42600 | 51.1985 | 0.30719 | 42.3096 |  | 2029-09-01 | 11:50 | 42600 | 284.117 | 1.7047 | 176.1838 |  | 2006-09-01 | 11:50 | 42600 | 256.023 | 1.5361 | 167.3079 |  | 2029-09-01 | 11:50 | 42600 | 106.674 | 0.64004 | 76.001 |  | 2006-09-01 | 11:50 | 42600 | 47.7476 | 0.28649 | 40.7524 |  | 2028-01-01 | 11:50 | 42600 | 283.951 | 1.7037 | 173.683 |  | 2007-01-01 | 11:50 | 42600 | 272.704 | 1.6362 | 168.285 |  | 2028-01-01 | 11:50 | 42600 | 32.4069 | 0.19444 | 27.7358 |  | 2007-01-01 | 11:50 | 42600 | 35.5718 | 0.21343 | 30.418 |  | 2029-09-01 | 11:50 | 42600 | 100.772 | 0.60463 | 79.7752 |  | 2029-09-01 | 11:50 | 42600 | 66.0866 | 0.39652 | 54.5679 |  | 2029-09-01 | 11:50 | 42600 | 43.7205 | 0.26232 | 37.382 |  | 2006-09-01 | 11:50 | 42600 | 42.6704 | 0.25602 | 36.8836 |  | 2028-01-01 | 11:50 | 42600 | 84.5529 | 0.50732 | 65.8344 |  | 2007-01-01 | 11:50 | 42600 | 90.232 | 0.54139 | 68.9079 |  | 2028-01-01 | 11:50 | 42600 | 38.7537 | 0.23252 | 33.0625 |  | 2007-01-01 | 11:50 | 42600 | 40.0315 | 0.24019 | 34.0182
| 2029-09-01 | 11:51 | 42660 | 399.31 | 2.3959 | 250.6532 |  | 2029-09-01 | 11:51 | 42660 | 301.147 | 1.8069 | 187.1434 |  | 2006-09-01 | 11:51 | 42660 | 260.855 | 1.5651 | 170.8432 |  | 2029-09-01 | 11:51 | 42660 | 197.687 | 1.1861 | 126.707 |  | 2006-09-01 | 11:51 | 42660 | 111.14 | 0.66684 | 85.9454 |  | 2028-01-01 | 11:51 | 42660 | 305.605 | 1.8336 | 187.6775 |  | 2007-01-01 | 11:51 | 42660 | 277.078 | 1.6625 | 171.0665 |  | 2028-01-01 | 11:51 | 42660 | 84.5996 | 0.5076 | 66.342 |  | 2007-01-01 | 11:51 | 42660 | 90.3518 | 0.54211 | 69.45 |  | 2029-09-01 | 11:51 | 42660 | 289.261 | 1.7356 | 179.4533 |  | 2006-09-01 | 11:51 | 42660 | 258.408 | 1.5504 | 169.0344 |  | 2029-09-01 | 11:51 | 42660 | 140.166 | 0.841 | 94.5298 |  | 2006-09-01 | 11:51 | 42660 | 67.1511 | 0.40291 | 55.6895 |  | 2028-01-01 | 11:51 | 42660 | 290.297 | 1.7418 | 177.7686 |  | 2007-01-01 | 11:51 | 42660 | 275.532 | 1.6532 | 170.0149 |  | 2028-01-01 | 11:51 | 42660 | 46.9427 | 0.28166 | 39.2947 |  | 2007-01-01 | 11:51 | 42660 | 51.2186 | 0.30731 | 42.6169 |  | 2029-09-01 | 11:51 | 42660 | 286.868 | 1.7212 | 177.905 |  | 2006-09-01 | 11:51 | 42660 | 258.168 | 1.549 | 168.8569 |  | 2029-09-01 | 11:51 | 42660 | 105.799 | 0.63479 | 76.6358 |  | 2006-09-01 | 11:51 | 42660 | 47.798 | 0.28679 | 41.0392 |  | 2028-01-01 | 11:51 | 42660 | 286.643 | 1.7199 | 175.4029 |  | 2007-01-01 | 11:51 | 42660 | 275.419 | 1.6525 | 169.9376 |  | 2028-01-01 | 11:51 | 42660 | 32.4079 | 0.19445 | 27.9303 |  | 2007-01-01 | 11:51 | 42660 | 35.5803 | 0.21348 | 30.6315 |  | 2029-09-01 | 11:51 | 42660 | 100.855 | 0.60513 | 80.3804 |  | 2029-09-01 | 11:51 | 42660 | 66.1047 | 0.39663 | 54.9646 |  | 2029-09-01 | 11:51 | 42660 | 43.7247 | 0.26235 | 37.6444 |  | 2006-09-01 | 11:51 | 42660 | 42.6709 | 0.25603 | 37.1396 |  | 2028-01-01 | 11:51 | 42660 | 84.5996 | 0.5076 | 66.342 |  | 2007-01-01 | 11:51 | 42660 | 90.3518 | 0.54211 | 69.45 |  | 2028-01-01 | 11:51 | 42660 | 38.7552 | 0.23253 | 33.295 |  | 2007-01-01 | 11:51 | 42660 | 40.0429 | 0.24026 | 34.2584
| 2029-09-01 | 11:52 | 42720 | 400.565 | 2.4034 | 253.0566 |  | 2029-09-01 | 11:52 | 42720 | 303.679 | 1.8221 | 188.9655 |  | 2006-09-01 | 11:52 | 42720 | 262.92 | 1.5775 | 172.4207 |  | 2029-09-01 | 11:52 | 42720 | 197.782 | 1.1867 | 127.8937 |  | 2006-09-01 | 11:52 | 42720 | 111.366 | 0.6682 | 86.6136 |  | 2028-01-01 | 11:52 | 42720 | 308.011 | 1.8481 | 189.5256 |  | 2007-01-01 | 11:52 | 42720 | 279.739 | 1.6784 | 172.745 |  | 2028-01-01 | 11:52 | 42720 | 84.6436 | 0.50786 | 66.8499 |  | 2007-01-01 | 11:52 | 42720 | 90.4673 | 0.5428 | 69.9928 |  | 2029-09-01 | 11:52 | 42720 | 291.948 | 1.7517 | 181.205 |  | 2006-09-01 | 11:52 | 42720 | 260.513 | 1.5631 | 170.5974 |  | 2029-09-01 | 11:52 | 42720 | 139.508 | 0.83705 | 95.3668 |  | 2006-09-01 | 11:52 | 42720 | 67.2268 | 0.40336 | 56.0928 |  | 2028-01-01 | 11:52 | 42720 | 292.906 | 1.7574 | 179.5261 |  | 2007-01-01 | 11:52 | 42720 | 278.214 | 1.6693 | 171.6842 |  | 2028-01-01 | 11:52 | 42720 | 46.9457 | 0.28167 | 39.5764 |  | 2007-01-01 | 11:52 | 42720 | 51.2383 | 0.30743 | 42.9244 |  | 2029-09-01 | 11:52 | 42720 | 289.586 | 1.7375 | 179.6425 |  | 2006-09-01 | 11:52 | 42720 | 260.277 | 1.5617 | 170.4186 |  | 2029-09-01 | 11:52 | 42720 | 104.928 | 0.62957 | 77.2654 |  | 2006-09-01 | 11:52 | 42720 | 47.8484 | 0.28709 | 41.3262 |  | 2028-01-01 | 11:52 | 42720 | 289.3 | 1.7358 | 177.1387 |  | 2007-01-01 | 11:52 | 42720 | 278.102 | 1.6686 | 171.6062 |  | 2028-01-01 | 11:52 | 42720 | 32.409 | 0.19445 | 28.1247 |  | 2007-01-01 | 11:52 | 42720 | 35.5886 | 0.21353 | 30.845 |  | 2029-09-01 | 11:52 | 42720 | 100.934 | 0.6056 | 80.986 |  | 2029-09-01 | 11:52 | 42720 | 66.122 | 0.39673 | 55.3613 |  | 2029-09-01 | 11:52 | 42720 | 43.7288 | 0.26237 | 37.9067 |  | 2006-09-01 | 11:52 | 42720 | 42.6714 | 0.25603 | 37.3957 |  | 2028-01-01 | 11:52 | 42720 | 84.6436 | 0.50786 | 66.8499 |  | 2007-01-01 | 11:52 | 42720 | 90.4673 | 0.5428 | 69.9928 |  | 2028-01-01 | 11:52 | 42720 | 38.7568 | 0.23254 | 33.5276 |  | 2007-01-01 | 11:52 | 42720 | 40.0541 | 0.24032 | 34.4988
| 2029-09-01 | 11:53 | 42780 | 401.809 | 2.4109 | 255.4674 |  | 2029-09-01 | 11:53 | 42780 | 306.182 | 1.8371 | 190.8026 |  | 2006-09-01 | 11:53 | 42780 | 264.95 | 1.5897 | 174.0104 |  | 2029-09-01 | 11:53 | 42780 | 197.842 | 1.1871 | 129.0808 |  | 2006-09-01 | 11:53 | 42780 | 111.585 | 0.66951 | 87.2831 |  | 2028-01-01 | 11:53 | 42780 | 310.387 | 1.8623 | 191.3879 |  | 2007-01-01 | 11:53 | 42780 | 282.368 | 1.6942 | 174.4392 |  | 2028-01-01 | 11:53 | 42780 | 84.685 | 0.50811 | 67.358 |  | 2007-01-01 | 11:53 | 42780 | 90.5786 | 0.54347 | 70.5362 |  | 2029-09-01 | 11:53 | 42780 | 294.603 | 1.7676 | 182.9726 |  | 2006-09-01 | 11:53 | 42780 | 262.583 | 1.5755 | 172.1729 |  | 2029-09-01 | 11:53 | 42780 | 138.836 | 0.83302 | 96.1998 |  | 2006-09-01 | 11:53 | 42780 | 67.3018 | 0.40381 | 56.4967 |  | 2028-01-01 | 11:53 | 42780 | 295.483 | 1.7729 | 181.299 |  | 2007-01-01 | 11:53 | 42780 | 280.864 | 1.6852 | 173.3694 |  | 2028-01-01 | 11:53 | 42780 | 46.9487 | 0.28169 | 39.8581 |  | 2007-01-01 | 11:53 | 42780 | 51.2577 | 0.30755 | 43.2319 |  | 2029-09-01 | 11:53 | 42780 | 292.272 | 1.7536 | 181.3962 |  | 2006-09-01 | 11:53 | 42780 | 262.351 | 1.5741 | 171.9927 |  | 2029-09-01 | 11:53 | 42780 | 104.064 | 0.62438 | 77.8897 |  | 2006-09-01 | 11:53 | 42780 | 47.8989 | 0.28739 | 41.6136 |  | 2028-01-01 | 11:53 | 42780 | 291.924 | 1.7515 | 178.8902 |  | 2007-01-01 | 11:53 | 42780 | 280.754 | 1.6845 | 173.2907 |  | 2028-01-01 | 11:53 | 42780 | 32.4101 | 0.19446 | 28.3192 |  | 2007-01-01 | 11:53 | 42780 | 35.5969 | 0.21358 | 31.0586 |  | 2029-09-01 | 11:53 | 42780 | 101.01 | 0.60606 | 81.592 |  | 2029-09-01 | 11:53 | 42780 | 66.1384 | 0.39683 | 55.7581 |  | 2029-09-01 | 11:53 | 42780 | 43.7328 | 0.2624 | 38.1691 |  | 2006-09-01 | 11:53 | 42780 | 42.6718 | 0.25603 | 37.6517 |  | 2028-01-01 | 11:53 | 42780 | 84.685 | 0.50811 | 67.358 |  | 2007-01-01 | 11:53 | 42780 | 90.5786 | 0.54347 | 70.5362 |  | 2028-01-01 | 11:53 | 42780 | 38.7584 | 0.23255 | 33.7601 |  | 2007-01-01 | 11:53 | 42780 | 40.0652 | 0.24039 | 34.7392
| 2029-09-01 | 11:54 | 42840 | 403.041 | 2.4182 | 257.8857 |  | 2029-09-01 | 11:54 | 42840 | 308.656 | 1.8519 | 192.6545 |  | 2006-09-01 | 11:54 | 42840 | 266.946 | 1.6017 | 175.6121 |  | 2029-09-01 | 11:54 | 42840 | 197.869 | 1.1872 | 130.268 |  | 2006-09-01 | 11:54 | 42840 | 111.797 | 0.67078 | 87.9538 |  | 2028-01-01 | 11:54 | 42840 | 312.734 | 1.8764 | 193.2643 |  | 2007-01-01 | 11:54 | 42840 | 284.968 | 1.7098 | 176.149 |  | 2028-01-01 | 11:54 | 42840 | 84.724 | 0.50834 | 67.8664 |  | 2007-01-01 | 11:54 | 42840 | 90.686 | 0.54412 | 71.0804 |  | 2029-09-01 | 11:54 | 42840 | 297.228 | 1.7834 | 184.7559 |  | 2006-09-01 | 11:54 | 42840 | 264.619 | 1.5877 | 173.7606 |  | 2029-09-01 | 11:54 | 42840 | 138.152 | 0.82891 | 97.0287 |  | 2006-09-01 | 11:54 | 42840 | 67.3761 | 0.40426 | 56.9009 |  | 2028-01-01 | 11:54 | 42840 | 298.026 | 1.7882 | 183.0871 |  | 2007-01-01 | 11:54 | 42840 | 283.484 | 1.7009 | 175.0703 |  | 2028-01-01 | 11:54 | 42840 | 46.9516 | 0.28171 | 40.1398 |  | 2007-01-01 | 11:54 | 42840 | 51.2766 | 0.30766 | 43.5396 |  | 2029-09-01 | 11:54 | 42840 | 294.927 | 1.7696 | 183.1657 |  | 2006-09-01 | 11:54 | 42840 | 264.391 | 1.5863 | 173.579 |  | 2029-09-01 | 11:54 | 42840 | 103.206 | 0.61924 | 78.509 |  | 2006-09-01 | 11:54 | 42840 | 47.9494 | 0.2877 | 41.9013 |  | 2028-01-01 | 11:54 | 42840 | 294.515 | 1.7671 | 180.6573 |  | 2007-01-01 | 11:54 | 42840 | 283.375 | 1.7003 | 174.9909 |  | 2028-01-01 | 11:54 | 42840 | 32.4112 | 0.19447 | 28.5136 |  | 2007-01-01 | 11:54 | 42840 | 35.6051 | 0.21363 | 31.2722 |  | 2029-09-01 | 11:54 | 42840 | 101.082 | 0.60649 | 82.1985 |  | 2029-09-01 | 11:54 | 42840 | 66.154 | 0.39692 | 56.1551 |  | 2029-09-01 | 11:54 | 42840 | 43.7367 | 0.26242 | 38.4315 |  | 2006-09-01 | 11:54 | 42840 | 42.6721 | 0.25603 | 37.9077 |  | 2028-01-01 | 11:54 | 42840 | 84.724 | 0.50834 | 67.8664 |  | 2007-01-01 | 11:54 | 42840 | 90.686 | 0.54412 | 71.0804 |  | 2028-01-01 | 11:54 | 42840 | 38.76 | 0.23256 | 33.9927 |  | 2007-01-01 | 11:54 | 42840 | 40.0762 | 0.24046 | 34.9796
| 2029-09-01 | 11:55 | 42900 | 404.261 | 2.4256 | 260.3112 |  | 2029-09-01 | 11:55 | 42900 | 311.102 | 1.8666 | 194.5211 |  | 2006-09-01 | 11:55 | 42900 | 268.909 | 1.6135 | 177.2255 |  | 2029-09-01 | 11:55 | 42900 | 197.863 | 1.1872 | 131.4552 |  | 2006-09-01 | 11:55 | 42900 | 112.002 | 0.67201 | 88.6259 |  | 2028-01-01 | 11:55 | 42900 | 315.051 | 1.8903 | 195.1546 |  | 2007-01-01 | 11:55 | 42900 | 287.537 | 1.7252 | 177.8742 |  | 2028-01-01 | 11:55 | 42900 | 84.7609 | 0.50857 | 68.3749 |  | 2007-01-01 | 11:55 | 42900 | 90.7897 | 0.54474 | 71.6251 |  | 2029-09-01 | 11:55 | 42900 | 299.822 | 1.7989 | 186.5549 |  | 2006-09-01 | 11:55 | 42900 | 266.621 | 1.5997 | 175.3604 |  | 2029-09-01 | 11:55 | 42900 | 137.458 | 0.82475 | 97.8535 |  | 2006-09-01 | 11:55 | 42900 | 67.4498 | 0.4047 | 57.3056 |  | 2028-01-01 | 11:55 | 42900 | 300.538 | 1.8032 | 184.8904 |  | 2007-01-01 | 11:55 | 42900 | 286.074 | 1.7164 | 176.7867 |  | 2028-01-01 | 11:55 | 42900 | 46.9545 | 0.28173 | 40.4215 |  | 2007-01-01 | 11:55 | 42900 | 51.2953 | 0.30777 | 43.8474 |  | 2029-09-01 | 11:55 | 42900 | 297.551 | 1.7853 | 184.951 |  | 2006-09-01 | 11:55 | 42900 | 266.396 | 1.5984 | 175.1774 |  | 2029-09-01 | 11:55 | 42900 | 102.357 | 0.61414 | 79.1231 |  | 2006-09-01 | 11:55 | 42900 | 48 | 0.288 | 42.1893 |  | 2028-01-01 | 11:55 | 42900 | 297.073 | 1.7824 | 182.4398 |  | 2007-01-01 | 11:55 | 42900 | 285.966 | 1.7158 | 176.7067 |  | 2028-01-01 | 11:55 | 42900 | 32.4124 | 0.19447 | 28.7081 |  | 2007-01-01 | 11:55 | 42900 | 35.6132 | 0.21368 | 31.4859 |  | 2029-09-01 | 11:55 | 42900 | 101.151 | 0.60691 | 82.8054 |  | 2029-09-01 | 11:55 | 42900 | 66.169 | 0.39701 | 56.5521 |  | 2029-09-01 | 11:55 | 42900 | 43.7406 | 0.26244 | 38.694 |  | 2006-09-01 | 11:55 | 42900 | 42.6724 | 0.25603 | 38.1638 |  | 2028-01-01 | 11:55 | 42900 | 84.7609 | 0.50857 | 68.3749 |  | 2007-01-01 | 11:55 | 42900 | 90.7897 | 0.54474 | 71.6251 |  | 2028-01-01 | 11:55 | 42900 | 38.7617 | 0.23257 | 34.2253 |  | 2007-01-01 | 11:55 | 42900 | 40.087 | 0.24052 | 35.2201
| 2029-09-01 | 11:56 | 42960 | 405.471 | 2.4328 | 262.7441 |  | 2029-09-01 | 11:56 | 42960 | 313.519 | 1.8811 | 196.4022 |  | 2006-09-01 | 11:56 | 42960 | 270.839 | 1.625 | 178.8505 |  | 2029-09-01 | 11:56 | 42960 | 197.827 | 1.187 | 132.6421 |  | 2006-09-01 | 11:56 | 42960 | 112.202 | 0.67321 | 89.2991 |  | 2028-01-01 | 11:56 | 42960 | 317.339 | 1.904 | 197.0587 |  | 2007-01-01 | 11:56 | 42960 | 290.078 | 1.7405 | 179.6147 |  | 2028-01-01 | 11:56 | 42960 | 84.7958 | 0.50877 | 68.8837 |  | 2007-01-01 | 11:56 | 42960 | 90.89 | 0.54534 | 72.1704 |  | 2029-09-01 | 11:56 | 42960 | 302.385 | 1.8143 | 188.3692 |  | 2006-09-01 | 11:56 | 42960 | 268.589 | 1.6115 | 176.9719 |  | 2029-09-01 | 11:56 | 42960 | 136.754 | 0.82052 | 98.674 |  | 2006-09-01 | 11:56 | 42960 | 67.5229 | 0.40514 | 57.7107 |  | 2028-01-01 | 11:56 | 42960 | 303.018 | 1.8181 | 186.7085 |  | 2007-01-01 | 11:56 | 42960 | 288.634 | 1.7318 | 178.5185 |  | 2028-01-01 | 11:56 | 42960 | 46.9573 | 0.28174 | 40.7033 |  | 2007-01-01 | 11:56 | 42960 | 51.3136 | 0.30788 | 44.1552 |  | 2029-09-01 | 11:56 | 42960 | 300.143 | 1.8009 | 186.7519 |  | 2006-09-01 | 11:56 | 42960 | 268.368 | 1.6102 | 176.7876 |  | 2029-09-01 | 11:56 | 42960 | 101.515 | 0.60909 | 79.7322 |  | 2006-09-01 | 11:56 | 42960 | 48.0506 | 0.2883 | 42.4776 |  | 2028-01-01 | 11:56 | 42960 | 299.599 | 1.7976 | 184.2374 |  | 2007-01-01 | 11:56 | 42960 | 288.528 | 1.7312 | 178.4379 |  | 2028-01-01 | 11:56 | 42960 | 32.4135 | 0.19448 | 28.9026 |  | 2007-01-01 | 11:56 | 42960 | 35.6212 | 0.21373 | 31.6996 |  | 2029-09-01 | 11:56 | 42960 | 101.217 | 0.6073 | 83.4127 |  | 2029-09-01 | 11:56 | 42960 | 66.1833 | 0.3971 | 56.9492 |  | 2029-09-01 | 11:56 | 42960 | 43.7444 | 0.26247 | 38.9565 |  | 2006-09-01 | 11:56 | 42960 | 42.6727 | 0.25604 | 38.4198 |  | 2028-01-01 | 11:56 | 42960 | 84.7958 | 0.50877 | 68.8837 |  | 2007-01-01 | 11:56 | 42960 | 90.89 | 0.54534 | 72.1704 |  | 2028-01-01 | 11:56 | 42960 | 38.7633 | 0.23258 | 34.4578 |  | 2007-01-01 | 11:56 | 42960 | 40.0977 | 0.24059 | 35.4607
| 2029-09-01 | 11:57 | 43020 | 406.669 | 2.44 | 265.1841 |  | 2029-09-01 | 11:57 | 43020 | 315.909 | 1.8955 | 198.2977 |  | 2006-09-01 | 11:57 | 43020 | 272.736 | 1.6364 | 180.487 |  | 2029-09-01 | 11:57 | 43020 | 197.761 | 1.1866 | 133.8287 |  | 2006-09-01 | 11:57 | 43020 | 112.396 | 0.67438 | 89.9734 |  | 2028-01-01 | 11:57 | 43020 | 319.599 | 1.9176 | 198.9762 |  | 2007-01-01 | 11:57 | 43020 | 292.589 | 1.7555 | 181.3702 |  | 2028-01-01 | 11:57 | 43020 | 84.8288 | 0.50897 | 69.3927 |  | 2007-01-01 | 11:57 | 43020 | 90.987 | 0.54592 | 72.7164 |  | 2029-09-01 | 11:57 | 43020 | 304.919 | 1.8295 | 190.1987 |  | 2006-09-01 | 11:57 | 43020 | 270.524 | 1.6231 | 178.595 |  | 2029-09-01 | 11:57 | 43020 | 136.043 | 0.81626 | 99.4903 |  | 2006-09-01 | 11:57 | 43020 | 67.5957 | 0.40557 | 58.1163 |  | 2028-01-01 | 11:57 | 43020 | 305.468 | 1.8328 | 188.5413 |  | 2007-01-01 | 11:57 | 43020 | 291.165 | 1.747 | 180.2655 |  | 2028-01-01 | 11:57 | 43020 | 46.9601 | 0.28176 | 40.985 |  | 2007-01-01 | 11:57 | 43020 | 51.3316 | 0.30799 | 44.4632 |  | 2029-09-01 | 11:57 | 43020 | 302.706 | 1.8162 | 188.5681 |  | 2006-09-01 | 11:57 | 43020 | 270.307 | 1.6218 | 178.4094 |  | 2029-09-01 | 11:57 | 43020 | 100.683 | 0.6041 | 80.3363 |  | 2006-09-01 | 11:57 | 43020 | 48.1014 | 0.28861 | 42.7662 |  | 2028-01-01 | 11:57 | 43020 | 302.094 | 1.8126 | 186.0499 |  | 2007-01-01 | 11:57 | 43020 | 291.061 | 1.7464 | 180.1843 |  | 2028-01-01 | 11:57 | 43020 | 32.4147 | 0.19449 | 29.0971 |  | 2007-01-01 | 11:57 | 43020 | 35.6291 | 0.21377 | 31.9134 |  | 2029-09-01 | 11:57 | 43020 | 101.28 | 0.60768 | 84.0204 |  | 2029-09-01 | 11:57 | 43020 | 66.197 | 0.39718 | 57.3464 |  | 2029-09-01 | 11:57 | 43020 | 43.7481 | 0.26249 | 39.2189 |  | 2006-09-01 | 11:57 | 43020 | 42.673 | 0.25604 | 38.6758 |  | 2028-01-01 | 11:57 | 43020 | 84.8288 | 0.50897 | 69.3927 |  | 2007-01-01 | 11:57 | 43020 | 90.987 | 0.54592 | 72.7164 |  | 2028-01-01 | 11:57 | 43020 | 38.765 | 0.23259 | 34.6904 |  | 2007-01-01 | 11:57 | 43020 | 40.1083 | 0.24065 | 35.7014
| 2029-09-01 | 11:58 | 43080 | 407.857 | 2.4471 | 267.6312 |  | 2029-09-01 | 11:58 | 43080 | 318.271 | 1.9096 | 200.2073 |  | 2006-09-01 | 11:58 | 43080 | 274.602 | 1.6476 | 182.1346 |  | 2029-09-01 | 11:58 | 43080 | 197.666 | 1.186 | 135.0147 |  | 2006-09-01 | 11:58 | 43080 | 112.585 | 0.67551 | 90.649 |  | 2028-01-01 | 11:58 | 43080 | 321.831 | 1.931 | 200.9072 |  | 2007-01-01 | 11:58 | 43080 | 295.073 | 1.7704 | 183.1407 |  | 2028-01-01 | 11:58 | 43080 | 84.8601 | 0.50916 | 69.9018 |  | 2007-01-01 | 11:58 | 43080 | 91.0808 | 0.54648 | 73.2628 |  | 2029-09-01 | 11:58 | 43080 | 307.423 | 1.8445 | 192.0432 |  | 2006-09-01 | 11:58 | 43080 | 272.427 | 1.6346 | 180.2296 |  | 2029-09-01 | 11:58 | 43080 | 135.324 | 0.81194 | 100.3022 |  | 2006-09-01 | 11:58 | 43080 | 67.668 | 0.40601 | 58.5223 |  | 2028-01-01 | 11:58 | 43080 | 307.887 | 1.8473 | 190.3886 |  | 2007-01-01 | 11:58 | 43080 | 293.668 | 1.762 | 182.0275 |  | 2028-01-01 | 11:58 | 43080 | 46.963 | 0.28178 | 41.2668 |  | 2007-01-01 | 11:58 | 43080 | 51.3492 | 0.3081 | 44.7713 |  | 2029-09-01 | 11:58 | 43080 | 305.239 | 1.8314 | 190.3996 |  | 2006-09-01 | 11:58 | 43080 | 272.214 | 1.6333 | 180.0427 |  | 2029-09-01 | 11:58 | 43080 | 99.8614 | 0.59917 | 80.9355 |  | 2006-09-01 | 11:58 | 43080 | 48.1522 | 0.28891 | 43.0552 |  | 2028-01-01 | 11:58 | 43080 | 304.558 | 1.8273 | 187.8773 |  | 2007-01-01 | 11:58 | 43080 | 293.565 | 1.7614 | 181.9457 |  | 2028-01-01 | 11:58 | 43080 | 32.4159 | 0.1945 | 29.2916 |  | 2007-01-01 | 11:58 | 43080 | 35.6369 | 0.21382 | 32.1272 |  | 2029-09-01 | 11:58 | 43080 | 101.34 | 0.60804 | 84.6284 |  | 2029-09-01 | 11:58 | 43080 | 66.2101 | 0.39726 | 57.7436 |  | 2029-09-01 | 11:58 | 43080 | 43.7518 | 0.26251 | 39.4815 |  | 2006-09-01 | 11:58 | 43080 | 42.6732 | 0.25604 | 38.9319 |  | 2028-01-01 | 11:58 | 43080 | 84.8601 | 0.50916 | 69.9018 |  | 2007-01-01 | 11:58 | 43080 | 91.0808 | 0.54648 | 73.2628 |  | 2028-01-01 | 11:58 | 43080 | 38.7667 | 0.2326 | 34.923 |  | 2007-01-01 | 11:58 | 43080 | 40.1187 | 0.24071 | 35.9421
| 2029-09-01 | 11:59 | 43140 | 409.033 | 2.4542 | 270.0854 |  | 2029-09-01 | 11:59 | 43140 | 320.606 | 1.9236 | 202.1309 |  | 2006-09-01 | 11:59 | 43140 | 276.437 | 1.6586 | 183.7932 |  | 2029-09-01 | 11:59 | 43140 | 197.545 | 1.1853 | 136.2 |  | 2006-09-01 | 11:59 | 43140 | 112.77 | 0.67662 | 91.3256 |  | 2028-01-01 | 11:59 | 43140 | 324.036 | 1.9442 | 202.8514 |  | 2007-01-01 | 11:59 | 43140 | 297.528 | 1.7852 | 184.9258 |  | 2028-01-01 | 11:59 | 43140 | 84.8898 | 0.50934 | 70.4112 |  | 2007-01-01 | 11:59 | 43140 | 91.1718 | 0.54703 | 73.8099 |  | 2029-09-01 | 11:59 | 43140 | 309.899 | 1.8594 | 193.9026 |  | 2006-09-01 | 11:59 | 43140 | 274.299 | 1.6458 | 181.8754 |  | 2029-09-01 | 11:59 | 43140 | 134.601 | 0.80761 | 101.1098 |  | 2006-09-01 | 11:59 | 43140 | 67.74 | 0.40644 | 58.9288 |  | 2028-01-01 | 11:59 | 43140 | 310.276 | 1.8617 | 192.2503 |  | 2007-01-01 | 11:59 | 43140 | 296.143 | 1.7769 | 183.8044 |  | 2028-01-01 | 11:59 | 43140 | 46.9658 | 0.28179 | 41.5486 |  | 2007-01-01 | 11:59 | 43140 | 51.3666 | 0.3082 | 45.0795 |  | 2029-09-01 | 11:59 | 43140 | 307.743 | 1.8465 | 192.246 |  | 2006-09-01 | 11:59 | 43140 | 274.089 | 1.6445 | 181.6873 |  | 2029-09-01 | 11:59 | 43140 | 99.0495 | 0.5943 | 81.5298 |  | 2006-09-01 | 11:59 | 43140 | 48.2032 | 0.28922 | 43.3444 |  | 2028-01-01 | 11:59 | 43140 | 306.991 | 1.8419 | 189.7192 |  | 2007-01-01 | 11:59 | 43140 | 296.041 | 1.7762 | 183.7219 |  | 2028-01-01 | 11:59 | 43140 | 32.4172 | 0.1945 | 29.4861 |  | 2007-01-01 | 11:59 | 43140 | 35.6446 | 0.21387 | 32.3411 |  | 2029-09-01 | 11:59 | 43140 | 101.398 | 0.60839 | 85.2368 |  | 2029-09-01 | 11:59 | 43140 | 66.2228 | 0.39734 | 58.141 |  | 2029-09-01 | 11:59 | 43140 | 43.7554 | 0.26253 | 39.744 |  | 2006-09-01 | 11:59 | 43140 | 42.6734 | 0.25604 | 39.1879 |  | 2028-01-01 | 11:59 | 43140 | 84.8898 | 0.50934 | 70.4112 |  | 2007-01-01 | 11:59 | 43140 | 91.1718 | 0.54703 | 73.8099 |  | 2028-01-01 | 11:59 | 43140 | 38.7685 | 0.23261 | 35.1556 |  | 2007-01-01 | 11:59 | 43140 | 40.129 | 0.24077 | 36.1829
3 | 2029-09-01 | 12:00 | 43200 | 410.199 | 2.4612 | 272.5466 |  | 2029-09-01 | 12:00 | 43200 | 322.914 | 1.9375 | 204.0684 |  | 2006-09-01 | 12:00 | 43200 | 278.242 | 1.6695 | 185.4626 |  | 2029-09-01 | 12:00 | 43200 | 197.397 | 1.1844 | 137.3843 |  | 2006-09-01 | 12:00 | 43200 | 112.949 | 0.67769 | 92.0033 |  | 2028-01-01 | 12:00 | 43200 | 326.214 | 1.9573 | 204.8087 |  | 2007-01-01 | 12:00 | 43200 | 299.957 | 1.7997 | 186.7256 |  | 2028-01-01 | 12:00 | 43200 | 84.9181 | 0.50951 | 70.9207 |  | 2007-01-01 | 12:00 | 43200 | 91.26 | 0.54756 | 74.3574 |  | 2029-09-01 | 12:00 | 43200 | 312.346 | 1.8741 | 195.7767 |  | 2006-09-01 | 12:00 | 43200 | 276.139 | 1.6568 | 183.5322 |  | 2029-09-01 | 12:00 | 43200 | 133.873 | 0.80324 | 101.9131 |  | 2006-09-01 | 12:00 | 43200 | 67.8117 | 0.40687 | 59.3356 |  | 2028-01-01 | 12:00 | 43200 | 312.636 | 1.8758 | 194.1261 |  | 2007-01-01 | 12:00 | 43200 | 298.59 | 1.7915 | 185.5959 |  | 2028-01-01 | 12:00 | 43200 | 46.9686 | 0.28181 | 41.8304 |  | 2007-01-01 | 12:00 | 43200 | 51.3838 | 0.3083 | 45.3878 |  | 2029-09-01 | 12:00 | 43200 | 310.218 | 1.8613 | 194.1073 |  | 2006-09-01 | 12:00 | 43200 | 275.933 | 1.6556 | 183.3428 |  | 2029-09-01 | 12:00 | 43200 | 98.2484 | 0.58949 | 82.1193 |  | 2006-09-01 | 12:00 | 43200 | 48.2543 | 0.28953 | 43.6339 |  | 2028-01-01 | 12:00 | 43200 | 309.394 | 1.8564 | 191.5756 |  | 2007-01-01 | 12:00 | 43200 | 298.49 | 1.7909 | 185.5128 |  | 2028-01-01 | 12:00 | 43200 | 32.4184 | 0.19451 | 29.6806 |  | 2007-01-01 | 12:00 | 43200 | 35.6522 | 0.21391 | 32.555 |  | 2029-09-01 | 12:00 | 43200 | 101.453 | 0.60872 | 85.8455 |  | 2029-09-01 | 12:00 | 43200 | 66.235 | 0.39741 | 58.5384 |  | 2029-09-01 | 12:00 | 43200 | 43.759 | 0.26255 | 40.0065 |  | 2006-09-01 | 12:00 | 43200 | 42.6736 | 0.25604 | 39.444 |  | 2028-01-01 | 12:00 | 43200 | 84.9181 | 0.50951 | 70.9207 |  | 2007-01-01 | 12:00 | 43200 | 91.26 | 0.54756 | 74.3574 |  | 2028-01-01 | 12:00 | 43200 | 38.7703 | 0.23262 | 35.3883 |  | 2007-01-01 | 12:00 | 43200 | 40.1391 | 0.24083 | 36.4237
| 2029-09-01 | 12:01 | 43260 | 405.019 | 0 | 272.5466 |  | 2029-09-01 | 12:01 | 43260 | 292.666 | 0 | 204.0684 |  | 2006-09-01 | 12:01 | 43260 | 204.026 | 0 | 185.4626 |  | 2029-09-01 | 12:01 | 43260 | 178.907 | 0 | 137.3843 |  | 2006-09-01 | 12:01 | 43260 | 82.8219 | 0 | 92.0033 |  | 2028-01-01 | 12:01 | 43260 | 293.795 | 0 | 204.8087 |  | 2007-01-01 | 12:01 | 43260 | 261.499 | 0 | 186.7256 |  | 2028-01-01 | 12:01 | 43260 | 76.4789 | 0 | 70.9207 |  | 2007-01-01 | 12:01 | 43260 | 79.5595 | 0 | 74.3574 |  | 2029-09-01 | 12:01 | 43260 | 267.076 | 0 | 195.7767 |  | 2006-09-01 | 12:01 | 43260 | 170.748 | 0 | 183.5322 |  | 2029-09-01 | 12:01 | 43260 | 114.47 | 0 | 101.9131 |  | 2006-09-01 | 12:01 | 43260 | 41.9307 | 0 | 59.3356 |  | 2028-01-01 | 12:01 | 43260 | 260.375 | 0 | 194.1261 |  | 2007-01-01 | 12:01 | 43260 | 238.446 | 0 | 185.5959 |  | 2028-01-01 | 12:01 | 43260 | 39.1172 | 0 | 41.8304 |  | 2007-01-01 | 12:01 | 43260 | 41.0337 | 0 | 45.3878 |  | 2029-09-01 | 12:01 | 43260 | 256.468 | 0 | 194.1073 |  | 2006-09-01 | 12:01 | 43260 | 155.557 | 0 | 183.3428 |  | 2029-09-01 | 12:01 | 43260 | 81.2256 | 0 | 82.1193 |  | 2006-09-01 | 12:01 | 43260 | 27.2034 | 0 | 43.6339 |  | 2028-01-01 | 12:01 | 43260 | 241.15 | 0 | 191.5756 |  | 2007-01-01 | 12:01 | 43260 | 223.488 | 0 | 185.5128 |  | 2028-01-01 | 12:01 | 43260 | 25.2678 | 0 | 29.6806 |  | 2007-01-01 | 12:01 | 43260 | 26.6938 | 0 | 32.555 |  | 2029-09-01 | 12:01 | 43260 | 95.3889 | 0 | 85.8455 |  | 2029-09-01 | 12:01 | 43260 | 60.3129 | 0 | 58.5384 |  | 2029-09-01 | 12:01 | 43260 | 38.0853 | 0 | 40.0065 |  | 2006-09-01 | 12:01 | 43260 | 36.9876 | 0 | 39.444 |  | 2028-01-01 | 12:01 | 43260 | 76.4789 | 0 | 70.9207 |  | 2007-01-01 | 12:01 | 43260 | 79.5595 | 0 | 74.3574 |  | 2028-01-01 | 12:01 | 43260 | 32.2452 | 0 | 35.3883 |  | 2007-01-01 | 12:01 | 43260 | 32.3944 | 0 | 36.4237
| 2029-09-01 | 12:02 | 43320 | 399.904 | 0 | 272.5466 |  | 2029-09-01 | 12:02 | 43320 | 265.155 | 0 | 204.0684 |  | 2006-09-01 | 12:02 | 43320 | 149.51 | 0 | 185.4626 |  | 2029-09-01 | 12:02 | 43320 | 162.089 | 0 | 137.3843 |  | 2006-09-01 | 12:02 | 43320 | 60.6919 | 0 | 92.0033 |  | 2028-01-01 | 12:02 | 43320 | 265.743 | 0 | 204.8087 |  | 2007-01-01 | 12:02 | 43320 | 227.51 | 0 | 186.7256 |  | 2028-01-01 | 12:02 | 43320 | 69.1767 | 0 | 70.9207 |  | 2007-01-01 | 12:02 | 43320 | 69.2184 | 0 | 74.3574 |  | 2029-09-01 | 12:02 | 43320 | 228.233 | 0 | 195.7767 |  | 2006-09-01 | 12:02 | 43320 | 105.482 | 0 | 183.5322 |  | 2029-09-01 | 12:02 | 43320 | 97.8216 | 0 | 101.9131 |  | 2006-09-01 | 12:02 | 43320 | 25.9033 | 0 | 59.3356 |  | 2028-01-01 | 12:02 | 43320 | 218.293 | 0 | 194.1261 |  | 2007-01-01 | 12:02 | 43320 | 189.918 | 0 | 185.5959 |  | 2028-01-01 | 12:02 | 43320 | 32.7951 | 0 | 41.8304 |  | 2007-01-01 | 12:02 | 43320 | 32.6827 | 0 | 45.3878 |  | 2029-09-01 | 12:02 | 43320 | 211.884 | 0 | 194.1073 |  | 2006-09-01 | 12:02 | 43320 | 87.6017 | 0 | 183.3428 |  | 2029-09-01 | 12:02 | 43320 | 67.1054 | 0 | 82.1193 |  | 2006-09-01 | 12:02 | 43320 | 15.3195 | 0 | 43.6339 |  | 2028-01-01 | 12:02 | 43320 | 189.378 | 0 | 191.5756 |  | 2007-01-01 | 12:02 | 43320 | 166.889 | 0 | 185.5128 |  | 2028-01-01 | 12:02 | 43320 | 19.8431 | 0 | 29.6806 |  | 2007-01-01 | 12:02 | 43320 | 19.9336 | 0 | 32.555 |  | 2029-09-01 | 12:02 | 43320 | 89.687 | 0 | 85.8455 |  | 2029-09-01 | 12:02 | 43320 | 54.9203 | 0 | 58.5384 |  | 2029-09-01 | 12:02 | 43320 | 33.1472 | 0 | 40.0065 |  | 2006-09-01 | 12:02 | 43320 | 32.0588 | 0 | 39.444 |  | 2028-01-01 | 12:02 | 43320 | 69.1767 | 0 | 70.9207 |  | 2007-01-01 | 12:02 | 43320 | 69.2184 | 0 | 74.3574 |  | 2028-01-01 | 12:02 | 43320 | 26.9256 | 0 | 35.3883 |  | 2007-01-01 | 12:02 | 43320 | 26.0949 | 0 | 36.4237
| 2029-09-01 | 12:03 | 43380 | 394.853 | 0 | 272.5466 |  | 2029-09-01 | 12:03 | 43380 | 240.142 | 0 | 204.0684 |  | 2006-09-01 | 12:03 | 43380 | 109.491 | 0 | 185.4626 |  | 2029-09-01 | 12:03 | 43380 | 146.799 | 0 | 137.3843 |  | 2006-09-01 | 12:03 | 43380 | 44.4467 | 0 | 92.0033 |  | 2028-01-01 | 12:03 | 43380 | 241.378 | 0 | 204.8087 |  | 2007-01-01 | 12:03 | 43380 | 197.53 | 0 | 186.7256 |  | 2028-01-01 | 12:03 | 43380 | 62.8341 | 0 | 70.9207 |  | 2007-01-01 | 12:03 | 43380 | 60.0972 | 0 | 74.3574 |  | 2029-09-01 | 12:03 | 43380 | 194.925 | 0 | 195.7767 |  | 2006-09-01 | 12:03 | 43380 | 65.1025 | 0 | 183.5322 |  | 2029-09-01 | 12:03 | 43380 | 83.5456 | 0 | 101.9131 |  | 2006-09-01 | 12:03 | 43380 | 15.9873 | 0 | 59.3356 |  | 2028-01-01 | 12:03 | 43380 | 184.217 | 0 | 194.1261 |  | 2007-01-01 | 12:03 | 43380 | 150.867 | 0 | 185.5959 |  | 2028-01-01 | 12:03 | 43380 | 27.6758 | 0 | 41.8304 |  | 2007-01-01 | 12:03 | 43380 | 25.9623 | 0 | 45.3878 |  | 2029-09-01 | 12:03 | 43380 | 174.928 | 0 | 194.1073 |  | 2006-09-01 | 12:03 | 43380 | 49.2799 | 0 | 183.3428 |  | 2029-09-01 | 12:03 | 43380 | 55.4012 | 0 | 82.1193 |  | 2006-09-01 | 12:03 | 43380 | 8.6179 | 0 | 43.6339 |  | 2028-01-01 | 12:03 | 43380 | 149.852 | 0 | 191.5756 |  | 2007-01-01 | 12:03 | 43380 | 124.292 | 0 | 185.5128 |  | 2028-01-01 | 12:03 | 43380 | 15.7016 | 0 | 29.6806 |  | 2007-01-01 | 12:03 | 43380 | 14.8458 | 0 | 32.555 |  | 2029-09-01 | 12:03 | 43380 | 84.3259 | 0 | 85.8455 |  | 2029-09-01 | 12:03 | 43380 | 50.0098 | 0 | 58.5384 |  | 2029-09-01 | 12:03 | 43380 | 28.8494 | 0 | 40.0065 |  | 2006-09-01 | 12:03 | 43380 | 27.7864 | 0 | 39.444 |  | 2028-01-01 | 12:03 | 43380 | 62.8341 | 0 | 70.9207 |  | 2007-01-01 | 12:03 | 43380 | 60.0972 | 0 | 74.3574 |  | 2028-01-01 | 12:03 | 43380 | 22.5706 | 0 | 35.3883 |  | 2007-01-01 | 12:03 | 43380 | 20.9803 | 0 | 36.4237
| 2029-09-01 | 12:04 | 43440 | 389.865 | 0 | 272.5466 |  | 2029-09-01 | 12:04 | 43440 | 217.41 | 0 | 204.0684 |  | 2006-09-01 | 12:04 | 43440 | 80.1327 | 0 | 185.4626 |  | 2029-09-01 | 12:04 | 43440 | 132.903 | 0 | 137.3843 |  | 2006-09-01 | 12:04 | 43440 | 32.5291 | 0 | 92.0033 |  | 2028-01-01 | 12:04 | 43440 | 220.136 | 0 | 204.8087 |  | 2007-01-01 | 12:04 | 43440 | 171.141 | 0 | 186.7256 |  | 2028-01-01 | 12:04 | 43440 | 57.3044 | 0 | 70.9207 |  | 2007-01-01 | 12:04 | 43440 | 52.0685 | 0 | 74.3574 |  | 2029-09-01 | 12:04 | 43440 | 166.38 | 0 | 195.7767 |  | 2006-09-01 | 12:04 | 43440 | 40.1434 | 0 | 183.5322 |  | 2029-09-01 | 12:04 | 43440 | 71.3111 | 0 | 101.9131 |  | 2006-09-01 | 12:04 | 43440 | 9.8581 | 0 | 59.3356 |  | 2028-01-01 | 12:04 | 43440 | 156.474 | 0 | 194.1261 |  | 2007-01-01 | 12:04 | 43440 | 119.525 | 0 | 185.5959 |  | 2028-01-01 | 12:04 | 43440 | 23.5078 | 0 | 41.8304 |  | 2007-01-01 | 12:04 | 43440 | 20.5688 | 0 | 45.3878 |  | 2029-09-01 | 12:04 | 43440 | 144.318 | 0 | 194.1073 |  | 2006-09-01 | 12:04 | 43440 | 27.6925 | 0 | 183.3428 |  | 2029-09-01 | 12:04 | 43440 | 45.7065 | 0 | 82.1193 |  | 2006-09-01 | 12:04 | 43440 | 4.8428 | 0 | 43.6339 |  | 2028-01-01 | 12:04 | 43440 | 119.486 | 0 | 191.5756 |  | 2007-01-01 | 12:04 | 43440 | 92.3199 | 0 | 185.5128 |  | 2028-01-01 | 12:04 | 43440 | 12.5198 | 0 | 29.6806 |  | 2007-01-01 | 12:04 | 43440 | 11.0269 | 0 | 32.555 |  | 2029-09-01 | 12:04 | 43440 | 79.2851 | 0 | 85.8455 |  | 2029-09-01 | 12:04 | 43440 | 45.5384 | 0 | 58.5384 |  | 2029-09-01 | 12:04 | 43440 | 25.1088 | 0 | 40.0065 |  | 2006-09-01 | 12:04 | 43440 | 24.083 | 0 | 39.444 |  | 2028-01-01 | 12:04 | 43440 | 57.3044 | 0 | 70.9207 |  | 2007-01-01 | 12:04 | 43440 | 52.0685 | 0 | 74.3574 |  | 2028-01-01 | 12:04 | 43440 | 18.9907 | 0 | 35.3883 |  | 2007-01-01 | 12:04 | 43440 | 16.8354 | 0 | 36.4237
| 2029-09-01 | 12:05 | 43500 | 384.94 | 0 | 272.5466 |  | 2029-09-01 | 12:05 | 43500 | 196.758 | 0 | 204.0684 |  | 2006-09-01 | 12:05 | 43500 | 58.609 | 0 | 185.4626 |  | 2029-09-01 | 12:05 | 43500 | 120.278 | 0 | 137.3843 |  | 2006-09-01 | 12:05 | 43500 | 23.7918 | 0 | 92.0033 |  | 2028-01-01 | 12:05 | 43500 | 201.549 | 0 | 204.8087 |  | 2007-01-01 | 12:05 | 43500 | 147.962 | 0 | 186.7256 |  | 2028-01-01 | 12:05 | 43500 | 52.466 | 0 | 70.9207 |  | 2007-01-01 | 12:05 | 43500 | 45.0164 | 0 | 74.3574 |  | 2029-09-01 | 12:05 | 43500 | 141.931 | 0 | 195.7767 |  | 2006-09-01 | 12:05 | 43500 | 24.7303 | 0 | 183.5322 |  | 2029-09-01 | 12:05 | 43500 | 60.8324 | 0 | 101.9131 |  | 2006-09-01 | 12:05 | 43500 | 6.073 | 0 | 59.3356 |  | 2028-01-01 | 12:05 | 43500 | 133.767 | 0 | 194.1261 |  | 2007-01-01 | 12:05 | 43500 | 94.4379 | 0 | 185.5959 |  | 2028-01-01 | 12:05 | 43500 | 20.0964 | 0 | 41.8304 |  | 2007-01-01 | 12:05 | 43500 | 16.2516 | 0 | 45.3878 |  | 2029-09-01 | 12:05 | 43500 | 118.98 | 0 | 194.1073 |  | 2006-09-01 | 12:05 | 43500 | 15.545 | 0 | 183.3428 |  | 2029-09-01 | 12:05 | 43500 | 37.682 | 0 | 82.1193 |  | 2006-09-01 | 12:05 | 43500 | 2.7185 | 0 | 43.6339 |  | 2028-01-01 | 12:05 | 43500 | 96.0135 | 0 | 191.5756 |  | 2007-01-01 | 12:05 | 43500 | 68.3867 | 0 | 185.5128 |  | 2028-01-01 | 12:05 | 43500 | 10.0603 | 0 | 29.6806 |  | 2007-01-01 | 12:05 | 43500 | 8.1683 | 0 | 32.555 |  | 2029-09-01 | 12:05 | 43500 | 74.5455 | 0 | 85.8455 |  | 2029-09-01 | 12:05 | 43500 | 41.4666 | 0 | 58.5384 |  | 2029-09-01 | 12:05 | 43500 | 21.8532 | 0 | 40.0065 |  | 2006-09-01 | 12:05 | 43500 | 20.873 | 0 | 39.444 |  | 2028-01-01 | 12:05 | 43500 | 52.466 | 0 | 70.9207 |  | 2007-01-01 | 12:05 | 43500 | 45.0164 | 0 | 74.3574 |  | 2028-01-01 | 12:05 | 43500 | 16.0363 | 0 | 35.3883 |  | 2007-01-01 | 12:05 | 43500 | 13.4827 | 0 | 36.4237
| 2029-09-01 | 12:06 | 43560 | 380.076 | 0 | 272.5466 |  | 2029-09-01 | 12:06 | 43560 | 178.004 | 0 | 204.0684 |  | 2006-09-01 | 12:06 | 43560 | 42.8394 | 0 | 185.4626 |  | 2029-09-01 | 12:06 | 43560 | 108.814 | 0 | 137.3843 |  | 2006-09-01 | 12:06 | 43560 | 17.3903 | 0 | 92.0033 |  | 2028-01-01 | 12:06 | 43560 | 185.228 | 0 | 204.8087 |  | 2007-01-01 | 12:06 | 43560 | 127.645 | 0 | 186.7256 |  | 2028-01-01 | 12:06 | 43560 | 48.2175 | 0 | 70.9207 |  | 2007-01-01 | 12:06 | 43560 | 38.8352 | 0 | 74.3574 |  | 2029-09-01 | 12:06 | 43560 | 121.004 | 0 | 195.7767 |  | 2006-09-01 | 12:06 | 43560 | 15.2209 | 0 | 183.5322 |  | 2029-09-01 | 12:06 | 43560 | 51.8629 | 0 | 101.9131 |  | 2006-09-01 | 12:06 | 43560 | 3.7378 | 0 | 59.3356 |  | 2028-01-01 | 12:06 | 43560 | 115.084 | 0 | 194.1261 |  | 2007-01-01 | 12:06 | 43560 | 74.4129 | 0 | 185.5959 |  | 2028-01-01 | 12:06 | 43560 | 17.2896 | 0 | 41.8304 |  | 2007-01-01 | 12:06 | 43560 | 12.8056 | 0 | 45.3878 |  | 2029-09-01 | 12:06 | 43560 | 98.0231 | 0 | 194.1073 |  | 2006-09-01 | 12:06 | 43560 | 8.7168 | 0 | 183.3428 |  | 2029-09-01 | 12:06 | 43560 | 31.0447 | 0 | 82.1193 |  | 2006-09-01 | 12:06 | 43560 | 1.5244 | 0 | 43.6339 |  | 2028-01-01 | 12:06 | 43560 | 77.7595 | 0 | 191.5756 |  | 2007-01-01 | 12:06 | 43560 | 50.5202 | 0 | 185.5128 |  | 2028-01-01 | 12:06 | 43560 | 8.1477 | 0 | 29.6806 |  | 2007-01-01 | 12:06 | 43560 | 6.0342 | 0 | 32.555 |  | 2029-09-01 | 12:06 | 43560 | 70.0892 | 0 | 85.8455 |  | 2029-09-01 | 12:06 | 43560 | 37.7589 | 0 | 58.5384 |  | 2029-09-01 | 12:06 | 43560 | 19.0196 | 0 | 40.0065 |  | 2006-09-01 | 12:06 | 43560 | 18.0905 | 0 | 39.444 |  | 2028-01-01 | 12:06 | 43560 | 48.2175 | 0 | 70.9207 |  | 2007-01-01 | 12:06 | 43560 | 38.8352 | 0 | 74.3574 |  | 2028-01-01 | 12:06 | 43560 | 13.5887 | 0 | 35.3883 |  | 2007-01-01 | 12:06 | 43560 | 10.776 | 0 | 36.4237
| 2029-09-01 | 12:07 | 43620 | 375.274 | 0 | 272.5466 |  | 2029-09-01 | 12:07 | 43620 | 160.978 | 0 | 204.0684 |  | 2006-09-01 | 12:07 | 43620 | 31.2929 | 0 | 185.4626 |  | 2029-09-01 | 12:07 | 43620 | 98.4057 | 0 | 137.3843 |  | 2006-09-01 | 12:07 | 43620 | 12.7031 | 0 | 92.0033 |  | 2028-01-01 | 12:07 | 43620 | 170.849 | 0 | 204.8087 |  | 2007-01-01 | 12:07 | 43620 | 109.876 | 0 | 186.7256 |  | 2028-01-01 | 12:07 | 43620 | 44.4744 | 0 | 70.9207 |  | 2007-01-01 | 12:07 | 43620 | 33.4291 | 0 | 74.3574 |  | 2029-09-01 | 12:07 | 43620 | 103.102 | 0 | 195.7767 |  | 2006-09-01 | 12:07 | 43620 | 9.3595 | 0 | 183.5322 |  | 2029-09-01 | 12:07 | 43620 | 44.1899 | 0 | 101.9131 |  | 2006-09-01 | 12:07 | 43620 | 2.2984 | 0 | 59.3356 |  | 2028-01-01 | 12:07 | 43620 | 99.6361 | 0 | 194.1261 |  | 2007-01-01 | 12:07 | 43620 | 58.4723 | 0 | 185.5959 |  | 2028-01-01 | 12:07 | 43620 | 14.9688 | 0 | 41.8304 |  | 2007-01-01 | 12:07 | 43620 | 10.0624 | 0 | 45.3878 |  | 2029-09-01 | 12:07 | 43620 | 80.7008 | 0 | 194.1073 |  | 2006-09-01 | 12:07 | 43620 | 4.8827 | 0 | 183.3428 |  | 2029-09-01 | 12:07 | 43620 | 25.5586 | 0 | 82.1193 |  | 2006-09-01 | 12:07 | 43620 | 0.85387 | 0 | 43.6339 |  | 2028-01-01 | 12:07 | 43620 | 63.4808 | 0 | 191.5756 |  | 2007-01-01 | 12:07 | 43620 | 37.2193 | 0 | 185.5128 |  | 2028-01-01 | 12:07 | 43620 | 6.6515 | 0 | 29.6806 |  | 2007-01-01 | 12:07 | 43620 | 4.4456 | 0 | 32.555 |  | 2029-09-01 | 12:07 | 43620 | 65.8992 | 0 | 85.8455 |  | 2029-09-01 | 12:07 | 43620 | 34.3827 | 0 | 58.5384 |  | 2029-09-01 | 12:07 | 43620 | 16.5535 | 0 | 40.0065 |  | 2006-09-01 | 12:07 | 43620 | 15.6787 | 0 | 39.444 |  | 2028-01-01 | 12:07 | 43620 | 44.4744 | 0 | 70.9207 |  | 2007-01-01 | 12:07 | 43620 | 33.4291 | 0 | 74.3574 |  | 2028-01-01 | 12:07 | 43620 | 11.5533 | 0 | 35.3883 |  | 2007-01-01 | 12:07 | 43620 | 8.5952 | 0 | 36.4237
| 2029-09-01 | 12:08 | 43680 | 370.532 | 0 | 272.5466 |  | 2029-09-01 | 12:08 | 43680 | 145.528 | 0 | 204.0684 |  | 2006-09-01 | 12:08 | 43680 | 22.8441 | 0 | 185.4626 |  | 2029-09-01 | 12:08 | 43680 | 88.961 | 0 | 137.3843 |  | 2006-09-01 | 12:08 | 43680 | 9.2734 | 0 | 92.0033 |  | 2028-01-01 | 12:08 | 43680 | 158.138 | 0 | 204.8087 |  | 2007-01-01 | 12:08 | 43680 | 94.3699 | 0 | 186.7256 |  | 2028-01-01 | 12:08 | 43680 | 41.1654 | 0 | 70.9207 |  | 2007-01-01 | 12:08 | 43680 | 28.7115 | 0 | 74.3574 |  | 2029-09-01 | 12:08 | 43680 | 87.7965 | 0 | 195.7767 |  | 2006-09-01 | 12:08 | 43680 | 5.7499 | 0 | 183.5322 |  | 2029-09-01 | 12:08 | 43680 | 37.6299 | 0 | 101.9131 |  | 2006-09-01 | 12:08 | 43680 | 1.412 | 0 | 59.3356 |  | 2028-01-01 | 12:08 | 43680 | 86.8006 | 0 | 194.1261 |  | 2007-01-01 | 12:08 | 43680 | 45.8183 | 0 | 185.5959 |  | 2028-01-01 | 12:08 | 43680 | 13.0404 | 0 | 41.8304 |  | 2007-01-01 | 12:08 | 43680 | 7.8848 | 0 | 45.3878 |  | 2029-09-01 | 12:08 | 43680 | 66.3932 | 0 | 194.1073 |  | 2006-09-01 | 12:08 | 43680 | 2.7321 | 0 | 183.3428 |  | 2029-09-01 | 12:08 | 43680 | 21.0273 | 0 | 82.1193 |  | 2006-09-01 | 12:08 | 43680 | 0.47779 | 0 | 43.6339 |  | 2028-01-01 | 12:08 | 43680 | 52.2484 | 0 | 191.5756 |  | 2007-01-01 | 12:08 | 43680 | 27.3447 | 0 | 185.5128 |  | 2028-01-01 | 12:08 | 43680 | 5.4746 | 0 | 29.6806 |  | 2007-01-01 | 12:08 | 43680 | 3.2661 | 0 | 32.555 |  | 2029-09-01 | 12:08 | 43680 | 61.9596 | 0 | 85.8455 |  | 2029-09-01 | 12:08 | 43680 | 31.3083 | 0 | 58.5384 |  | 2029-09-01 | 12:08 | 43680 | 14.4071 | 0 | 40.0065 |  | 2006-09-01 | 12:08 | 43680 | 13.5883 | 0 | 39.444 |  | 2028-01-01 | 12:08 | 43680 | 41.1654 | 0 | 70.9207 |  | 2007-01-01 | 12:08 | 43680 | 28.7115 | 0 | 74.3574 |  | 2028-01-01 | 12:08 | 43680 | 9.8544 | 0 | 35.3883 |  | 2007-01-01 | 12:08 | 43680 | 6.8415 | 0 | 36.4237
| 2029-09-01 | 12:09 | 43740 | 365.849 | 0 | 272.5466 |  | 2029-09-01 | 12:09 | 43740 | 131.512 | 0 | 204.0684 |  | 2006-09-01 | 12:09 | 43740 | 16.6658 | 0 | 185.4626 |  | 2029-09-01 | 12:09 | 43740 | 80.3935 | 0 | 137.3843 |  | 2006-09-01 | 12:09 | 43740 | 6.7653 | 0 | 92.0033 |  | 2028-01-01 | 12:09 | 43740 | 146.865 | 0 | 204.8087 |  | 2007-01-01 | 12:09 | 43740 | 80.8691 | 0 | 186.7256 |  | 2028-01-01 | 12:09 | 43740 | 38.231 | 0 | 70.9207 |  | 2007-01-01 | 12:09 | 43740 | 24.6039 | 0 | 74.3574 |  | 2029-09-01 | 12:09 | 43740 | 74.719 | 0 | 195.7767 |  | 2006-09-01 | 12:09 | 43740 | 3.5292 | 0 | 183.5322 |  | 2029-09-01 | 12:09 | 43740 | 32.0249 | 0 | 101.9131 |  | 2006-09-01 | 12:09 | 43740 | 0.86666 | 0 | 59.3356 |  | 2028-01-01 | 12:09 | 43740 | 76.0858 | 0 | 194.1261 |  | 2007-01-01 | 12:09 | 43740 | 35.8015 | 0 | 185.5959 |  | 2028-01-01 | 12:09 | 43740 | 11.4307 | 0 | 41.8304 |  | 2007-01-01 | 12:09 | 43740 | 6.161 | 0 | 45.3878 |  | 2029-09-01 | 12:09 | 43740 | 54.584 | 0 | 194.1073 |  | 2006-09-01 | 12:09 | 43740 | 1.5272 | 0 | 183.3428 |  | 2029-09-01 | 12:09 | 43740 | 17.2872 | 0 | 82.1193 |  | 2006-09-01 | 12:09 | 43740 | 0.26706 | 0 | 43.6339 |  | 2028-01-01 | 12:09 | 43740 | 43.3653 | 0 | 191.5756 |  | 2007-01-01 | 12:09 | 43740 | 20.0341 | 0 | 185.5128 |  | 2028-01-01 | 12:09 | 43740 | 4.5438 | 0 | 29.6806 |  | 2007-01-01 | 12:09 | 43740 | 2.3929 | 0 | 32.555 |  | 2029-09-01 | 12:09 | 43740 | 58.2554 | 0 | 85.8455 |  | 2029-09-01 | 12:09 | 43740 | 28.5088 | 0 | 58.5384 |  | 2029-09-01 | 12:09 | 43740 | 12.539 | 0 | 40.0065 |  | 2006-09-01 | 12:09 | 43740 | 11.7764 | 0 | 39.444 |  | 2028-01-01 | 12:09 | 43740 | 38.231 | 0 | 70.9207 |  | 2007-01-01 | 12:09 | 43740 | 24.6039 | 0 | 74.3574 |  | 2028-01-01 | 12:09 | 43740 | 8.4315 | 0 | 35.3883 |  | 2007-01-01 | 12:09 | 43740 | 5.4343 | 0 | 36.4237
| 2029-09-01 | 12:10 | 43800 | 361.225 | 0 | 272.5466 |  | 2029-09-01 | 12:10 | 43800 | 118.804 | 0 | 204.0684 |  | 2006-09-01 | 12:10 | 43800 | 12.1507 | 0 | 185.4626 |  | 2029-09-01 | 12:10 | 43800 | 72.6246 | 0 | 137.3843 |  | 2006-09-01 | 12:10 | 43800 | 4.9325 | 0 | 92.0033 |  | 2028-01-01 | 12:10 | 43800 | 136.85 | 0 | 204.8087 |  | 2007-01-01 | 12:10 | 43800 | 69.142 | 0 | 186.7256 |  | 2028-01-01 | 12:10 | 43800 | 35.6366 | 0 | 70.9207 |  | 2007-01-01 | 12:10 | 43800 | 21.036 | 0 | 74.3574 |  | 2029-09-01 | 12:10 | 43800 | 63.5519 | 0 | 195.7767 |  | 2006-09-01 | 12:10 | 43800 | 2.1641 | 0 | 183.5322 |  | 2029-09-01 | 12:10 | 43800 | 27.2386 | 0 | 101.9131 |  | 2006-09-01 | 12:10 | 43800 | 0.53144 | 0 | 59.3356 |  | 2028-01-01 | 12:10 | 43800 | 67.3912 | 0 | 194.1261 |  | 2007-01-01 | 12:10 | 43800 | 27.895 | 0 | 185.5959 |  | 2028-01-01 | 12:10 | 43800 | 10.1308 | 0 | 41.8304 |  | 2007-01-01 | 12:10 | 43800 | 4.8004 | 0 | 45.3878 |  | 2029-09-01 | 12:10 | 43800 | 44.8439 | 0 | 194.1073 |  | 2006-09-01 | 12:10 | 43800 | 0.85271 | 0 | 183.3428 |  | 2029-09-01 | 12:10 | 43800 | 14.2024 | 0 | 82.1193 |  | 2006-09-01 | 12:10 | 43800 | 0.14912 | 0 | 43.6339 |  | 2028-01-01 | 12:10 | 43800 | 36.7162 | 0 | 191.5756 |  | 2007-01-01 | 12:10 | 43800 | 14.637 | 0 | 185.5128 |  | 2028-01-01 | 12:10 | 43800 | 3.8506 | 0 | 29.6806 |  | 2007-01-01 | 12:10 | 43800 | 1.7483 | 0 | 32.555 |  | 2029-09-01 | 12:10 | 43800 | 54.7726 | 0 | 85.8455 |  | 2029-09-01 | 12:10 | 43800 | 25.9596 | 0 | 58.5384 |  | 2029-09-01 | 12:10 | 43800 | 10.9131 | 0 | 40.0065 |  | 2006-09-01 | 12:10 | 43800 | 10.206 | 0 | 39.444 |  | 2028-01-01 | 12:10 | 43800 | 35.6366 | 0 | 70.9207 |  | 2007-01-01 | 12:10 | 43800 | 21.036 | 0 | 74.3574 |  | 2028-01-01 | 12:10 | 43800 | 7.2586 | 0 | 35.3883 |  | 2007-01-01 | 12:10 | 43800 | 4.3074 | 0 | 36.4237
| 2029-09-01 | 12:11 | 43860 | 356.659 | 0 | 272.5466 |  | 2029-09-01 | 12:11 | 43860 | 107.284 | 0 | 204.0684 |  | 2006-09-01 | 12:11 | 43860 | 8.8532 | 0 | 185.4626 |  | 2029-09-01 | 12:11 | 43860 | 65.5825 | 0 | 137.3843 |  | 2006-09-01 | 12:11 | 43860 | 3.5939 | 0 | 92.0033 |  | 2028-01-01 | 12:11 | 43860 | 127.958 | 0 | 204.8087 |  | 2007-01-01 | 12:11 | 43860 | 58.9853 | 0 | 186.7256 |  | 2028-01-01 | 12:11 | 43860 | 33.3526 | 0 | 70.9207 |  | 2007-01-01 | 12:11 | 43860 | 17.9459 | 0 | 74.3574 |  | 2029-09-01 | 12:11 | 43860 | 54.0219 | 0 | 195.7767 |  | 2006-09-01 | 12:11 | 43860 | 1.3258 | 0 | 183.5322 |  | 2029-09-01 | 12:11 | 43860 | 23.154 | 0 | 101.9131 |  | 2006-09-01 | 12:11 | 43860 | 0.32559 | 0 | 59.3356 |  | 2028-01-01 | 12:11 | 43860 | 60.575 | 0 | 194.1261 |  | 2007-01-01 | 12:11 | 43860 | 21.6719 | 0 | 185.5959 |  | 2028-01-01 | 12:11 | 43860 | 9.1223 | 0 | 41.8304 |  | 2007-01-01 | 12:11 | 43860 | 3.7295 | 0 | 45.3878 |  | 2029-09-01 | 12:11 | 43860 | 36.8161 | 0 | 194.1073 |  | 2006-09-01 | 12:11 | 43860 | 0.47562 | 0 | 183.3428 |  | 2029-09-01 | 12:11 | 43860 | 11.6599 | 0 | 82.1193 |  | 2006-09-01 | 12:11 | 43860 | 0.083175 | 0 | 43.6339 |  | 2028-01-01 | 12:11 | 43860 | 32.076 | 0 | 191.5756 |  | 2007-01-01 | 12:11 | 43860 | 10.6637 | 0 | 185.5128 |  | 2028-01-01 | 12:11 | 43860 | 3.3729 | 0 | 29.6806 |  | 2007-01-01 | 12:11 | 43860 | 1.2737 | 0 | 32.555 |  | 2029-09-01 | 12:11 | 43860 | 51.498 | 0 | 85.8455 |  | 2029-09-01 | 12:11 | 43860 | 23.6383 | 0 | 58.5384 |  | 2029-09-01 | 12:11 | 43860 | 9.498 | 0 | 40.0065 |  | 2006-09-01 | 12:11 | 43860 | 8.8448 | 0 | 39.444 |  | 2028-01-01 | 12:11 | 43860 | 33.3526 | 0 | 70.9207 |  | 2007-01-01 | 12:11 | 43860 | 17.9459 | 0 | 74.3574 |  | 2028-01-01 | 12:11 | 43860 | 6.3114 | 0 | 35.3883 |  | 2007-01-01 | 12:11 | 43860 | 3.4072 | 0 | 36.4237
| 2029-09-01 | 12:12 | 43920 | 352.151 | 0 | 272.5466 |  | 2029-09-01 | 12:12 | 43920 | 96.8456 | 0 | 204.0684 |  | 2006-09-01 | 12:12 | 43920 | 6.4466 | 0 | 185.4626 |  | 2029-09-01 | 12:12 | 43920 | 59.2017 | 0 | 137.3843 |  | 2006-09-01 | 12:12 | 43920 | 2.617 | 0 | 92.0033 |  | 2028-01-01 | 12:12 | 43920 | 120.024 | 0 | 204.8087 |  | 2007-01-01 | 12:12 | 43920 | 50.2084 | 0 | 186.7256 |  | 2028-01-01 | 12:12 | 43920 | 31.3298 | 0 | 70.9207 |  | 2007-01-01 | 12:12 | 43920 | 15.2756 | 0 | 74.3574 |  | 2029-09-01 | 12:12 | 43920 | 45.8938 | 0 | 195.7767 |  | 2006-09-01 | 12:12 | 43920 | 0.81152 | 0 | 183.5322 |  | 2029-09-01 | 12:12 | 43920 | 19.6703 | 0 | 101.9131 |  | 2006-09-01 | 12:12 | 43920 | 0.19929 | 0 | 59.3356 |  | 2028-01-01 | 12:12 | 43920 | 55.1538 | 0 | 194.1261 |  | 2007-01-01 | 12:12 | 43920 | 16.7882 | 0 | 185.5959 |  | 2028-01-01 | 12:12 | 43920 | 8.3281 | 0 | 41.8304 |  | 2007-01-01 | 12:12 | 43920 | 2.8891 | 0 | 45.3878 |  | 2029-09-01 | 12:12 | 43920 | 30.2042 | 0 | 194.1073 |  | 2006-09-01 | 12:12 | 43920 | 0.26501 | 0 | 183.3428 |  | 2029-09-01 | 12:12 | 43920 | 9.5659 | 0 | 82.1193 |  | 2006-09-01 | 12:12 | 43920 | 0.046344 | 0 | 43.6339 |  | 2028-01-01 | 12:12 | 43920 | 28.7354 | 0 | 191.5756 |  | 2007-01-01 | 12:12 | 43920 | 7.747 | 0 | 185.5128 |  | 2028-01-01 | 12:12 | 43920 | 3.0332 | 0 | 29.6806 |  | 2007-01-01 | 12:12 | 43920 | 0.92532 | 0 | 32.555 |  | 2029-09-01 | 12:12 | 43920 | 48.4191 | 0 | 85.8455 |  | 2029-09-01 | 12:12 | 43920 | 21.5246 | 0 | 58.5384 |  | 2029-09-01 | 12:12 | 43920 | 8.2664 | 0 | 40.0065 |  | 2006-09-01 | 12:12 | 43920 | 7.6651 | 0 | 39.444 |  | 2028-01-01 | 12:12 | 43920 | 31.3298 | 0 | 70.9207 |  | 2007-01-01 | 12:12 | 43920 | 15.2756 | 0 | 74.3574 |  | 2028-01-01 | 12:12 | 43920 | 5.5474 | 0 | 35.3883 |  | 2007-01-01 | 12:12 | 43920 | 2.6896 | 0 | 36.4237
| 2029-09-01 | 12:13 | 43980 | 347.699 | 0 | 272.5466 |  | 2029-09-01 | 12:13 | 43980 | 87.3911 | 0 | 204.0684 |  | 2006-09-01 | 12:13 | 43980 | 4.6912 | 0 | 185.4626 |  | 2029-09-01 | 12:13 | 43980 | 53.4221 | 0 | 137.3843 |  | 2006-09-01 | 12:13 | 43980 | 1.9044 | 0 | 92.0033 |  | 2028-01-01 | 12:13 | 43980 | 112.873 | 0 | 204.8087 |  | 2007-01-01 | 12:13 | 43980 | 42.6426 | 0 | 186.7256 |  | 2028-01-01 | 12:13 | 43980 | 29.5154 | 0 | 70.9207 |  | 2007-01-01 | 12:13 | 43980 | 12.9738 | 0 | 74.3574 |  | 2029-09-01 | 12:13 | 43980 | 38.9656 | 0 | 195.7767 |  | 2006-09-01 | 12:13 | 43980 | 0.49626 | 0 | 183.5322 |  | 2029-09-01 | 12:13 | 43980 | 16.7008 | 0 | 101.9131 |  | 2006-09-01 | 12:13 | 43980 | 0.12187 | 0 | 59.3356 |  | 2028-01-01 | 12:13 | 43980 | 50.6733 | 0 | 194.1261 |  | 2007-01-01 | 12:13 | 43980 | 12.9667 | 0 | 185.5959 |  | 2028-01-01 | 12:13 | 43980 | 7.6758 | 0 | 41.8304 |  | 2007-01-01 | 12:13 | 43980 | 2.2314 | 0 | 45.3878 |  | 2029-09-01 | 12:13 | 43980 | 24.7624 | 0 | 194.1073 |  | 2006-09-01 | 12:13 | 43980 | 0.1475 | 0 | 183.3428 |  | 2029-09-01 | 12:13 | 43980 | 7.8424 | 0 | 82.1193 |  | 2006-09-01 | 12:13 | 43980 | 0.025795 | 0 | 43.6339 |  | 2028-01-01 | 12:13 | 43980 | 26.1151 | 0 | 191.5756 |  | 2007-01-01 | 12:13 | 43980 | 5.612 | 0 | 185.5128 |  | 2028-01-01 | 12:13 | 43980 | 2.7686 | 0 | 29.6806 |  | 2007-01-01 | 12:13 | 43980 | 0.67031 | 0 | 32.555 |  | 2029-09-01 | 12:13 | 43980 | 45.5242 | 0 | 85.8455 |  | 2029-09-01 | 12:13 | 43980 | 19.5998 | 0 | 58.5384 |  | 2029-09-01 | 12:13 | 43980 | 7.1945 | 0 | 40.0065 |  | 2006-09-01 | 12:13 | 43980 | 6.6427 | 0 | 39.444 |  | 2028-01-01 | 12:13 | 43980 | 29.5154 | 0 | 70.9207 |  | 2007-01-01 | 12:13 | 43980 | 12.9738 | 0 | 74.3574 |  | 2028-01-01 | 12:13 | 43980 | 4.9275 | 0 | 35.3883 |  | 2007-01-01 | 12:13 | 43980 | 2.1187 | 0 | 36.4237
| 2029-09-01 | 12:14 | 44040 | 343.302 | 0 | 272.5466 |  | 2029-09-01 | 12:14 | 44040 | 78.8307 | 0 | 204.0684 |  | 2006-09-01 | 12:14 | 44040 | 3.4116 | 0 | 185.4626 |  | 2029-09-01 | 12:14 | 44040 | 48.1892 | 0 | 137.3843 |  | 2006-09-01 | 12:14 | 44040 | 1.3849 | 0 | 92.0033 |  | 2028-01-01 | 12:14 | 44040 | 106.333 | 0 | 204.8087 |  | 2007-01-01 | 12:14 | 44040 | 36.1388 | 0 | 186.7256 |  | 2028-01-01 | 12:14 | 44040 | 27.8587 | 0 | 70.9207 |  | 2007-01-01 | 12:14 | 44040 | 10.995 | 0 | 74.3574 |  | 2029-09-01 | 12:14 | 44040 | 33.0637 | 0 | 195.7767 |  | 2006-09-01 | 12:14 | 44040 | 0.30319 | 0 | 183.5322 |  | 2029-09-01 | 12:14 | 44040 | 14.1713 | 0 | 101.9131 |  | 2006-09-01 | 12:14 | 44040 | 0.074456 | 0 | 59.3356 |  | 2028-01-01 | 12:14 | 44040 | 46.7615 | 0 | 194.1261 |  | 2007-01-01 | 12:14 | 44040 | 9.9853 | 0 | 185.5959 |  | 2028-01-01 | 12:14 | 44040 | 7.1066 | 0 | 41.8304 |  | 2007-01-01 | 12:14 | 44040 | 1.7184 | 0 | 45.3878 |  | 2029-09-01 | 12:14 | 44040 | 20.2867 | 0 | 194.1073 |  | 2006-09-01 | 12:14 | 44040 | 0.082013 | 0 | 183.3428 |  | 2029-09-01 | 12:14 | 44040 | 6.425 | 0 | 82.1193 |  | 2006-09-01 | 12:14 | 44040 | 0.014342 | 0 | 43.6339 |  | 2028-01-01 | 12:14 | 44040 | 23.8156 | 0 | 191.5756 |  | 2007-01-01 | 12:14 | 44040 | 4.0537 | 0 | 185.5128 |  | 2028-01-01 | 12:14 | 44040 | 2.5356 | 0 | 29.6806 |  | 2007-01-01 | 12:14 | 44040 | 0.48418 | 0 | 32.555 |  | 2029-09-01 | 12:14 | 44040 | 42.8024 | 0 | 85.8455 |  | 2029-09-01 | 12:14 | 44040 | 17.8472 | 0 | 58.5384 |  | 2029-09-01 | 12:14 | 44040 | 6.2616 | 0 | 40.0065 |  | 2006-09-01 | 12:14 | 44040 | 5.7565 | 0 | 39.444 |  | 2028-01-01 | 12:14 | 44040 | 27.8587 | 0 | 70.9207 |  | 2007-01-01 | 12:14 | 44040 | 10.995 | 0 | 74.3574 |  | 2028-01-01 | 12:14 | 44040 | 4.417 | 0 | 35.3883 |  | 2007-01-01 | 12:14 | 44040 | 1.6657 | 0 | 36.4237
| 2029-09-01 | 12:15 | 44100 | 338.961 | 0 | 272.5466 |  | 2029-09-01 | 12:15 | 44100 | 71.0828 | 0 | 204.0684 |  | 2006-09-01 | 12:15 | 44100 | 2.4795 | 0 | 185.4626 |  | 2029-09-01 | 12:15 | 44100 | 43.4529 | 0 | 137.3843 |  | 2006-09-01 | 12:15 | 44100 | 1.0065 | 0 | 92.0033 |  | 2028-01-01 | 12:15 | 44100 | 100.25 | 0 | 204.8087 |  | 2007-01-01 | 12:15 | 44100 | 30.562 | 0 | 186.7256 |  | 2028-01-01 | 12:15 | 44100 | 26.3152 | 0 | 70.9207 |  | 2007-01-01 | 12:15 | 44100 | 9.2983 | 0 | 74.3574 |  | 2029-09-01 | 12:15 | 44100 | 28.0392 | 0 | 195.7767 |  | 2006-09-01 | 12:15 | 44100 | 0.18507 | 0 | 183.5322 |  | 2029-09-01 | 12:15 | 44100 | 12.0177 | 0 | 101.9131 |  | 2006-09-01 | 12:15 | 44100 | 0.045448 | 0 | 59.3356 |  | 2028-01-01 | 12:15 | 44100 | 43.1521 | 0 | 194.1261 |  | 2007-01-01 | 12:15 | 44100 | 7.6663 | 0 | 185.5959 |  | 2028-01-01 | 12:15 | 44100 | 6.5786 | 0 | 41.8304 |  | 2007-01-01 | 12:15 | 44100 | 1.3193 | 0 | 45.3878 |  | 2029-09-01 | 12:15 | 44100 | 16.6084 | 0 | 194.1073 |  | 2006-09-01 | 12:15 | 44100 | 0.045552 | 0 | 183.3428 |  | 2029-09-01 | 12:15 | 44100 | 5.26 | 0 | 82.1193 |  | 2006-09-01 | 12:15 | 44100 | 0.007966 | 0 | 43.6339 |  | 2028-01-01 | 12:15 | 44100 | 21.6105 | 0 | 191.5756 |  | 2007-01-01 | 12:15 | 44100 | 2.9196 | 0 | 185.5128 |  | 2028-01-01 | 12:15 | 44100 | 2.31 | 0 | 29.6806 |  | 2007-01-01 | 12:15 | 44100 | 0.34872 | 0 | 32.555 |  | 2029-09-01 | 12:15 | 44100 | 40.2432 | 0 | 85.8455 |  | 2029-09-01 | 12:15 | 44100 | 16.2512 | 0 | 58.5384 |  | 2029-09-01 | 12:15 | 44100 | 5.4497 | 0 | 40.0065 |  | 2006-09-01 | 12:15 | 44100 | 4.9885 | 0 | 39.444 |  | 2028-01-01 | 12:15 | 44100 | 26.3152 | 0 | 70.9207 |  | 2007-01-01 | 12:15 | 44100 | 9.2983 | 0 | 74.3574 |  | 2028-01-01 | 12:15 | 44100 | 3.987 | 0 | 35.3883 |  | 2007-01-01 | 12:15 | 44100 | 1.307 | 0 | 36.4237
| 2029-09-01 | 12:16 | 44160 | 334.675 | 0 | 272.5466 |  | 2029-09-01 | 12:16 | 44160 | 64.0729 | 0 | 204.0684 |  | 2006-09-01 | 12:16 | 44160 | 1.8009 | 0 | 185.4626 |  | 2029-09-01 | 12:16 | 44160 | 39.1678 | 0 | 137.3843 |  | 2006-09-01 | 12:16 | 44160 | 0.73107 | 0 | 92.0033 |  | 2028-01-01 | 12:16 | 44160 | 94.4992 | 0 | 204.8087 |  | 2007-01-01 | 12:16 | 44160 | 25.7917 | 0 | 186.7256 |  | 2028-01-01 | 12:16 | 44160 | 24.8488 | 0 | 70.9207 |  | 2007-01-01 | 12:16 | 44160 | 7.847 | 0 | 74.3574 |  | 2029-09-01 | 12:16 | 44160 | 23.7641 | 0 | 195.7767 |  | 2006-09-01 | 12:16 | 44160 | 0.11286 | 0 | 183.5322 |  | 2029-09-01 | 12:16 | 44160 | 10.1854 | 0 | 101.9131 |  | 2006-09-01 | 12:16 | 44160 | 0.027716 | 0 | 59.3356 |  | 2028-01-01 | 12:16 | 44160 | 39.6822 | 0 | 194.1261 |  | 2007-01-01 | 12:16 | 44160 | 5.8679 | 0 | 185.5959 |  | 2028-01-01 | 12:16 | 44160 | 6.0665 | 0 | 41.8304 |  | 2007-01-01 | 12:16 | 44160 | 1.0098 | 0 | 45.3878 |  | 2029-09-01 | 12:16 | 44160 | 13.5874 | 0 | 194.1073 |  | 2006-09-01 | 12:16 | 44160 | 0.025274 | 0 | 183.3428 |  | 2029-09-01 | 12:16 | 44160 | 4.3032 | 0 | 82.1193 |  | 2006-09-01 | 12:16 | 44160 | 0.0044199 | 0 | 43.6339 |  | 2028-01-01 | 12:16 | 44160 | 19.4083 | 0 | 191.5756 |  | 2007-01-01 | 12:16 | 44160 | 2.0967 | 0 | 185.5128 |  | 2028-01-01 | 12:16 | 44160 | 2.0818 | 0 | 29.6806 |  | 2007-01-01 | 12:16 | 44160 | 0.25043 | 0 | 32.555 |  | 2029-09-01 | 12:16 | 44160 | 37.837 | 0 | 85.8455 |  | 2029-09-01 | 12:16 | 44160 | 14.798 | 0 | 58.5384 |  | 2029-09-01 | 12:16 | 44160 | 4.743 | 0 | 40.0065 |  | 2006-09-01 | 12:16 | 44160 | 4.3229 | 0 | 39.444 |  | 2028-01-01 | 12:16 | 44160 | 24.8488 | 0 | 70.9207 |  | 2007-01-01 | 12:16 | 44160 | 7.847 | 0 | 74.3574 |  | 2028-01-01 | 12:16 | 44160 | 3.6148 | 0 | 35.3883 |  | 2007-01-01 | 12:16 | 44160 | 1.0235 | 0 | 36.4237
| 2029-09-01 | 12:17 | 44220 | 330.442 | 0 | 272.5466 |  | 2029-09-01 | 12:17 | 44220 | 57.7332 | 0 | 204.0684 |  | 2006-09-01 | 12:17 | 44220 | 1.3072 | 0 | 185.4626 |  | 2029-09-01 | 12:17 | 44220 | 35.2923 | 0 | 137.3843 |  | 2006-09-01 | 12:17 | 44220 | 0.53066 | 0 | 92.0033 |  | 2028-01-01 | 12:17 | 44220 | 88.9862 | 0 | 204.8087 |  | 2007-01-01 | 12:17 | 44220 | 21.7211 | 0 | 186.7256 |  | 2028-01-01 | 12:17 | 44220 | 23.4332 | 0 | 70.9207 |  | 2007-01-01 | 12:17 | 44220 | 6.6085 | 0 | 74.3574 |  | 2029-09-01 | 12:17 | 44220 | 20.1288 | 0 | 195.7767 |  | 2006-09-01 | 12:17 | 44220 | 0.068766 | 0 | 183.5322 |  | 2029-09-01 | 12:17 | 44220 | 8.6273 | 0 | 101.9131 |  | 2006-09-01 | 12:17 | 44220 | 0.016887 | 0 | 59.3356 |  | 2028-01-01 | 12:17 | 44220 | 36.2751 | 0 | 194.1261 |  | 2007-01-01 | 12:17 | 44220 | 4.4776 | 0 | 185.5959 |  | 2028-01-01 | 12:17 | 44220 | 5.5589 | 0 | 41.8304 |  | 2007-01-01 | 12:17 | 44220 | 0.77054 | 0 | 45.3878 |  | 2029-09-01 | 12:17 | 44220 | 11.1081 | 0 | 194.1073 |  | 2006-09-01 | 12:17 | 44220 | 0.014008 | 0 | 183.3428 |  | 2029-09-01 | 12:17 | 44220 | 3.518 | 0 | 82.1193 |  | 2006-09-01 | 12:17 | 44220 | 0.0024497 | 0 | 43.6339 |  | 2028-01-01 | 12:17 | 44220 | 17.2051 | 0 | 191.5756 |  | 2007-01-01 | 12:17 | 44220 | 1.5013 | 0 | 185.5128 |  | 2028-01-01 | 12:17 | 44220 | 1.8511 | 0 | 29.6806 |  | 2007-01-01 | 12:17 | 44220 | 0.17932 | 0 | 32.555 |  | 2029-09-01 | 12:17 | 44220 | 35.5746 | 0 | 85.8455 |  | 2029-09-01 | 12:17 | 44220 | 13.4747 | 0 | 58.5384 |  | 2029-09-01 | 12:17 | 44220 | 4.128 | 0 | 40.0065 |  | 2006-09-01 | 12:17 | 44220 | 3.746 | 0 | 39.444 |  | 2028-01-01 | 12:17 | 44220 | 23.4332 | 0 | 70.9207 |  | 2007-01-01 | 12:17 | 44220 | 6.6085 | 0 | 74.3574 |  | 2028-01-01 | 12:17 | 44220 | 3.2833 | 0 | 35.3883 |  | 2007-01-01 | 12:17 | 44220 | 0.79997 | 0 | 36.4237
| 2029-09-01 | 12:18 | 44280 | 326.263 | 0 | 272.5466 |  | 2029-09-01 | 12:18 | 44280 | 52.0016 | 0 | 204.0684 |  | 2006-09-01 | 12:18 | 44280 | 0.94826 | 0 | 185.4626 |  | 2029-09-01 | 12:18 | 44280 | 31.7885 | 0 | 137.3843 |  | 2006-09-01 | 12:18 | 44280 | 0.38494 | 0 | 92.0033 |  | 2028-01-01 | 12:18 | 44280 | 83.6469 | 0 | 204.8087 |  | 2007-01-01 | 12:18 | 44280 | 18.2555 | 0 | 186.7256 |  | 2028-01-01 | 12:18 | 44280 | 22.0512 | 0 | 70.9207 |  | 2007-01-01 | 12:18 | 44280 | 5.5541 | 0 | 74.3574 |  | 2029-09-01 | 12:18 | 44280 | 17.0396 | 0 | 195.7767 |  | 2006-09-01 | 12:18 | 44280 | 0.04186 | 0 | 183.5322 |  | 2029-09-01 | 12:18 | 44280 | 7.3032 | 0 | 101.9131 |  | 2006-09-01 | 12:18 | 44280 | 0.01028 | 0 | 59.3356 |  | 2028-01-01 | 12:18 | 44280 | 32.916 | 0 | 194.1261 |  | 2007-01-01 | 12:18 | 44280 | 3.4061 | 0 | 185.5959 |  | 2028-01-01 | 12:18 | 44280 | 5.0541 | 0 | 41.8304 |  | 2007-01-01 | 12:18 | 44280 | 0.58614 | 0 | 45.3878 |  | 2029-09-01 | 12:18 | 44280 | 9.0749 | 0 | 194.1073 |  | 2006-09-01 | 12:18 | 44280 | 0.0077561 | 0 | 183.3428 |  | 2029-09-01 | 12:18 | 44280 | 2.8741 | 0 | 82.1193 |  | 2006-09-01 | 12:18 | 44280 | 0.0013564 | 0 | 43.6339 |  | 2028-01-01 | 12:18 | 44280 | 15.0416 | 0 | 191.5756 |  | 2007-01-01 | 12:18 | 44280 | 1.0718 | 0 | 185.5128 |  | 2028-01-01 | 12:18 | 44280 | 1.6226 | 0 | 29.6806 |  | 2007-01-01 | 12:18 | 44280 | 0.12802 | 0 | 32.555 |  | 2029-09-01 | 12:18 | 44280 | 33.4475 | 0 | 85.8455 |  | 2029-09-01 | 12:18 | 44280 | 12.2697 | 0 | 58.5384 |  | 2029-09-01 | 12:18 | 44280 | 3.5927 | 0 | 40.0065 |  | 2006-09-01 | 12:18 | 44280 | 3.2461 | 0 | 39.444 |  | 2028-01-01 | 12:18 | 44280 | 22.0512 | 0 | 70.9207 |  | 2007-01-01 | 12:18 | 44280 | 5.5541 | 0 | 74.3574 |  | 2028-01-01 | 12:18 | 44280 | 2.9809 | 0 | 35.3883 |  | 2007-01-01 | 12:18 | 44280 | 0.62408 | 0 | 36.4237
| 2029-09-01 | 12:19 | 44340 | 322.136 | 0 | 272.5466 |  | 2029-09-01 | 12:19 | 44340 | 46.8218 | 0 | 204.0684 |  | 2006-09-01 | 12:19 | 44340 | 0.68744 | 0 | 185.4626 |  | 2029-09-01 | 12:19 | 44340 | 28.6221 | 0 | 137.3843 |  | 2006-09-01 | 12:19 | 44340 | 0.27907 | 0 | 92.0033 |  | 2028-01-01 | 12:19 | 44340 | 78.4441 | 0 | 204.8087 |  | 2007-01-01 | 12:19 | 44340 | 15.3118 | 0 | 186.7256 |  | 2028-01-01 | 12:19 | 44340 | 20.6938 | 0 | 70.9207 |  | 2007-01-01 | 12:19 | 44340 | 4.6585 | 0 | 74.3574 |  | 2029-09-01 | 12:19 | 44340 | 14.4159 | 0 | 195.7767 |  | 2006-09-01 | 12:19 | 44340 | 0.025458 | 0 | 183.5322 |  | 2029-09-01 | 12:19 | 44340 | 6.1787 | 0 | 101.9131 |  | 2006-09-01 | 12:19 | 44340 | 0.0062518 | 0 | 59.3356 |  | 2028-01-01 | 12:19 | 44340 | 29.6276 | 0 | 194.1261 |  | 2007-01-01 | 12:19 | 44340 | 2.5828 | 0 | 185.5959 |  | 2028-01-01 | 12:19 | 44340 | 4.5564 | 0 | 41.8304 |  | 2007-01-01 | 12:19 | 44340 | 0.44446 | 0 | 45.3878 |  | 2029-09-01 | 12:19 | 44340 | 7.4085 | 0 | 194.1073 |  | 2006-09-01 | 12:19 | 44340 | 0.0042898 | 0 | 183.3428 |  | 2029-09-01 | 12:19 | 44340 | 2.3463 | 0 | 82.1193 |  | 2006-09-01 | 12:19 | 44340 | 0.00075019 | 0 | 43.6339 |  | 2028-01-01 | 12:19 | 44340 | 12.9721 | 0 | 191.5756 |  | 2007-01-01 | 12:19 | 44340 | 0.76288 | 0 | 185.5128 |  | 2028-01-01 | 12:19 | 44340 | 1.4025 | 0 | 29.6806 |  | 2007-01-01 | 12:19 | 44340 | 0.09112 | 0 | 32.555 |  | 2029-09-01 | 12:19 | 44340 | 31.4475 | 0 | 85.8455 |  | 2029-09-01 | 12:19 | 44340 | 11.1724 | 0 | 58.5384 |  | 2029-09-01 | 12:19 | 44340 | 3.1268 | 0 | 40.0065 |  | 2006-09-01 | 12:19 | 44340 | 2.8129 | 0 | 39.444 |  | 2028-01-01 | 12:19 | 44340 | 20.6938 | 0 | 70.9207 |  | 2007-01-01 | 12:19 | 44340 | 4.6585 | 0 | 74.3574 |  | 2028-01-01 | 12:19 | 44340 | 2.6999 | 0 | 35.3883 |  | 2007-01-01 | 12:19 | 44340 | 0.48594 | 0 | 36.4237
| 2029-09-01 | 12:20 | 44400 | 318.061 | 0 | 272.5466 |  | 2029-09-01 | 12:20 | 44400 | 42.1424 | 0 | 204.0684 |  | 2006-09-01 | 12:20 | 44400 | 0.49805 | 0 | 185.4626 |  | 2029-09-01 | 12:20 | 44400 | 25.7617 | 0 | 137.3843 |  | 2006-09-01 | 12:20 | 44400 | 0.20218 | 0 | 92.0033 |  | 2028-01-01 | 12:20 | 44400 | 73.363 | 0 | 204.8087 |  | 2007-01-01 | 12:20 | 44400 | 12.8169 | 0 | 186.7256 |  | 2028-01-01 | 12:20 | 44400 | 19.3585 | 0 | 70.9207 |  | 2007-01-01 | 12:20 | 44400 | 3.8995 | 0 | 74.3574 |  | 2029-09-01 | 12:20 | 44400 | 12.1889 | 0 | 195.7767 |  | 2006-09-01 | 12:20 | 44400 | 0.015469 | 0 | 183.5322 |  | 2029-09-01 | 12:20 | 44400 | 5.2242 | 0 | 101.9131 |  | 2006-09-01 | 12:20 | 44400 | 0.0037987 | 0 | 59.3356 |  | 2028-01-01 | 12:20 | 44400 | 26.4503 | 0 | 194.1261 |  | 2007-01-01 | 12:20 | 44400 | 1.9522 | 0 | 185.5959 |  | 2028-01-01 | 12:20 | 44400 | 4.0729 | 0 | 41.8304 |  | 2007-01-01 | 12:20 | 44400 | 0.33596 | 0 | 45.3878 |  | 2029-09-01 | 12:20 | 44400 | 6.0439 | 0 | 194.1073 |  | 2006-09-01 | 12:20 | 44400 | 0.0023702 | 0 | 183.3428 |  | 2029-09-01 | 12:20 | 44400 | 1.9142 | 0 | 82.1193 |  | 2006-09-01 | 12:20 | 44400 | 0.00041449 | 0 | 43.6339 |  | 2028-01-01 | 12:20 | 44400 | 11.0457 | 0 | 191.5756 |  | 2007-01-01 | 12:20 | 44400 | 0.54138 | 0 | 185.5128 |  | 2028-01-01 | 12:20 | 44400 | 1.1967 | 0 | 29.6806 |  | 2007-01-01 | 12:20 | 44400 | 0.064664 | 0 | 32.555 |  | 2029-09-01 | 12:20 | 44400 | 29.567 | 0 | 85.8455 |  | 2029-09-01 | 12:20 | 44400 | 10.1733 | 0 | 58.5384 |  | 2029-09-01 | 12:20 | 44400 | 2.7213 | 0 | 40.0065 |  | 2006-09-01 | 12:20 | 44400 | 2.4374 | 0 | 39.444 |  | 2028-01-01 | 12:20 | 44400 | 19.3585 | 0 | 70.9207 |  | 2007-01-01 | 12:20 | 44400 | 3.8995 | 0 | 74.3574 |  | 2028-01-01 | 12:20 | 44400 | 2.4359 | 0 | 35.3883 |  | 2007-01-01 | 12:20 | 44400 | 0.37768 | 0 | 36.4237
| 2029-09-01 | 12:21 | 44460 | 314.037 | 0 | 272.5466 |  | 2029-09-01 | 12:21 | 44460 | 37.9168 | 0 | 204.0684 |  | 2006-09-01 | 12:21 | 44460 | 0.36061 | 0 | 185.4626 |  | 2029-09-01 | 12:21 | 44460 | 23.1785 | 0 | 137.3843 |  | 2006-09-01 | 12:21 | 44460 | 0.14639 | 0 | 92.0033 |  | 2028-01-01 | 12:21 | 44460 | 68.4046 | 0 | 204.8087 |  | 2007-01-01 | 12:21 | 44460 | 10.7071 | 0 | 186.7256 |  | 2028-01-01 | 12:21 | 44460 | 18.0474 | 0 | 70.9207 |  | 2007-01-01 | 12:21 | 44460 | 3.2576 | 0 | 74.3574 |  | 2029-09-01 | 12:21 | 44460 | 10.2998 | 0 | 195.7767 |  | 2006-09-01 | 12:21 | 44460 | 0.0093905 | 0 | 183.5322 |  | 2029-09-01 | 12:21 | 44460 | 4.4146 | 0 | 101.9131 |  | 2006-09-01 | 12:21 | 44460 | 0.0023061 | 0 | 59.3356 |  | 2028-01-01 | 12:21 | 44460 | 23.4273 | 0 | 194.1261 |  | 2007-01-01 | 12:21 | 44460 | 1.4709 | 0 | 185.5959 |  | 2028-01-01 | 12:21 | 44460 | 3.6109 | 0 | 41.8304 |  | 2007-01-01 | 12:21 | 44460 | 0.25312 | 0 | 45.3878 |  | 2029-09-01 | 12:21 | 44460 | 4.9272 | 0 | 194.1073 |  | 2006-09-01 | 12:21 | 44460 | 0.0013082 | 0 | 183.3428 |  | 2029-09-01 | 12:21 | 44460 | 1.5605 | 0 | 82.1193 |  | 2006-09-01 | 12:21 | 44460 | 0.00022877 | 0 | 43.6339 |  | 2028-01-01 | 12:21 | 44460 | 9.2974 | 0 | 191.5756 |  | 2007-01-01 | 12:21 | 44460 | 0.38303 | 0 | 185.5128 |  | 2028-01-01 | 12:21 | 44460 | 1.0091 | 0 | 29.6806 |  | 2007-01-01 | 12:21 | 44460 | 0.04575 | 0 | 32.555 |  | 2029-09-01 | 12:21 | 44460 | 27.799 | 0 | 85.8455 |  | 2029-09-01 | 12:21 | 44460 | 9.2635 | 0 | 58.5384 |  | 2029-09-01 | 12:21 | 44460 | 2.3684 | 0 | 40.0065 |  | 2006-09-01 | 12:21 | 44460 | 2.1121 | 0 | 39.444 |  | 2028-01-01 | 12:21 | 44460 | 18.0474 | 0 | 70.9207 |  | 2007-01-01 | 12:21 | 44460 | 3.2576 | 0 | 74.3574 |  | 2028-01-01 | 12:21 | 44460 | 2.1869 | 0 | 35.3883 |  | 2007-01-01 | 12:21 | 44460 | 0.29299 | 0 | 36.4237
| 2029-09-01 | 12:22 | 44520 | 310.064 | 0 | 272.5466 |  | 2029-09-01 | 12:22 | 44520 | 34.1023 | 0 | 204.0684 |  | 2006-09-01 | 12:22 | 44520 | 0.26093 | 0 | 185.4626 |  | 2029-09-01 | 12:22 | 44520 | 20.8467 | 0 | 137.3843 |  | 2006-09-01 | 12:22 | 44520 | 0.10593 | 0 | 92.0033 |  | 2028-01-01 | 12:22 | 44520 | 63.5813 | 0 | 204.8087 |  | 2007-01-01 | 12:22 | 44520 | 8.9268 | 0 | 186.7256 |  | 2028-01-01 | 12:22 | 44520 | 16.7657 | 0 | 70.9207 |  | 2007-01-01 | 12:22 | 44520 | 2.7159 | 0 | 74.3574 |  | 2029-09-01 | 12:22 | 44520 | 8.6984 | 0 | 195.7767 |  | 2006-09-01 | 12:22 | 44520 | 0.0056955 | 0 | 183.5322 |  | 2029-09-01 | 12:22 | 44520 | 3.7282 | 0 | 101.9131 |  | 2006-09-01 | 12:22 | 44520 | 0.0013986 | 0 | 59.3356 |  | 2028-01-01 | 12:22 | 44520 | 20.5962 | 0 | 194.1261 |  | 2007-01-01 | 12:22 | 44520 | 1.1047 | 0 | 185.5959 |  | 2028-01-01 | 12:22 | 44520 | 3.1768 | 0 | 41.8304 |  | 2007-01-01 | 12:22 | 44520 | 0.1901 | 0 | 45.3878 |  | 2029-09-01 | 12:22 | 44520 | 4.014 | 0 | 194.1073 |  | 2006-09-01 | 12:22 | 44520 | 0.00072129 | 0 | 183.3428 |  | 2029-09-01 | 12:22 | 44520 | 1.2712 | 0 | 82.1193 |  | 2006-09-01 | 12:22 | 44520 | 0.00012614 | 0 | 43.6339 |  | 2028-01-01 | 12:22 | 44520 | 7.746 | 0 | 191.5756 |  | 2007-01-01 | 12:22 | 44520 | 0.27017 | 0 | 185.5128 |  | 2028-01-01 | 12:22 | 44520 | 0.84204 | 0 | 29.6806 |  | 2007-01-01 | 12:22 | 44520 | 0.03227 | 0 | 32.555 |  | 2029-09-01 | 12:22 | 44520 | 26.1367 | 0 | 85.8455 |  | 2029-09-01 | 12:22 | 44520 | 8.4351 | 0 | 58.5384 |  | 2029-09-01 | 12:22 | 44520 | 2.0613 | 0 | 40.0065 |  | 2006-09-01 | 12:22 | 44520 | 1.8301 | 0 | 39.444 |  | 2028-01-01 | 12:22 | 44520 | 16.7657 | 0 | 70.9207 |  | 2007-01-01 | 12:22 | 44520 | 2.7159 | 0 | 74.3574 |  | 2028-01-01 | 12:22 | 44520 | 1.9525 | 0 | 35.3883 |  | 2007-01-01 | 12:22 | 44520 | 0.22687 | 0 | 36.4237
| 2029-09-01 | 12:23 | 44580 | 306.14 | 0 | 272.5466 |  | 2029-09-01 | 12:23 | 44580 | 30.6602 | 0 | 204.0684 |  | 2006-09-01 | 12:23 | 44580 | 0.18869 | 0 | 185.4626 |  | 2029-09-01 | 12:23 | 44580 | 18.7426 | 0 | 137.3843 |  | 2006-09-01 | 12:23 | 44580 | 0.076598 | 0 | 92.0033 |  | 2028-01-01 | 12:23 | 44580 | 58.9109 | 0 | 204.8087 |  | 2007-01-01 | 12:23 | 44580 | 7.4278 | 0 | 186.7256 |  | 2028-01-01 | 12:23 | 44580 | 15.52 | 0 | 70.9207 |  | 2007-01-01 | 12:23 | 44580 | 2.2599 | 0 | 74.3574 |  | 2029-09-01 | 12:23 | 44580 | 7.3415 | 0 | 195.7767 |  | 2006-09-01 | 12:23 | 44580 | 0.0034513 | 0 | 183.5322 |  | 2029-09-01 | 12:23 | 44580 | 3.1466 | 0 | 101.9131 |  | 2006-09-01 | 12:23 | 44580 | 0.00084753 | 0 | 59.3356 |  | 2028-01-01 | 12:23 | 44580 | 17.9842 | 0 | 194.1261 |  | 2007-01-01 | 12:23 | 44580 | 0.82698 | 0 | 185.5959 |  | 2028-01-01 | 12:23 | 44580 | 2.7755 | 0 | 41.8304 |  | 2007-01-01 | 12:23 | 44580 | 0.14231 | 0 | 45.3878 |  | 2029-09-01 | 12:23 | 44580 | 3.2677 | 0 | 194.1073 |  | 2006-09-01 | 12:23 | 44580 | 0.00039728 | 0 | 183.3428 |  | 2029-09-01 | 12:23 | 44580 | 1.0349 | 0 | 82.1193 |  | 2006-09-01 | 12:23 | 44580 | 6.9475e-05 | 0 | 43.6339 |  | 2028-01-01 | 12:23 | 44580 | 6.3955 | 0 | 191.5756 |  | 2007-01-01 | 12:23 | 44580 | 0.18998 | 0 | 185.5128 |  | 2028-01-01 | 12:23 | 44580 | 0.69624 | 0 | 29.6806 |  | 2007-01-01 | 12:23 | 44580 | 0.022692 | 0 | 32.555 |  | 2029-09-01 | 12:23 | 44580 | 24.5737 | 0 | 85.8455 |  | 2029-09-01 | 12:23 | 44580 | 7.6807 | 0 | 58.5384 |  | 2029-09-01 | 12:23 | 44580 | 1.794 | 0 | 40.0065 |  | 2006-09-01 | 12:23 | 44580 | 1.5857 | 0 | 39.444 |  | 2028-01-01 | 12:23 | 44580 | 15.52 | 0 | 70.9207 |  | 2007-01-01 | 12:23 | 44580 | 2.2599 | 0 | 74.3574 |  | 2028-01-01 | 12:23 | 44580 | 1.7327 | 0 | 35.3883 |  | 2007-01-01 | 12:23 | 44580 | 0.17535 | 0 | 36.4237
| 2029-09-01 | 12:24 | 44640 | 302.266 | 0 | 272.5466 |  | 2029-09-01 | 12:24 | 44640 | 27.5554 | 0 | 204.0684 |  | 2006-09-01 | 12:24 | 44640 | 0.13636 | 0 | 185.4626 |  | 2029-09-01 | 12:24 | 44640 | 16.8446 | 0 | 137.3843 |  | 2006-09-01 | 12:24 | 44640 | 0.055356 | 0 | 92.0033 |  | 2028-01-01 | 12:24 | 44640 | 54.4226 | 0 | 204.8087 |  | 2007-01-01 | 12:24 | 44640 | 6.1684 | 0 | 186.7256 |  | 2028-01-01 | 12:24 | 44640 | 14.3201 | 0 | 70.9207 |  | 2007-01-01 | 12:24 | 44640 | 1.8767 | 0 | 74.3574 |  | 2029-09-01 | 12:24 | 44640 | 6.1926 | 0 | 195.7767 |  | 2006-09-01 | 12:24 | 44640 | 0.0020894 | 0 | 183.5322 |  | 2029-09-01 | 12:24 | 44640 | 2.6542 | 0 | 101.9131 |  | 2006-09-01 | 12:24 | 44640 | 0.00051311 | 0 | 59.3356 |  | 2028-01-01 | 12:24 | 44640 | 15.6112 | 0 | 194.1261 |  | 2007-01-01 | 12:24 | 44640 | 0.61705 | 0 | 185.5959 |  | 2028-01-01 | 12:24 | 44640 | 2.4101 | 0 | 41.8304 |  | 2007-01-01 | 12:24 | 44640 | 0.10619 | 0 | 45.3878 |  | 2029-09-01 | 12:24 | 44640 | 2.6583 | 0 | 194.1073 |  | 2006-09-01 | 12:24 | 44640 | 0.00021859 | 0 | 183.3428 |  | 2029-09-01 | 12:24 | 44640 | 0.84189 | 0 | 82.1193 |  | 2006-09-01 | 12:24 | 44640 | 3.8226e-05 | 0 | 43.6339 |  | 2028-01-01 | 12:24 | 44640 | 5.2408 | 0 | 191.5756 |  | 2007-01-01 | 12:24 | 44640 | 0.13318 | 0 | 185.5128 |  | 2028-01-01 | 12:24 | 44640 | 0.57129 | 0 | 29.6806 |  | 2007-01-01 | 12:24 | 44640 | 0.015908 | 0 | 32.555 |  | 2029-09-01 | 12:24 | 44640 | 23.1042 | 0 | 85.8455 |  | 2029-09-01 | 12:24 | 44640 | 6.9938 | 0 | 58.5384 |  | 2029-09-01 | 12:24 | 44640 | 1.5614 | 0 | 40.0065 |  | 2006-09-01 | 12:24 | 44640 | 1.374 | 0 | 39.444 |  | 2028-01-01 | 12:24 | 44640 | 14.3201 | 0 | 70.9207 |  | 2007-01-01 | 12:24 | 44640 | 1.8767 | 0 | 74.3574 |  | 2028-01-01 | 12:24 | 44640 | 1.5282 | 0 | 35.3883 |  | 2007-01-01 | 12:24 | 44640 | 0.13528 | 0 | 36.4237
| 2029-09-01 | 12:25 | 44700 | 298.441 | 0 | 272.5466 |  | 2029-09-01 | 12:25 | 44700 | 24.7559 | 0 | 204.0684 |  | 2006-09-01 | 12:25 | 44700 | 0.098484 | 0 | 185.4626 |  | 2029-09-01 | 12:25 | 44700 | 15.1332 | 0 | 137.3843 |  | 2006-09-01 | 12:25 | 44700 | 0.03998 | 0 | 92.0033 |  | 2028-01-01 | 12:25 | 44700 | 50.1762 | 0 | 204.8087 |  | 2007-01-01 | 12:25 | 44700 | 5.1125 | 0 | 186.7256 |  | 2028-01-01 | 12:25 | 44700 | 13.184 | 0 | 70.9207 |  | 2007-01-01 | 12:25 | 44700 | 1.5554 | 0 | 74.3574 |  | 2029-09-01 | 12:25 | 44700 | 5.2204 | 0 | 195.7767 |  | 2006-09-01 | 12:25 | 44700 | 0.0012638 | 0 | 183.5322 |  | 2029-09-01 | 12:25 | 44700 | 2.2375 | 0 | 101.9131 |  | 2006-09-01 | 12:25 | 44700 | 0.00031036 | 0 | 59.3356 |  | 2028-01-01 | 12:25 | 44700 | 13.4997 | 0 | 194.1261 |  | 2007-01-01 | 12:25 | 44700 | 0.45892 | 0 | 185.5959 |  | 2028-01-01 | 12:25 | 44700 | 2.0847 | 0 | 41.8304 |  | 2007-01-01 | 12:25 | 44700 | 0.078975 | 0 | 45.3878 |  | 2029-09-01 | 12:25 | 44700 | 2.161 | 0 | 194.1073 |  | 2006-09-01 | 12:25 | 44700 | 0.00012014 | 0 | 183.3428 |  | 2029-09-01 | 12:25 | 44700 | 0.6844 | 0 | 82.1193 |  | 2006-09-01 | 12:25 | 44700 | 2.101e-05 | 0 | 43.6339 |  | 2028-01-01 | 12:25 | 44700 | 4.2742 | 0 | 191.5756 |  | 2007-01-01 | 12:25 | 44700 | 0.093074 | 0 | 185.5128 |  | 2028-01-01 | 12:25 | 44700 | 0.46647 | 0 | 29.6806 |  | 2007-01-01 | 12:25 | 44700 | 0.011117 | 0 | 32.555 |  | 2029-09-01 | 12:25 | 44700 | 21.7225 | 0 | 85.8455 |  | 2029-09-01 | 12:25 | 44700 | 6.3684 | 0 | 58.5384 |  | 2029-09-01 | 12:25 | 44700 | 1.3589 | 0 | 40.0065 |  | 2006-09-01 | 12:25 | 44700 | 1.1905 | 0 | 39.444 |  | 2028-01-01 | 12:25 | 44700 | 13.184 | 0 | 70.9207 |  | 2007-01-01 | 12:25 | 44700 | 1.5554 | 0 | 74.3574 |  | 2028-01-01 | 12:25 | 44700 | 1.3392 | 0 | 35.3883 |  | 2007-01-01 | 12:25 | 44700 | 0.10418 | 0 | 36.4237
| 2029-09-01 | 12:26 | 44760 | 294.664 | 0 | 272.5466 |  | 2029-09-01 | 12:26 | 44760 | 22.2325 | 0 | 204.0684 |  | 2006-09-01 | 12:26 | 44760 | 0.071083 | 0 | 185.4626 |  | 2029-09-01 | 12:26 | 44760 | 13.5907 | 0 | 137.3843 |  | 2006-09-01 | 12:26 | 44760 | 0.028856 | 0 | 92.0033 |  | 2028-01-01 | 12:26 | 44760 | 46.1899 | 0 | 204.8087 |  | 2007-01-01 | 12:26 | 44760 | 4.229 | 0 | 186.7256 |  | 2028-01-01 | 12:26 | 44760 | 12.1177 | 0 | 70.9207 |  | 2007-01-01 | 12:26 | 44760 | 1.2867 | 0 | 74.3574 |  | 2029-09-01 | 12:26 | 44760 | 4.3982 | 0 | 195.7767 |  | 2006-09-01 | 12:26 | 44760 | 0.00076376 | 0 | 183.5322 |  | 2029-09-01 | 12:26 | 44760 | 1.8851 | 0 | 101.9131 |  | 2006-09-01 | 12:26 | 44760 | 0.00018756 | 0 | 59.3356 |  | 2028-01-01 | 12:26 | 44760 | 11.6416 | 0 | 194.1261 |  | 2007-01-01 | 12:26 | 44760 | 0.34023 | 0 | 185.5959 |  | 2028-01-01 | 12:26 | 44760 | 1.798 | 0 | 41.8304 |  | 2007-01-01 | 12:26 | 44760 | 0.05855 | 0 | 45.3878 |  | 2029-09-01 | 12:26 | 44760 | 1.7555 | 0 | 194.1073 |  | 2006-09-01 | 12:26 | 44760 | 6.5967e-05 | 0 | 183.3428 |  | 2029-09-01 | 12:26 | 44760 | 0.55597 | 0 | 82.1193 |  | 2006-09-01 | 12:26 | 44760 | 1.1536e-05 | 0 | 43.6339 |  | 2028-01-01 | 12:26 | 44760 | 3.474 | 0 | 191.5756 |  | 2007-01-01 | 12:26 | 44760 | 0.064839 | 0 | 185.5128 |  | 2028-01-01 | 12:26 | 44760 | 0.37954 | 0 | 29.6806 |  | 2007-01-01 | 12:26 | 44760 | 0.0077445 | 0 | 32.555 |  | 2029-09-01 | 12:26 | 44760 | 20.4235 | 0 | 85.8455 |  | 2029-09-01 | 12:26 | 44760 | 5.7988 | 0 | 58.5384 |  | 2029-09-01 | 12:26 | 44760 | 1.1826 | 0 | 40.0065 |  | 2006-09-01 | 12:26 | 44760 | 1.0315 | 0 | 39.444 |  | 2028-01-01 | 12:26 | 44760 | 12.1177 | 0 | 70.9207 |  | 2007-01-01 | 12:26 | 44760 | 1.2867 | 0 | 74.3574 |  | 2028-01-01 | 12:26 | 44760 | 1.1677 | 0 | 35.3883 |  | 2007-01-01 | 12:26 | 44760 | 0.080081 | 0 | 36.4237
| 2029-09-01 | 12:27 | 44820 | 290.934 | 0 | 272.5466 |  | 2029-09-01 | 12:27 | 44820 | 19.959 | 0 | 204.0684 |  | 2006-09-01 | 12:27 | 44820 | 0.051274 | 0 | 185.4626 |  | 2029-09-01 | 12:27 | 44820 | 12.2009 | 0 | 137.3843 |  | 2006-09-01 | 12:27 | 44820 | 0.020815 | 0 | 92.0033 |  | 2028-01-01 | 12:27 | 44820 | 42.4699 | 0 | 204.8087 |  | 2007-01-01 | 12:27 | 44820 | 3.4915 | 0 | 186.7256 |  | 2028-01-01 | 12:27 | 44820 | 11.1233 | 0 | 70.9207 |  | 2007-01-01 | 12:27 | 44820 | 1.0623 | 0 | 74.3574 |  | 2029-09-01 | 12:27 | 44820 | 3.7033 | 0 | 195.7767 |  | 2006-09-01 | 12:27 | 44820 | 0.00046113 | 0 | 183.5322 |  | 2029-09-01 | 12:27 | 44820 | 1.5873 | 0 | 101.9131 |  | 2006-09-01 | 12:27 | 44820 | 0.00011324 | 0 | 59.3356 |  | 2028-01-01 | 12:27 | 44820 | 10.0192 | 0 | 194.1261 |  | 2007-01-01 | 12:27 | 44820 | 0.25144 | 0 | 185.5959 |  | 2028-01-01 | 12:27 | 44820 | 1.5476 | 0 | 41.8304 |  | 2007-01-01 | 12:27 | 44820 | 0.043271 | 0 | 45.3878 |  | 2029-09-01 | 12:27 | 44820 | 1.425 | 0 | 194.1073 |  | 2006-09-01 | 12:27 | 44820 | 3.6183e-05 | 0 | 183.3428 |  | 2029-09-01 | 12:27 | 44820 | 0.45133 | 0 | 82.1193 |  | 2006-09-01 | 12:27 | 44820 | 6.3276e-06 | 0 | 43.6339 |  | 2028-01-01 | 12:27 | 44820 | 2.8168 | 0 | 191.5756 |  | 2007-01-01 | 12:27 | 44820 | 0.045027 | 0 | 185.5128 |  | 2028-01-01 | 12:27 | 44820 | 0.30804 | 0 | 29.6806 |  | 2007-01-01 | 12:27 | 44820 | 0.0053781 | 0 | 32.555 |  | 2029-09-01 | 12:27 | 44820 | 19.2021 | 0 | 85.8455 |  | 2029-09-01 | 12:27 | 44820 | 5.2802 | 0 | 58.5384 |  | 2029-09-01 | 12:27 | 44820 | 1.0293 | 0 | 40.0065 |  | 2006-09-01 | 12:27 | 44820 | 0.89375 | 0 | 39.444 |  | 2028-01-01 | 12:27 | 44820 | 11.1233 | 0 | 70.9207 |  | 2007-01-01 | 12:27 | 44820 | 1.0623 | 0 | 74.3574 |  | 2028-01-01 | 12:27 | 44820 | 1.0139 | 0 | 35.3883 |  | 2007-01-01 | 12:27 | 44820 | 0.061447 | 0 | 36.4237
| 2029-09-01 | 12:28 | 44880 | 287.251 | 0 | 272.5466 |  | 2029-09-01 | 12:28 | 44880 | 17.9114 | 0 | 204.0684 |  | 2006-09-01 | 12:28 | 44880 | 0.036962 | 0 | 185.4626 |  | 2029-09-01 | 12:28 | 44880 | 10.9492 | 0 | 137.3843 |  | 2006-09-01 | 12:28 | 44880 | 0.015005 | 0 | 92.0033 |  | 2028-01-01 | 12:28 | 44880 | 39.0144 | 0 | 204.8087 |  | 2007-01-01 | 12:28 | 44880 | 2.877 | 0 | 186.7256 |  | 2028-01-01 | 12:28 | 44880 | 10.2007 | 0 | 70.9207 |  | 2007-01-01 | 12:28 | 44880 | 0.8753 | 0 | 74.3574 |  | 2029-09-01 | 12:28 | 44880 | 3.1163 | 0 | 195.7767 |  | 2006-09-01 | 12:28 | 44880 | 0.00027817 | 0 | 183.5322 |  | 2029-09-01 | 12:28 | 44880 | 1.3357 | 0 | 101.9131 |  | 2006-09-01 | 12:28 | 44880 | 6.831e-05 | 0 | 59.3356 |  | 2028-01-01 | 12:28 | 44880 | 8.6107 | 0 | 194.1261 |  | 2007-01-01 | 12:28 | 44880 | 0.18525 | 0 | 185.5959 |  | 2028-01-01 | 12:28 | 44880 | 1.3301 | 0 | 41.8304 |  | 2007-01-01 | 12:28 | 44880 | 0.031879 | 0 | 45.3878 |  | 2029-09-01 | 12:28 | 44880 | 1.156 | 0 | 194.1073 |  | 2006-09-01 | 12:28 | 44880 | 1.9826e-05 | 0 | 183.3428 |  | 2029-09-01 | 12:28 | 44880 | 0.36612 | 0 | 82.1193 |  | 2006-09-01 | 12:28 | 44880 | 3.4671e-06 | 0 | 43.6339 |  | 2028-01-01 | 12:28 | 44880 | 2.2801 | 0 | 191.5756 |  | 2007-01-01 | 12:28 | 44880 | 0.031169 | 0 | 185.5128 |  | 2028-01-01 | 12:28 | 44880 | 0.24956 | 0 | 29.6806 |  | 2007-01-01 | 12:28 | 44880 | 0.0037229 | 0 | 32.555 |  | 2029-09-01 | 12:28 | 44880 | 18.0537 | 0 | 85.8455 |  | 2029-09-01 | 12:28 | 44880 | 4.808 | 0 | 58.5384 |  | 2029-09-01 | 12:28 | 44880 | 0.8958 | 0 | 40.0065 |  | 2006-09-01 | 12:28 | 44880 | 0.77437 | 0 | 39.444 |  | 2028-01-01 | 12:28 | 44880 | 10.2007 | 0 | 70.9207 |  | 2007-01-01 | 12:28 | 44880 | 0.8753 | 0 | 74.3574 |  | 2028-01-01 | 12:28 | 44880 | 0.87745 | 0 | 35.3883 |  | 2007-01-01 | 12:28 | 44880 | 0.047064 | 0 | 36.4237
| 2029-09-01 | 12:29 | 44940 | 283.615 | 0 | 272.5466 |  | 2029-09-01 | 12:29 | 44940 | 16.0679 | 0 | 204.0684 |  | 2006-09-01 | 12:29 | 44940 | 0.026628 | 0 | 185.4626 |  | 2029-09-01 | 12:29 | 44940 | 9.8223 | 0 | 137.3843 |  | 2006-09-01 | 12:29 | 44940 | 0.01081 | 0 | 92.0033 |  | 2028-01-01 | 12:29 | 44940 | 35.8162 | 0 | 204.8087 |  | 2007-01-01 | 12:29 | 44940 | 2.366 | 0 | 186.7256 |  | 2028-01-01 | 12:29 | 44940 | 9.3479 | 0 | 70.9207 |  | 2007-01-01 | 12:29 | 44940 | 0.71985 | 0 | 74.3574 |  | 2029-09-01 | 12:29 | 44940 | 2.6208 | 0 | 195.7767 |  | 2006-09-01 | 12:29 | 44940 | 0.00016765 | 0 | 183.5322 |  | 2029-09-01 | 12:29 | 44940 | 1.1233 | 0 | 101.9131 |  | 2006-09-01 | 12:29 | 44940 | 4.117e-05 | 0 | 59.3356 |  | 2028-01-01 | 12:29 | 44940 | 7.3928 | 0 | 194.1261 |  | 2007-01-01 | 12:29 | 44940 | 0.13606 | 0 | 185.5959 |  | 2028-01-01 | 12:29 | 44940 | 1.142 | 0 | 41.8304 |  | 2007-01-01 | 12:29 | 44940 | 0.023414 | 0 | 45.3878 |  | 2029-09-01 | 12:29 | 44940 | 0.93709 | 0 | 194.1073 |  | 2006-09-01 | 12:29 | 44940 | 1.0852e-05 | 0 | 183.3428 |  | 2029-09-01 | 12:29 | 44940 | 0.29678 | 0 | 82.1193 |  | 2006-09-01 | 12:29 | 44940 | 1.8977e-06 | 0 | 43.6339 |  | 2028-01-01 | 12:29 | 44940 | 1.8434 | 0 | 191.5756 |  | 2007-01-01 | 12:29 | 44940 | 0.021506 | 0 | 185.5128 |  | 2028-01-01 | 12:29 | 44940 | 0.20193 | 0 | 29.6806 |  | 2007-01-01 | 12:29 | 44940 | 0.0025687 | 0 | 32.555 |  | 2029-09-01 | 12:29 | 44940 | 16.974 | 0 | 85.8455 |  | 2029-09-01 | 12:29 | 44940 | 4.378 | 0 | 58.5384 |  | 2029-09-01 | 12:29 | 44940 | 0.77963 | 0 | 40.0065 |  | 2006-09-01 | 12:29 | 44940 | 0.67092 | 0 | 39.444 |  | 2028-01-01 | 12:29 | 44940 | 9.3479 | 0 | 70.9207 |  | 2007-01-01 | 12:29 | 44940 | 0.71985 | 0 | 74.3574 |  | 2028-01-01 | 12:29 | 44940 | 0.75728 | 0 | 35.3883 |  | 2007-01-01 | 12:29 | 44940 | 0.035983 | 0 | 36.4237
| 2029-09-01 | 12:30 | 45000 | 280.024 | 0 | 272.5466 |  | 2029-09-01 | 12:30 | 45000 | 14.4088 | 0 | 204.0684 |  | 2006-09-01 | 12:30 | 45000 | 0.019172 | 0 | 185.4626 |  | 2029-09-01 | 12:30 | 45000 | 8.8081 | 0 | 137.3843 |  | 2006-09-01 | 12:30 | 45000 | 0.0077829 | 0 | 92.0033 |  | 2028-01-01 | 12:30 | 45000 | 32.8641 | 0 | 204.8087 |  | 2007-01-01 | 12:30 | 45000 | 1.9421 | 0 | 186.7256 |  | 2028-01-01 | 12:30 | 45000 | 8.5621 | 0 | 70.9207 |  | 2007-01-01 | 12:30 | 45000 | 0.59087 | 0 | 74.3574 |  | 2029-09-01 | 12:30 | 45000 | 2.2028 | 0 | 195.7767 |  | 2006-09-01 | 12:30 | 45000 | 0.00010095 | 0 | 183.5322 |  | 2029-09-01 | 12:30 | 45000 | 0.94412 | 0 | 101.9131 |  | 2006-09-01 | 12:30 | 45000 | 2.479e-05 | 0 | 59.3356 |  | 2028-01-01 | 12:30 | 45000 | 6.3428 | 0 | 194.1261 |  | 2007-01-01 | 12:30 | 45000 | 0.099621 | 0 | 185.5959 |  | 2028-01-01 | 12:30 | 45000 | 0.97981 | 0 | 41.8304 |  | 2007-01-01 | 12:30 | 45000 | 0.017144 | 0 | 45.3878 |  | 2029-09-01 | 12:30 | 45000 | 0.75909 | 0 | 194.1073 |  | 2006-09-01 | 12:30 | 45000 | 5.9338e-06 | 0 | 183.3428 |  | 2029-09-01 | 12:30 | 45000 | 0.24041 | 0 | 82.1193 |  | 2006-09-01 | 12:30 | 45000 | 1.0377e-06 | 0 | 43.6339 |  | 2028-01-01 | 12:30 | 45000 | 1.4892 | 0 | 191.5756 |  | 2007-01-01 | 12:30 | 45000 | 0.014791 | 0 | 185.5128 |  | 2028-01-01 | 12:30 | 45000 | 0.16325 | 0 | 29.6806 |  | 2007-01-01 | 12:30 | 45000 | 0.0017667 | 0 | 32.555 |  | 2029-09-01 | 12:30 | 45000 | 15.9588 | 0 | 85.8455 |  | 2029-09-01 | 12:30 | 45000 | 3.9864 | 0 | 58.5384 |  | 2029-09-01 | 12:30 | 45000 | 0.67852 | 0 | 40.0065 |  | 2006-09-01 | 12:30 | 45000 | 0.58129 | 0 | 39.444 |  | 2028-01-01 | 12:30 | 45000 | 8.5621 | 0 | 70.9207 |  | 2007-01-01 | 12:30 | 45000 | 0.59087 | 0 | 74.3574 |  | 2028-01-01 | 12:30 | 45000 | 0.6521 | 0 | 35.3883 |  | 2007-01-01 | 12:30 | 45000 | 0.027461 | 0 | 36.4237
| 2029-09-01 | 12:31 | 45060 | 276.478 | 0 | 272.5466 |  | 2029-09-01 | 12:31 | 45060 | 12.9162 | 0 | 204.0684 |  | 2006-09-01 | 12:31 | 45060 | 0.013795 | 0 | 185.4626 |  | 2029-09-01 | 12:31 | 45060 | 7.8956 | 0 | 137.3843 |  | 2006-09-01 | 12:31 | 45060 | 0.0056 | 0 | 92.0033 |  | 2028-01-01 | 12:31 | 45060 | 30.145 | 0 | 204.8087 |  | 2007-01-01 | 12:31 | 45060 | 1.591 | 0 | 186.7256 |  | 2028-01-01 | 12:31 | 45060 | 7.8395 | 0 | 70.9207 |  | 2007-01-01 | 12:31 | 45060 | 0.48406 | 0 | 74.3574 |  | 2029-09-01 | 12:31 | 45060 | 1.8503 | 0 | 195.7767 |  | 2006-09-01 | 12:31 | 45060 | 6.073e-05 | 0 | 183.5322 |  | 2029-09-01 | 12:31 | 45060 | 0.79305 | 0 | 101.9131 |  | 2006-09-01 | 12:31 | 45060 | 1.4914e-05 | 0 | 59.3356 |  | 2028-01-01 | 12:31 | 45060 | 5.4395 | 0 | 194.1261 |  | 2007-01-01 | 12:31 | 45060 | 0.07272 | 0 | 185.5959 |  | 2028-01-01 | 12:31 | 45060 | 0.84026 | 0 | 41.8304 |  | 2007-01-01 | 12:31 | 45060 | 0.012514 | 0 | 45.3878 |  | 2029-09-01 | 12:31 | 45060 | 0.61446 | 0 | 194.1073 |  | 2006-09-01 | 12:31 | 45060 | 3.2412e-06 | 0 | 183.3428 |  | 2029-09-01 | 12:31 | 45060 | 0.1946 | 0 | 82.1193 |  | 2006-09-01 | 12:31 | 45060 | 5.6682e-07 | 0 | 43.6339 |  | 2028-01-01 | 12:31 | 45060 | 1.2024 | 0 | 191.5756 |  | 2007-01-01 | 12:31 | 45060 | 0.010139 | 0 | 185.5128 |  | 2028-01-01 | 12:31 | 45060 | 0.1319 | 0 | 29.6806 |  | 2007-01-01 | 12:31 | 45060 | 0.001211 | 0 | 32.555 |  | 2029-09-01 | 12:31 | 45060 | 15.0043 | 0 | 85.8455 |  | 2029-09-01 | 12:31 | 45060 | 3.6299 | 0 | 58.5384 |  | 2029-09-01 | 12:31 | 45060 | 0.59053 | 0 | 40.0065 |  | 2006-09-01 | 12:31 | 45060 | 0.50362 | 0 | 39.444 |  | 2028-01-01 | 12:31 | 45060 | 7.8395 | 0 | 70.9207 |  | 2007-01-01 | 12:31 | 45060 | 0.48406 | 0 | 74.3574 |  | 2028-01-01 | 12:31 | 45060 | 0.56049 | 0 | 35.3883 |  | 2007-01-01 | 12:31 | 45060 | 0.020921 | 0 | 36.4237
| 2029-09-01 | 12:32 | 45120 | 272.977 | 0 | 272.5466 |  | 2029-09-01 | 12:32 | 45120 | 11.5739 | 0 | 204.0684 |  | 2006-09-01 | 12:32 | 45120 | 0.0099194 | 0 | 185.4626 |  | 2029-09-01 | 12:32 | 45120 | 7.0751 | 0 | 137.3843 |  | 2006-09-01 | 12:32 | 45120 | 0.0040268 | 0 | 92.0033 |  | 2028-01-01 | 12:32 | 45120 | 27.6446 | 0 | 204.8087 |  | 2007-01-01 | 12:32 | 45120 | 1.301 | 0 | 186.7256 |  | 2028-01-01 | 12:32 | 45120 | 7.1762 | 0 | 70.9207 |  | 2007-01-01 | 12:32 | 45120 | 0.39581 | 0 | 74.3574 |  | 2029-09-01 | 12:32 | 45120 | 1.5533 | 0 | 195.7767 |  | 2006-09-01 | 12:32 | 45120 | 3.6502e-05 | 0 | 183.5322 |  | 2029-09-01 | 12:32 | 45120 | 0.66575 | 0 | 101.9131 |  | 2006-09-01 | 12:32 | 45120 | 8.9639e-06 | 0 | 59.3356 |  | 2028-01-01 | 12:32 | 45120 | 4.6637 | 0 | 194.1261 |  | 2007-01-01 | 12:32 | 45120 | 0.052923 | 0 | 185.5959 |  | 2028-01-01 | 12:32 | 45120 | 0.7204 | 0 | 41.8304 |  | 2007-01-01 | 12:32 | 45120 | 0.0091074 | 0 | 45.3878 |  | 2029-09-01 | 12:32 | 45120 | 0.49704 | 0 | 194.1073 |  | 2006-09-01 | 12:32 | 45120 | 1.7686e-06 | 0 | 183.3428 |  | 2029-09-01 | 12:32 | 45120 | 0.15741 | 0 | 82.1193 |  | 2006-09-01 | 12:32 | 45120 | 3.0929e-07 | 0 | 43.6339 |  | 2028-01-01 | 12:32 | 45120 | 0.97056 | 0 | 191.5756 |  | 2007-01-01 | 12:32 | 45120 | 0.0069274 | 0 | 185.5128 |  | 2028-01-01 | 12:32 | 45120 | 0.10654 | 0 | 29.6806 |  | 2007-01-01 | 12:32 | 45120 | 0.00082743 | 0 | 32.555 |  | 2029-09-01 | 12:32 | 45120 | 14.107 | 0 | 85.8455 |  | 2029-09-01 | 12:32 | 45120 | 3.3052 | 0 | 58.5384 |  | 2029-09-01 | 12:32 | 45120 | 0.51394 | 0 | 40.0065 |  | 2006-09-01 | 12:32 | 45120 | 0.43632 | 0 | 39.444 |  | 2028-01-01 | 12:32 | 45120 | 7.1762 | 0 | 70.9207 |  | 2007-01-01 | 12:32 | 45120 | 0.39581 | 0 | 74.3574 |  | 2028-01-01 | 12:32 | 45120 | 0.48102 | 0 | 35.3883 |  | 2007-01-01 | 12:32 | 45120 | 0.015909 | 0 | 36.4237
| 2029-09-01 | 12:33 | 45180 | 269.52 | 0 | 272.5466 |  | 2029-09-01 | 12:33 | 45180 | 10.3673 | 0 | 204.0684 |  | 2006-09-01 | 12:33 | 45180 | 0.0071284 | 0 | 185.4626 |  | 2029-09-01 | 12:33 | 45180 | 6.3375 | 0 | 137.3843 |  | 2006-09-01 | 12:33 | 45180 | 0.0028938 | 0 | 92.0033 |  | 2028-01-01 | 12:33 | 45180 | 25.3483 | 0 | 204.8087 |  | 2007-01-01 | 12:33 | 45180 | 1.0617 | 0 | 186.7256 |  | 2028-01-01 | 12:33 | 45180 | 6.5683 | 0 | 70.9207 |  | 2007-01-01 | 12:33 | 45180 | 0.32302 | 0 | 74.3574 |  | 2029-09-01 | 12:33 | 45180 | 1.3032 | 0 | 195.7767 |  | 2006-09-01 | 12:33 | 45180 | 2.192e-05 | 0 | 183.5322 |  | 2029-09-01 | 12:33 | 45180 | 0.55855 | 0 | 101.9131 |  | 2006-09-01 | 12:33 | 45180 | 5.383e-06 | 0 | 59.3356 |  | 2028-01-01 | 12:33 | 45180 | 3.9982 | 0 | 194.1261 |  | 2007-01-01 | 12:33 | 45180 | 0.038399 | 0 | 185.5959 |  | 2028-01-01 | 12:33 | 45180 | 0.61756 | 0 | 41.8304 |  | 2007-01-01 | 12:33 | 45180 | 0.0066081 | 0 | 45.3878 |  | 2029-09-01 | 12:33 | 45180 | 0.40176 | 0 | 194.1073 |  | 2006-09-01 | 12:33 | 45180 | 9.6409e-07 | 0 | 183.3428 |  | 2029-09-01 | 12:33 | 45180 | 0.12724 | 0 | 82.1193 |  | 2006-09-01 | 12:33 | 45180 | 1.686e-07 | 0 | 43.6339 |  | 2028-01-01 | 12:33 | 45180 | 0.78333 | 0 | 191.5756 |  | 2007-01-01 | 12:33 | 45180 | 0.0047172 | 0 | 185.5128 |  | 2028-01-01 | 12:33 | 45180 | 0.086041 | 0 | 29.6806 |  | 2007-01-01 | 12:33 | 45180 | 0.00056343 | 0 | 32.555 |  | 2029-09-01 | 12:33 | 45180 | 13.2632 | 0 | 85.8455 |  | 2029-09-01 | 12:33 | 45180 | 3.0096 | 0 | 58.5384 |  | 2029-09-01 | 12:33 | 45180 | 0.44729 | 0 | 40.0065 |  | 2006-09-01 | 12:33 | 45180 | 0.37801 | 0 | 39.444 |  | 2028-01-01 | 12:33 | 45180 | 6.5683 | 0 | 70.9207 |  | 2007-01-01 | 12:33 | 45180 | 0.32302 | 0 | 74.3574 |  | 2028-01-01 | 12:33 | 45180 | 0.41229 | 0 | 35.3883 |  | 2007-01-01 | 12:33 | 45180 | 0.012077 | 0 | 36.4237
| 2029-09-01 | 12:34 | 45240 | 266.107 | 0 | 272.5466 |  | 2029-09-01 | 12:34 | 45240 | 9.283 | 0 | 204.0684 |  | 2006-09-01 | 12:34 | 45240 | 0.0051195 | 0 | 185.4626 |  | 2029-09-01 | 12:34 | 45240 | 5.6747 | 0 | 137.3843 |  | 2006-09-01 | 12:34 | 45240 | 0.0020783 | 0 | 92.0033 |  | 2028-01-01 | 12:34 | 45240 | 23.2417 | 0 | 204.8087 |  | 2007-01-01 | 12:34 | 45240 | 0.86482 | 0 | 186.7256 |  | 2028-01-01 | 12:34 | 45240 | 6.0117 | 0 | 70.9207 |  | 2007-01-01 | 12:34 | 45240 | 0.26312 | 0 | 74.3574 |  | 2029-09-01 | 12:34 | 45240 | 1.0927 | 0 | 195.7767 |  | 2006-09-01 | 12:34 | 45240 | 1.3152e-05 | 0 | 183.5322 |  | 2029-09-01 | 12:34 | 45240 | 0.46833 | 0 | 101.9131 |  | 2006-09-01 | 12:34 | 45240 | 3.2297e-06 | 0 | 59.3356 |  | 2028-01-01 | 12:34 | 45240 | 3.4276 | 0 | 194.1261 |  | 2007-01-01 | 12:34 | 45240 | 0.027778 | 0 | 185.5959 |  | 2028-01-01 | 12:34 | 45240 | 0.52941 | 0 | 41.8304 |  | 2007-01-01 | 12:34 | 45240 | 0.0047802 | 0 | 45.3878 |  | 2029-09-01 | 12:34 | 45240 | 0.32452 | 0 | 194.1073 |  | 2006-09-01 | 12:34 | 45240 | 5.2499e-07 | 0 | 183.3428 |  | 2029-09-01 | 12:34 | 45240 | 0.10278 | 0 | 82.1193 |  | 2006-09-01 | 12:34 | 45240 | 9.1809e-08 | 0 | 43.6339 |  | 2028-01-01 | 12:34 | 45240 | 0.63222 | 0 | 191.5756 |  | 2007-01-01 | 12:34 | 45240 | 0.0032013 | 0 | 185.5128 |  | 2028-01-01 | 12:34 | 45240 | 0.069484 | 0 | 29.6806 |  | 2007-01-01 | 12:34 | 45240 | 0.00038237 | 0 | 32.555 |  | 2029-09-01 | 12:34 | 45240 | 12.4699 | 0 | 85.8455 |  | 2029-09-01 | 12:34 | 45240 | 2.7404 | 0 | 58.5384 |  | 2029-09-01 | 12:34 | 45240 | 0.38928 | 0 | 40.0065 |  | 2006-09-01 | 12:34 | 45240 | 0.32749 | 0 | 39.444 |  | 2028-01-01 | 12:34 | 45240 | 6.0117 | 0 | 70.9207 |  | 2007-01-01 | 12:34 | 45240 | 0.26312 | 0 | 74.3574 |  | 2028-01-01 | 12:34 | 45240 | 0.35303 | 0 | 35.3883 |  | 2007-01-01 | 12:34 | 45240 | 0.0091514 | 0 | 36.4237
| 2029-09-01 | 12:35 | 45300 | 262.736 | 0 | 272.5466 |  | 2029-09-01 | 12:35 | 45300 | 8.309 | 0 | 204.0684 |  | 2006-09-01 | 12:35 | 45300 | 0.0036745 | 0 | 185.4626 |  | 2029-09-01 | 12:35 | 45300 | 5.0793 | 0 | 137.3843 |  | 2006-09-01 | 12:35 | 45300 | 0.0014917 | 0 | 92.0033 |  | 2028-01-01 | 12:35 | 45300 | 21.3105 | 0 | 204.8087 |  | 2007-01-01 | 12:35 | 45300 | 0.7031 | 0 | 186.7256 |  | 2028-01-01 | 12:35 | 45300 | 5.5025 | 0 | 70.9207 |  | 2007-01-01 | 12:35 | 45300 | 0.21391 | 0 | 74.3574 |  | 2029-09-01 | 12:35 | 45300 | 0.91565 | 0 | 195.7767 |  | 2006-09-01 | 12:35 | 45300 | 7.8836e-06 | 0 | 183.5322 |  | 2029-09-01 | 12:35 | 45300 | 0.39245 | 0 | 101.9131 |  | 2006-09-01 | 12:35 | 45300 | 1.936e-06 | 0 | 59.3356 |  | 2028-01-01 | 12:35 | 45300 | 2.9389 | 0 | 194.1261 |  | 2007-01-01 | 12:35 | 45300 | 0.020034 | 0 | 185.5959 |  | 2028-01-01 | 12:35 | 45300 | 0.4539 | 0 | 41.8304 |  | 2007-01-01 | 12:35 | 45300 | 0.0034477 | 0 | 45.3878 |  | 2029-09-01 | 12:35 | 45300 | 0.26194 | 0 | 194.1073 |  | 2006-09-01 | 12:35 | 45300 | 2.8559e-07 | 0 | 183.3428 |  | 2029-09-01 | 12:35 | 45300 | 0.08296 | 0 | 82.1193 |  | 2006-09-01 | 12:35 | 45300 | 4.9943e-08 | 0 | 43.6339 |  | 2028-01-01 | 12:35 | 45300 | 0.51032 | 0 | 191.5756 |  | 2007-01-01 | 12:35 | 45300 | 0.0021651 | 0 | 185.5128 |  | 2028-01-01 | 12:35 | 45300 | 0.056118 | 0 | 29.6806 |  | 2007-01-01 | 12:35 | 45300 | 0.00025861 | 0 | 32.555 |  | 2029-09-01 | 12:35 | 45300 | 11.7241 | 0 | 85.8455 |  | 2029-09-01 | 12:35 | 45300 | 2.4953 | 0 | 58.5384 |  | 2029-09-01 | 12:35 | 45300 | 0.3388 | 0 | 40.0065 |  | 2006-09-01 | 12:35 | 45300 | 0.28372 | 0 | 39.444 |  | 2028-01-01 | 12:35 | 45300 | 5.5025 | 0 | 70.9207 |  | 2007-01-01 | 12:35 | 45300 | 0.21391 | 0 | 74.3574 |  | 2028-01-01 | 12:35 | 45300 | 0.30203 | 0 | 35.3883 |  | 2007-01-01 | 12:35 | 45300 | 0.0069222 | 0 | 36.4237
| 2029-09-01 | 12:36 | 45360 | 259.408 | 0 | 272.5466 |  | 2029-09-01 | 12:36 | 45360 | 7.4345 | 0 | 204.0684 |  | 2006-09-01 | 12:36 | 45360 | 0.0026357 | 0 | 185.4626 |  | 2029-09-01 | 12:36 | 45360 | 4.5447 | 0 | 137.3843 |  | 2006-09-01 | 12:36 | 45360 | 0.00107 | 0 | 92.0033 |  | 2028-01-01 | 12:36 | 45360 | 19.5413 | 0 | 204.8087 |  | 2007-01-01 | 12:36 | 45360 | 0.57053 | 0 | 186.7256 |  | 2028-01-01 | 12:36 | 45360 | 5.0369 | 0 | 70.9207 |  | 2007-01-01 | 12:36 | 45360 | 0.17358 | 0 | 74.3574 |  | 2029-09-01 | 12:36 | 45360 | 0.76683 | 0 | 195.7767 |  | 2006-09-01 | 12:36 | 45360 | 4.7215e-06 | 0 | 183.5322 |  | 2029-09-01 | 12:36 | 45360 | 0.32867 | 0 | 101.9131 |  | 2006-09-01 | 12:36 | 45360 | 1.1595e-06 | 0 | 59.3356 |  | 2028-01-01 | 12:36 | 45360 | 2.5203 | 0 | 194.1261 |  | 2007-01-01 | 12:36 | 45360 | 0.014406 | 0 | 185.5959 |  | 2028-01-01 | 12:36 | 45360 | 0.38922 | 0 | 41.8304 |  | 2007-01-01 | 12:36 | 45360 | 0.0024792 | 0 | 45.3878 |  | 2029-09-01 | 12:36 | 45360 | 0.21128 | 0 | 194.1073 |  | 2006-09-01 | 12:36 | 45360 | 1.552e-07 | 0 | 183.3428 |  | 2029-09-01 | 12:36 | 45360 | 0.066915 | 0 | 82.1193 |  | 2006-09-01 | 12:36 | 45360 | 2.714e-08 | 0 | 43.6339 |  | 2028-01-01 | 12:36 | 45360 | 0.41202 | 0 | 191.5756 |  | 2007-01-01 | 12:36 | 45360 | 0.0014593 | 0 | 185.5128 |  | 2028-01-01 | 12:36 | 45360 | 0.045331 | 0 | 29.6806 |  | 2007-01-01 | 12:36 | 45360 | 0.0001743 | 0 | 32.555 |  | 2029-09-01 | 12:36 | 45360 | 11.0228 | 0 | 85.8455 |  | 2029-09-01 | 12:36 | 45360 | 2.2721 | 0 | 58.5384 |  | 2029-09-01 | 12:36 | 45360 | 0.29486 | 0 | 40.0065 |  | 2006-09-01 | 12:36 | 45360 | 0.24579 | 0 | 39.444 |  | 2028-01-01 | 12:36 | 45360 | 5.0369 | 0 | 70.9207 |  | 2007-01-01 | 12:36 | 45360 | 0.17358 | 0 | 74.3574 |  | 2028-01-01 | 12:36 | 45360 | 0.25823 | 0 | 35.3883 |  | 2007-01-01 | 12:36 | 45360 | 0.0052268 | 0 | 36.4237
| 2029-09-01 | 12:37 | 45420 | 256.122 | 0 | 272.5466 |  | 2029-09-01 | 12:37 | 45420 | 6.6495 | 0 | 204.0684 |  | 2006-09-01 | 12:37 | 45420 | 0.0018894 | 0 | 185.4626 |  | 2029-09-01 | 12:37 | 45420 | 4.0648 | 0 | 137.3843 |  | 2006-09-01 | 12:37 | 45420 | 0.00076701 | 0 | 92.0033 |  | 2028-01-01 | 12:37 | 45420 | 17.9211 | 0 | 204.8087 |  | 2007-01-01 | 12:37 | 45420 | 0.46208 | 0 | 186.7256 |  | 2028-01-01 | 12:37 | 45420 | 4.6114 | 0 | 70.9207 |  | 2007-01-01 | 12:37 | 45420 | 0.14058 | 0 | 74.3574 |  | 2029-09-01 | 12:37 | 45420 | 0.64181 | 0 | 195.7767 |  | 2006-09-01 | 12:37 | 45420 | 2.8252e-06 | 0 | 183.5322 |  | 2029-09-01 | 12:37 | 45420 | 0.27508 | 0 | 101.9131 |  | 2006-09-01 | 12:37 | 45420 | 6.9379e-07 | 0 | 59.3356 |  | 2028-01-01 | 12:37 | 45420 | 2.1618 | 0 | 194.1261 |  | 2007-01-01 | 12:37 | 45420 | 0.010329 | 0 | 185.5959 |  | 2028-01-01 | 12:37 | 45420 | 0.33385 | 0 | 41.8304 |  | 2007-01-01 | 12:37 | 45420 | 0.0017775 | 0 | 45.3878 |  | 2029-09-01 | 12:37 | 45420 | 0.1703 | 0 | 194.1073 |  | 2006-09-01 | 12:37 | 45420 | 8.4252e-08 | 0 | 183.3428 |  | 2029-09-01 | 12:37 | 45420 | 0.053934 | 0 | 82.1193 |  | 2006-09-01 | 12:37 | 45420 | 1.4734e-08 | 0 | 43.6339 |  | 2028-01-01 | 12:37 | 45420 | 0.33275 | 0 | 191.5756 |  | 2007-01-01 | 12:37 | 45420 | 0.00098012 | 0 | 185.5128 |  | 2028-01-01 | 12:37 | 45420 | 0.036628 | 0 | 29.6806 |  | 2007-01-01 | 12:37 | 45420 | 0.00011707 | 0 | 32.555 |  | 2029-09-01 | 12:37 | 45420 | 10.3635 | 0 | 85.8455 |  | 2029-09-01 | 12:37 | 45420 | 2.0689 | 0 | 58.5384 |  | 2029-09-01 | 12:37 | 45420 | 0.25662 | 0 | 40.0065 |  | 2006-09-01 | 12:37 | 45420 | 0.21293 | 0 | 39.444 |  | 2028-01-01 | 12:37 | 45420 | 4.6114 | 0 | 70.9207 |  | 2007-01-01 | 12:37 | 45420 | 0.14058 | 0 | 74.3574 |  | 2028-01-01 | 12:37 | 45420 | 0.22067 | 0 | 35.3883 |  | 2007-01-01 | 12:37 | 45420 | 0.0039397 | 0 | 36.4237
| 2029-09-01 | 12:38 | 45480 | 252.877 | 0 | 272.5466 |  | 2029-09-01 | 12:38 | 45480 | 5.9452 | 0 | 204.0684 |  | 2006-09-01 | 12:38 | 45480 | 0.0013536 | 0 | 185.4626 |  | 2029-09-01 | 12:38 | 45480 | 3.6343 | 0 | 137.3843 |  | 2006-09-01 | 12:38 | 45480 | 0.00054949 | 0 | 92.0033 |  | 2028-01-01 | 12:38 | 45480 | 16.4379 | 0 | 204.8087 |  | 2007-01-01 | 12:38 | 45480 | 0.37353 | 0 | 186.7256 |  | 2028-01-01 | 12:38 | 45480 | 4.2227 | 0 | 70.9207 |  | 2007-01-01 | 12:38 | 45480 | 0.11364 | 0 | 74.3574 |  | 2029-09-01 | 12:38 | 45480 | 0.53685 | 0 | 195.7767 |  | 2006-09-01 | 12:38 | 45480 | 1.689e-06 | 0 | 183.5322 |  | 2029-09-01 | 12:38 | 45480 | 0.2301 | 0 | 101.9131 |  | 2006-09-01 | 12:38 | 45480 | 4.1477e-07 | 0 | 59.3356 |  | 2028-01-01 | 12:38 | 45480 | 1.855 | 0 | 194.1261 |  | 2007-01-01 | 12:38 | 45480 | 0.0073836 | 0 | 185.5959 |  | 2028-01-01 | 12:38 | 45480 | 0.28644 | 0 | 41.8304 |  | 2007-01-01 | 12:38 | 45480 | 0.0012706 | 0 | 45.3878 |  | 2029-09-01 | 12:38 | 45480 | 0.13716 | 0 | 194.1073 |  | 2006-09-01 | 12:38 | 45480 | 4.5691e-08 | 0 | 183.3428 |  | 2029-09-01 | 12:38 | 45480 | 0.04344 | 0 | 82.1193 |  | 2006-09-01 | 12:38 | 45480 | 7.9903e-09 | 0 | 43.6339 |  | 2028-01-01 | 12:38 | 45480 | 0.26882 | 0 | 191.5756 |  | 2007-01-01 | 12:38 | 45480 | 0.000656 | 0 | 185.5128 |  | 2028-01-01 | 12:38 | 45480 | 0.029605 | 0 | 29.6806 |  | 2007-01-01 | 12:38 | 45480 | 7.8354e-05 | 0 | 32.555 |  | 2029-09-01 | 12:38 | 45480 | 9.7436 | 0 | 85.8455 |  | 2029-09-01 | 12:38 | 45480 | 1.8839 | 0 | 58.5384 |  | 2029-09-01 | 12:38 | 45480 | 0.22334 | 0 | 40.0065 |  | 2006-09-01 | 12:38 | 45480 | 0.18446 | 0 | 39.444 |  | 2028-01-01 | 12:38 | 45480 | 4.2227 | 0 | 70.9207 |  | 2007-01-01 | 12:38 | 45480 | 0.11364 | 0 | 74.3574 |  | 2028-01-01 | 12:38 | 45480 | 0.18849 | 0 | 35.3883 |  | 2007-01-01 | 12:38 | 45480 | 0.0029642 | 0 | 36.4237
| 2029-09-01 | 12:39 | 45540 | 249.673 | 0 | 272.5466 |  | 2029-09-01 | 12:39 | 45540 | 5.3135 | 0 | 204.0684 |  | 2006-09-01 | 12:39 | 45540 | 0.0009691 | 0 | 185.4626 |  | 2029-09-01 | 12:39 | 45540 | 3.2482 | 0 | 137.3843 |  | 2006-09-01 | 12:39 | 45540 | 0.00039342 | 0 | 92.0033 |  | 2028-01-01 | 12:39 | 45540 | 15.0775 | 0 | 204.8087 |  | 2007-01-01 | 12:39 | 45540 | 0.30138 | 0 | 186.7256 |  | 2028-01-01 | 12:39 | 45540 | 3.8668 | 0 | 70.9207 |  | 2007-01-01 | 12:39 | 45540 | 0.091693 | 0 | 74.3574 |  | 2029-09-01 | 12:39 | 45540 | 0.44879 | 0 | 195.7767 |  | 2006-09-01 | 12:39 | 45540 | 1.0089e-06 | 0 | 183.5322 |  | 2029-09-01 | 12:39 | 45540 | 0.19235 | 0 | 101.9131 |  | 2006-09-01 | 12:39 | 45540 | 2.4774e-07 | 0 | 59.3356 |  | 2028-01-01 | 12:39 | 45540 | 1.5917 | 0 | 194.1261 |  | 2007-01-01 | 12:39 | 45540 | 0.0052626 | 0 | 185.5959 |  | 2028-01-01 | 12:39 | 45540 | 0.24578 | 0 | 41.8304 |  | 2007-01-01 | 12:39 | 45540 | 0.00090564 | 0 | 45.3878 |  | 2029-09-01 | 12:39 | 45540 | 0.1104 | 0 | 194.1073 |  | 2006-09-01 | 12:39 | 45540 | 2.4754e-08 | 0 | 183.3428 |  | 2029-09-01 | 12:39 | 45540 | 0.034964 | 0 | 82.1193 |  | 2006-09-01 | 12:39 | 45540 | 4.3288e-09 | 0 | 43.6339 |  | 2028-01-01 | 12:39 | 45540 | 0.21718 | 0 | 191.5756 |  | 2007-01-01 | 12:39 | 45540 | 0.00043747 | 0 | 185.5128 |  | 2028-01-01 | 12:39 | 45540 | 0.023929 | 0 | 29.6806 |  | 2007-01-01 | 12:39 | 45540 | 5.2253e-05 | 0 | 32.555 |  | 2029-09-01 | 12:39 | 45540 | 9.1608 | 0 | 85.8455 |  | 2029-09-01 | 12:39 | 45540 | 1.7153 | 0 | 58.5384 |  | 2029-09-01 | 12:39 | 45540 | 0.19437 | 0 | 40.0065 |  | 2006-09-01 | 12:39 | 45540 | 0.1598 | 0 | 39.444 |  | 2028-01-01 | 12:39 | 45540 | 3.8668 | 0 | 70.9207 |  | 2007-01-01 | 12:39 | 45540 | 0.091693 | 0 | 74.3574 |  | 2028-01-01 | 12:39 | 45540 | 0.16094 | 0 | 35.3883 |  | 2007-01-01 | 12:39 | 45540 | 0.0022264 | 0 | 36.4237
| 2029-09-01 | 12:40 | 45600 | 246.509 | 0 | 272.5466 |  | 2029-09-01 | 12:40 | 45600 | 4.7472 | 0 | 204.0684 |  | 2006-09-01 | 12:40 | 45600 | 0.00069341 | 0 | 185.4626 |  | 2029-09-01 | 12:40 | 45600 | 2.902 | 0 | 137.3843 |  | 2006-09-01 | 12:40 | 45600 | 0.0002815 | 0 | 92.0033 |  | 2028-01-01 | 12:40 | 45600 | 13.8298 | 0 | 204.8087 |  | 2007-01-01 | 12:40 | 45600 | 0.24271 | 0 | 186.7256 |  | 2028-01-01 | 12:40 | 45600 | 3.541 | 0 | 70.9207 |  | 2007-01-01 | 12:40 | 45600 | 0.073842 | 0 | 74.3574 |  | 2029-09-01 | 12:40 | 45600 | 0.37494 | 0 | 195.7767 |  | 2006-09-01 | 12:40 | 45600 | 6.0205e-07 | 0 | 183.5322 |  | 2029-09-01 | 12:40 | 45600 | 0.1607 | 0 | 101.9131 |  | 2006-09-01 | 12:40 | 45600 | 1.4785e-07 | 0 | 59.3356 |  | 2028-01-01 | 12:40 | 45600 | 1.3658 | 0 | 194.1261 |  | 2007-01-01 | 12:40 | 45600 | 0.00374 | 0 | 185.5959 |  | 2028-01-01 | 12:40 | 45600 | 0.21089 | 0 | 41.8304 |  | 2007-01-01 | 12:40 | 45600 | 0.0006436 | 0 | 45.3878 |  | 2029-09-01 | 12:40 | 45600 | 0.08879 | 0 | 194.1073 |  | 2006-09-01 | 12:40 | 45600 | 1.3397e-08 | 0 | 183.3428 |  | 2029-09-01 | 12:40 | 45600 | 0.028121 | 0 | 82.1193 |  | 2006-09-01 | 12:40 | 45600 | 2.3428e-09 | 0 | 43.6339 |  | 2028-01-01 | 12:40 | 45600 | 0.17547 | 0 | 191.5756 |  | 2007-01-01 | 12:40 | 45600 | 0.00029068 | 0 | 185.5128 |  | 2028-01-01 | 12:40 | 45600 | 0.019341 | 0 | 29.6806 |  | 2007-01-01 | 12:40 | 45600 | 3.472e-05 | 0 | 32.555 |  | 2029-09-01 | 12:40 | 45600 | 8.6128 | 0 | 85.8455 |  | 2029-09-01 | 12:40 | 45600 | 1.5619 | 0 | 58.5384 |  | 2029-09-01 | 12:40 | 45600 | 0.16916 | 0 | 40.0065 |  | 2006-09-01 | 12:40 | 45600 | 0.13843 | 0 | 39.444 |  | 2028-01-01 | 12:40 | 45600 | 3.541 | 0 | 70.9207 |  | 2007-01-01 | 12:40 | 45600 | 0.073842 | 0 | 74.3574 |  | 2028-01-01 | 12:40 | 45600 | 0.13737 | 0 | 35.3883 |  | 2007-01-01 | 12:40 | 45600 | 0.0016693 | 0 | 36.4237
| 2029-09-01 | 12:41 | 45660 | 243.386 | 0 | 272.5466 |  | 2029-09-01 | 12:41 | 45660 | 4.2397 | 0 | 204.0684 |  | 2006-09-01 | 12:41 | 45660 | 0.00049584 | 0 | 185.4626 |  | 2029-09-01 | 12:41 | 45660 | 2.5917 | 0 | 137.3843 |  | 2006-09-01 | 12:41 | 45660 | 0.00020129 | 0 | 92.0033 |  | 2028-01-01 | 12:41 | 45660 | 12.6859 | 0 | 204.8087 |  | 2007-01-01 | 12:41 | 45660 | 0.19509 | 0 | 186.7256 |  | 2028-01-01 | 12:41 | 45660 | 3.2428 | 0 | 70.9207 |  | 2007-01-01 | 12:41 | 45660 | 0.059353 | 0 | 74.3574 |  | 2029-09-01 | 12:41 | 45660 | 0.31306 | 0 | 195.7767 |  | 2006-09-01 | 12:41 | 45660 | 3.5896e-07 | 0 | 183.5322 |  | 2029-09-01 | 12:41 | 45660 | 0.13418 | 0 | 101.9131 |  | 2006-09-01 | 12:41 | 45660 | 8.8152e-08 | 0 | 59.3356 |  | 2028-01-01 | 12:41 | 45660 | 1.1721 | 0 | 194.1261 |  | 2007-01-01 | 12:41 | 45660 | 0.0026501 | 0 | 185.5959 |  | 2028-01-01 | 12:41 | 45660 | 0.18096 | 0 | 41.8304 |  | 2007-01-01 | 12:41 | 45660 | 0.00045604 | 0 | 45.3878 |  | 2029-09-01 | 12:41 | 45660 | 0.071361 | 0 | 194.1073 |  | 2006-09-01 | 12:41 | 45660 | 7.243e-09 | 0 | 183.3428 |  | 2029-09-01 | 12:41 | 45660 | 0.022601 | 0 | 82.1193 |  | 2006-09-01 | 12:41 | 45660 | 1.2666e-09 | 0 | 43.6339 |  | 2028-01-01 | 12:41 | 45660 | 0.14177 | 0 | 191.5756 |  | 2007-01-01 | 12:41 | 45660 | 0.00019245 | 0 | 185.5128 |  | 2028-01-01 | 12:41 | 45660 | 0.015633 | 0 | 29.6806 |  | 2007-01-01 | 12:41 | 45660 | 2.2987e-05 | 0 | 32.555 |  | 2029-09-01 | 12:41 | 45660 | 8.0976 | 0 | 85.8455 |  | 2029-09-01 | 12:41 | 45660 | 1.4222 | 0 | 58.5384 |  | 2029-09-01 | 12:41 | 45660 | 0.14722 | 0 | 40.0065 |  | 2006-09-01 | 12:41 | 45660 | 0.11991 | 0 | 39.444 |  | 2028-01-01 | 12:41 | 45660 | 3.2428 | 0 | 70.9207 |  | 2007-01-01 | 12:41 | 45660 | 0.059353 | 0 | 74.3574 |  | 2028-01-01 | 12:41 | 45660 | 0.11723 | 0 | 35.3883 |  | 2007-01-01 | 12:41 | 45660 | 0.0012493 | 0 | 36.4237
| 2029-09-01 | 12:42 | 45720 | 240.301 | 0 | 272.5466 |  | 2029-09-01 | 12:42 | 45720 | 3.785 | 0 | 204.0684 |  | 2006-09-01 | 12:42 | 45720 | 0.00035435 | 0 | 185.4626 |  | 2029-09-01 | 12:42 | 45720 | 2.3138 | 0 | 137.3843 |  | 2006-09-01 | 12:42 | 45720 | 0.00014385 | 0 | 92.0033 |  | 2028-01-01 | 12:42 | 45720 | 11.6373 | 0 | 204.8087 |  | 2007-01-01 | 12:42 | 45720 | 0.15651 | 0 | 186.7256 |  | 2028-01-01 | 12:42 | 45720 | 2.97 | 0 | 70.9207 |  | 2007-01-01 | 12:42 | 45720 | 0.047618 | 0 | 74.3574 |  | 2029-09-01 | 12:42 | 45720 | 0.26123 | 0 | 195.7767 |  | 2006-09-01 | 12:42 | 45720 | 2.1384e-07 | 0 | 183.5322 |  | 2029-09-01 | 12:42 | 45720 | 0.11196 | 0 | 101.9131 |  | 2006-09-01 | 12:42 | 45720 | 5.2513e-08 | 0 | 59.3356 |  | 2028-01-01 | 12:42 | 45720 | 1.0059 | 0 | 194.1261 |  | 2007-01-01 | 12:42 | 45720 | 0.0018723 | 0 | 185.5959 |  | 2028-01-01 | 12:42 | 45720 | 0.1553 | 0 | 41.8304 |  | 2007-01-01 | 12:42 | 45720 | 0.00032221 | 0 | 45.3878 |  | 2029-09-01 | 12:42 | 45720 | 0.057312 | 0 | 194.1073 |  | 2006-09-01 | 12:42 | 45720 | 3.912e-09 | 0 | 183.3428 |  | 2029-09-01 | 12:42 | 45720 | 0.018151 | 0 | 82.1193 |  | 2006-09-01 | 12:42 | 45720 | 6.8412e-10 | 0 | 43.6339 |  | 2028-01-01 | 12:42 | 45720 | 0.11455 | 0 | 191.5756 |  | 2007-01-01 | 12:42 | 45720 | 0.00012696 | 0 | 185.5128 |  | 2028-01-01 | 12:42 | 45720 | 0.012637 | 0 | 29.6806 |  | 2007-01-01 | 12:42 | 45720 | 1.5164e-05 | 0 | 32.555 |  | 2029-09-01 | 12:42 | 45720 | 7.6132 | 0 | 85.8455 |  | 2029-09-01 | 12:42 | 45720 | 1.295 | 0 | 58.5384 |  | 2029-09-01 | 12:42 | 45720 | 0.12813 | 0 | 40.0065 |  | 2006-09-01 | 12:42 | 45720 | 0.10387 | 0 | 39.444 |  | 2028-01-01 | 12:42 | 45720 | 2.97 | 0 | 70.9207 |  | 2007-01-01 | 12:42 | 45720 | 0.047618 | 0 | 74.3574 |  | 2028-01-01 | 12:42 | 45720 | 0.10001 | 0 | 35.3883 |  | 2007-01-01 | 12:42 | 45720 | 0.00093342 | 0 | 36.4237
| 2029-09-01 | 12:43 | 45780 | 237.256 | 0 | 272.5466 |  | 2029-09-01 | 12:43 | 45780 | 3.3778 | 0 | 204.0684 |  | 2006-09-01 | 12:43 | 45780 | 0.00025307 | 0 | 185.4626 |  | 2029-09-01 | 12:43 | 45780 | 2.0648 | 0 | 137.3843 |  | 2006-09-01 | 12:43 | 45780 | 0.00010274 | 0 | 92.0033 |  | 2028-01-01 | 12:43 | 45780 | 10.6763 | 0 | 204.8087 |  | 2007-01-01 | 12:43 | 45780 | 0.12533 | 0 | 186.7256 |  | 2028-01-01 | 12:43 | 45780 | 2.7205 | 0 | 70.9207 |  | 2007-01-01 | 12:43 | 45780 | 0.03813 | 0 | 74.3574 |  | 2029-09-01 | 12:43 | 45780 | 0.21785 | 0 | 195.7767 |  | 2006-09-01 | 12:43 | 45780 | 1.2727e-07 | 0 | 183.5322 |  | 2029-09-01 | 12:43 | 45780 | 0.093372 | 0 | 101.9131 |  | 2006-09-01 | 12:43 | 45780 | 3.1254e-08 | 0 | 59.3356 |  | 2028-01-01 | 12:43 | 45780 | 0.86343 | 0 | 194.1261 |  | 2007-01-01 | 12:43 | 45780 | 0.001319 | 0 | 185.5959 |  | 2028-01-01 | 12:43 | 45780 | 0.13329 | 0 | 41.8304 |  | 2007-01-01 | 12:43 | 45780 | 0.00022698 | 0 | 45.3878 |  | 2029-09-01 | 12:43 | 45780 | 0.045996 | 0 | 194.1073 |  | 2006-09-01 | 12:43 | 45780 | 2.1107e-09 | 0 | 183.3428 |  | 2029-09-01 | 12:43 | 45780 | 0.014567 | 0 | 82.1193 |  | 2006-09-01 | 12:43 | 45780 | 3.6912e-10 | 0 | 43.6339 |  | 2028-01-01 | 12:43 | 45780 | 0.092573 | 0 | 191.5756 |  | 2007-01-01 | 12:43 | 45780 | 8.3459e-05 | 0 | 185.5128 |  | 2028-01-01 | 12:43 | 45780 | 0.010216 | 0 | 29.6806 |  | 2007-01-01 | 12:43 | 45780 | 9.9685e-06 | 0 | 32.555 |  | 2029-09-01 | 12:43 | 45780 | 7.1578 | 0 | 85.8455 |  | 2029-09-01 | 12:43 | 45780 | 1.1792 | 0 | 58.5384 |  | 2029-09-01 | 12:43 | 45780 | 0.11151 | 0 | 40.0065 |  | 2006-09-01 | 12:43 | 45780 | 0.089981 | 0 | 39.444 |  | 2028-01-01 | 12:43 | 45780 | 2.7205 | 0 | 70.9207 |  | 2007-01-01 | 12:43 | 45780 | 0.03813 | 0 | 74.3574 |  | 2028-01-01 | 12:43 | 45780 | 0.085304 | 0 | 35.3883 |  | 2007-01-01 | 12:43 | 45780 | 0.00069615 | 0 | 36.4237
| 2029-09-01 | 12:44 | 45840 | 234.249 | 0 | 272.5466 |  | 2029-09-01 | 12:44 | 45840 | 3.0133 | 0 | 204.0684 |  | 2006-09-01 | 12:44 | 45840 | 0.00018063 | 0 | 185.4626 |  | 2029-09-01 | 12:44 | 45840 | 1.842 | 0 | 137.3843 |  | 2006-09-01 | 12:44 | 45840 | 7.333e-05 | 0 | 92.0033 |  | 2028-01-01 | 12:44 | 45840 | 9.7956 | 0 | 204.8087 |  | 2007-01-01 | 12:44 | 45840 | 0.10017 | 0 | 186.7256 |  | 2028-01-01 | 12:44 | 45840 | 2.4922 | 0 | 70.9207 |  | 2007-01-01 | 12:44 | 45840 | 0.030476 | 0 | 74.3574 |  | 2029-09-01 | 12:44 | 45840 | 0.18157 | 0 | 195.7767 |  | 2006-09-01 | 12:44 | 45840 | 7.5682e-08 | 0 | 183.5322 |  | 2029-09-01 | 12:44 | 45840 | 0.07782 | 0 | 101.9131 |  | 2006-09-01 | 12:44 | 45840 | 1.8585e-08 | 0 | 59.3356 |  | 2028-01-01 | 12:44 | 45840 | 0.74123 | 0 | 194.1261 |  | 2007-01-01 | 12:44 | 45840 | 0.00092651 | 0 | 185.5959 |  | 2028-01-01 | 12:44 | 45840 | 0.11442 | 0 | 41.8304 |  | 2007-01-01 | 12:44 | 45840 | 0.00015944 | 0 | 45.3878 |  | 2029-09-01 | 12:44 | 45840 | 0.036888 | 0 | 194.1073 |  | 2006-09-01 | 12:44 | 45840 | 1.1377e-09 | 0 | 183.3428 |  | 2029-09-01 | 12:44 | 45840 | 0.011683 | 0 | 82.1193 |  | 2006-09-01 | 12:44 | 45840 | 1.9896e-10 | 0 | 43.6339 |  | 2028-01-01 | 12:44 | 45840 | 0.074822 | 0 | 191.5756 |  | 2007-01-01 | 12:44 | 45840 | 5.467e-05 | 0 | 185.5128 |  | 2028-01-01 | 12:44 | 45840 | 0.00826 | 0 | 29.6806 |  | 2007-01-01 | 12:44 | 45840 | 6.5299e-06 | 0 | 32.555 |  | 2029-09-01 | 12:44 | 45840 | 6.7296 | 0 | 85.8455 |  | 2029-09-01 | 12:44 | 45840 | 1.0737 | 0 | 58.5384 |  | 2029-09-01 | 12:44 | 45840 | 0.097048 | 0 | 40.0065 |  | 2006-09-01 | 12:44 | 45840 | 0.077943 | 0 | 39.444 |  | 2028-01-01 | 12:44 | 45840 | 2.4922 | 0 | 70.9207 |  | 2007-01-01 | 12:44 | 45840 | 0.030476 | 0 | 74.3574 |  | 2028-01-01 | 12:44 | 45840 | 0.072751 | 0 | 35.3883 |  | 2007-01-01 | 12:44 | 45840 | 0.00051829 | 0 | 36.4237
| 2029-09-01 | 12:45 | 45900 | 231.279 | 0 | 272.5466 |  | 2029-09-01 | 12:45 | 45900 | 2.687 | 0 | 204.0684 |  | 2006-09-01 | 12:45 | 45900 | 0.00012885 | 0 | 185.4626 |  | 2029-09-01 | 12:45 | 45900 | 1.6426 | 0 | 137.3843 |  | 2006-09-01 | 12:45 | 45900 | 5.2307e-05 | 0 | 92.0033 |  | 2028-01-01 | 12:45 | 45900 | 8.9887 | 0 | 204.8087 |  | 2007-01-01 | 12:45 | 45900 | 0.079909 | 0 | 186.7256 |  | 2028-01-01 | 12:45 | 45900 | 2.2834 | 0 | 70.9207 |  | 2007-01-01 | 12:45 | 45900 | 0.024312 | 0 | 74.3574 |  | 2029-09-01 | 12:45 | 45900 | 0.15123 | 0 | 195.7767 |  | 2006-09-01 | 12:45 | 45900 | 4.4964e-08 | 0 | 183.5322 |  | 2029-09-01 | 12:45 | 45900 | 0.064819 | 0 | 101.9131 |  | 2006-09-01 | 12:45 | 45900 | 1.1042e-08 | 0 | 59.3356 |  | 2028-01-01 | 12:45 | 45900 | 0.63644 | 0 | 194.1261 |  | 2007-01-01 | 12:45 | 45900 | 0.00064893 | 0 | 185.5959 |  | 2028-01-01 | 12:45 | 45900 | 0.098241 | 0 | 41.8304 |  | 2007-01-01 | 12:45 | 45900 | 0.00011167 | 0 | 45.3878 |  | 2029-09-01 | 12:45 | 45900 | 0.029562 | 0 | 194.1073 |  | 2006-09-01 | 12:45 | 45900 | 6.126e-10 | 0 | 183.3428 |  | 2029-09-01 | 12:45 | 45900 | 0.0093624 | 0 | 82.1193 |  | 2006-09-01 | 12:45 | 45900 | 1.0713e-10 | 0 | 43.6339 |  | 2028-01-01 | 12:45 | 45900 | 0.060487 | 0 | 191.5756 |  | 2007-01-01 | 12:45 | 45900 | 3.5687e-05 | 0 | 185.5128 |  | 2028-01-01 | 12:45 | 45900 | 0.0066798 | 0 | 29.6806 |  | 2007-01-01 | 12:45 | 45900 | 4.2625e-06 | 0 | 32.555 |  | 2029-09-01 | 12:45 | 45900 | 6.327 | 0 | 85.8455 |  | 2029-09-01 | 12:45 | 45900 | 0.97765 | 0 | 58.5384 |  | 2029-09-01 | 12:45 | 45900 | 0.084461 | 0 | 40.0065 |  | 2006-09-01 | 12:45 | 45900 | 0.067515 | 0 | 39.444 |  | 2028-01-01 | 12:45 | 45900 | 2.2834 | 0 | 70.9207 |  | 2007-01-01 | 12:45 | 45900 | 0.024312 | 0 | 74.3574 |  | 2028-01-01 | 12:45 | 45900 | 0.062039 | 0 | 35.3883 |  | 2007-01-01 | 12:45 | 45900 | 0.00038519 | 0 | 36.4237
| 2029-09-01 | 12:46 | 45960 | 228.348 | 0 | 272.5466 |  | 2029-09-01 | 12:46 | 45960 | 2.3952 | 0 | 204.0684 |  | 2006-09-01 | 12:46 | 45960 | 9.1852e-05 | 0 | 185.4626 |  | 2029-09-01 | 12:46 | 45960 | 1.4642 | 0 | 137.3843 |  | 2006-09-01 | 12:46 | 45960 | 3.7289e-05 | 0 | 92.0033 |  | 2028-01-01 | 12:46 | 45960 | 8.2495 | 0 | 204.8087 |  | 2007-01-01 | 12:46 | 45960 | 0.063628 | 0 | 186.7256 |  | 2028-01-01 | 12:46 | 45960 | 2.0924 | 0 | 70.9207 |  | 2007-01-01 | 12:46 | 45960 | 0.019358 | 0 | 74.3574 |  | 2029-09-01 | 12:46 | 45960 | 0.12589 | 0 | 195.7767 |  | 2006-09-01 | 12:46 | 45960 | 2.6691e-08 | 0 | 183.5322 |  | 2029-09-01 | 12:46 | 45960 | 0.053958 | 0 | 101.9131 |  | 2006-09-01 | 12:46 | 45960 | 6.5545e-09 | 0 | 59.3356 |  | 2028-01-01 | 12:46 | 45960 | 0.54658 | 0 | 194.1261 |  | 2007-01-01 | 12:46 | 45960 | 0.0004532 | 0 | 185.5959 |  | 2028-01-01 | 12:46 | 45960 | 0.084365 | 0 | 41.8304 |  | 2007-01-01 | 12:46 | 45960 | 7.7991e-05 | 0 | 45.3878 |  | 2029-09-01 | 12:46 | 45960 | 0.023674 | 0 | 194.1073 |  | 2006-09-01 | 12:46 | 45960 | 3.2952e-10 | 0 | 183.3428 |  | 2029-09-01 | 12:46 | 45960 | 0.0074976 | 0 | 82.1193 |  | 2006-09-01 | 12:46 | 45960 | 5.7627e-11 | 0 | 43.6339 |  | 2028-01-01 | 12:46 | 45960 | 0.048909 | 0 | 191.5756 |  | 2007-01-01 | 12:46 | 45960 | 2.3214e-05 | 0 | 185.5128 |  | 2028-01-01 | 12:46 | 45960 | 0.005403 | 0 | 29.6806 |  | 2007-01-01 | 12:46 | 45960 | 2.7727e-06 | 0 | 32.555 |  | 2029-09-01 | 12:46 | 45960 | 5.9485 | 0 | 85.8455 |  | 2029-09-01 | 12:46 | 45960 | 0.8902 | 0 | 58.5384 |  | 2029-09-01 | 12:46 | 45960 | 0.073507 | 0 | 40.0065 |  | 2006-09-01 | 12:46 | 45960 | 0.058482 | 0 | 39.444 |  | 2028-01-01 | 12:46 | 45960 | 2.0924 | 0 | 70.9207 |  | 2007-01-01 | 12:46 | 45960 | 0.019358 | 0 | 74.3574 |  | 2028-01-01 | 12:46 | 45960 | 0.052901 | 0 | 35.3883 |  | 2007-01-01 | 12:46 | 45960 | 0.00028577 | 0 | 36.4237
| 2029-09-01 | 12:47 | 46020 | 225.453 | 0 | 272.5466 |  | 2029-09-01 | 12:47 | 46020 | 2.1342 | 0 | 204.0684 |  | 2006-09-01 | 12:47 | 46020 | 6.5439e-05 | 0 | 185.4626 |  | 2029-09-01 | 12:47 | 46020 | 1.3046 | 0 | 137.3843 |  | 2006-09-01 | 12:47 | 46020 | 2.6566e-05 | 0 | 92.0033 |  | 2028-01-01 | 12:47 | 46020 | 7.5722 | 0 | 204.8087 |  | 2007-01-01 | 12:47 | 46020 | 0.050568 | 0 | 186.7256 |  | 2028-01-01 | 12:47 | 46020 | 1.9178 | 0 | 70.9207 |  | 2007-01-01 | 12:47 | 46020 | 0.015385 | 0 | 74.3574 |  | 2029-09-01 | 12:47 | 46020 | 0.10473 | 0 | 195.7767 |  | 2006-09-01 | 12:47 | 46020 | 1.5829e-08 | 0 | 183.5322 |  | 2029-09-01 | 12:47 | 46020 | 0.044889 | 0 | 101.9131 |  | 2006-09-01 | 12:47 | 46020 | 3.8873e-09 | 0 | 59.3356 |  | 2028-01-01 | 12:47 | 46020 | 0.46952 | 0 | 194.1261 |  | 2007-01-01 | 12:47 | 46020 | 0.0003156 | 0 | 185.5959 |  | 2028-01-01 | 12:47 | 46020 | 0.072467 | 0 | 41.8304 |  | 2007-01-01 | 12:47 | 46020 | 5.4311e-05 | 0 | 45.3878 |  | 2029-09-01 | 12:47 | 46020 | 0.018945 | 0 | 194.1073 |  | 2006-09-01 | 12:47 | 46020 | 1.7708e-10 | 0 | 183.3428 |  | 2029-09-01 | 12:47 | 46020 | 0.0059999 | 0 | 82.1193 |  | 2006-09-01 | 12:47 | 46020 | 3.0967e-11 | 0 | 43.6339 |  | 2028-01-01 | 12:47 | 46020 | 0.039558 | 0 | 191.5756 |  | 2007-01-01 | 12:47 | 46020 | 1.5049e-05 | 0 | 185.5128 |  | 2028-01-01 | 12:47 | 46020 | 0.0043714 | 0 | 29.6806 |  | 2007-01-01 | 12:47 | 46020 | 1.7974e-06 | 0 | 32.555 |  | 2029-09-01 | 12:47 | 46020 | 5.5926 | 0 | 85.8455 |  | 2029-09-01 | 12:47 | 46020 | 0.81057 | 0 | 58.5384 |  | 2029-09-01 | 12:47 | 46020 | 0.063973 | 0 | 40.0065 |  | 2006-09-01 | 12:47 | 46020 | 0.050656 | 0 | 39.444 |  | 2028-01-01 | 12:47 | 46020 | 1.9178 | 0 | 70.9207 |  | 2007-01-01 | 12:47 | 46020 | 0.015385 | 0 | 74.3574 |  | 2028-01-01 | 12:47 | 46020 | 0.045108 | 0 | 35.3883 |  | 2007-01-01 | 12:47 | 46020 | 0.00021164 | 0 | 36.4237
| 2029-09-01 | 12:48 | 46080 | 222.594 | 0 | 272.5466 |  | 2029-09-01 | 12:48 | 46080 | 1.901 | 0 | 204.0684 |  | 2006-09-01 | 12:48 | 46080 | 4.6592e-05 | 0 | 185.4626 |  | 2029-09-01 | 12:48 | 46080 | 1.1621 | 0 | 137.3843 |  | 2006-09-01 | 12:48 | 46080 | 1.8915e-05 | 0 | 92.0033 |  | 2028-01-01 | 12:48 | 46080 | 6.9517 | 0 | 204.8087 |  | 2007-01-01 | 12:48 | 46080 | 0.040113 | 0 | 186.7256 |  | 2028-01-01 | 12:48 | 46080 | 1.7581 | 0 | 70.9207 |  | 2007-01-01 | 12:48 | 46080 | 0.012204 | 0 | 74.3574 |  | 2029-09-01 | 12:48 | 46080 | 0.087078 | 0 | 195.7767 |  | 2006-09-01 | 12:48 | 46080 | 9.3797e-09 | 0 | 183.5322 |  | 2029-09-01 | 12:48 | 46080 | 0.037322 | 0 | 101.9131 |  | 2006-09-01 | 12:48 | 46080 | 2.3034e-09 | 0 | 59.3356 |  | 2028-01-01 | 12:48 | 46080 | 0.40342 | 0 | 194.1261 |  | 2007-01-01 | 12:48 | 46080 | 0.00021915 | 0 | 185.5959 |  | 2028-01-01 | 12:48 | 46080 | 0.062263 | 0 | 41.8304 |  | 2007-01-01 | 12:48 | 46080 | 3.7712e-05 | 0 | 45.3878 |  | 2029-09-01 | 12:48 | 46080 | 0.015149 | 0 | 194.1073 |  | 2006-09-01 | 12:48 | 46080 | 9.5059e-11 | 0 | 183.3428 |  | 2029-09-01 | 12:48 | 46080 | 0.0047979 | 0 | 82.1193 |  | 2006-09-01 | 12:48 | 46080 | 1.6624e-11 | 0 | 43.6339 |  | 2028-01-01 | 12:48 | 46080 | 0.032004 | 0 | 191.5756 |  | 2007-01-01 | 12:48 | 46080 | 9.7216e-06 | 0 | 185.5128 |  | 2028-01-01 | 12:48 | 46080 | 0.0035377 | 0 | 29.6806 |  | 2007-01-01 | 12:48 | 46080 | 1.1612e-06 | 0 | 32.555 |  | 2029-09-01 | 12:48 | 46080 | 5.2581 | 0 | 85.8455 |  | 2029-09-01 | 12:48 | 46080 | 0.73806 | 0 | 58.5384 |  | 2029-09-01 | 12:48 | 46080 | 0.055676 | 0 | 40.0065 |  | 2006-09-01 | 12:48 | 46080 | 0.043877 | 0 | 39.444 |  | 2028-01-01 | 12:48 | 46080 | 1.7581 | 0 | 70.9207 |  | 2007-01-01 | 12:48 | 46080 | 0.012204 | 0 | 74.3574 |  | 2028-01-01 | 12:48 | 46080 | 0.038464 | 0 | 35.3883 |  | 2007-01-01 | 12:48 | 46080 | 0.00015646 | 0 | 36.4237
| 2029-09-01 | 12:49 | 46140 | 219.772 | 0 | 272.5466 |  | 2029-09-01 | 12:49 | 46140 | 1.6925 | 0 | 204.0684 |  | 2006-09-01 | 12:49 | 46140 | 3.3153e-05 | 0 | 185.4626 |  | 2029-09-01 | 12:49 | 46140 | 1.0347 | 0 | 137.3843 |  | 2006-09-01 | 12:49 | 46140 | 1.3459e-05 | 0 | 92.0033 |  | 2028-01-01 | 12:49 | 46140 | 6.3833 | 0 | 204.8087 |  | 2007-01-01 | 12:49 | 46140 | 0.03176 | 0 | 186.7256 |  | 2028-01-01 | 12:49 | 46140 | 1.6121 | 0 | 70.9207 |  | 2007-01-01 | 12:49 | 46140 | 0.0096628 | 0 | 74.3574 |  | 2029-09-01 | 12:49 | 46140 | 0.072355 | 0 | 195.7767 |  | 2006-09-01 | 12:49 | 46140 | 5.553e-09 | 0 | 183.5322 |  | 2029-09-01 | 12:49 | 46140 | 0.031012 | 0 | 101.9131 |  | 2006-09-01 | 12:49 | 46140 | 1.3637e-09 | 0 | 59.3356 |  | 2028-01-01 | 12:49 | 46140 | 0.34673 | 0 | 194.1261 |  | 2007-01-01 | 12:49 | 46140 | 0.00015173 | 0 | 185.5959 |  | 2028-01-01 | 12:49 | 46140 | 0.053511 | 0 | 41.8304 |  | 2007-01-01 | 12:49 | 46140 | 2.6112e-05 | 0 | 45.3878 |  | 2029-09-01 | 12:49 | 46140 | 0.012106 | 0 | 194.1073 |  | 2006-09-01 | 12:49 | 46140 | 5.0979e-11 | 0 | 183.3428 |  | 2029-09-01 | 12:49 | 46140 | 0.0038339 | 0 | 82.1193 |  | 2006-09-01 | 12:49 | 46140 | 8.9153e-12 | 0 | 43.6339 |  | 2028-01-01 | 12:49 | 46140 | 0.025902 | 0 | 191.5756 |  | 2007-01-01 | 12:49 | 46140 | 6.2588e-06 | 0 | 185.5128 |  | 2028-01-01 | 12:49 | 46140 | 0.002864 | 0 | 29.6806 |  | 2007-01-01 | 12:49 | 46140 | 7.4756e-07 | 0 | 32.555 |  | 2029-09-01 | 12:49 | 46140 | 4.9435 | 0 | 85.8455 |  | 2029-09-01 | 12:49 | 46140 | 0.67204 | 0 | 58.5384 |  | 2029-09-01 | 12:49 | 46140 | 0.048455 | 0 | 40.0065 |  | 2006-09-01 | 12:49 | 46140 | 0.038004 | 0 | 39.444 |  | 2028-01-01 | 12:49 | 46140 | 1.6121 | 0 | 70.9207 |  | 2007-01-01 | 12:49 | 46140 | 0.0096628 | 0 | 74.3574 |  | 2028-01-01 | 12:49 | 46140 | 0.0328 | 0 | 35.3883 |  | 2007-01-01 | 12:49 | 46140 | 0.00011547 | 0 | 36.4237
| 2029-09-01 | 12:50 | 46200 | 216.985 | 0 | 272.5466 |  | 2029-09-01 | 12:50 | 46200 | 1.5064 | 0 | 204.0684 |  | 2006-09-01 | 12:50 | 46200 | 2.3576e-05 | 0 | 185.4626 |  | 2029-09-01 | 12:50 | 46200 | 0.92087 | 0 | 137.3843 |  | 2006-09-01 | 12:50 | 46200 | 9.5712e-06 | 0 | 92.0033 |  | 2028-01-01 | 12:50 | 46200 | 5.8626 | 0 | 204.8087 |  | 2007-01-01 | 12:50 | 46200 | 0.025099 | 0 | 186.7256 |  | 2028-01-01 | 12:50 | 46200 | 1.4785 | 0 | 70.9207 |  | 2007-01-01 | 12:50 | 46200 | 0.0076363 | 0 | 74.3574 |  | 2029-09-01 | 12:50 | 46200 | 0.060085 | 0 | 195.7767 |  | 2006-09-01 | 12:50 | 46200 | 3.2846e-09 | 0 | 183.5322 |  | 2029-09-01 | 12:50 | 46200 | 0.025753 | 0 | 101.9131 |  | 2006-09-01 | 12:50 | 46200 | 8.0662e-10 | 0 | 59.3356 |  | 2028-01-01 | 12:50 | 46200 | 0.2981 | 0 | 194.1261 |  | 2007-01-01 | 12:50 | 46200 | 0.00010476 | 0 | 185.5959 |  | 2028-01-01 | 12:50 | 46200 | 0.046003 | 0 | 41.8304 |  | 2007-01-01 | 12:50 | 46200 | 1.8028e-05 | 0 | 45.3878 |  | 2029-09-01 | 12:50 | 46200 | 0.0096664 | 0 | 194.1073 |  | 2006-09-01 | 12:50 | 46200 | 2.7312e-11 | 0 | 183.3428 |  | 2029-09-01 | 12:50 | 46200 | 0.0030614 | 0 | 82.1193 |  | 2006-09-01 | 12:50 | 46200 | 4.7763e-12 | 0 | 43.6339 |  | 2028-01-01 | 12:50 | 46200 | 0.02097 | 0 | 191.5756 |  | 2007-01-01 | 12:50 | 46200 | 4.0157e-06 | 0 | 185.5128 |  | 2028-01-01 | 12:50 | 46200 | 0.0023193 | 0 | 29.6806 |  | 2007-01-01 | 12:50 | 46200 | 4.7964e-07 | 0 | 32.555 |  | 2029-09-01 | 12:50 | 46200 | 4.6478 | 0 | 85.8455 |  | 2029-09-01 | 12:50 | 46200 | 0.61193 | 0 | 58.5384 |  | 2029-09-01 | 12:50 | 46200 | 0.04217 | 0 | 40.0065 |  | 2006-09-01 | 12:50 | 46200 | 0.032918 | 0 | 39.444 |  | 2028-01-01 | 12:50 | 46200 | 1.4785 | 0 | 70.9207 |  | 2007-01-01 | 12:50 | 46200 | 0.0076363 | 0 | 74.3574 |  | 2028-01-01 | 12:50 | 46200 | 0.027972 | 0 | 35.3883 |  | 2007-01-01 | 12:50 | 46200 | 8.5067e-05 | 0 | 36.4237
| 2029-09-01 | 12:51 | 46260 | 214.234 | 0 | 272.5466 |  | 2029-09-01 | 12:51 | 46260 | 1.3402 | 0 | 204.0684 |  | 2006-09-01 | 12:51 | 46260 | 1.6755e-05 | 0 | 185.4626 |  | 2029-09-01 | 12:51 | 46260 | 0.81929 | 0 | 137.3843 |  | 2006-09-01 | 12:51 | 46260 | 6.8021e-06 | 0 | 92.0033 |  | 2028-01-01 | 12:51 | 46260 | 5.3855 | 0 | 204.8087 |  | 2007-01-01 | 12:51 | 46260 | 0.019798 | 0 | 186.7256 |  | 2028-01-01 | 12:51 | 46260 | 1.3564 | 0 | 70.9207 |  | 2007-01-01 | 12:51 | 46260 | 0.0060234 | 0 | 74.3574 |  | 2029-09-01 | 12:51 | 46260 | 0.049865 | 0 | 195.7767 |  | 2006-09-01 | 12:51 | 46260 | 1.9412e-09 | 0 | 183.5322 |  | 2029-09-01 | 12:51 | 46260 | 0.021372 | 0 | 101.9131 |  | 2006-09-01 | 12:51 | 46260 | 4.7669e-10 | 0 | 59.3356 |  | 2028-01-01 | 12:51 | 46260 | 0.25638 | 0 | 194.1261 |  | 2007-01-01 | 12:51 | 46260 | 7.2121e-05 | 0 | 185.5959 |  | 2028-01-01 | 12:51 | 46260 | 0.039563 | 0 | 41.8304 |  | 2007-01-01 | 12:51 | 46260 | 1.2411e-05 | 0 | 45.3878 |  | 2029-09-01 | 12:51 | 46260 | 0.0077131 | 0 | 194.1073 |  | 2006-09-01 | 12:51 | 46260 | 1.4618e-11 | 0 | 183.3428 |  | 2029-09-01 | 12:51 | 46260 | 0.0024428 | 0 | 82.1193 |  | 2006-09-01 | 12:51 | 46260 | 2.5565e-12 | 0 | 43.6339 |  | 2028-01-01 | 12:51 | 46260 | 0.016984 | 0 | 191.5756 |  | 2007-01-01 | 12:51 | 46260 | 2.5677e-06 | 0 | 185.5128 |  | 2028-01-01 | 12:51 | 46260 | 0.001879 | 0 | 29.6806 |  | 2007-01-01 | 12:51 | 46260 | 3.0669e-07 | 0 | 32.555 |  | 2029-09-01 | 12:51 | 46260 | 4.3697 | 0 | 85.8455 |  | 2029-09-01 | 12:51 | 46260 | 0.55719 | 0 | 58.5384 |  | 2029-09-01 | 12:51 | 46260 | 0.036701 | 0 | 40.0065 |  | 2006-09-01 | 12:51 | 46260 | 0.028511 | 0 | 39.444 |  | 2028-01-01 | 12:51 | 46260 | 1.3564 | 0 | 70.9207 |  | 2007-01-01 | 12:51 | 46260 | 0.0060234 | 0 | 74.3574 |  | 2028-01-01 | 12:51 | 46260 | 0.023857 | 0 | 35.3883 |  | 2007-01-01 | 12:51 | 46260 | 6.256e-05 | 0 | 36.4237
| 2029-09-01 | 12:52 | 46320 | 211.517 | 0 | 272.5466 |  | 2029-09-01 | 12:52 | 46320 | 1.1919 | 0 | 204.0684 |  | 2006-09-01 | 12:52 | 46320 | 1.1901e-05 | 0 | 185.4626 |  | 2029-09-01 | 12:52 | 46320 | 0.72863 | 0 | 137.3843 |  | 2006-09-01 | 12:52 | 46320 | 4.8312e-06 | 0 | 92.0033 |  | 2028-01-01 | 12:52 | 46320 | 4.9484 | 0 | 204.8087 |  | 2007-01-01 | 12:52 | 46320 | 0.015587 | 0 | 186.7256 |  | 2028-01-01 | 12:52 | 46320 | 1.2446 | 0 | 70.9207 |  | 2007-01-01 | 12:52 | 46320 | 0.0047423 | 0 | 74.3574 |  | 2029-09-01 | 12:52 | 46320 | 0.041359 | 0 | 195.7767 |  | 2006-09-01 | 12:52 | 46320 | 1.1462e-09 | 0 | 183.5322 |  | 2029-09-01 | 12:52 | 46320 | 0.017726 | 0 | 101.9131 |  | 2006-09-01 | 12:52 | 46320 | 2.8147e-10 | 0 | 59.3356 |  | 2028-01-01 | 12:52 | 46320 | 0.22057 | 0 | 194.1261 |  | 2007-01-01 | 12:52 | 46320 | 4.951e-05 | 0 | 185.5959 |  | 2028-01-01 | 12:52 | 46320 | 0.034036 | 0 | 41.8304 |  | 2007-01-01 | 12:52 | 46320 | 8.5201e-06 | 0 | 45.3878 |  | 2029-09-01 | 12:52 | 46320 | 0.00615 | 0 | 194.1073 |  | 2006-09-01 | 12:52 | 46320 | 7.8163e-12 | 0 | 183.3428 |  | 2029-09-01 | 12:52 | 46320 | 0.0019478 | 0 | 82.1193 |  | 2006-09-01 | 12:52 | 46320 | 1.3668e-12 | 0 | 43.6339 |  | 2028-01-01 | 12:52 | 46320 | 0.013762 | 0 | 191.5756 |  | 2007-01-01 | 12:52 | 46320 | 1.6363e-06 | 0 | 185.5128 |  | 2028-01-01 | 12:52 | 46320 | 0.0015229 | 0 | 29.6806 |  | 2007-01-01 | 12:52 | 46320 | 1.9544e-07 | 0 | 32.555 |  | 2029-09-01 | 12:52 | 46320 | 4.1082 | 0 | 85.8455 |  | 2029-09-01 | 12:52 | 46320 | 0.50735 | 0 | 58.5384 |  | 2029-09-01 | 12:52 | 46320 | 0.031941 | 0 | 40.0065 |  | 2006-09-01 | 12:52 | 46320 | 0.024694 | 0 | 39.444 |  | 2028-01-01 | 12:52 | 46320 | 1.2446 | 0 | 70.9207 |  | 2007-01-01 | 12:52 | 46320 | 0.0047423 | 0 | 74.3574 |  | 2028-01-01 | 12:52 | 46320 | 0.020351 | 0 | 35.3883 |  | 2007-01-01 | 12:52 | 46320 | 4.5927e-05 | 0 | 36.4237
| 2029-09-01 | 12:53 | 46380 | 208.834 | 0 | 272.5466 |  | 2029-09-01 | 12:53 | 46380 | 1.0596 | 0 | 204.0684 |  | 2006-09-01 | 12:53 | 46380 | 8.4473e-06 | 0 | 185.4626 |  | 2029-09-01 | 12:53 | 46380 | 0.64775 | 0 | 137.3843 |  | 2006-09-01 | 12:53 | 46380 | 3.4293e-06 | 0 | 92.0033 |  | 2028-01-01 | 12:53 | 46380 | 4.5489 | 0 | 204.8087 |  | 2007-01-01 | 12:53 | 46380 | 0.012249 | 0 | 186.7256 |  | 2028-01-01 | 12:53 | 46380 | 1.1427 | 0 | 70.9207 |  | 2007-01-01 | 12:53 | 46380 | 0.0037267 | 0 | 74.3574 |  | 2029-09-01 | 12:53 | 46380 | 0.034283 | 0 | 195.7767 |  | 2006-09-01 | 12:53 | 46380 | 6.7618e-10 | 0 | 183.5322 |  | 2029-09-01 | 12:53 | 46380 | 0.014694 | 0 | 101.9131 |  | 2006-09-01 | 12:53 | 46380 | 1.6605e-10 | 0 | 59.3356 |  | 2028-01-01 | 12:53 | 46380 | 0.18991 | 0 | 194.1261 |  | 2007-01-01 | 12:53 | 46380 | 3.3891e-05 | 0 | 185.5959 |  | 2028-01-01 | 12:53 | 46380 | 0.029304 | 0 | 41.8304 |  | 2007-01-01 | 12:53 | 46380 | 5.8323e-06 | 0 | 45.3878 |  | 2029-09-01 | 12:53 | 46380 | 0.0049002 | 0 | 194.1073 |  | 2006-09-01 | 12:53 | 46380 | 4.1749e-12 | 0 | 183.3428 |  | 2029-09-01 | 12:53 | 46380 | 0.0015519 | 0 | 82.1193 |  | 2006-09-01 | 12:53 | 46380 | 7.3007e-13 | 0 | 43.6339 |  | 2028-01-01 | 12:53 | 46380 | 0.011161 | 0 | 191.5756 |  | 2007-01-01 | 12:53 | 46380 | 1.0392e-06 | 0 | 185.5128 |  | 2028-01-01 | 12:53 | 46380 | 0.0012354 | 0 | 29.6806 |  | 2007-01-01 | 12:53 | 46380 | 1.2412e-07 | 0 | 32.555 |  | 2029-09-01 | 12:53 | 46380 | 3.8625 | 0 | 85.8455 |  | 2029-09-01 | 12:53 | 46380 | 0.46196 | 0 | 58.5384 |  | 2029-09-01 | 12:53 | 46380 | 0.027798 | 0 | 40.0065 |  | 2006-09-01 | 12:53 | 46380 | 0.021388 | 0 | 39.444 |  | 2028-01-01 | 12:53 | 46380 | 1.1427 | 0 | 70.9207 |  | 2007-01-01 | 12:53 | 46380 | 0.0037267 | 0 | 74.3574 |  | 2028-01-01 | 12:53 | 46380 | 0.017365 | 0 | 35.3883 |  | 2007-01-01 | 12:53 | 46380 | 3.3658e-05 | 0 | 36.4237
| 2029-09-01 | 12:54 | 46440 | 206.186 | 0 | 272.5466 |  | 2029-09-01 | 12:54 | 46440 | 0.94166 | 0 | 204.0684 |  | 2006-09-01 | 12:54 | 46440 | 5.9924e-06 | 0 | 185.4626 |  | 2029-09-01 | 12:54 | 46440 | 0.57563 | 0 | 137.3843 |  | 2006-09-01 | 12:54 | 46440 | 2.4327e-06 | 0 | 92.0033 |  | 2028-01-01 | 12:54 | 46440 | 4.1843 | 0 | 204.8087 |  | 2007-01-01 | 12:54 | 46440 | 0.0096077 | 0 | 186.7256 |  | 2028-01-01 | 12:54 | 46440 | 1.0498 | 0 | 70.9207 |  | 2007-01-01 | 12:54 | 46440 | 0.0029231 | 0 | 74.3574 |  | 2029-09-01 | 12:54 | 46440 | 0.0284 | 0 | 195.7767 |  | 2006-09-01 | 12:54 | 46440 | 3.9856e-10 | 0 | 183.5322 |  | 2029-09-01 | 12:54 | 46440 | 0.012172 | 0 | 101.9131 |  | 2006-09-01 | 12:54 | 46440 | 9.7874e-11 | 0 | 59.3356 |  | 2028-01-01 | 12:54 | 46440 | 0.16369 | 0 | 194.1261 |  | 2007-01-01 | 12:54 | 46440 | 2.3134e-05 | 0 | 185.5959 |  | 2028-01-01 | 12:54 | 46440 | 0.025256 | 0 | 41.8304 |  | 2007-01-01 | 12:54 | 46440 | 3.9811e-06 | 0 | 45.3878 |  | 2029-09-01 | 12:54 | 46440 | 0.0039015 | 0 | 194.1073 |  | 2006-09-01 | 12:54 | 46440 | 2.2285e-12 | 0 | 183.3428 |  | 2029-09-01 | 12:54 | 46440 | 0.0012356 | 0 | 82.1193 |  | 2006-09-01 | 12:54 | 46440 | 3.8955e-13 | 0 | 43.6339 |  | 2028-01-01 | 12:54 | 46440 | 0.0090637 | 0 | 191.5756 |  | 2007-01-01 | 12:54 | 46440 | 6.5778e-07 | 0 | 185.5128 |  | 2028-01-01 | 12:54 | 46440 | 0.0010035 | 0 | 29.6806 |  | 2007-01-01 | 12:54 | 46440 | 7.8566e-08 | 0 | 32.555 |  | 2029-09-01 | 12:54 | 46440 | 3.6314 | 0 | 85.8455 |  | 2029-09-01 | 12:54 | 46440 | 0.42064 | 0 | 58.5384 |  | 2029-09-01 | 12:54 | 46440 | 0.024192 | 0 | 40.0065 |  | 2006-09-01 | 12:54 | 46440 | 0.018524 | 0 | 39.444 |  | 2028-01-01 | 12:54 | 46440 | 1.0498 | 0 | 70.9207 |  | 2007-01-01 | 12:54 | 46440 | 0.0029231 | 0 | 74.3574 |  | 2028-01-01 | 12:54 | 46440 | 0.014823 | 0 | 35.3883 |  | 2007-01-01 | 12:54 | 46440 | 2.4623e-05 | 0 | 36.4237
| 2029-09-01 | 12:55 | 46500 | 203.57 | 0 | 272.5466 |  | 2029-09-01 | 12:55 | 46500 | 0.83649 | 0 | 204.0684 |  | 2006-09-01 | 12:55 | 46500 | 4.2483e-06 | 0 | 185.4626 |  | 2029-09-01 | 12:55 | 46500 | 0.51135 | 0 | 137.3843 |  | 2006-09-01 | 12:55 | 46500 | 1.7247e-06 | 0 | 92.0033 |  | 2028-01-01 | 12:55 | 46500 | 3.8513 | 0 | 204.8087 |  | 2007-01-01 | 12:55 | 46500 | 0.0075218 | 0 | 186.7256 |  | 2028-01-01 | 12:55 | 46500 | 0.96512 | 0 | 70.9207 |  | 2007-01-01 | 12:55 | 46500 | 0.0022885 | 0 | 74.3574 |  | 2029-09-01 | 12:55 | 46500 | 0.023512 | 0 | 195.7767 |  | 2006-09-01 | 12:55 | 46500 | 2.3471e-10 | 0 | 183.5322 |  | 2029-09-01 | 12:55 | 46500 | 0.010077 | 0 | 101.9131 |  | 2006-09-01 | 12:55 | 46500 | 5.7639e-11 | 0 | 59.3356 |  | 2028-01-01 | 12:55 | 46500 | 0.14123 | 0 | 194.1261 |  | 2007-01-01 | 12:55 | 46500 | 1.5746e-05 | 0 | 185.5959 |  | 2028-01-01 | 12:55 | 46500 | 0.02179 | 0 | 41.8304 |  | 2007-01-01 | 12:55 | 46500 | 2.7098e-06 | 0 | 45.3878 |  | 2029-09-01 | 12:55 | 46500 | 0.0031041 | 0 | 194.1073 |  | 2006-09-01 | 12:55 | 46500 | 1.1879e-12 | 0 | 183.3428 |  | 2029-09-01 | 12:55 | 46500 | 0.00098309 | 0 | 82.1193 |  | 2006-09-01 | 12:55 | 46500 | 2.0765e-13 | 0 | 43.6339 |  | 2028-01-01 | 12:55 | 46500 | 0.0073699 | 0 | 191.5756 |  | 2007-01-01 | 12:55 | 46500 | 4.1495e-07 | 0 | 185.5128 |  | 2028-01-01 | 12:55 | 46500 | 0.00081616 | 0 | 29.6806 |  | 2007-01-01 | 12:55 | 46500 | 4.9563e-08 | 0 | 32.555 |  | 2029-09-01 | 12:55 | 46500 | 3.4141 | 0 | 85.8455 |  | 2029-09-01 | 12:55 | 46500 | 0.38301 | 0 | 58.5384 |  | 2029-09-01 | 12:55 | 46500 | 0.021055 | 0 | 40.0065 |  | 2006-09-01 | 12:55 | 46500 | 0.016043 | 0 | 39.444 |  | 2028-01-01 | 12:55 | 46500 | 0.96512 | 0 | 70.9207 |  | 2007-01-01 | 12:55 | 46500 | 0.0022885 | 0 | 74.3574 |  | 2028-01-01 | 12:55 | 46500 | 0.01266 | 0 | 35.3883 |  | 2007-01-01 | 12:55 | 46500 | 1.7982e-05 | 0 | 36.4237
| 2029-09-01 | 12:56 | 46560 | 200.988 | 0 | 272.5466 |  | 2029-09-01 | 12:56 | 46560 | 0.74279 | 0 | 204.0684 |  | 2006-09-01 | 12:56 | 46560 | 3.01e-06 | 0 | 185.4626 |  | 2029-09-01 | 12:56 | 46560 | 0.45407 | 0 | 137.3843 |  | 2006-09-01 | 12:56 | 46560 | 1.222e-06 | 0 | 92.0033 |  | 2028-01-01 | 12:56 | 46560 | 3.547 | 0 | 204.8087 |  | 2007-01-01 | 12:56 | 46560 | 0.0058778 | 0 | 186.7256 |  | 2028-01-01 | 12:56 | 46560 | 0.88786 | 0 | 70.9207 |  | 2007-01-01 | 12:56 | 46560 | 0.0017883 | 0 | 74.3574 |  | 2029-09-01 | 12:56 | 46560 | 0.019454 | 0 | 195.7767 |  | 2006-09-01 | 12:56 | 46560 | 1.381e-10 | 0 | 183.5322 |  | 2029-09-01 | 12:56 | 46560 | 0.008338 | 0 | 101.9131 |  | 2006-09-01 | 12:56 | 46560 | 3.3914e-11 | 0 | 59.3356 |  | 2028-01-01 | 12:56 | 46560 | 0.12198 | 0 | 194.1261 |  | 2007-01-01 | 12:56 | 46560 | 1.0688e-05 | 0 | 185.5959 |  | 2028-01-01 | 12:56 | 46560 | 0.01882 | 0 | 41.8304 |  | 2007-01-01 | 12:56 | 46560 | 1.8392e-06 | 0 | 45.3878 |  | 2029-09-01 | 12:56 | 46560 | 0.0024679 | 0 | 194.1073 |  | 2006-09-01 | 12:56 | 46560 | 6.3346e-13 | 0 | 183.3428 |  | 2029-09-01 | 12:56 | 46560 | 0.00078159 | 0 | 82.1193 |  | 2006-09-01 | 12:56 | 46560 | 1.1058e-13 | 0 | 43.6339 |  | 2028-01-01 | 12:56 | 46560 | 0.0060005 | 0 | 191.5756 |  | 2007-01-01 | 12:56 | 46560 | 2.6089e-07 | 0 | 185.5128 |  | 2028-01-01 | 12:56 | 46560 | 0.00066465 | 0 | 29.6806 |  | 2007-01-01 | 12:56 | 46560 | 3.1162e-08 | 0 | 32.555 |  | 2029-09-01 | 12:56 | 46560 | 3.2098 | 0 | 85.8455 |  | 2029-09-01 | 12:56 | 46560 | 0.34875 | 0 | 58.5384 |  | 2029-09-01 | 12:56 | 46560 | 0.018324 | 0 | 40.0065 |  | 2006-09-01 | 12:56 | 46560 | 0.013895 | 0 | 39.444 |  | 2028-01-01 | 12:56 | 46560 | 0.88786 | 0 | 70.9207 |  | 2007-01-01 | 12:56 | 46560 | 0.0017883 | 0 | 74.3574 |  | 2028-01-01 | 12:56 | 46560 | 0.010818 | 0 | 35.3883 |  | 2007-01-01 | 12:56 | 46560 | 1.3109e-05 | 0 | 36.4237
| 2029-09-01 | 12:57 | 46620 | 198.438 | 0 | 272.5466 |  | 2029-09-01 | 12:57 | 46620 | 0.65933 | 0 | 204.0684 |  | 2006-09-01 | 12:57 | 46620 | 2.1313e-06 | 0 | 185.4626 |  | 2029-09-01 | 12:57 | 46620 | 0.40305 | 0 | 137.3843 |  | 2006-09-01 | 12:57 | 46620 | 8.6526e-07 | 0 | 92.0033 |  | 2028-01-01 | 12:57 | 46620 | 3.2687 | 0 | 204.8087 |  | 2007-01-01 | 12:57 | 46620 | 0.0045844 | 0 | 186.7256 |  | 2028-01-01 | 12:57 | 46620 | 0.81732 | 0 | 70.9207 |  | 2007-01-01 | 12:57 | 46620 | 0.0013948 | 0 | 74.3574 |  | 2029-09-01 | 12:57 | 46620 | 0.016086 | 0 | 195.7767 |  | 2006-09-01 | 12:57 | 46620 | 8.1189e-11 | 0 | 183.5322 |  | 2029-09-01 | 12:57 | 46620 | 0.0068946 | 0 | 101.9131 |  | 2006-09-01 | 12:57 | 46620 | 1.9937e-11 | 0 | 59.3356 |  | 2028-01-01 | 12:57 | 46620 | 0.10547 | 0 | 194.1261 |  | 2007-01-01 | 12:57 | 46620 | 7.2336e-06 | 0 | 185.5959 |  | 2028-01-01 | 12:57 | 46620 | 0.016271 | 0 | 41.8304 |  | 2007-01-01 | 12:57 | 46620 | 1.2448e-06 | 0 | 45.3878 |  | 2029-09-01 | 12:57 | 46620 | 0.0019606 | 0 | 194.1073 |  | 2006-09-01 | 12:57 | 46620 | 3.3786e-13 | 0 | 183.3428 |  | 2029-09-01 | 12:57 | 46620 | 0.00062094 | 0 | 82.1193 |  | 2006-09-01 | 12:57 | 46620 | 5.8826e-14 | 0 | 43.6339 |  | 2028-01-01 | 12:57 | 46620 | 0.0048921 | 0 | 191.5756 |  | 2007-01-01 | 12:57 | 46620 | 1.6348e-07 | 0 | 185.5128 |  | 2028-01-01 | 12:57 | 46620 | 0.00054198 | 0 | 29.6806 |  | 2007-01-01 | 12:57 | 46620 | 1.9527e-08 | 0 | 32.555 |  | 2029-09-01 | 12:57 | 46620 | 3.0178 | 0 | 85.8455 |  | 2029-09-01 | 12:57 | 46620 | 0.31755 | 0 | 58.5384 |  | 2029-09-01 | 12:57 | 46620 | 0.015947 | 0 | 40.0065 |  | 2006-09-01 | 12:57 | 46620 | 0.012034 | 0 | 39.444 |  | 2028-01-01 | 12:57 | 46620 | 0.81732 | 0 | 70.9207 |  | 2007-01-01 | 12:57 | 46620 | 0.0013948 | 0 | 74.3574 |  | 2028-01-01 | 12:57 | 46620 | 0.0092482 | 0 | 35.3883 |  | 2007-01-01 | 12:57 | 46620 | 9.5399e-06 | 0 | 36.4237
| 2029-09-01 | 12:58 | 46680 | 195.921 | 0 | 272.5466 |  | 2029-09-01 | 12:58 | 46680 | 0.58502 | 0 | 204.0684 |  | 2006-09-01 | 12:58 | 46680 | 1.5083e-06 | 0 | 185.4626 |  | 2029-09-01 | 12:58 | 46680 | 0.35762 | 0 | 137.3843 |  | 2006-09-01 | 12:58 | 46680 | 6.1231e-07 | 0 | 92.0033 |  | 2028-01-01 | 12:58 | 46680 | 3.014 | 0 | 204.8087 |  | 2007-01-01 | 12:58 | 46680 | 0.003569 | 0 | 186.7256 |  | 2028-01-01 | 12:58 | 46680 | 0.75287 | 0 | 70.9207 |  | 2007-01-01 | 12:58 | 46680 | 0.0010858 | 0 | 74.3574 |  | 2029-09-01 | 12:58 | 46680 | 0.013293 | 0 | 195.7767 |  | 2006-09-01 | 12:58 | 46680 | 4.7688e-11 | 0 | 183.5322 |  | 2029-09-01 | 12:58 | 46680 | 0.0056976 | 0 | 101.9131 |  | 2006-09-01 | 12:58 | 46680 | 1.1711e-11 | 0 | 59.3356 |  | 2028-01-01 | 12:58 | 46680 | 0.091284 | 0 | 194.1261 |  | 2007-01-01 | 12:58 | 46680 | 4.8821e-06 | 0 | 185.5959 |  | 2028-01-01 | 12:58 | 46680 | 0.014082 | 0 | 41.8304 |  | 2007-01-01 | 12:58 | 46680 | 8.4014e-07 | 0 | 45.3878 |  | 2029-09-01 | 12:58 | 46680 | 0.0015565 | 0 | 194.1073 |  | 2006-09-01 | 12:58 | 46680 | 1.8043e-13 | 0 | 183.3428 |  | 2029-09-01 | 12:58 | 46680 | 0.00049295 | 0 | 82.1193 |  | 2006-09-01 | 12:58 | 46680 | 3.1494e-14 | 0 | 43.6339 |  | 2028-01-01 | 12:58 | 46680 | 0.0039936 | 0 | 191.5756 |  | 2007-01-01 | 12:58 | 46680 | 1.021e-07 | 0 | 185.5128 |  | 2028-01-01 | 12:58 | 46680 | 0.00044253 | 0 | 29.6806 |  | 2007-01-01 | 12:58 | 46680 | 1.2195e-08 | 0 | 32.555 |  | 2029-09-01 | 12:58 | 46680 | 2.8372 | 0 | 85.8455 |  | 2029-09-01 | 12:58 | 46680 | 0.28914 | 0 | 58.5384 |  | 2029-09-01 | 12:58 | 46680 | 0.013879 | 0 | 40.0065 |  | 2006-09-01 | 12:58 | 46680 | 0.010422 | 0 | 39.444 |  | 2028-01-01 | 12:58 | 46680 | 0.75287 | 0 | 70.9207 |  | 2007-01-01 | 12:58 | 46680 | 0.0010858 | 0 | 74.3574 |  | 2028-01-01 | 12:58 | 46680 | 0.0079109 | 0 | 35.3883 |  | 2007-01-01 | 12:58 | 46680 | 6.9304e-06 | 0 | 36.4237
| 2029-09-01 | 12:59 | 46740 | 193.435 | 0 | 272.5466 |  | 2029-09-01 | 12:59 | 46740 | 0.51889 | 0 | 204.0684 |  | 2006-09-01 | 12:59 | 46740 | 1.0667e-06 | 0 | 185.4626 |  | 2029-09-01 | 12:59 | 46740 | 0.3172 | 0 | 137.3843 |  | 2006-09-01 | 12:59 | 46740 | 4.3304e-07 | 0 | 92.0033 |  | 2028-01-01 | 12:59 | 46740 | 2.7807 | 0 | 204.8087 |  | 2007-01-01 | 12:59 | 46740 | 0.0027733 | 0 | 186.7256 |  | 2028-01-01 | 12:59 | 46740 | 0.69392 | 0 | 70.9207 |  | 2007-01-01 | 12:59 | 46740 | 0.00084375 | 0 | 74.3574 |  | 2029-09-01 | 12:59 | 46740 | 0.010979 | 0 | 195.7767 |  | 2006-09-01 | 12:59 | 46740 | 2.7986e-11 | 0 | 183.5322 |  | 2029-09-01 | 12:59 | 46740 | 0.0047056 | 0 | 101.9131 |  | 2006-09-01 | 12:59 | 46740 | 6.8723e-12 | 0 | 59.3356 |  | 2028-01-01 | 12:59 | 46740 | 0.079087 | 0 | 194.1261 |  | 2007-01-01 | 12:59 | 46740 | 3.2857e-06 | 0 | 185.5959 |  | 2028-01-01 | 12:59 | 46740 | 0.012201 | 0 | 41.8304 |  | 2007-01-01 | 12:59 | 46740 | 5.6543e-07 | 0 | 45.3878 |  | 2029-09-01 | 12:59 | 46740 | 0.0012348 | 0 | 194.1073 |  | 2006-09-01 | 12:59 | 46740 | 9.6666e-14 | 0 | 183.3428 |  | 2029-09-01 | 12:59 | 46740 | 0.00039106 | 0 | 82.1193 |  | 2006-09-01 | 12:59 | 46740 | 1.6721e-14 | 0 | 43.6339 |  | 2028-01-01 | 12:59 | 46740 | 0.0032644 | 0 | 191.5756 |  | 2007-01-01 | 12:59 | 46740 | 6.3557e-08 | 0 | 185.5128 |  | 2028-01-01 | 12:59 | 46740 | 0.0003618 | 0 | 29.6806 |  | 2007-01-01 | 12:59 | 46740 | 7.5914e-09 | 0 | 32.555 |  | 2029-09-01 | 12:59 | 46740 | 2.6675 | 0 | 85.8455 |  | 2029-09-01 | 12:59 | 46740 | 0.26327 | 0 | 58.5384 |  | 2029-09-01 | 12:59 | 46740 | 0.012079 | 0 | 40.0065 |  | 2006-09-01 | 12:59 | 46740 | 0.0090255 | 0 | 39.444 |  | 2028-01-01 | 12:59 | 46740 | 0.69392 | 0 | 70.9207 |  | 2007-01-01 | 12:59 | 46740 | 0.00084375 | 0 | 74.3574 |  | 2028-01-01 | 12:59 | 46740 | 0.0067708 | 0 | 35.3883 |  | 2007-01-01 | 12:59 | 46740 | 5.0259e-06 | 0 | 36.4237
4 | 2029-09-01 | 13:00 | 46800 | 190.981 | 1.1459 | 273.6925 |  | 2029-09-01 | 13:00 | 46800 | 0.46005 | 0.0027603 | 204.0712 |  | 2006-09-01 | 13:00 | 46800 | 7.5392e-07 | 4.5235e-09 | 185.4626 |  | 2029-09-01 | 13:00 | 46800 | 0.28123 | 0.0016874 | 137.386 |  | 2006-09-01 | 13:00 | 46800 | 3.0607e-07 | 1.8364e-09 | 92.0033 |  | 2028-01-01 | 13:00 | 46800 | 2.567 | 0.015402 | 204.8241 |  | 2007-01-01 | 13:00 | 46800 | 0.0021509 | 1.2906e-05 | 186.7256 |  | 2028-01-01 | 13:00 | 46800 | 0.63999 | 0.0038399 | 70.9245 |  | 2007-01-01 | 13:00 | 46800 | 0.00065441 | 3.9264e-06 | 74.3574 |  | 2029-09-01 | 13:00 | 46800 | 0.0090618 | 5.4371e-05 | 195.7768 |  | 2006-09-01 | 13:00 | 46800 | 1.641e-11 | 9.846e-14 | 183.5322 |  | 2029-09-01 | 13:00 | 46800 | 0.0038839 | 2.3303e-05 | 101.9131 |  | 2006-09-01 | 13:00 | 46800 | 4.0295e-12 | 2.4177e-14 | 59.3356 |  | 2028-01-01 | 13:00 | 46800 | 0.06859 | 0.00041154 | 194.1265 |  | 2007-01-01 | 13:00 | 46800 | 2.2051e-06 | 1.3231e-08 | 185.5959 |  | 2028-01-01 | 13:00 | 46800 | 0.010581 | 6.3485e-05 | 41.8305 |  | 2007-01-01 | 13:00 | 46800 | 3.7947e-07 | 2.2768e-09 | 45.3878 |  | 2029-09-01 | 13:00 | 46800 | 0.00097883 | 5.873e-06 | 194.1073 |  | 2006-09-01 | 13:00 | 46800 | 5.1271e-14 | 3.0762e-16 | 183.3428 |  | 2029-09-01 | 13:00 | 46800 | 0.00031 | 1.86e-06 | 82.1193 |  | 2006-09-01 | 13:00 | 46800 | 8.8686e-15 | 5.3212e-17 | 43.6339 |  | 2028-01-01 | 13:00 | 46800 | 0.0026719 | 1.6032e-05 | 191.5756 |  | 2007-01-01 | 13:00 | 46800 | 3.9432e-08 | 2.3659e-10 | 185.5128 |  | 2028-01-01 | 13:00 | 46800 | 0.00029618 | 1.7771e-06 | 29.6806 |  | 2007-01-01 | 13:00 | 46800 | 4.7098e-09 | 2.8259e-11 | 32.555 |  | 2029-09-01 | 13:00 | 46800 | 2.5078 | 0.015047 | 85.8606 |  | 2029-09-01 | 13:00 | 46800 | 0.23972 | 0.0014383 | 58.5398 |  | 2029-09-01 | 13:00 | 46800 | 0.010512 | 6.3073e-05 | 40.0066 |  | 2006-09-01 | 13:00 | 46800 | 0.0078163 | 4.6898e-05 | 39.444 |  | 2028-01-01 | 13:00 | 46800 | 0.63999 | 0.0038399 | 70.9245 |  | 2007-01-01 | 13:00 | 46800 | 0.00065441 | 3.9264e-06 | 74.3574 |  | 2028-01-01 | 13:00 | 46800 | 0.0057985 | 3.4791e-05 | 35.3883 |  | 2007-01-01 | 13:00 | 46800 | 3.6384e-06 | 2.1831e-08 | 36.4237
| 2029-09-01 | 13:01 | 46860 | 194.964 | 1.1698 | 274.8623 |  | 2029-09-01 | 13:01 | 46860 | 6.9053 | 0.041432 | 204.1126 |  | 2006-09-01 | 13:01 | 46860 | 6.4215 | 0.038529 | 185.5012 |  | 2029-09-01 | 13:01 | 46860 | 6.5389 | 0.039233 | 137.4253 |  | 2006-09-01 | 13:01 | 46860 | 6.2181 | 0.037309 | 92.0406 |  | 2028-01-01 | 13:01 | 46860 | 8.996 | 0.053976 | 204.8781 |  | 2007-01-01 | 13:01 | 46860 | 6.4449 | 0.038669 | 186.7643 |  | 2028-01-01 | 13:01 | 46860 | 6.6893 | 0.040136 | 70.9647 |  | 2007-01-01 | 13:01 | 46860 | 6.0982 | 0.036589 | 74.394 |  | 2029-09-01 | 13:01 | 46860 | 6.4601 | 0.038761 | 195.8155 |  | 2006-09-01 | 13:01 | 46860 | 6.4215 | 0.038529 | 183.5708 |  | 2029-09-01 | 13:01 | 46860 | 6.1043 | 0.036626 | 101.9497 |  | 2006-09-01 | 13:01 | 46860 | 6.0291 | 0.036175 | 59.3718 |  | 2028-01-01 | 13:01 | 46860 | 6.529 | 0.039174 | 194.1657 |  | 2007-01-01 | 13:01 | 46860 | 6.4428 | 0.038657 | 185.6346 |  | 2028-01-01 | 13:01 | 46860 | 5.7776 | 0.034665 | 41.8651 |  | 2007-01-01 | 13:01 | 46860 | 5.7942 | 0.034765 | 45.4226 |  | 2029-09-01 | 13:01 | 46860 | 6.4521 | 0.038713 | 194.1461 |  | 2006-09-01 | 13:01 | 46860 | 6.4215 | 0.038529 | 183.3814 |  | 2029-09-01 | 13:01 | 46860 | 5.9413 | 0.035648 | 82.1549 |  | 2006-09-01 | 13:01 | 46860 | 5.851 | 0.035106 | 43.669 |  | 2028-01-01 | 13:01 | 46860 | 6.4639 | 0.038783 | 191.6144 |  | 2007-01-01 | 13:01 | 46860 | 6.4428 | 0.038657 | 185.5515 |  | 2028-01-01 | 13:01 | 46860 | 5.4764 | 0.032858 | 29.7135 |  | 2007-01-01 | 13:01 | 46860 | 5.5193 | 0.033116 | 32.5881 |  | 2029-09-01 | 13:01 | 46860 | 8.5004 | 0.051002 | 85.9116 |  | 2029-09-01 | 13:01 | 46860 | 6.1678 | 0.037007 | 58.5768 |  | 2029-09-01 | 13:01 | 46860 | 5.6958 | 0.034175 | 40.0408 |  | 2006-09-01 | 13:01 | 46860 | 5.6706 | 0.034023 | 39.478 |  | 2028-01-01 | 13:01 | 46860 | 6.6893 | 0.040136 | 70.9647 |  | 2007-01-01 | 13:01 | 46860 | 6.0982 | 0.036589 | 74.394 |  | 2028-01-01 | 13:01 | 46860 | 5.6174 | 0.033704 | 35.422 |  | 2007-01-01 | 13:01 | 46860 | 5.616 | 0.033696 | 36.4574
| 2029-09-01 | 13:02 | 46920 | 198.899 | 1.1934 | 276.0557 |  | 2029-09-01 | 13:02 | 46920 | 13.2674 | 0.079604 | 204.1922 |  | 2006-09-01 | 13:02 | 46920 | 12.7307 | 0.076384 | 185.5776 |  | 2029-09-01 | 13:02 | 46920 | 12.5406 | 0.075244 | 137.5005 |  | 2006-09-01 | 13:02 | 46920 | 12.1322 | 0.072793 | 92.1134 |  | 2028-01-01 | 13:02 | 46920 | 15.3438 | 0.092063 | 204.9702 |  | 2007-01-01 | 13:02 | 46920 | 12.7897 | 0.076738 | 186.841 |  | 2028-01-01 | 13:02 | 46920 | 12.3226 | 0.073936 | 71.0386 |  | 2007-01-01 | 13:02 | 46920 | 11.7817 | 0.07069 | 74.4647 |  | 2029-09-01 | 13:02 | 46920 | 12.8279 | 0.076967 | 195.8925 |  | 2006-09-01 | 13:02 | 46920 | 12.7307 | 0.076384 | 183.6472 |  | 2029-09-01 | 13:02 | 46920 | 11.7975 | 0.070785 | 102.0205 |  | 2006-09-01 | 13:02 | 46920 | 11.5873 | 0.069524 | 59.4413 |  | 2028-01-01 | 13:02 | 46920 | 12.9078 | 0.077447 | 194.2431 |  | 2007-01-01 | 13:02 | 46920 | 12.7876 | 0.076726 | 185.7113 |  | 2028-01-01 | 13:02 | 46920 | 10.8618 | 0.065171 | 41.9303 |  | 2007-01-01 | 13:02 | 46920 | 10.9266 | 0.06556 | 45.4881 |  | 2029-09-01 | 13:02 | 46920 | 12.8201 | 0.076921 | 194.223 |  | 2006-09-01 | 13:02 | 46920 | 12.7307 | 0.076384 | 183.4578 |  | 2029-09-01 | 13:02 | 46920 | 11.3399 | 0.068039 | 82.223 |  | 2006-09-01 | 13:02 | 46920 | 11.084 | 0.066504 | 43.7355 |  | 2028-01-01 | 13:02 | 46920 | 12.8435 | 0.077061 | 191.6914 |  | 2007-01-01 | 13:02 | 46920 | 12.7876 | 0.076726 | 185.6282 |  | 2028-01-01 | 13:02 | 46920 | 10.06 | 0.06036 | 29.7738 |  | 2007-01-01 | 13:02 | 46920 | 10.1765 | 0.061059 | 32.6492 |  | 2029-09-01 | 13:02 | 46920 | 14.1333 | 0.0848 | 85.9964 |  | 2029-09-01 | 13:02 | 46920 | 11.5646 | 0.069388 | 58.6462 |  | 2029-09-01 | 13:02 | 46920 | 10.6428 | 0.063857 | 40.1046 |  | 2006-09-01 | 13:02 | 46920 | 10.5779 | 0.063467 | 39.5415 |  | 2028-01-01 | 13:02 | 46920 | 12.3226 | 0.073936 | 71.0386 |  | 2007-01-01 | 13:02 | 46920 | 11.7817 | 0.07069 | 74.4647 |  | 2028-01-01 | 13:02 | 46920 | 10.4306 | 0.062584 | 35.4846 |  | 2007-01-01 | 13:02 | 46920 | 10.4371 | 0.062623 | 36.52
| 2029-09-01 | 13:03 | 46980 | 202.786 | 1.2167 | 277.2724 |  | 2029-09-01 | 13:03 | 46980 | 19.5476 | 0.11729 | 204.3095 |  | 2006-09-01 | 13:03 | 46980 | 18.93 | 0.11358 | 185.6911 |  | 2029-09-01 | 13:03 | 46980 | 18.2962 | 0.10978 | 137.6103 |  | 2006-09-01 | 13:03 | 46980 | 17.7557 | 0.10653 | 92.2199 |  | 2028-01-01 | 13:03 | 46980 | 21.6114 | 0.12967 | 205.0998 |  | 2007-01-01 | 13:03 | 46980 | 19.0377 | 0.11423 | 186.9552 |  | 2028-01-01 | 13:03 | 46980 | 17.5689 | 0.10541 | 71.144 |  | 2007-01-01 | 13:03 | 46980 | 17.0792 | 0.10248 | 74.5672 |  | 2029-09-01 | 13:03 | 46980 | 19.1139 | 0.11468 | 196.0072 |  | 2006-09-01 | 13:03 | 46980 | 18.93 | 0.11358 | 183.7607 |  | 2029-09-01 | 13:03 | 46980 | 17.1092 | 0.10266 | 102.1232 |  | 2006-09-01 | 13:03 | 46980 | 16.7082 | 0.10025 | 59.5416 |  | 2028-01-01 | 13:03 | 46980 | 19.206 | 0.11524 | 194.3583 |  | 2007-01-01 | 13:03 | 46980 | 19.0356 | 0.11421 | 185.8255 |  | 2028-01-01 | 13:03 | 46980 | 15.3448 | 0.092069 | 42.0224 |  | 2007-01-01 | 13:03 | 46980 | 15.4731 | 0.092839 | 45.581 |  | 2029-09-01 | 13:03 | 46980 | 19.1061 | 0.11464 | 194.3376 |  | 2006-09-01 | 13:03 | 46980 | 18.93 | 0.11358 | 183.5713 |  | 2029-09-01 | 13:03 | 46980 | 16.244 | 0.097464 | 82.3204 |  | 2006-09-01 | 13:03 | 46980 | 15.76 | 0.09456 | 43.8301 |  | 2028-01-01 | 13:03 | 46980 | 19.1426 | 0.11486 | 191.8063 |  | 2007-01-01 | 13:03 | 46980 | 19.0356 | 0.11421 | 185.7424 |  | 2028-01-01 | 13:03 | 46980 | 13.8974 | 0.083384 | 29.8572 |  | 2007-01-01 | 13:03 | 46980 | 14.1069 | 0.084641 | 32.7338 |  | 2029-09-01 | 13:03 | 46980 | 19.4283 | 0.11657 | 86.113 |  | 2029-09-01 | 13:03 | 46980 | 16.4778 | 0.098867 | 58.7451 |  | 2029-09-01 | 13:03 | 46980 | 14.9475 | 0.089685 | 40.1943 |  | 2006-09-01 | 13:03 | 46980 | 14.8307 | 0.088984 | 39.6305 |  | 2028-01-01 | 13:03 | 46980 | 17.5689 | 0.10541 | 71.144 |  | 2007-01-01 | 13:03 | 46980 | 17.0792 | 0.10248 | 74.5672 |  | 2028-01-01 | 13:03 | 46980 | 14.5593 | 0.087356 | 35.5719 |  | 2007-01-01 | 13:03 | 46980 | 14.5759 | 0.087455 | 36.6075
| 2029-09-01 | 13:04 | 47040 | 206.626 | 1.2398 | 278.5121 |  | 2029-09-01 | 13:04 | 47040 | 25.7474 | 0.15448 | 204.464 |  | 2006-09-01 | 13:04 | 47040 | 25.0218 | 0.15013 | 185.8413 |  | 2029-09-01 | 13:04 | 47040 | 23.815 | 0.14289 | 137.7532 |  | 2006-09-01 | 13:04 | 47040 | 23.1012 | 0.13861 | 92.3585 |  | 2028-01-01 | 13:04 | 47040 | 27.7998 | 0.1668 | 205.2666 |  | 2007-01-01 | 13:04 | 47040 | 25.19 | 0.15114 | 187.1064 |  | 2028-01-01 | 13:04 | 47040 | 22.4552 | 0.13473 | 71.2787 |  | 2007-01-01 | 13:04 | 47040 | 22.017 | 0.1321 | 74.6993 |  | 2029-09-01 | 13:04 | 47040 | 25.3192 | 0.15192 | 196.1591 |  | 2006-09-01 | 13:04 | 47040 | 25.0218 | 0.15013 | 183.9109 |  | 2029-09-01 | 13:04 | 47040 | 22.0639 | 0.13238 | 102.2555 |  | 2006-09-01 | 13:04 | 47040 | 21.4234 | 0.12854 | 59.6701 |  | 2028-01-01 | 13:04 | 47040 | 25.4247 | 0.15255 | 194.5109 |  | 2007-01-01 | 13:04 | 47040 | 25.188 | 0.15113 | 185.9766 |  | 2028-01-01 | 13:04 | 47040 | 19.2982 | 0.11579 | 42.1382 |  | 2007-01-01 | 13:04 | 47040 | 19.5009 | 0.11701 | 45.698 |  | 2029-09-01 | 13:04 | 47040 | 25.3115 | 0.15187 | 194.4895 |  | 2006-09-01 | 13:04 | 47040 | 25.0218 | 0.15013 | 183.7215 |  | 2029-09-01 | 13:04 | 47040 | 20.697 | 0.12418 | 82.4446 |  | 2006-09-01 | 13:04 | 47040 | 19.934 | 0.1196 | 43.9497 |  | 2028-01-01 | 13:04 | 47040 | 25.362 | 0.15217 | 191.9585 |  | 2007-01-01 | 13:04 | 47040 | 25.188 | 0.15113 | 185.8936 |  | 2028-01-01 | 13:04 | 47040 | 17.1107 | 0.10266 | 29.9599 |  | 2007-01-01 | 13:04 | 47040 | 17.4245 | 0.10455 | 32.8383 |  | 2029-09-01 | 13:04 | 47040 | 24.4059 | 0.14644 | 86.2594 |  | 2029-09-01 | 13:04 | 47040 | 20.9509 | 0.12571 | 58.8708 |  | 2029-09-01 | 13:04 | 47040 | 18.6933 | 0.11216 | 40.3065 |  | 2006-09-01 | 13:04 | 47040 | 18.5167 | 0.1111 | 39.7416 |  | 2028-01-01 | 13:04 | 47040 | 22.4552 | 0.13473 | 71.2787 |  | 2007-01-01 | 13:04 | 47040 | 22.017 | 0.1321 | 74.6993 |  | 2028-01-01 | 13:04 | 47040 | 18.1013 | 0.10861 | 35.6806 |  | 2007-01-01 | 13:04 | 47040 | 18.1289 | 0.10877 | 36.7162
| 2029-09-01 | 13:05 | 47100 | 210.421 | 1.2625 | 279.7747 |  | 2029-09-01 | 13:05 | 47100 | 31.8679 | 0.19121 | 204.6552 |  | 2006-09-01 | 13:05 | 47100 | 31.0081 | 0.18605 | 186.0273 |  | 2029-09-01 | 13:05 | 47100 | 29.1061 | 0.17464 | 137.9278 |  | 2006-09-01 | 13:05 | 47100 | 28.1813 | 0.16909 | 92.5276 |  | 2028-01-01 | 13:05 | 47100 | 33.9098 | 0.20346 | 205.4701 |  | 2007-01-01 | 13:05 | 47100 | 31.2478 | 0.18749 | 187.2938 |  | 2028-01-01 | 13:05 | 47100 | 27.0065 | 0.16204 | 71.4408 |  | 2007-01-01 | 13:05 | 47100 | 26.6196 | 0.15972 | 74.859 |  | 2029-09-01 | 13:05 | 47100 | 31.4452 | 0.18867 | 196.3478 |  | 2006-09-01 | 13:05 | 47100 | 31.0081 | 0.18605 | 184.0969 |  | 2029-09-01 | 13:05 | 47100 | 26.6843 | 0.16011 | 102.4156 |  | 2006-09-01 | 13:05 | 47100 | 25.7621 | 0.15457 | 59.8247 |  | 2028-01-01 | 13:05 | 47100 | 31.5647 | 0.18939 | 194.7003 |  | 2007-01-01 | 13:05 | 47100 | 31.2458 | 0.18747 | 186.1641 |  | 2028-01-01 | 13:05 | 47100 | 22.7852 | 0.13671 | 42.2749 |  | 2007-01-01 | 13:05 | 47100 | 23.0697 | 0.13842 | 45.8364 |  | 2029-09-01 | 13:05 | 47100 | 31.4376 | 0.18863 | 194.6781 |  | 2006-09-01 | 13:05 | 47100 | 31.0081 | 0.18605 | 183.9075 |  | 2029-09-01 | 13:05 | 47100 | 24.7388 | 0.14843 | 82.593 |  | 2006-09-01 | 13:05 | 47100 | 23.6559 | 0.14194 | 44.0916 |  | 2028-01-01 | 13:05 | 47100 | 31.5028 | 0.18902 | 192.1475 |  | 2007-01-01 | 13:05 | 47100 | 31.2458 | 0.18747 | 186.081 |  | 2028-01-01 | 13:05 | 47100 | 19.8023 | 0.11881 | 30.0787 |  | 2007-01-01 | 13:05 | 47100 | 20.2253 | 0.12135 | 32.9597 |  | 2029-09-01 | 13:05 | 47100 | 29.0854 | 0.17451 | 86.4339 |  | 2029-09-01 | 13:05 | 47100 | 25.0236 | 0.15014 | 59.0209 |  | 2029-09-01 | 13:05 | 47100 | 21.9532 | 0.13172 | 40.4382 |  | 2006-09-01 | 13:05 | 47100 | 21.7116 | 0.13027 | 39.8718 |  | 2028-01-01 | 13:05 | 47100 | 27.0065 | 0.16204 | 71.4408 |  | 2007-01-01 | 13:05 | 47100 | 26.6196 | 0.15972 | 74.859 |  | 2028-01-01 | 13:05 | 47100 | 21.1401 | 0.12684 | 35.8074 |  | 2007-01-01 | 13:05 | 47100 | 21.1792 | 0.12708 | 36.8433
| 2029-09-01 | 13:06 | 47160 | 214.172 | 1.285 | 281.0597 |  | 2029-09-01 | 13:06 | 47160 | 37.9105 | 0.22746 | 204.8827 |  | 2006-09-01 | 13:06 | 47160 | 36.8913 | 0.22135 | 186.2487 |  | 2029-09-01 | 13:06 | 47160 | 34.1782 | 0.20507 | 138.1329 |  | 2006-09-01 | 13:06 | 47160 | 33.0076 | 0.19805 | 92.7256 |  | 2028-01-01 | 13:06 | 47160 | 39.9426 | 0.23966 | 205.7098 |  | 2007-01-01 | 13:06 | 47160 | 37.2122 | 0.22327 | 187.5171 |  | 2028-01-01 | 13:06 | 47160 | 31.2462 | 0.18748 | 71.6282 |  | 2007-01-01 | 13:06 | 47160 | 30.9098 | 0.18546 | 75.0445 |  | 2029-09-01 | 13:06 | 47160 | 37.4933 | 0.22496 | 196.5727 |  | 2006-09-01 | 13:06 | 47160 | 36.8913 | 0.22135 | 184.3183 |  | 2029-09-01 | 13:06 | 47160 | 30.9918 | 0.18595 | 102.6016 |  | 2006-09-01 | 13:06 | 47160 | 29.7516 | 0.17851 | 60.0032 |  | 2028-01-01 | 13:06 | 47160 | 37.6269 | 0.22576 | 194.926 |  | 2007-01-01 | 13:06 | 47160 | 37.2102 | 0.22326 | 186.3874 |  | 2028-01-01 | 13:06 | 47160 | 25.8614 | 0.15517 | 42.43 |  | 2007-01-01 | 13:06 | 47160 | 26.2319 | 0.15739 | 45.9938 |  | 2029-09-01 | 13:06 | 47160 | 37.4858 | 0.22491 | 194.903 |  | 2006-09-01 | 13:06 | 47160 | 36.8913 | 0.22135 | 184.1289 |  | 2029-09-01 | 13:06 | 47160 | 28.406 | 0.17044 | 82.7635 |  | 2006-09-01 | 13:06 | 47160 | 26.971 | 0.16183 | 44.2534 |  | 2028-01-01 | 13:06 | 47160 | 37.5658 | 0.22539 | 192.3729 |  | 2007-01-01 | 13:06 | 47160 | 37.2102 | 0.22326 | 186.3043 |  | 2028-01-01 | 13:06 | 47160 | 22.0576 | 0.13235 | 30.211 |  | 2007-01-01 | 13:06 | 47160 | 22.5904 | 0.13554 | 33.0952 |  | 2029-09-01 | 13:06 | 47160 | 33.4848 | 0.20091 | 86.6348 |  | 2029-09-01 | 13:06 | 47160 | 28.732 | 0.17239 | 59.1933 |  | 2029-09-01 | 13:06 | 47160 | 24.7902 | 0.14874 | 40.5869 |  | 2006-09-01 | 13:06 | 47160 | 24.481 | 0.14689 | 40.0187 |  | 2028-01-01 | 13:06 | 47160 | 31.2462 | 0.18748 | 71.6282 |  | 2007-01-01 | 13:06 | 47160 | 30.9098 | 0.18546 | 75.0445 |  | 2028-01-01 | 13:06 | 47160 | 23.7474 | 0.14248 | 35.9499 |  | 2007-01-01 | 13:06 | 47160 | 23.7978 | 0.14279 | 36.9861
| 2029-09-01 | 13:07 | 47220 | 217.88 | 1.3073 | 282.367 |  | 2029-09-01 | 13:07 | 47220 | 43.8768 | 0.26326 | 205.1459 |  | 2006-09-01 | 13:07 | 47220 | 42.6735 | 0.25604 | 186.5047 |  | 2029-09-01 | 13:07 | 47220 | 39.0398 | 0.23424 | 138.3671 |  | 2006-09-01 | 13:07 | 47220 | 37.5916 | 0.22555 | 92.9512 |  | 2028-01-01 | 13:07 | 47220 | 45.8989 | 0.27539 | 205.9851 |  | 2007-01-01 | 13:07 | 47220 | 43.0843 | 0.25851 | 187.7756 |  | 2028-01-01 | 13:07 | 47220 | 35.196 | 0.21118 | 71.8394 |  | 2007-01-01 | 13:07 | 47220 | 34.9088 | 0.20945 | 75.2539 |  | 2029-09-01 | 13:07 | 47220 | 43.4649 | 0.26079 | 196.8335 |  | 2006-09-01 | 13:07 | 47220 | 42.6735 | 0.25604 | 184.5743 |  | 2029-09-01 | 13:07 | 47220 | 35.0064 | 0.21004 | 102.8116 |  | 2006-09-01 | 13:07 | 47220 | 33.4175 | 0.2005 | 60.2037 |  | 2028-01-01 | 13:07 | 47220 | 43.6124 | 0.26167 | 195.1877 |  | 2007-01-01 | 13:07 | 47220 | 43.0824 | 0.25849 | 186.6459 |  | 2028-01-01 | 13:07 | 47220 | 28.5757 | 0.17145 | 42.6015 |  | 2007-01-01 | 13:07 | 47220 | 29.0344 | 0.17421 | 46.168 |  | 2029-09-01 | 13:07 | 47220 | 43.4575 | 0.26075 | 195.1638 |  | 2006-09-01 | 13:07 | 47220 | 42.6735 | 0.25604 | 184.3849 |  | 2029-09-01 | 13:07 | 47220 | 31.7316 | 0.19039 | 82.9539 |  | 2006-09-01 | 13:07 | 47220 | 29.9202 | 0.17952 | 44.433 |  | 2028-01-01 | 13:07 | 47220 | 43.5521 | 0.26131 | 192.6342 |  | 2007-01-01 | 13:07 | 47220 | 43.0824 | 0.25849 | 186.5628 |  | 2028-01-01 | 13:07 | 47220 | 23.9478 | 0.14369 | 30.3547 |  | 2007-01-01 | 13:07 | 47220 | 24.5882 | 0.14753 | 33.2428 |  | 2029-09-01 | 13:07 | 47220 | 37.6213 | 0.22573 | 86.8605 |  | 2029-09-01 | 13:07 | 47220 | 32.1089 | 0.19265 | 59.386 |  | 2029-09-01 | 13:07 | 47220 | 27.2596 | 0.16356 | 40.7505 |  | 2006-09-01 | 13:07 | 47220 | 26.8819 | 0.16129 | 40.18 |  | 2028-01-01 | 13:07 | 47220 | 35.196 | 0.21118 | 71.8394 |  | 2007-01-01 | 13:07 | 47220 | 34.9088 | 0.20945 | 75.2539 |  | 2028-01-01 | 13:07 | 47220 | 25.9849 | 0.15591 | 36.1058 |  | 2007-01-01 | 13:07 | 47220 | 26.0459 | 0.15628 | 37.1424
| 2029-09-01 | 13:08 | 47280 | 221.551 | 1.3293 | 283.6963 |  | 2029-09-01 | 13:08 | 47280 | 49.7688 | 0.29861 | 205.4445 |  | 2006-09-01 | 13:08 | 47280 | 48.3567 | 0.29014 | 186.7948 |  | 2029-09-01 | 13:08 | 47280 | 43.699 | 0.26219 | 138.6293 |  | 2006-09-01 | 13:08 | 47280 | 41.9441 | 0.25166 | 93.2029 |  | 2028-01-01 | 13:08 | 47280 | 51.7797 | 0.31068 | 206.2958 |  | 2007-01-01 | 13:08 | 47280 | 48.8653 | 0.29319 | 188.0688 |  | 2028-01-01 | 13:08 | 47280 | 38.876 | 0.23326 | 72.0727 |  | 2007-01-01 | 13:08 | 47280 | 38.6365 | 0.23182 | 75.4857 |  | 2029-09-01 | 13:08 | 47280 | 49.3622 | 0.29617 | 197.1297 |  | 2006-09-01 | 13:08 | 47280 | 48.3567 | 0.29014 | 184.8644 |  | 2029-09-01 | 13:08 | 47280 | 38.7471 | 0.23248 | 103.0441 |  | 2006-09-01 | 13:08 | 47280 | 36.7834 | 0.2207 | 60.4244 |  | 2028-01-01 | 13:08 | 47280 | 49.522 | 0.29713 | 195.4848 |  | 2007-01-01 | 13:08 | 47280 | 48.8634 | 0.29318 | 186.9391 |  | 2028-01-01 | 13:08 | 47280 | 30.9711 | 0.18583 | 42.7873 |  | 2007-01-01 | 13:08 | 47280 | 31.5182 | 0.18911 | 46.3571 |  | 2029-09-01 | 13:08 | 47280 | 49.3549 | 0.29613 | 195.4599 |  | 2006-09-01 | 13:08 | 47280 | 48.3567 | 0.29014 | 184.6751 |  | 2029-09-01 | 13:08 | 47280 | 34.7462 | 0.20848 | 83.1623 |  | 2006-09-01 | 13:08 | 47280 | 32.5403 | 0.19524 | 44.6282 |  | 2028-01-01 | 13:08 | 47280 | 49.4624 | 0.29677 | 192.931 |  | 2007-01-01 | 13:08 | 47280 | 48.8634 | 0.29318 | 186.856 |  | 2028-01-01 | 13:08 | 47280 | 25.5327 | 0.1532 | 30.5079 |  | 2007-01-01 | 13:08 | 47280 | 26.276 | 0.15766 | 33.4004 |  | 2029-09-01 | 13:08 | 47280 | 41.5116 | 0.24907 | 87.1096 |  | 2029-09-01 | 13:08 | 47280 | 35.1848 | 0.21111 | 59.5971 |  | 2029-09-01 | 13:08 | 47280 | 29.4096 | 0.17646 | 40.927 |  | 2006-09-01 | 13:08 | 47280 | 28.9634 | 0.17378 | 40.3538 |  | 2028-01-01 | 13:08 | 47280 | 38.876 | 0.23326 | 72.0727 |  | 2007-01-01 | 13:08 | 47280 | 38.6365 | 0.23182 | 75.4857 |  | 2028-01-01 | 13:08 | 47280 | 27.9051 | 0.16743 | 36.2732 |  | 2007-01-01 | 13:08 | 47280 | 27.976 | 0.16786 | 37.3102
| 2029-09-01 | 13:09 | 47340 | 225.173 | 1.351 | 285.0473 |  | 2029-09-01 | 13:09 | 47340 | 55.5851 | 0.33351 | 205.7781 |  | 2006-09-01 | 13:09 | 47340 | 53.9431 | 0.32366 | 187.1185 |  | 2029-09-01 | 13:09 | 47340 | 48.1636 | 0.28898 | 138.9183 |  | 2006-09-01 | 13:09 | 47340 | 46.0755 | 0.27645 | 93.4793 |  | 2028-01-01 | 13:09 | 47340 | 57.5858 | 0.34551 | 206.6413 |  | 2007-01-01 | 13:09 | 47340 | 54.5564 | 0.32734 | 188.3962 |  | 2028-01-01 | 13:09 | 47340 | 42.3049 | 0.25383 | 72.3265 |  | 2007-01-01 | 13:09 | 47340 | 42.1114 | 0.25267 | 75.7384 |  | 2029-09-01 | 13:09 | 47340 | 55.1837 | 0.3311 | 197.4608 |  | 2006-09-01 | 13:09 | 47340 | 53.9431 | 0.32366 | 185.1881 |  | 2029-09-01 | 13:09 | 47340 | 42.2314 | 0.25339 | 103.2975 |  | 2006-09-01 | 13:09 | 47340 | 39.8715 | 0.23923 | 60.6636 |  | 2028-01-01 | 13:09 | 47340 | 55.3566 | 0.33214 | 195.817 |  | 2007-01-01 | 13:09 | 47340 | 54.5545 | 0.32733 | 187.2664 |  | 2028-01-01 | 13:09 | 47340 | 33.0857 | 0.19851 | 42.9858 |  | 2007-01-01 | 13:09 | 47340 | 33.7201 | 0.20232 | 46.5594 |  | 2029-09-01 | 13:09 | 47340 | 55.1765 | 0.33106 | 195.791 |  | 2006-09-01 | 13:09 | 47340 | 53.9431 | 0.32366 | 184.9987 |  | 2029-09-01 | 13:09 | 47340 | 37.4773 | 0.22486 | 83.3872 |  | 2006-09-01 | 13:09 | 47340 | 34.8648 | 0.20919 | 44.8374 |  | 2028-01-01 | 13:09 | 47340 | 55.2978 | 0.33179 | 193.2628 |  | 2007-01-01 | 13:09 | 47340 | 54.5545 | 0.32733 | 187.1833 |  | 2028-01-01 | 13:09 | 47340 | 26.8623 | 0.16117 | 30.6691 |  | 2007-01-01 | 13:09 | 47340 | 27.7026 | 0.16622 | 33.5666 |  | 2029-09-01 | 13:09 | 47340 | 45.1685 | 0.27101 | 87.3806 |  | 2029-09-01 | 13:09 | 47340 | 37.985 | 0.22791 | 59.825 |  | 2029-09-01 | 13:09 | 47340 | 31.2803 | 0.18768 | 41.1146 |  | 2006-09-01 | 13:09 | 47340 | 30.7684 | 0.18461 | 40.5384 |  | 2028-01-01 | 13:09 | 47340 | 42.3049 | 0.25383 | 72.3265 |  | 2007-01-01 | 13:09 | 47340 | 42.1114 | 0.25267 | 75.7384 |  | 2028-01-01 | 13:09 | 47340 | 29.5534 | 0.17732 | 36.4505 |  | 2007-01-01 | 13:09 | 47340 | 29.6331 | 0.1778 | 37.488
| 2029-09-01 | 13:10 | 47400 | 228.746 | 1.3725 | 286.4198 |  | 2029-09-01 | 13:10 | 47400 | 61.3266 | 0.36796 | 206.146 |  | 2006-09-01 | 13:10 | 47400 | 59.4346 | 0.35661 | 187.4751 |  | 2029-09-01 | 13:10 | 47400 | 52.4412 | 0.31465 | 139.2329 |  | 2006-09-01 | 13:10 | 47400 | 49.9959 | 0.29998 | 93.7793 |  | 2028-01-01 | 13:10 | 47400 | 63.3183 | 0.37991 | 207.0213 |  | 2007-01-01 | 13:10 | 47400 | 60.1586 | 0.36095 | 188.7571 |  | 2028-01-01 | 13:10 | 47400 | 45.5003 | 0.273 | 72.5995 |  | 2007-01-01 | 13:10 | 47400 | 45.3506 | 0.2721 | 76.0105 |  | 2029-09-01 | 13:10 | 47400 | 60.9303 | 0.36558 | 197.8264 |  | 2006-09-01 | 13:10 | 47400 | 59.4346 | 0.35661 | 185.5447 |  | 2029-09-01 | 13:10 | 47400 | 45.476 | 0.27286 | 103.5704 |  | 2006-09-01 | 13:10 | 47400 | 42.7024 | 0.25621 | 60.9199 |  | 2028-01-01 | 13:10 | 47400 | 61.1172 | 0.3667 | 196.1837 |  | 2007-01-01 | 13:10 | 47400 | 60.1567 | 0.36094 | 187.6273 |  | 2028-01-01 | 13:10 | 47400 | 34.9528 | 0.20972 | 43.1956 |  | 2007-01-01 | 13:10 | 47400 | 35.6723 | 0.21403 | 46.7735 |  | 2029-09-01 | 13:10 | 47400 | 60.9232 | 0.36554 | 196.1565 |  | 2006-09-01 | 13:10 | 47400 | 59.4346 | 0.35661 | 185.3553 |  | 2029-09-01 | 13:10 | 47400 | 39.9504 | 0.2397 | 83.6269 |  | 2006-09-01 | 13:10 | 47400 | 36.9238 | 0.22154 | 45.0589 |  | 2028-01-01 | 13:10 | 47400 | 61.0591 | 0.36635 | 193.6291 |  | 2007-01-01 | 13:10 | 47400 | 60.1567 | 0.36094 | 187.5442 |  | 2028-01-01 | 13:10 | 47400 | 27.9782 | 0.16787 | 30.8369 |  | 2007-01-01 | 13:10 | 47400 | 28.9088 | 0.17345 | 33.7401 |  | 2029-09-01 | 13:10 | 47400 | 48.6059 | 0.29164 | 87.6723 |  | 2029-09-01 | 13:10 | 47400 | 40.5341 | 0.2432 | 60.0682 |  | 2029-09-01 | 13:10 | 47400 | 32.908 | 0.19745 | 41.3121 |  | 2006-09-01 | 13:10 | 47400 | 32.3336 | 0.194 | 40.7324 |  | 2028-01-01 | 13:10 | 47400 | 45.5003 | 0.273 | 72.5995 |  | 2007-01-01 | 13:10 | 47400 | 45.3506 | 0.2721 | 76.0105 |  | 2028-01-01 | 13:10 | 47400 | 30.9684 | 0.18581 | 36.6363 |  | 2007-01-01 | 13:10 | 47400 | 31.0559 | 0.18634 | 37.6744
| 2029-09-01 | 13:11 | 47460 | 232.272 | 1.3936 | 287.8134 |  | 2029-09-01 | 13:11 | 47460 | 66.9942 | 0.40197 | 206.548 |  | 2006-09-01 | 13:11 | 47460 | 64.8333 | 0.389 | 187.8641 |  | 2029-09-01 | 13:11 | 47460 | 56.5391 | 0.33923 | 139.5722 |  | 2006-09-01 | 13:11 | 47460 | 53.7149 | 0.32229 | 94.1016 |  | 2028-01-01 | 13:11 | 47460 | 68.9779 | 0.41387 | 207.4351 |  | 2007-01-01 | 13:11 | 47460 | 65.673 | 0.39404 | 189.1511 |  | 2028-01-01 | 13:11 | 47460 | 48.4784 | 0.29087 | 72.8904 |  | 2007-01-01 | 13:11 | 47460 | 48.3703 | 0.29022 | 76.3007 |  | 2029-09-01 | 13:11 | 47460 | 66.6029 | 0.39962 | 198.226 |  | 2006-09-01 | 13:11 | 47460 | 64.8333 | 0.389 | 185.9337 |  | 2029-09-01 | 13:11 | 47460 | 48.4963 | 0.29098 | 103.8613 |  | 2006-09-01 | 13:11 | 47460 | 45.2951 | 0.27177 | 61.1916 |  | 2028-01-01 | 13:11 | 47460 | 66.8046 | 0.40083 | 196.5845 |  | 2007-01-01 | 13:11 | 47460 | 65.6712 | 0.39403 | 188.0213 |  | 2028-01-01 | 13:11 | 47460 | 36.6019 | 0.21961 | 43.4152 |  | 2007-01-01 | 13:11 | 47460 | 37.4034 | 0.22442 | 46.9979 |  | 2029-09-01 | 13:11 | 47460 | 66.5959 | 0.39958 | 196.5561 |  | 2006-09-01 | 13:11 | 47460 | 64.8333 | 0.389 | 185.7443 |  | 2029-09-01 | 13:11 | 47460 | 42.1886 | 0.25313 | 83.88 |  | 2006-09-01 | 13:11 | 47460 | 38.7446 | 0.23247 | 45.2914 |  | 2028-01-01 | 13:11 | 47460 | 66.7473 | 0.40048 | 194.0296 |  | 2007-01-01 | 13:11 | 47460 | 65.6712 | 0.39403 | 187.9383 |  | 2028-01-01 | 13:11 | 47460 | 28.9154 | 0.17349 | 31.0104 |  | 2007-01-01 | 13:11 | 47460 | 29.9291 | 0.17957 | 33.9197 |  | 2029-09-01 | 13:11 | 47460 | 51.8369 | 0.31102 | 87.9833 |  | 2029-09-01 | 13:11 | 47460 | 42.8548 | 0.25713 | 60.3253 |  | 2029-09-01 | 13:11 | 47460 | 34.3242 | 0.20595 | 41.518 |  | 2006-09-01 | 13:11 | 47460 | 33.6912 | 0.20215 | 40.9346 |  | 2028-01-01 | 13:11 | 47460 | 48.4784 | 0.29087 | 72.8904 |  | 2007-01-01 | 13:11 | 47460 | 48.3703 | 0.29022 | 76.3007 |  | 2028-01-01 | 13:11 | 47460 | 32.1834 | 0.1931 | 36.8294 |  | 2007-01-01 | 13:11 | 47460 | 32.2776 | 0.19367 | 37.868
| 2029-09-01 | 13:12 | 47520 | 235.752 | 1.4145 | 289.2279 |  | 2029-09-01 | 13:12 | 47520 | 72.5887 | 0.43553 | 206.9835 |  | 2006-09-01 | 13:12 | 47520 | 70.1409 | 0.42085 | 188.285 |  | 2029-09-01 | 13:12 | 47520 | 60.4643 | 0.36279 | 139.935 |  | 2006-09-01 | 13:12 | 47520 | 57.2416 | 0.34345 | 94.445 |  | 2028-01-01 | 13:12 | 47520 | 74.5656 | 0.44739 | 207.8825 |  | 2007-01-01 | 13:12 | 47520 | 71.101 | 0.42661 | 189.5777 |  | 2028-01-01 | 13:12 | 47520 | 51.2541 | 0.30752 | 73.1979 |  | 2007-01-01 | 13:12 | 47520 | 51.1855 | 0.30711 | 76.6079 |  | 2029-09-01 | 13:12 | 47520 | 72.2025 | 0.43322 | 198.6592 |  | 2006-09-01 | 13:12 | 47520 | 70.1409 | 0.42085 | 186.3546 |  | 2029-09-01 | 13:12 | 47520 | 51.307 | 0.30784 | 104.1692 |  | 2006-09-01 | 13:12 | 47520 | 47.6675 | 0.286 | 61.4776 |  | 2028-01-01 | 13:12 | 47520 | 72.4197 | 0.43452 | 197.019 |  | 2007-01-01 | 13:12 | 47520 | 71.0992 | 0.4266 | 188.4479 |  | 2028-01-01 | 13:12 | 47520 | 38.0589 | 0.22835 | 43.6435 |  | 2007-01-01 | 13:12 | 47520 | 38.9388 | 0.23363 | 47.2315 |  | 2029-09-01 | 13:12 | 47520 | 72.1956 | 0.43317 | 196.9892 |  | 2006-09-01 | 13:12 | 47520 | 70.1409 | 0.42085 | 186.1652 |  | 2029-09-01 | 13:12 | 47520 | 44.2129 | 0.26528 | 84.1453 |  | 2006-09-01 | 13:12 | 47520 | 40.3516 | 0.24211 | 45.5335 |  | 2028-01-01 | 13:12 | 47520 | 72.3631 | 0.43418 | 194.4638 |  | 2007-01-01 | 13:12 | 47520 | 71.0992 | 0.4266 | 188.3649 |  | 2028-01-01 | 13:12 | 47520 | 29.703 | 0.17822 | 31.1887 |  | 2007-01-01 | 13:12 | 47520 | 30.7926 | 0.18476 | 34.1044 |  | 2029-09-01 | 13:12 | 47520 | 54.8739 | 0.32924 | 88.3125 |  | 2029-09-01 | 13:12 | 47520 | 44.9673 | 0.2698 | 60.5951 |  | 2029-09-01 | 13:12 | 47520 | 35.5564 | 0.21334 | 41.7314 |  | 2006-09-01 | 13:12 | 47520 | 34.8688 | 0.20921 | 41.1438 |  | 2028-01-01 | 13:12 | 47520 | 51.2541 | 0.30752 | 73.1979 |  | 2007-01-01 | 13:12 | 47520 | 51.1855 | 0.30711 | 76.6079 |  | 2028-01-01 | 13:12 | 47520 | 33.2269 | 0.19936 | 37.0288 |  | 2007-01-01 | 13:12 | 47520 | 33.3266 | 0.19996 | 38.068
| 2029-09-01 | 13:13 | 47580 | 239.185 | 1.4351 | 290.663 |  | 2029-09-01 | 13:13 | 47580 | 78.1111 | 0.46867 | 207.4522 |  | 2006-09-01 | 13:13 | 47580 | 75.3595 | 0.45216 | 188.7371 |  | 2029-09-01 | 13:13 | 47580 | 64.2237 | 0.38534 | 140.3203 |  | 2006-09-01 | 13:13 | 47580 | 60.5849 | 0.36351 | 94.8085 |  | 2028-01-01 | 13:13 | 47580 | 80.0822 | 0.48049 | 208.363 |  | 2007-01-01 | 13:13 | 47580 | 76.4435 | 0.45866 | 190.0364 |  | 2028-01-01 | 13:13 | 47580 | 53.8417 | 0.32305 | 73.521 |  | 2007-01-01 | 13:13 | 47580 | 53.81 | 0.32286 | 76.9307 |  | 2029-09-01 | 13:13 | 47580 | 77.7298 | 0.46638 | 199.1256 |  | 2006-09-01 | 13:13 | 47580 | 75.3595 | 0.45216 | 186.8067 |  | 2029-09-01 | 13:13 | 47580 | 53.9218 | 0.32353 | 104.4927 |  | 2006-09-01 | 13:13 | 47580 | 49.8362 | 0.29902 | 61.7767 |  | 2028-01-01 | 13:13 | 47580 | 77.9634 | 0.46778 | 197.4868 |  | 2007-01-01 | 13:13 | 47580 | 76.4418 | 0.45865 | 188.9066 |  | 2028-01-01 | 13:13 | 47580 | 39.3466 | 0.23608 | 43.8796 |  | 2007-01-01 | 13:13 | 47580 | 40.3009 | 0.24181 | 47.4733 |  | 2029-09-01 | 13:13 | 47580 | 77.723 | 0.46634 | 197.4556 |  | 2006-09-01 | 13:13 | 47580 | 75.3595 | 0.45216 | 186.6173 |  | 2029-09-01 | 13:13 | 47580 | 46.0426 | 0.27626 | 84.4216 |  | 2006-09-01 | 13:13 | 47580 | 41.767 | 0.2506 | 45.7841 |  | 2028-01-01 | 13:13 | 47580 | 77.9075 | 0.46744 | 194.9312 |  | 2007-01-01 | 13:13 | 47580 | 76.4418 | 0.45865 | 188.8235 |  | 2028-01-01 | 13:13 | 47580 | 30.3654 | 0.18219 | 31.3709 |  | 2007-01-01 | 13:13 | 47580 | 31.5238 | 0.18914 | 34.2936 |  | 2029-09-01 | 13:13 | 47580 | 57.7285 | 0.34637 | 88.6589 |  | 2029-09-01 | 13:13 | 47580 | 46.8903 | 0.28134 | 60.8765 |  | 2029-09-01 | 13:13 | 47580 | 36.6284 | 0.21977 | 41.9511 |  | 2006-09-01 | 13:13 | 47580 | 35.8905 | 0.21534 | 41.3591 |  | 2028-01-01 | 13:13 | 47580 | 53.8417 | 0.32305 | 73.521 |  | 2007-01-01 | 13:13 | 47580 | 53.81 | 0.32286 | 76.9307 |  | 2028-01-01 | 13:13 | 47580 | 34.1233 | 0.20474 | 37.2335 |  | 2007-01-01 | 13:13 | 47580 | 34.2274 | 0.20536 | 38.2734
| 2029-09-01 | 13:14 | 47640 | 242.571 | 1.4554 | 292.1185 |  | 2029-09-01 | 13:14 | 47640 | 83.562 | 0.50137 | 207.9535 |  | 2006-09-01 | 13:14 | 47640 | 80.4908 | 0.48294 | 189.2201 |  | 2029-09-01 | 13:14 | 47640 | 67.8238 | 0.40694 | 140.7272 |  | 2006-09-01 | 13:14 | 47640 | 63.7531 | 0.38252 | 95.1911 |  | 2028-01-01 | 13:14 | 47640 | 85.5286 | 0.51317 | 208.8762 |  | 2007-01-01 | 13:14 | 47640 | 81.7017 | 0.49021 | 190.5266 |  | 2028-01-01 | 13:14 | 47640 | 56.2541 | 0.33752 | 73.8585 |  | 2007-01-01 | 13:14 | 47640 | 56.257 | 0.33754 | 77.2683 |  | 2029-09-01 | 13:14 | 47640 | 83.1856 | 0.49911 | 199.6247 |  | 2006-09-01 | 13:14 | 47640 | 80.4908 | 0.48294 | 187.2897 |  | 2029-09-01 | 13:14 | 47640 | 56.3533 | 0.33812 | 104.8308 |  | 2006-09-01 | 13:14 | 47640 | 51.8164 | 0.3109 | 62.0876 |  | 2028-01-01 | 13:14 | 47640 | 83.4365 | 0.50062 | 197.9874 |  | 2007-01-01 | 13:14 | 47640 | 81.7 | 0.4902 | 189.3968 |  | 2028-01-01 | 13:14 | 47640 | 40.4851 | 0.24291 | 44.1225 |  | 2007-01-01 | 13:14 | 47640 | 41.5097 | 0.24906 | 47.7224 |  | 2029-09-01 | 13:14 | 47640 | 83.1788 | 0.49907 | 197.9547 |  | 2006-09-01 | 13:14 | 47640 | 80.4908 | 0.48294 | 187.1003 |  | 2029-09-01 | 13:14 | 47640 | 47.6952 | 0.28617 | 84.7077 |  | 2006-09-01 | 13:14 | 47640 | 43.0108 | 0.25806 | 46.0422 |  | 2028-01-01 | 13:14 | 47640 | 83.3813 | 0.50029 | 195.4315 |  | 2007-01-01 | 13:14 | 47640 | 81.7 | 0.4902 | 189.3137 |  | 2028-01-01 | 13:14 | 47640 | 30.9231 | 0.18554 | 31.5564 |  | 2007-01-01 | 13:14 | 47640 | 32.1436 | 0.19286 | 34.4864 |  | 2029-09-01 | 13:14 | 47640 | 60.4113 | 0.36247 | 89.0214 |  | 2029-09-01 | 13:14 | 47640 | 48.6406 | 0.29184 | 61.1683 |  | 2029-09-01 | 13:14 | 47640 | 37.5609 | 0.22537 | 42.1765 |  | 2006-09-01 | 13:14 | 47640 | 36.7772 | 0.22066 | 41.5798 |  | 2028-01-01 | 13:14 | 47640 | 56.2541 | 0.33752 | 73.8585 |  | 2007-01-01 | 13:14 | 47640 | 56.257 | 0.33754 | 77.2683 |  | 2028-01-01 | 13:14 | 47640 | 34.8934 | 0.20936 | 37.4429 |  | 2007-01-01 | 13:14 | 47640 | 35.0011 | 0.21001 | 38.4834
| 2029-09-01 | 13:15 | 47700 | 245.908 | 1.4754 | 293.5939 |  | 2029-09-01 | 13:15 | 47700 | 88.9404 | 0.53364 | 208.4872 |  | 2006-09-01 | 13:15 | 47700 | 85.5367 | 0.51322 | 189.7333 |  | 2029-09-01 | 13:15 | 47700 | 71.2709 | 0.42763 | 141.1549 |  | 2006-09-01 | 13:15 | 47700 | 66.7544 | 0.40053 | 95.5916 |  | 2028-01-01 | 13:15 | 47700 | 90.9056 | 0.54543 | 209.4216 |  | 2007-01-01 | 13:15 | 47700 | 86.8768 | 0.52126 | 191.0479 |  | 2028-01-01 | 13:15 | 47700 | 58.5035 | 0.35102 | 74.2095 |  | 2007-01-01 | 13:15 | 47700 | 58.5385 | 0.35123 | 77.6195 |  | 2029-09-01 | 13:15 | 47700 | 88.5689 | 0.53141 | 200.1561 |  | 2006-09-01 | 13:15 | 47700 | 85.5367 | 0.51322 | 187.8029 |  | 2029-09-01 | 13:15 | 47700 | 58.6138 | 0.35168 | 105.1825 |  | 2006-09-01 | 13:15 | 47700 | 53.6226 | 0.32174 | 62.4093 |  | 2028-01-01 | 13:15 | 47700 | 88.84 | 0.53304 | 198.5205 |  | 2007-01-01 | 13:15 | 47700 | 86.8751 | 0.52125 | 189.918 |  | 2028-01-01 | 13:15 | 47700 | 41.4922 | 0.24895 | 44.3715 |  | 2007-01-01 | 13:15 | 47700 | 42.5826 | 0.2555 | 47.9779 |  | 2029-09-01 | 13:15 | 47700 | 88.5622 | 0.53137 | 198.486 |  | 2006-09-01 | 13:15 | 47700 | 85.5367 | 0.51322 | 187.6135 |  | 2029-09-01 | 13:15 | 47700 | 49.1868 | 0.29512 | 85.0029 |  | 2006-09-01 | 13:15 | 47700 | 44.1008 | 0.2646 | 46.3068 |  | 2028-01-01 | 13:15 | 47700 | 88.7855 | 0.53271 | 195.9642 |  | 2007-01-01 | 13:15 | 47700 | 86.8751 | 0.52125 | 189.835 |  | 2028-01-01 | 13:15 | 47700 | 31.3931 | 0.18836 | 31.7447 |  | 2007-01-01 | 13:15 | 47700 | 32.6692 | 0.19602 | 34.6824 |  | 2029-09-01 | 13:15 | 47700 | 62.9317 | 0.37759 | 89.399 |  | 2029-09-01 | 13:15 | 47700 | 50.2329 | 0.3014 | 61.4697 |  | 2029-09-01 | 13:15 | 47700 | 38.3714 | 0.23023 | 42.4067 |  | 2006-09-01 | 13:15 | 47700 | 37.5467 | 0.22528 | 41.8051 |  | 2028-01-01 | 13:15 | 47700 | 58.5035 | 0.35102 | 74.2095 |  | 2007-01-01 | 13:15 | 47700 | 58.5385 | 0.35123 | 77.6195 |  | 2028-01-01 | 13:15 | 47700 | 35.5554 | 0.21333 | 37.6562 |  | 2007-01-01 | 13:15 | 47700 | 35.6656 | 0.21399 | 38.6974
| 2029-09-01 | 13:16 | 47760 | 249.195 | 1.4952 | 295.0891 |  | 2029-09-01 | 13:16 | 47760 | 94.2472 | 0.56548 | 209.0527 |  | 2006-09-01 | 13:16 | 47760 | 90.4989 | 0.54299 | 190.2763 |  | 2029-09-01 | 13:16 | 47760 | 74.5713 | 0.44743 | 141.6023 |  | 2006-09-01 | 13:16 | 47760 | 69.5965 | 0.41758 | 96.0092 |  | 2028-01-01 | 13:16 | 47760 | 96.214 | 0.57728 | 209.9989 |  | 2007-01-01 | 13:16 | 47760 | 91.9699 | 0.55182 | 191.5997 |  | 2028-01-01 | 13:16 | 47760 | 60.6012 | 0.36361 | 74.5731 |  | 2007-01-01 | 13:16 | 47760 | 60.6659 | 0.364 | 77.9835 |  | 2029-09-01 | 13:16 | 47760 | 93.8804 | 0.56328 | 200.7194 |  | 2006-09-01 | 13:16 | 47760 | 90.4989 | 0.54299 | 188.3459 |  | 2029-09-01 | 13:16 | 47760 | 60.7143 | 0.36429 | 105.5468 |  | 2006-09-01 | 13:16 | 47760 | 55.2679 | 0.33161 | 62.7409 |  | 2028-01-01 | 13:16 | 47760 | 94.1745 | 0.56505 | 199.0855 |  | 2007-01-01 | 13:16 | 47760 | 91.9682 | 0.55181 | 190.4699 |  | 2028-01-01 | 13:16 | 47760 | 42.3833 | 0.2543 | 44.6258 |  | 2007-01-01 | 13:16 | 47760 | 43.5353 | 0.26121 | 48.2391 |  | 2029-09-01 | 13:16 | 47760 | 93.8738 | 0.56324 | 199.0493 |  | 2006-09-01 | 13:16 | 47760 | 90.4989 | 0.54299 | 188.1565 |  | 2029-09-01 | 13:16 | 47760 | 50.532 | 0.30319 | 85.3061 |  | 2006-09-01 | 13:16 | 47760 | 45.0533 | 0.27032 | 46.5771 |  | 2028-01-01 | 13:16 | 47760 | 94.1207 | 0.56472 | 196.5289 |  | 2007-01-01 | 13:16 | 47760 | 91.9682 | 0.55181 | 190.3868 |  | 2028-01-01 | 13:16 | 47760 | 31.7897 | 0.19074 | 31.9355 |  | 2007-01-01 | 13:16 | 47760 | 33.1155 | 0.19869 | 34.8811 |  | 2029-09-01 | 13:16 | 47760 | 65.2991 | 0.39179 | 89.7908 |  | 2029-09-01 | 13:16 | 47760 | 51.6812 | 0.31009 | 61.7798 |  | 2029-09-01 | 13:16 | 47760 | 39.0757 | 0.23445 | 42.6412 |  | 2006-09-01 | 13:16 | 47760 | 38.2149 | 0.22929 | 42.0344 |  | 2028-01-01 | 13:16 | 47760 | 60.6012 | 0.36361 | 74.5731 |  | 2007-01-01 | 13:16 | 47760 | 60.6659 | 0.364 | 77.9835 |  | 2028-01-01 | 13:16 | 47760 | 36.1246 | 0.21675 | 37.873 |  | 2007-01-01 | 13:16 | 47760 | 36.2365 | 0.21742 | 38.9148
| 2029-09-01 | 13:17 | 47820 | 252.432 | 1.5146 | 296.6037 |  | 2029-09-01 | 13:17 | 47820 | 99.4828 | 0.5969 | 209.6496 |  | 2006-09-01 | 13:17 | 47820 | 95.3791 | 0.57227 | 190.8485 |  | 2029-09-01 | 13:17 | 47820 | 77.7309 | 0.46639 | 142.0687 |  | 2006-09-01 | 13:17 | 47820 | 72.2868 | 0.43372 | 96.4429 |  | 2028-01-01 | 13:17 | 47820 | 101.455 | 0.60873 | 210.6076 |  | 2007-01-01 | 13:17 | 47820 | 96.9821 | 0.58189 | 192.1816 |  | 2028-01-01 | 13:17 | 47820 | 62.5577 | 0.37535 | 74.9485 |  | 2007-01-01 | 13:17 | 47820 | 62.6496 | 0.3759 | 78.3594 |  | 2029-09-01 | 13:17 | 47820 | 99.1208 | 0.59472 | 201.3141 |  | 2006-09-01 | 13:17 | 47820 | 95.3791 | 0.57227 | 188.9181 |  | 2029-09-01 | 13:17 | 47820 | 62.6657 | 0.37599 | 105.9228 |  | 2006-09-01 | 13:17 | 47820 | 56.7647 | 0.34059 | 63.0815 |  | 2028-01-01 | 13:17 | 47820 | 99.4411 | 0.59665 | 199.6822 |  | 2007-01-01 | 13:17 | 47820 | 96.9804 | 0.58188 | 191.0517 |  | 2028-01-01 | 13:17 | 47820 | 43.1723 | 0.25903 | 44.8848 |  | 2007-01-01 | 13:17 | 47820 | 44.3815 | 0.26629 | 48.5054 |  | 2029-09-01 | 13:17 | 47820 | 99.1143 | 0.59469 | 199.644 |  | 2006-09-01 | 13:17 | 47820 | 95.3791 | 0.57227 | 188.7288 |  | 2029-09-01 | 13:17 | 47820 | 51.7442 | 0.31047 | 85.6165 |  | 2006-09-01 | 13:17 | 47820 | 45.8828 | 0.2753 | 46.8524 |  | 2028-01-01 | 13:17 | 47820 | 99.3879 | 0.59633 | 197.1253 |  | 2007-01-01 | 13:17 | 47820 | 96.9804 | 0.58188 | 190.9687 |  | 2028-01-01 | 13:17 | 47820 | 32.125 | 0.19275 | 32.1282 |  | 2007-01-01 | 13:17 | 47820 | 33.4949 | 0.20097 | 35.0821 |  | 2029-09-01 | 13:17 | 47820 | 67.5227 | 0.40514 | 90.1959 |  | 2029-09-01 | 13:17 | 47820 | 52.9983 | 0.31799 | 62.0978 |  | 2029-09-01 | 13:17 | 47820 | 39.6876 | 0.23813 | 42.8793 |  | 2006-09-01 | 13:17 | 47820 | 38.7951 | 0.23277 | 42.2671 |  | 2028-01-01 | 13:17 | 47820 | 62.5577 | 0.37535 | 74.9485 |  | 2007-01-01 | 13:17 | 47820 | 62.6496 | 0.3759 | 78.3594 |  | 2028-01-01 | 13:17 | 47820 | 36.6142 | 0.21969 | 38.0927 |  | 2007-01-01 | 13:17 | 47820 | 36.727 | 0.22036 | 39.1351
| 2029-09-01 | 13:18 | 47880 | 255.621 | 1.5337 | 298.1374 |  | 2029-09-01 | 13:18 | 47880 | 104.648 | 0.62789 | 210.2775 |  | 2006-09-01 | 13:18 | 47880 | 100.179 | 0.60107 | 191.4496 |  | 2029-09-01 | 13:18 | 47880 | 80.7556 | 0.48453 | 142.5532 |  | 2006-09-01 | 13:18 | 47880 | 74.8324 | 0.44899 | 96.8919 |  | 2028-01-01 | 13:18 | 47880 | 106.629 | 0.63977 | 211.2474 |  | 2007-01-01 | 13:18 | 47880 | 101.915 | 0.61149 | 192.7931 |  | 2028-01-01 | 13:18 | 47880 | 64.3827 | 0.3863 | 75.3348 |  | 2007-01-01 | 13:18 | 47880 | 64.4996 | 0.387 | 78.7464 |  | 2029-09-01 | 13:18 | 47880 | 104.291 | 0.62575 | 201.9399 |  | 2006-09-01 | 13:18 | 47880 | 100.179 | 0.60107 | 189.5192 |  | 2029-09-01 | 13:18 | 47880 | 64.4778 | 0.38687 | 106.3097 |  | 2006-09-01 | 13:18 | 47880 | 58.1244 | 0.34875 | 63.4302 |  | 2028-01-01 | 13:18 | 47880 | 104.64 | 0.62784 | 200.31 |  | 2007-01-01 | 13:18 | 47880 | 101.913 | 0.61148 | 191.6632 |  | 2028-01-01 | 13:18 | 47880 | 43.8713 | 0.26323 | 45.148 |  | 2007-01-01 | 13:18 | 47880 | 45.1335 | 0.2708 | 48.7762 |  | 2029-09-01 | 13:18 | 47880 | 104.284 | 0.6257 | 200.2697 |  | 2006-09-01 | 13:18 | 47880 | 100.179 | 0.60107 | 189.3298 |  | 2029-09-01 | 13:18 | 47880 | 52.8356 | 0.31701 | 85.9335 |  | 2006-09-01 | 13:18 | 47880 | 46.6023 | 0.27961 | 47.132 |  | 2028-01-01 | 13:18 | 47880 | 104.588 | 0.62753 | 197.7528 |  | 2007-01-01 | 13:18 | 47880 | 101.913 | 0.61148 | 191.5801 |  | 2028-01-01 | 13:18 | 47880 | 32.4088 | 0.19445 | 32.3227 |  | 2007-01-01 | 13:18 | 47880 | 33.8177 | 0.20291 | 35.285 |  | 2029-09-01 | 13:18 | 47880 | 69.611 | 0.41767 | 90.6136 |  | 2029-09-01 | 13:18 | 47880 | 54.196 | 0.32518 | 62.4229 |  | 2029-09-01 | 13:18 | 47880 | 40.219 | 0.24131 | 43.1206 |  | 2006-09-01 | 13:18 | 47880 | 39.2992 | 0.2358 | 42.5029 |  | 2028-01-01 | 13:18 | 47880 | 64.3827 | 0.3863 | 75.3348 |  | 2007-01-01 | 13:18 | 47880 | 64.4996 | 0.387 | 78.7464 |  | 2028-01-01 | 13:18 | 47880 | 37.0355 | 0.22221 | 38.3149 |  | 2007-01-01 | 13:18 | 47880 | 37.1485 | 0.22289 | 39.358
| 2029-09-01 | 13:19 | 47940 | 258.761 | 1.5526 | 299.69 |  | 2029-09-01 | 13:19 | 47940 | 109.744 | 0.65846 | 210.9359 |  | 2006-09-01 | 13:19 | 47940 | 104.9 | 0.6294 | 192.079 |  | 2029-09-01 | 13:19 | 47940 | 83.6513 | 0.50191 | 143.0551 |  | 2006-09-01 | 13:19 | 47940 | 77.2401 | 0.46344 | 97.3553 |  | 2028-01-01 | 13:19 | 47940 | 111.736 | 0.67042 | 211.9178 |  | 2007-01-01 | 13:19 | 47940 | 106.768 | 0.64061 | 193.4337 |  | 2028-01-01 | 13:19 | 47940 | 66.0855 | 0.39651 | 75.7313 |  | 2007-01-01 | 13:19 | 47940 | 66.225 | 0.39735 | 79.1437 |  | 2029-09-01 | 13:19 | 47940 | 109.391 | 0.65635 | 202.5962 |  | 2006-09-01 | 13:19 | 47940 | 104.9 | 0.6294 | 190.1486 |  | 2029-09-01 | 13:19 | 47940 | 66.1602 | 0.39696 | 106.7066 |  | 2006-09-01 | 13:19 | 47940 | 59.3576 | 0.35615 | 63.7864 |  | 2028-01-01 | 13:19 | 47940 | 109.773 | 0.65864 | 200.9686 |  | 2007-01-01 | 13:19 | 47940 | 106.767 | 0.6406 | 192.3038 |  | 2028-01-01 | 13:19 | 47940 | 44.4909 | 0.26695 | 45.415 |  | 2007-01-01 | 13:19 | 47940 | 45.8021 | 0.27481 | 49.051 |  | 2029-09-01 | 13:19 | 47940 | 109.384 | 0.6563 | 200.926 |  | 2006-09-01 | 13:19 | 47940 | 104.9 | 0.6294 | 189.9592 |  | 2029-09-01 | 13:19 | 47940 | 53.8175 | 0.32291 | 86.2564 |  | 2006-09-01 | 13:19 | 47940 | 47.2237 | 0.28334 | 47.4154 |  | 2028-01-01 | 13:19 | 47940 | 109.722 | 0.65833 | 198.4111 |  | 2007-01-01 | 13:19 | 47940 | 106.767 | 0.6406 | 192.2207 |  | 2028-01-01 | 13:19 | 47940 | 32.6496 | 0.1959 | 32.5186 |  | 2007-01-01 | 13:19 | 47940 | 34.093 | 0.20456 | 35.4896 |  | 2029-09-01 | 13:19 | 47940 | 71.5719 | 0.42943 | 91.043 |  | 2029-09-01 | 13:19 | 47940 | 55.2848 | 0.33171 | 62.7547 |  | 2029-09-01 | 13:19 | 47940 | 40.6804 | 0.24408 | 43.3647 |  | 2006-09-01 | 13:19 | 47940 | 39.7372 | 0.23842 | 42.7413 |  | 2028-01-01 | 13:19 | 47940 | 66.0855 | 0.39651 | 75.7313 |  | 2007-01-01 | 13:19 | 47940 | 66.225 | 0.39735 | 79.1437 |  | 2028-01-01 | 13:19 | 47940 | 37.3982 | 0.22439 | 38.5393 |  | 2007-01-01 | 13:19 | 47940 | 37.5108 | 0.22506 | 39.5831
| 2029-09-01 | 13:20 | 48000 | 261.854 | 1.5711 | 301.2611 |  | 2029-09-01 | 13:20 | 48000 | 114.77 | 0.68862 | 211.6245 |  | 2006-09-01 | 13:20 | 48000 | 109.545 | 0.65727 | 192.7363 |  | 2029-09-01 | 13:20 | 48000 | 86.4251 | 0.51855 | 143.5737 |  | 2006-09-01 | 13:20 | 48000 | 79.5163 | 0.4771 | 97.8324 |  | 2028-01-01 | 13:20 | 48000 | 116.779 | 0.70067 | 212.6185 |  | 2007-01-01 | 13:20 | 48000 | 111.545 | 0.66927 | 194.103 |  | 2028-01-01 | 13:20 | 48000 | 67.6744 | 0.40605 | 76.1373 |  | 2007-01-01 | 13:20 | 48000 | 67.8343 | 0.40701 | 79.5507 |  | 2029-09-01 | 13:20 | 48000 | 114.422 | 0.68653 | 203.2827 |  | 2006-09-01 | 13:20 | 48000 | 109.545 | 0.65727 | 190.8059 |  | 2029-09-01 | 13:20 | 48000 | 67.7228 | 0.40634 | 107.113 |  | 2006-09-01 | 13:20 | 48000 | 60.4742 | 0.36285 | 64.1492 |  | 2028-01-01 | 13:20 | 48000 | 114.841 | 0.68905 | 201.6577 |  | 2007-01-01 | 13:20 | 48000 | 111.543 | 0.66926 | 192.9731 |  | 2028-01-01 | 13:20 | 48000 | 45.0406 | 0.27024 | 45.6852 |  | 2007-01-01 | 13:20 | 48000 | 46.3968 | 0.27838 | 49.3294 |  | 2029-09-01 | 13:20 | 48000 | 114.415 | 0.68649 | 201.6125 |  | 2006-09-01 | 13:20 | 48000 | 109.545 | 0.65727 | 190.6165 |  | 2029-09-01 | 13:20 | 48000 | 54.7007 | 0.3282 | 86.5846 |  | 2006-09-01 | 13:20 | 48000 | 47.7574 | 0.28654 | 47.7019 |  | 2028-01-01 | 13:20 | 48000 | 114.79 | 0.68874 | 199.0999 |  | 2007-01-01 | 13:20 | 48000 | 111.543 | 0.66926 | 192.89 |  | 2028-01-01 | 13:20 | 48000 | 32.8543 | 0.19713 | 32.7157 |  | 2007-01-01 | 13:20 | 48000 | 34.3281 | 0.20597 | 35.6955 |  | 2029-09-01 | 13:20 | 48000 | 73.4132 | 0.44048 | 91.4835 |  | 2029-09-01 | 13:20 | 48000 | 56.2746 | 0.33765 | 63.0923 |  | 2029-09-01 | 13:20 | 48000 | 41.0809 | 0.24649 | 43.6112 |  | 2006-09-01 | 13:20 | 48000 | 40.118 | 0.24071 | 42.982 |  | 2028-01-01 | 13:20 | 48000 | 67.6744 | 0.40605 | 76.1373 |  | 2007-01-01 | 13:20 | 48000 | 67.8343 | 0.40701 | 79.5507 |  | 2028-01-01 | 13:20 | 48000 | 37.7107 | 0.22626 | 38.7655 |  | 2007-01-01 | 13:20 | 48000 | 37.8223 | 0.22693 | 39.81
| 2029-09-01 | 13:21 | 48060 | 264.9 | 1.5894 | 302.8505 |  | 2029-09-01 | 13:21 | 48060 | 119.728 | 0.71837 | 212.3429 |  | 2006-09-01 | 13:21 | 48060 | 114.113 | 0.68468 | 193.421 |  | 2029-09-01 | 13:21 | 48060 | 89.0746 | 0.53445 | 144.1081 |  | 2006-09-01 | 13:21 | 48060 | 81.6673 | 0.49 | 98.3224 |  | 2028-01-01 | 13:21 | 48060 | 121.757 | 0.73054 | 213.349 |  | 2007-01-01 | 13:21 | 48060 | 116.245 | 0.69747 | 194.8004 |  | 2028-01-01 | 13:21 | 48060 | 69.1573 | 0.41494 | 76.5523 |  | 2007-01-01 | 13:21 | 48060 | 69.3355 | 0.41601 | 79.9667 |  | 2029-09-01 | 13:21 | 48060 | 119.385 | 0.71631 | 203.999 |  | 2006-09-01 | 13:21 | 48060 | 114.113 | 0.68468 | 191.4906 |  | 2029-09-01 | 13:21 | 48060 | 69.1694 | 0.41502 | 107.528 |  | 2006-09-01 | 13:21 | 48060 | 61.4833 | 0.3689 | 64.5181 |  | 2028-01-01 | 13:21 | 48060 | 119.843 | 0.71906 | 202.3767 |  | 2007-01-01 | 13:21 | 48060 | 116.243 | 0.69746 | 193.6705 |  | 2028-01-01 | 13:21 | 48060 | 45.5286 | 0.27317 | 45.9584 |  | 2007-01-01 | 13:21 | 48060 | 46.9261 | 0.28156 | 49.6109 |  | 2029-09-01 | 13:21 | 48060 | 119.378 | 0.71627 | 202.3287 |  | 2006-09-01 | 13:21 | 48060 | 114.113 | 0.68468 | 191.3012 |  | 2029-09-01 | 13:21 | 48060 | 55.4916 | 0.33295 | 86.9176 |  | 2006-09-01 | 13:21 | 48060 | 48.213 | 0.28928 | 47.9912 |  | 2028-01-01 | 13:21 | 48060 | 119.793 | 0.71876 | 199.8186 |  | 2007-01-01 | 13:21 | 48060 | 116.243 | 0.69746 | 193.5875 |  | 2028-01-01 | 13:21 | 48060 | 33.0289 | 0.19817 | 32.9139 |  | 2007-01-01 | 13:21 | 48060 | 34.5292 | 0.20718 | 35.9027 |  | 2029-09-01 | 13:21 | 48060 | 75.1422 | 0.45085 | 91.9343 |  | 2029-09-01 | 13:21 | 48060 | 57.1744 | 0.34305 | 63.4353 |  | 2029-09-01 | 13:21 | 48060 | 41.4285 | 0.24857 | 43.8598 |  | 2006-09-01 | 13:21 | 48060 | 40.4493 | 0.2427 | 43.2247 |  | 2028-01-01 | 13:21 | 48060 | 69.1573 | 0.41494 | 76.5523 |  | 2007-01-01 | 13:21 | 48060 | 69.3355 | 0.41601 | 79.9667 |  | 2028-01-01 | 13:21 | 48060 | 37.9801 | 0.22788 | 38.9934 |  | 2007-01-01 | 13:21 | 48060 | 38.0903 | 0.22854 | 40.0386
| 2029-09-01 | 13:22 | 48120 | 267.902 | 1.6074 | 304.4579 |  | 2029-09-01 | 13:22 | 48120 | 124.619 | 0.74771 | 213.0906 |  | 2006-09-01 | 13:22 | 48120 | 118.608 | 0.71165 | 194.1326 |  | 2029-09-01 | 13:22 | 48120 | 91.6058 | 0.54963 | 144.6578 |  | 2006-09-01 | 13:22 | 48120 | 83.699 | 0.50219 | 98.8246 |  | 2028-01-01 | 13:22 | 48120 | 126.671 | 0.76003 | 214.1091 |  | 2007-01-01 | 13:22 | 48120 | 120.87 | 0.72522 | 195.5257 |  | 2028-01-01 | 13:22 | 48120 | 70.5415 | 0.42325 | 76.9755 |  | 2007-01-01 | 13:22 | 48120 | 70.7361 | 0.42442 | 80.3912 |  | 2029-09-01 | 13:22 | 48120 | 124.28 | 0.74568 | 204.7447 |  | 2006-09-01 | 13:22 | 48120 | 118.608 | 0.71165 | 192.2022 |  | 2029-09-01 | 13:22 | 48120 | 70.5076 | 0.42305 | 107.951 |  | 2006-09-01 | 13:22 | 48120 | 62.3932 | 0.37436 | 64.8925 |  | 2028-01-01 | 13:22 | 48120 | 124.782 | 0.74869 | 203.1254 |  | 2007-01-01 | 13:22 | 48120 | 120.868 | 0.72521 | 194.3957 |  | 2028-01-01 | 13:22 | 48120 | 45.9623 | 0.27577 | 46.2342 |  | 2007-01-01 | 13:22 | 48120 | 47.3976 | 0.28439 | 49.8953 |  | 2029-09-01 | 13:22 | 48120 | 124.274 | 0.74564 | 203.0744 |  | 2006-09-01 | 13:22 | 48120 | 118.608 | 0.71165 | 192.0128 |  | 2029-09-01 | 13:22 | 48120 | 56.1983 | 0.33719 | 87.2548 |  | 2006-09-01 | 13:22 | 48120 | 48.5989 | 0.29159 | 48.2828 |  | 2028-01-01 | 13:22 | 48120 | 124.732 | 0.74839 | 200.567 |  | 2007-01-01 | 13:22 | 48120 | 120.868 | 0.72521 | 194.3127 |  | 2028-01-01 | 13:22 | 48120 | 33.1782 | 0.19907 | 33.113 |  | 2007-01-01 | 13:22 | 48120 | 34.7019 | 0.20821 | 36.1109 |  | 2029-09-01 | 13:22 | 48120 | 76.7656 | 0.46059 | 92.3949 |  | 2029-09-01 | 13:22 | 48120 | 57.9924 | 0.34795 | 63.7833 |  | 2029-09-01 | 13:22 | 48120 | 41.7302 | 0.25038 | 44.1101 |  | 2006-09-01 | 13:22 | 48120 | 40.7375 | 0.24442 | 43.4692 |  | 2028-01-01 | 13:22 | 48120 | 70.5415 | 0.42325 | 76.9755 |  | 2007-01-01 | 13:22 | 48120 | 70.7361 | 0.42442 | 80.3912 |  | 2028-01-01 | 13:22 | 48120 | 38.2125 | 0.22927 | 39.2227 |  | 2007-01-01 | 13:22 | 48120 | 38.3209 | 0.22993 | 40.2685
| 2029-09-01 | 13:23 | 48180 | 270.858 | 1.6251 | 306.0831 |  | 2029-09-01 | 13:23 | 48180 | 129.444 | 0.77666 | 213.8673 |  | 2006-09-01 | 13:23 | 48180 | 123.031 | 0.73819 | 194.8708 |  | 2029-09-01 | 13:23 | 48180 | 94.0235 | 0.56414 | 145.2219 |  | 2006-09-01 | 13:23 | 48180 | 85.6171 | 0.5137 | 99.3383 |  | 2028-01-01 | 13:23 | 48180 | 131.523 | 0.78914 | 214.8982 |  | 2007-01-01 | 13:23 | 48180 | 125.42 | 0.75252 | 196.2782 |  | 2028-01-01 | 13:23 | 48180 | 71.834 | 0.431 | 77.4065 |  | 2007-01-01 | 13:23 | 48180 | 72.0428 | 0.43226 | 80.8234 |  | 2029-09-01 | 13:23 | 48180 | 129.109 | 0.77465 | 205.5194 |  | 2006-09-01 | 13:23 | 48180 | 123.031 | 0.73819 | 192.9404 |  | 2029-09-01 | 13:23 | 48180 | 71.7449 | 0.43047 | 108.3815 |  | 2006-09-01 | 13:23 | 48180 | 63.2119 | 0.37927 | 65.2718 |  | 2028-01-01 | 13:23 | 48180 | 129.657 | 0.77794 | 203.9034 |  | 2007-01-01 | 13:23 | 48180 | 125.419 | 0.75251 | 195.1483 |  | 2028-01-01 | 13:23 | 48180 | 46.3479 | 0.27809 | 46.5122 |  | 2007-01-01 | 13:23 | 48180 | 47.8178 | 0.28691 | 50.1822 |  | 2029-09-01 | 13:23 | 48180 | 129.103 | 0.77462 | 203.849 |  | 2006-09-01 | 13:23 | 48180 | 123.031 | 0.73819 | 192.751 |  | 2029-09-01 | 13:23 | 48180 | 56.8287 | 0.34097 | 87.5958 |  | 2006-09-01 | 13:23 | 48180 | 48.9228 | 0.29354 | 48.5763 |  | 2028-01-01 | 13:23 | 48180 | 129.608 | 0.77765 | 201.3447 |  | 2007-01-01 | 13:23 | 48180 | 125.419 | 0.75251 | 195.0652 |  | 2028-01-01 | 13:23 | 48180 | 33.3063 | 0.19984 | 33.3128 |  | 2007-01-01 | 13:23 | 48180 | 34.8504 | 0.2091 | 36.32 |  | 2029-09-01 | 13:23 | 48180 | 78.2897 | 0.46974 | 92.8647 |  | 2029-09-01 | 13:23 | 48180 | 58.7356 | 0.35241 | 64.1357 |  | 2029-09-01 | 13:23 | 48180 | 41.9917 | 0.25195 | 44.3621 |  | 2006-09-01 | 13:23 | 48180 | 40.9885 | 0.24593 | 43.7151 |  | 2028-01-01 | 13:23 | 48180 | 71.834 | 0.431 | 77.4065 |  | 2007-01-01 | 13:23 | 48180 | 72.0428 | 0.43226 | 80.8234 |  | 2028-01-01 | 13:23 | 48180 | 38.4132 | 0.23048 | 39.4532 |  | 2007-01-01 | 13:23 | 48180 | 38.5194 | 0.23112 | 40.4996
| 2029-09-01 | 13:24 | 48240 | 273.769 | 1.6426 | 307.7257 |  | 2029-09-01 | 13:24 | 48240 | 134.203 | 0.80522 | 214.6725 |  | 2006-09-01 | 13:24 | 48240 | 127.383 | 0.7643 | 195.6351 |  | 2029-09-01 | 13:24 | 48240 | 96.3324 | 0.57799 | 145.7999 |  | 2006-09-01 | 13:24 | 48240 | 87.427 | 0.52456 | 99.8629 |  | 2028-01-01 | 13:24 | 48240 | 136.312 | 0.81787 | 215.7161 |  | 2007-01-01 | 13:24 | 48240 | 129.898 | 0.77939 | 197.0576 |  | 2028-01-01 | 13:24 | 48240 | 73.0409 | 0.43825 | 77.8448 |  | 2007-01-01 | 13:24 | 48240 | 73.2623 | 0.43957 | 81.263 |  | 2029-09-01 | 13:24 | 48240 | 133.872 | 0.80323 | 206.3226 |  | 2006-09-01 | 13:24 | 48240 | 127.383 | 0.7643 | 193.7047 |  | 2029-09-01 | 13:24 | 48240 | 72.8879 | 0.43733 | 108.8188 |  | 2006-09-01 | 13:24 | 48240 | 63.9466 | 0.38368 | 65.6554 |  | 2028-01-01 | 13:24 | 48240 | 134.47 | 0.80682 | 204.7102 |  | 2007-01-01 | 13:24 | 48240 | 129.897 | 0.77938 | 195.9276 |  | 2028-01-01 | 13:24 | 48240 | 46.6914 | 0.28015 | 46.7924 |  | 2007-01-01 | 13:24 | 48240 | 48.1927 | 0.28916 | 50.4714 |  | 2029-09-01 | 13:24 | 48240 | 133.866 | 0.8032 | 204.6522 |  | 2006-09-01 | 13:24 | 48240 | 127.383 | 0.7643 | 193.5153 |  | 2029-09-01 | 13:24 | 48240 | 57.39 | 0.34434 | 87.9401 |  | 2006-09-01 | 13:24 | 48240 | 49.1915 | 0.29515 | 48.8715 |  | 2028-01-01 | 13:24 | 48240 | 134.421 | 0.80653 | 202.1512 |  | 2007-01-01 | 13:24 | 48240 | 129.897 | 0.77938 | 195.8446 |  | 2028-01-01 | 13:24 | 48240 | 33.4167 | 0.2005 | 33.5133 |  | 2007-01-01 | 13:24 | 48240 | 34.9786 | 0.20987 | 36.5299 |  | 2029-09-01 | 13:24 | 48240 | 79.7204 | 0.47832 | 93.343 |  | 2029-09-01 | 13:24 | 48240 | 59.4109 | 0.35647 | 64.4922 |  | 2029-09-01 | 13:24 | 48240 | 42.2185 | 0.25331 | 44.6154 |  | 2006-09-01 | 13:24 | 48240 | 41.2073 | 0.24724 | 43.9623 |  | 2028-01-01 | 13:24 | 48240 | 73.0409 | 0.43825 | 77.8448 |  | 2007-01-01 | 13:24 | 48240 | 73.2623 | 0.43957 | 81.263 |  | 2028-01-01 | 13:24 | 48240 | 38.5867 | 0.23152 | 39.6847 |  | 2007-01-01 | 13:24 | 48240 | 38.6905 | 0.23214 | 40.7318
| 2029-09-01 | 13:25 | 48300 | 276.635 | 1.6598 | 309.3855 |  | 2029-09-01 | 13:25 | 48300 | 138.895 | 0.83337 | 215.5059 |  | 2006-09-01 | 13:25 | 48300 | 131.665 | 0.78999 | 196.4251 |  | 2029-09-01 | 13:25 | 48300 | 98.5368 | 0.59122 | 146.3911 |  | 2006-09-01 | 13:25 | 48300 | 89.1339 | 0.5348 | 100.3977 |  | 2028-01-01 | 13:25 | 48300 | 141.04 | 0.84624 | 216.5623 |  | 2007-01-01 | 13:25 | 48300 | 134.304 | 0.80582 | 197.8634 |  | 2028-01-01 | 13:25 | 48300 | 74.1683 | 0.44501 | 78.2898 |  | 2007-01-01 | 13:25 | 48300 | 74.4004 | 0.4464 | 81.7094 |  | 2029-09-01 | 13:25 | 48300 | 138.569 | 0.83141 | 207.154 |  | 2006-09-01 | 13:25 | 48300 | 131.665 | 0.78999 | 194.4947 |  | 2029-09-01 | 13:25 | 48300 | 73.943 | 0.44366 | 109.2625 |  | 2006-09-01 | 13:25 | 48300 | 64.6039 | 0.38762 | 66.0431 |  | 2028-01-01 | 13:25 | 48300 | 139.221 | 0.83533 | 205.5455 |  | 2007-01-01 | 13:25 | 48300 | 134.303 | 0.80582 | 196.7335 |  | 2028-01-01 | 13:25 | 48300 | 46.9975 | 0.28198 | 47.0744 |  | 2007-01-01 | 13:25 | 48300 | 48.5274 | 0.29116 | 50.7625 |  | 2029-09-01 | 13:25 | 48300 | 138.564 | 0.83138 | 205.4836 |  | 2006-09-01 | 13:25 | 48300 | 131.665 | 0.78999 | 194.3053 |  | 2029-09-01 | 13:25 | 48300 | 57.8884 | 0.34733 | 88.2874 |  | 2006-09-01 | 13:25 | 48300 | 49.4112 | 0.29647 | 49.1679 |  | 2028-01-01 | 13:25 | 48300 | 139.173 | 0.83504 | 202.9862 |  | 2007-01-01 | 13:25 | 48300 | 134.303 | 0.80582 | 196.6504 |  | 2028-01-01 | 13:25 | 48300 | 33.5123 | 0.20107 | 33.7144 |  | 2007-01-01 | 13:25 | 48300 | 35.0897 | 0.21054 | 36.7404 |  | 2029-09-01 | 13:25 | 48300 | 81.063 | 0.48638 | 93.8294 |  | 2029-09-01 | 13:25 | 48300 | 60.0243 | 0.36015 | 64.8523 |  | 2029-09-01 | 13:25 | 48300 | 42.4148 | 0.25449 | 44.8699 |  | 2006-09-01 | 13:25 | 48300 | 41.398 | 0.24839 | 44.2107 |  | 2028-01-01 | 13:25 | 48300 | 74.1683 | 0.44501 | 78.2898 |  | 2007-01-01 | 13:25 | 48300 | 74.4004 | 0.4464 | 81.7094 |  | 2028-01-01 | 13:25 | 48300 | 38.7369 | 0.23242 | 39.9171 |  | 2007-01-01 | 13:25 | 48300 | 38.8379 | 0.23303 | 40.9648
| 2029-09-01 | 13:26 | 48360 | 279.458 | 1.6767 | 311.0622 |  | 2029-09-01 | 13:26 | 48360 | 143.523 | 0.86114 | 216.367 |  | 2006-09-01 | 13:26 | 48360 | 135.879 | 0.81527 | 197.2404 |  | 2029-09-01 | 13:26 | 48360 | 100.641 | 0.60385 | 146.995 |  | 2006-09-01 | 13:26 | 48360 | 90.7428 | 0.54446 | 100.9421 |  | 2028-01-01 | 13:26 | 48360 | 145.707 | 0.87424 | 217.4365 |  | 2007-01-01 | 13:26 | 48360 | 138.64 | 0.83184 | 198.6952 |  | 2028-01-01 | 13:26 | 48360 | 75.2215 | 0.45133 | 78.7411 |  | 2007-01-01 | 13:26 | 48360 | 75.4629 | 0.45278 | 82.1622 |  | 2029-09-01 | 13:26 | 48360 | 143.202 | 0.85921 | 208.0132 |  | 2006-09-01 | 13:26 | 48360 | 135.879 | 0.81527 | 195.31 |  | 2029-09-01 | 13:26 | 48360 | 74.9161 | 0.4495 | 109.712 |  | 2006-09-01 | 13:26 | 48360 | 65.1901 | 0.39114 | 66.4342 |  | 2028-01-01 | 13:26 | 48360 | 143.912 | 0.86347 | 206.409 |  | 2007-01-01 | 13:26 | 48360 | 138.638 | 0.83183 | 197.5653 |  | 2028-01-01 | 13:26 | 48360 | 47.2708 | 0.28362 | 47.358 |  | 2007-01-01 | 13:26 | 48360 | 48.8267 | 0.29296 | 51.0555 |  | 2029-09-01 | 13:26 | 48360 | 143.196 | 0.85918 | 206.3427 |  | 2006-09-01 | 13:26 | 48360 | 135.879 | 0.81527 | 195.1206 |  | 2029-09-01 | 13:26 | 48360 | 58.3299 | 0.34998 | 88.6374 |  | 2006-09-01 | 13:26 | 48360 | 49.5872 | 0.29752 | 49.4654 |  | 2028-01-01 | 13:26 | 48360 | 143.864 | 0.86318 | 203.8494 |  | 2007-01-01 | 13:26 | 48360 | 138.638 | 0.83183 | 197.4822 |  | 2028-01-01 | 13:26 | 48360 | 33.5955 | 0.20157 | 33.9159 |  | 2007-01-01 | 13:26 | 48360 | 35.1864 | 0.21112 | 36.9516 |  | 2029-09-01 | 13:26 | 48360 | 82.3229 | 0.49394 | 94.3233 |  | 2029-09-01 | 13:26 | 48360 | 60.5811 | 0.36349 | 65.2158 |  | 2029-09-01 | 13:26 | 48360 | 42.5847 | 0.25551 | 45.1254 |  | 2006-09-01 | 13:26 | 48360 | 41.5645 | 0.24939 | 44.4601 |  | 2028-01-01 | 13:26 | 48360 | 75.2215 | 0.45133 | 78.7411 |  | 2007-01-01 | 13:26 | 48360 | 75.4629 | 0.45278 | 82.1622 |  | 2028-01-01 | 13:26 | 48360 | 38.8671 | 0.2332 | 40.1503 |  | 2007-01-01 | 13:26 | 48360 | 38.9652 | 0.23379 | 41.1986
| 2029-09-01 | 13:27 | 48420 | 282.236 | 1.6934 | 312.7556 |  | 2029-09-01 | 13:27 | 48420 | 148.087 | 0.88852 | 217.2555 |  | 2006-09-01 | 13:27 | 48420 | 140.026 | 0.84016 | 198.0805 |  | 2029-09-01 | 13:27 | 48420 | 102.649 | 0.61589 | 147.6108 |  | 2006-09-01 | 13:27 | 48420 | 92.2583 | 0.55355 | 101.4957 |  | 2028-01-01 | 13:27 | 48420 | 150.315 | 0.90189 | 218.3384 |  | 2007-01-01 | 13:27 | 48420 | 142.906 | 0.85744 | 199.5527 |  | 2028-01-01 | 13:27 | 48420 | 76.2058 | 0.45723 | 79.1983 |  | 2007-01-01 | 13:27 | 48420 | 76.4549 | 0.45873 | 82.6209 |  | 2029-09-01 | 13:27 | 48420 | 147.769 | 0.88661 | 208.8999 |  | 2006-09-01 | 13:27 | 48420 | 140.026 | 0.84016 | 196.1501 |  | 2029-09-01 | 13:27 | 48420 | 75.8127 | 0.45488 | 110.1668 |  | 2006-09-01 | 13:27 | 48420 | 65.7109 | 0.39427 | 66.8285 |  | 2028-01-01 | 13:27 | 48420 | 148.542 | 0.89125 | 207.3002 |  | 2007-01-01 | 13:27 | 48420 | 142.904 | 0.85742 | 198.4227 |  | 2028-01-01 | 13:27 | 48420 | 47.5151 | 0.28509 | 47.6431 |  | 2007-01-01 | 13:27 | 48420 | 49.0945 | 0.29457 | 51.3501 |  | 2029-09-01 | 13:27 | 48420 | 147.764 | 0.88658 | 207.2293 |  | 2006-09-01 | 13:27 | 48420 | 140.026 | 0.84016 | 195.9607 |  | 2029-09-01 | 13:27 | 48420 | 58.7198 | 0.35232 | 88.9897 |  | 2006-09-01 | 13:27 | 48420 | 49.7246 | 0.29835 | 49.7638 |  | 2028-01-01 | 13:27 | 48420 | 148.495 | 0.89097 | 204.7404 |  | 2007-01-01 | 13:27 | 48420 | 142.904 | 0.85742 | 198.3396 |  | 2028-01-01 | 13:27 | 48420 | 33.6682 | 0.20201 | 34.1179 |  | 2007-01-01 | 13:27 | 48420 | 35.2709 | 0.21163 | 37.1632 |  | 2029-09-01 | 13:27 | 48420 | 83.5049 | 0.50103 | 94.8243 |  | 2029-09-01 | 13:27 | 48420 | 61.0865 | 0.36652 | 65.5823 |  | 2029-09-01 | 13:27 | 48420 | 42.7315 | 0.25639 | 45.3818 |  | 2006-09-01 | 13:27 | 48420 | 41.71 | 0.25026 | 44.7104 |  | 2028-01-01 | 13:27 | 48420 | 76.2058 | 0.45723 | 79.1983 |  | 2007-01-01 | 13:27 | 48420 | 76.4549 | 0.45873 | 82.6209 |  | 2028-01-01 | 13:27 | 48420 | 38.98 | 0.23388 | 40.3842 |  | 2007-01-01 | 13:27 | 48420 | 39.0752 | 0.23445 | 41.433
| 2029-09-01 | 13:28 | 48480 | 284.97 | 1.7098 | 314.4655 |  | 2029-09-01 | 13:28 | 48480 | 152.586 | 0.91552 | 218.1711 |  | 2006-09-01 | 13:28 | 48480 | 144.109 | 0.86465 | 198.9452 |  | 2029-09-01 | 13:28 | 48480 | 104.564 | 0.62738 | 148.2382 |  | 2006-09-01 | 13:28 | 48480 | 93.6851 | 0.56211 | 102.0578 |  | 2028-01-01 | 13:28 | 48480 | 154.863 | 0.92918 | 219.2676 |  | 2007-01-01 | 13:28 | 48480 | 147.103 | 0.88262 | 200.4353 |  | 2028-01-01 | 13:28 | 48480 | 77.1259 | 0.46276 | 79.6611 |  | 2007-01-01 | 13:28 | 48480 | 77.3813 | 0.46429 | 83.0852 |  | 2029-09-01 | 13:28 | 48480 | 152.273 | 0.91364 | 209.8135 |  | 2006-09-01 | 13:28 | 48480 | 144.109 | 0.86465 | 197.0148 |  | 2029-09-01 | 13:28 | 48480 | 76.6379 | 0.45983 | 110.6267 |  | 2006-09-01 | 13:28 | 48480 | 66.1716 | 0.39703 | 67.2255 |  | 2028-01-01 | 13:28 | 48480 | 153.113 | 0.91868 | 208.2189 |  | 2007-01-01 | 13:28 | 48480 | 147.102 | 0.88261 | 199.3053 |  | 2028-01-01 | 13:28 | 48480 | 47.7338 | 0.2864 | 47.9295 |  | 2007-01-01 | 13:28 | 48480 | 49.3346 | 0.29601 | 51.6461 |  | 2029-09-01 | 13:28 | 48480 | 152.267 | 0.9136 | 208.1429 |  | 2006-09-01 | 13:28 | 48480 | 144.109 | 0.86465 | 196.8254 |  | 2029-09-01 | 13:28 | 48480 | 59.0628 | 0.35438 | 89.3441 |  | 2006-09-01 | 13:28 | 48480 | 49.8277 | 0.29897 | 50.0628 |  | 2028-01-01 | 13:28 | 48480 | 153.066 | 0.9184 | 205.6588 |  | 2007-01-01 | 13:28 | 48480 | 147.102 | 0.88261 | 199.2222 |  | 2028-01-01 | 13:28 | 48480 | 33.7323 | 0.20239 | 34.3203 |  | 2007-01-01 | 13:28 | 48480 | 35.3452 | 0.21207 | 37.3752 |  | 2029-09-01 | 13:28 | 48480 | 84.6136 | 0.50768 | 95.332 |  | 2029-09-01 | 13:28 | 48480 | 61.545 | 0.36927 | 65.9516 |  | 2029-09-01 | 13:28 | 48480 | 42.8582 | 0.25715 | 45.6389 |  | 2006-09-01 | 13:28 | 48480 | 41.8372 | 0.25102 | 44.9614 |  | 2028-01-01 | 13:28 | 48480 | 77.1259 | 0.46276 | 79.6611 |  | 2007-01-01 | 13:28 | 48480 | 77.3813 | 0.46429 | 83.0852 |  | 2028-01-01 | 13:28 | 48480 | 39.0783 | 0.23447 | 40.6187 |  | 2007-01-01 | 13:28 | 48480 | 39.1703 | 0.23502 | 41.668
| 2029-09-01 | 13:29 | 48540 | 287.66 | 1.726 | 316.1914 |  | 2029-09-01 | 13:29 | 48540 | 157.022 | 0.94213 | 219.1132 |  | 2006-09-01 | 13:29 | 48540 | 148.127 | 0.88876 | 199.8339 |  | 2029-09-01 | 13:29 | 48540 | 106.39 | 0.63834 | 148.8766 |  | 2006-09-01 | 13:29 | 48540 | 95.0275 | 0.57017 | 102.628 |  | 2028-01-01 | 13:29 | 48540 | 159.353 | 0.95612 | 220.2237 |  | 2007-01-01 | 13:29 | 48540 | 151.234 | 0.9074 | 201.3427 |  | 2028-01-01 | 13:29 | 48540 | 77.9862 | 0.46792 | 80.129 |  | 2007-01-01 | 13:29 | 48540 | 78.2466 | 0.46948 | 83.5547 |  | 2029-09-01 | 13:29 | 48540 | 156.713 | 0.94028 | 210.7538 |  | 2006-09-01 | 13:29 | 48540 | 148.127 | 0.88876 | 197.9035 |  | 2029-09-01 | 13:29 | 48540 | 77.3965 | 0.46438 | 111.0911 |  | 2006-09-01 | 13:29 | 48540 | 66.5771 | 0.39946 | 67.625 |  | 2028-01-01 | 13:29 | 48540 | 157.625 | 0.94575 | 209.1647 |  | 2007-01-01 | 13:29 | 48540 | 151.233 | 0.9074 | 200.2127 |  | 2028-01-01 | 13:29 | 48540 | 47.93 | 0.28758 | 48.2171 |  | 2007-01-01 | 13:29 | 48540 | 49.55 | 0.2973 | 51.9434 |  | 2029-09-01 | 13:29 | 48540 | 156.708 | 0.94025 | 209.0832 |  | 2006-09-01 | 13:29 | 48540 | 148.127 | 0.88876 | 197.7141 |  | 2029-09-01 | 13:29 | 48540 | 59.3634 | 0.35618 | 89.7003 |  | 2006-09-01 | 13:29 | 48540 | 49.9004 | 0.2994 | 50.3622 |  | 2028-01-01 | 13:29 | 48540 | 157.579 | 0.94547 | 206.6043 |  | 2007-01-01 | 13:29 | 48540 | 151.233 | 0.9074 | 200.1296 |  | 2028-01-01 | 13:29 | 48540 | 33.789 | 0.20273 | 34.5231 |  | 2007-01-01 | 13:29 | 48540 | 35.4108 | 0.21246 | 37.5877 |  | 2029-09-01 | 13:29 | 48540 | 85.6531 | 0.51392 | 95.8459 |  | 2029-09-01 | 13:29 | 48540 | 61.9607 | 0.37176 | 66.3234 |  | 2029-09-01 | 13:29 | 48540 | 42.9674 | 0.2578 | 45.8967 |  | 2006-09-01 | 13:29 | 48540 | 41.9487 | 0.25169 | 45.2131 |  | 2028-01-01 | 13:29 | 48540 | 77.9862 | 0.46792 | 80.129 |  | 2007-01-01 | 13:29 | 48540 | 78.2466 | 0.46948 | 83.5547 |  | 2028-01-01 | 13:29 | 48540 | 39.1639 | 0.23498 | 40.8537 |  | 2007-01-01 | 13:29 | 48540 | 39.2528 | 0.23552 | 41.9036
| 2029-09-01 | 13:30 | 48600 | 290.306 | 1.7418 | 317.9333 |  | 2029-09-01 | 13:30 | 48600 | 161.395 | 0.96837 | 220.0816 |  | 2006-09-01 | 13:30 | 48600 | 152.082 | 0.91249 | 200.7464 |  | 2029-09-01 | 13:30 | 48600 | 108.131 | 0.64879 | 149.5254 |  | 2006-09-01 | 13:30 | 48600 | 96.2895 | 0.57774 | 103.2057 |  | 2028-01-01 | 13:30 | 48600 | 163.785 | 0.98271 | 221.2064 |  | 2007-01-01 | 13:30 | 48600 | 155.298 | 0.93179 | 202.2745 |  | 2028-01-01 | 13:30 | 48600 | 78.7909 | 0.47275 | 80.6017 |  | 2007-01-01 | 13:30 | 48600 | 79.0551 | 0.47433 | 84.029 |  | 2029-09-01 | 13:30 | 48600 | 161.09 | 0.96654 | 211.7203 |  | 2006-09-01 | 13:30 | 48600 | 152.082 | 0.91249 | 198.816 |  | 2029-09-01 | 13:30 | 48600 | 78.093 | 0.46856 | 111.5596 |  | 2006-09-01 | 13:30 | 48600 | 66.932 | 0.40159 | 68.0265 |  | 2028-01-01 | 13:30 | 48600 | 162.079 | 0.97247 | 210.1372 |  | 2007-01-01 | 13:30 | 48600 | 155.297 | 0.93178 | 201.1445 |  | 2028-01-01 | 13:30 | 48600 | 48.1063 | 0.28864 | 48.5057 |  | 2007-01-01 | 13:30 | 48600 | 49.7438 | 0.29846 | 52.2418 |  | 2029-09-01 | 13:30 | 48600 | 161.084 | 0.9665 | 210.0497 |  | 2006-09-01 | 13:30 | 48600 | 152.082 | 0.91249 | 198.6266 |  | 2029-09-01 | 13:30 | 48600 | 59.6255 | 0.35775 | 90.058 |  | 2006-09-01 | 13:30 | 48600 | 49.9463 | 0.29968 | 50.6618 |  | 2028-01-01 | 13:30 | 48600 | 162.034 | 0.9722 | 207.5765 |  | 2007-01-01 | 13:30 | 48600 | 155.297 | 0.93178 | 201.0614 |  | 2028-01-01 | 13:30 | 48600 | 33.8396 | 0.20304 | 34.7261 |  | 2007-01-01 | 13:30 | 48600 | 35.4693 | 0.21282 | 37.8005 |  | 2029-09-01 | 13:30 | 48600 | 86.6275 | 0.51977 | 96.3657 |  | 2029-09-01 | 13:30 | 48600 | 62.3374 | 0.37402 | 66.6974 |  | 2029-09-01 | 13:30 | 48600 | 43.0613 | 0.25837 | 46.1551 |  | 2006-09-01 | 13:30 | 48600 | 42.0464 | 0.25228 | 45.4654 |  | 2028-01-01 | 13:30 | 48600 | 78.7909 | 0.47275 | 80.6017 |  | 2007-01-01 | 13:30 | 48600 | 79.0551 | 0.47433 | 84.029 |  | 2028-01-01 | 13:30 | 48600 | 39.2386 | 0.23543 | 41.0891 |  | 2007-01-01 | 13:30 | 48600 | 39.3243 | 0.23595 | 42.1395
| 2029-09-01 | 13:31 | 48660 | 292.908 | 1.7574 | 319.6907 |  | 2029-09-01 | 13:31 | 48660 | 165.704 | 0.99422 | 221.0758 |  | 2006-09-01 | 13:31 | 48660 | 155.977 | 0.93586 | 201.6823 |  | 2029-09-01 | 13:31 | 48660 | 109.79 | 0.65874 | 150.1841 |  | 2006-09-01 | 13:31 | 48660 | 97.4751 | 0.58485 | 103.7905 |  | 2028-01-01 | 13:31 | 48660 | 168.16 | 1.009 | 222.2154 |  | 2007-01-01 | 13:31 | 48660 | 159.298 | 0.95579 | 203.2303 |  | 2028-01-01 | 13:31 | 48660 | 79.5436 | 0.47726 | 81.079 |  | 2007-01-01 | 13:31 | 48660 | 79.8108 | 0.47886 | 84.5079 |  | 2029-09-01 | 13:31 | 48660 | 165.403 | 0.99242 | 212.7127 |  | 2006-09-01 | 13:31 | 48660 | 155.977 | 0.93586 | 199.7519 |  | 2029-09-01 | 13:31 | 48660 | 78.7317 | 0.47239 | 112.032 |  | 2006-09-01 | 13:31 | 48660 | 67.2404 | 0.40344 | 68.43 |  | 2028-01-01 | 13:31 | 48660 | 166.475 | 0.99885 | 211.136 |  | 2007-01-01 | 13:31 | 48660 | 159.297 | 0.95578 | 202.1003 |  | 2028-01-01 | 13:31 | 48660 | 48.2651 | 0.28959 | 48.7953 |  | 2007-01-01 | 13:31 | 48660 | 49.9183 | 0.29951 | 52.5414 |  | 2029-09-01 | 13:31 | 48660 | 165.398 | 0.99239 | 211.0421 |  | 2006-09-01 | 13:31 | 48660 | 155.977 | 0.93586 | 199.5625 |  | 2029-09-01 | 13:31 | 48660 | 59.8527 | 0.35912 | 90.4171 |  | 2006-09-01 | 13:31 | 48660 | 49.9684 | 0.29981 | 50.9616 |  | 2028-01-01 | 13:31 | 48660 | 166.431 | 0.99859 | 208.5751 |  | 2007-01-01 | 13:31 | 48660 | 159.297 | 0.95578 | 202.0172 |  | 2028-01-01 | 13:31 | 48660 | 33.8852 | 0.20331 | 34.9294 |  | 2007-01-01 | 13:31 | 48660 | 35.5216 | 0.21313 | 38.0137 |  | 2029-09-01 | 13:31 | 48660 | 87.5405 | 0.52524 | 96.8909 |  | 2029-09-01 | 13:31 | 48660 | 62.6783 | 0.37607 | 67.0735 |  | 2029-09-01 | 13:31 | 48660 | 43.1417 | 0.25885 | 46.414 |  | 2006-09-01 | 13:31 | 48660 | 42.1323 | 0.25279 | 45.7182 |  | 2028-01-01 | 13:31 | 48660 | 79.5436 | 0.47726 | 81.079 |  | 2007-01-01 | 13:31 | 48660 | 79.8108 | 0.47886 | 84.5079 |  | 2028-01-01 | 13:31 | 48660 | 39.304 | 0.23582 | 41.3249 |  | 2007-01-01 | 13:31 | 48660 | 39.3866 | 0.23632 | 42.3758
| 2029-09-01 | 13:32 | 48720 | 295.464 | 1.7728 | 321.4635 |  | 2029-09-01 | 13:32 | 48720 | 169.95 | 1.0197 | 222.0955 |  | 2006-09-01 | 13:32 | 48720 | 159.811 | 0.95887 | 202.6412 |  | 2029-09-01 | 13:32 | 48720 | 111.371 | 0.66823 | 150.8523 |  | 2006-09-01 | 13:32 | 48720 | 98.5881 | 0.59153 | 104.3821 |  | 2028-01-01 | 13:32 | 48720 | 172.479 | 1.0349 | 223.2503 |  | 2007-01-01 | 13:32 | 48720 | 163.234 | 0.9794 | 204.2097 |  | 2028-01-01 | 13:32 | 48720 | 80.2482 | 0.48149 | 81.5605 |  | 2007-01-01 | 13:32 | 48720 | 80.5172 | 0.4831 | 84.991 |  | 2029-09-01 | 13:32 | 48720 | 169.653 | 1.0179 | 213.7306 |  | 2006-09-01 | 13:32 | 48720 | 159.811 | 0.95887 | 200.7108 |  | 2029-09-01 | 13:32 | 48720 | 79.3163 | 0.4759 | 112.5079 |  | 2006-09-01 | 13:32 | 48720 | 67.5062 | 0.40504 | 68.835 |  | 2028-01-01 | 13:32 | 48720 | 170.816 | 1.0249 | 212.1609 |  | 2007-01-01 | 13:32 | 48720 | 163.232 | 0.97939 | 203.0797 |  | 2028-01-01 | 13:32 | 48720 | 48.4084 | 0.29045 | 49.0858 |  | 2007-01-01 | 13:32 | 48720 | 50.0759 | 0.30046 | 52.8418 |  | 2029-09-01 | 13:32 | 48720 | 169.648 | 1.0179 | 212.06 |  | 2006-09-01 | 13:32 | 48720 | 159.811 | 0.95887 | 200.5214 |  | 2029-09-01 | 13:32 | 48720 | 60.0483 | 0.36029 | 90.7774 |  | 2006-09-01 | 13:32 | 48720 | 49.9696 | 0.29982 | 51.2615 |  | 2028-01-01 | 13:32 | 48720 | 170.772 | 1.0246 | 209.5997 |  | 2007-01-01 | 13:32 | 48720 | 163.232 | 0.97939 | 202.9966 |  | 2028-01-01 | 13:32 | 48720 | 33.9264 | 0.20356 | 35.133 |  | 2007-01-01 | 13:32 | 48720 | 35.5689 | 0.21341 | 38.2271 |  | 2029-09-01 | 13:32 | 48720 | 88.3951 | 0.53037 | 97.4213 |  | 2029-09-01 | 13:32 | 48720 | 62.9863 | 0.37792 | 67.4514 |  | 2029-09-01 | 13:32 | 48720 | 43.2102 | 0.25926 | 46.6732 |  | 2006-09-01 | 13:32 | 48720 | 42.2078 | 0.25325 | 45.9714 |  | 2028-01-01 | 13:32 | 48720 | 80.2482 | 0.48149 | 81.5605 |  | 2007-01-01 | 13:32 | 48720 | 80.5172 | 0.4831 | 84.991 |  | 2028-01-01 | 13:32 | 48720 | 39.3615 | 0.23617 | 41.5611 |  | 2007-01-01 | 13:32 | 48720 | 39.4409 | 0.23665 | 42.6125
| 2029-09-01 | 13:33 | 48780 | 297.975 | 1.7878 | 323.2513 |  | 2029-09-01 | 13:33 | 48780 | 174.133 | 1.0448 | 223.1403 |  | 2006-09-01 | 13:33 | 48780 | 163.586 | 0.98152 | 203.6227 |  | 2029-09-01 | 13:33 | 48780 | 112.876 | 0.67726 | 151.5296 |  | 2006-09-01 | 13:33 | 48780 | 99.6321 | 0.59779 | 104.9799 |  | 2028-01-01 | 13:33 | 48780 | 176.742 | 1.0605 | 224.3107 |  | 2007-01-01 | 13:33 | 48780 | 167.107 | 1.0026 | 205.2123 |  | 2028-01-01 | 13:33 | 48780 | 80.9078 | 0.48545 | 82.0459 |  | 2007-01-01 | 13:33 | 48780 | 81.1779 | 0.48707 | 85.478 |  | 2029-09-01 | 13:33 | 48780 | 173.839 | 1.043 | 214.7737 |  | 2006-09-01 | 13:33 | 48780 | 163.586 | 0.98152 | 201.6923 |  | 2029-09-01 | 13:33 | 48780 | 79.8506 | 0.4791 | 112.987 |  | 2006-09-01 | 13:33 | 48780 | 67.7329 | 0.4064 | 69.2414 |  | 2028-01-01 | 13:33 | 48780 | 175.1 | 1.0506 | 213.2115 |  | 2007-01-01 | 13:33 | 48780 | 167.106 | 1.0026 | 204.0823 |  | 2028-01-01 | 13:33 | 48780 | 48.5381 | 0.29123 | 49.377 |  | 2007-01-01 | 13:33 | 48780 | 50.2185 | 0.30131 | 53.1431 |  | 2029-09-01 | 13:33 | 48780 | 173.834 | 1.043 | 213.103 |  | 2006-09-01 | 13:33 | 48780 | 163.586 | 0.98152 | 201.5029 |  | 2029-09-01 | 13:33 | 48780 | 60.2153 | 0.36129 | 91.1387 |  | 2006-09-01 | 13:33 | 48780 | 49.9523 | 0.29971 | 51.5612 |  | 2028-01-01 | 13:33 | 48780 | 175.057 | 1.0503 | 210.65 |  | 2007-01-01 | 13:33 | 48780 | 167.106 | 1.0026 | 203.9992 |  | 2028-01-01 | 13:33 | 48780 | 33.964 | 0.20378 | 35.3368 |  | 2007-01-01 | 13:33 | 48780 | 35.6119 | 0.21367 | 38.4407 |  | 2029-09-01 | 13:33 | 48780 | 89.1948 | 0.53517 | 97.9565 |  | 2029-09-01 | 13:33 | 48780 | 63.2643 | 0.37959 | 67.831 |  | 2029-09-01 | 13:33 | 48780 | 43.2682 | 0.25961 | 46.9328 |  | 2006-09-01 | 13:33 | 48780 | 42.2745 | 0.25365 | 46.2251 |  | 2028-01-01 | 13:33 | 48780 | 80.9078 | 0.48545 | 82.0459 |  | 2007-01-01 | 13:33 | 48780 | 81.1779 | 0.48707 | 85.478 |  | 2028-01-01 | 13:33 | 48780 | 39.4121 | 0.23647 | 41.7976 |  | 2007-01-01 | 13:33 | 48780 | 39.4885 | 0.23693 | 42.8494
| 2029-09-01 | 13:34 | 48840 | 300.442 | 1.8027 | 325.054 |  | 2029-09-01 | 13:34 | 48840 | 178.253 | 1.0695 | 224.2098 |  | 2006-09-01 | 13:34 | 48840 | 167.303 | 1.0038 | 204.6265 |  | 2029-09-01 | 13:34 | 48840 | 114.309 | 0.68585 | 152.2154 |  | 2006-09-01 | 13:34 | 48840 | 100.61 | 0.60366 | 105.5835 |  | 2028-01-01 | 13:34 | 48840 | 180.951 | 1.0857 | 225.3964 |  | 2007-01-01 | 13:34 | 48840 | 170.919 | 1.0255 | 206.2378 |  | 2028-01-01 | 13:34 | 48840 | 81.5256 | 0.48915 | 82.5351 |  | 2007-01-01 | 13:34 | 48840 | 81.796 | 0.49078 | 85.9688 |  | 2029-09-01 | 13:34 | 48840 | 177.964 | 1.0678 | 215.8415 |  | 2006-09-01 | 13:34 | 48840 | 167.303 | 1.0038 | 202.6961 |  | 2029-09-01 | 13:34 | 48840 | 80.3381 | 0.48203 | 113.469 |  | 2006-09-01 | 13:34 | 48840 | 67.9238 | 0.40754 | 69.649 |  | 2028-01-01 | 13:34 | 48840 | 179.329 | 1.076 | 214.2875 |  | 2007-01-01 | 13:34 | 48840 | 170.918 | 1.0255 | 205.1078 |  | 2028-01-01 | 13:34 | 48840 | 48.6558 | 0.29193 | 49.6689 |  | 2007-01-01 | 13:34 | 48840 | 50.3478 | 0.30209 | 53.4452 |  | 2029-09-01 | 13:34 | 48840 | 177.959 | 1.0678 | 214.1707 |  | 2006-09-01 | 13:34 | 48840 | 167.303 | 1.0038 | 202.5067 |  | 2029-09-01 | 13:34 | 48840 | 60.3564 | 0.36214 | 91.5009 |  | 2006-09-01 | 13:34 | 48840 | 49.9189 | 0.29951 | 51.8607 |  | 2028-01-01 | 13:34 | 48840 | 179.287 | 1.0757 | 211.7257 |  | 2007-01-01 | 13:34 | 48840 | 170.918 | 1.0255 | 205.0247 |  | 2028-01-01 | 13:34 | 48840 | 33.9987 | 0.20399 | 35.5408 |  | 2007-01-01 | 13:34 | 48840 | 35.6513 | 0.21391 | 38.6547 |  | 2029-09-01 | 13:34 | 48840 | 89.9433 | 0.53966 | 98.4961 |  | 2029-09-01 | 13:34 | 48840 | 63.5154 | 0.38109 | 68.2121 |  | 2029-09-01 | 13:34 | 48840 | 43.3175 | 0.2599 | 47.1927 |  | 2006-09-01 | 13:34 | 48840 | 42.3334 | 0.254 | 46.4791 |  | 2028-01-01 | 13:34 | 48840 | 81.5256 | 0.48915 | 82.5351 |  | 2007-01-01 | 13:34 | 48840 | 81.796 | 0.49078 | 85.9688 |  | 2028-01-01 | 13:34 | 48840 | 39.4568 | 0.23674 | 42.0343 |  | 2007-01-01 | 13:34 | 48840 | 39.5302 | 0.23718 | 43.0866
| 2029-09-01 | 13:35 | 48900 | 302.867 | 1.8172 | 326.8712 |  | 2029-09-01 | 13:35 | 48900 | 182.314 | 1.0939 | 225.3037 |  | 2006-09-01 | 13:35 | 48900 | 170.964 | 1.0258 | 205.6523 |  | 2029-09-01 | 13:35 | 48900 | 115.672 | 0.69403 | 152.9095 |  | 2006-09-01 | 13:35 | 48900 | 101.526 | 0.60916 | 106.1927 |  | 2028-01-01 | 13:35 | 48900 | 185.105 | 1.1106 | 226.5071 |  | 2007-01-01 | 13:35 | 48900 | 174.671 | 1.048 | 207.2858 |  | 2028-01-01 | 13:35 | 48900 | 82.1043 | 0.49263 | 83.0277 |  | 2007-01-01 | 13:35 | 48900 | 82.3746 | 0.49425 | 86.4631 |  | 2029-09-01 | 13:35 | 48900 | 182.028 | 1.0922 | 216.9336 |  | 2006-09-01 | 13:35 | 48900 | 170.964 | 1.0258 | 203.7219 |  | 2029-09-01 | 13:35 | 48900 | 80.7818 | 0.48469 | 113.9537 |  | 2006-09-01 | 13:35 | 48900 | 68.082 | 0.40849 | 70.0575 |  | 2028-01-01 | 13:35 | 48900 | 183.504 | 1.101 | 215.3885 |  | 2007-01-01 | 13:35 | 48900 | 174.67 | 1.048 | 206.1558 |  | 2028-01-01 | 13:35 | 48900 | 48.7628 | 0.29258 | 49.9615 |  | 2007-01-01 | 13:35 | 48900 | 50.4654 | 0.30279 | 53.748 |  | 2029-09-01 | 13:35 | 48900 | 182.023 | 1.0921 | 215.2629 |  | 2006-09-01 | 13:35 | 48900 | 170.964 | 1.0258 | 203.5325 |  | 2029-09-01 | 13:35 | 48900 | 60.4741 | 0.36284 | 91.8637 |  | 2006-09-01 | 13:35 | 48900 | 49.8712 | 0.29923 | 52.1599 |  | 2028-01-01 | 13:35 | 48900 | 183.462 | 1.1008 | 212.8265 |  | 2007-01-01 | 13:35 | 48900 | 174.67 | 1.048 | 206.0728 |  | 2028-01-01 | 13:35 | 48900 | 34.0308 | 0.20418 | 35.7449 |  | 2007-01-01 | 13:35 | 48900 | 35.6876 | 0.21413 | 38.8688 |  | 2029-09-01 | 13:35 | 48900 | 90.6439 | 0.54386 | 99.04 |  | 2029-09-01 | 13:35 | 48900 | 63.742 | 0.38245 | 68.5945 |  | 2029-09-01 | 13:35 | 48900 | 43.3591 | 0.26015 | 47.4529 |  | 2006-09-01 | 13:35 | 48900 | 42.3856 | 0.25431 | 46.7334 |  | 2028-01-01 | 13:35 | 48900 | 82.1043 | 0.49263 | 83.0277 |  | 2007-01-01 | 13:35 | 48900 | 82.3746 | 0.49425 | 86.4631 |  | 2028-01-01 | 13:35 | 48900 | 39.4964 | 0.23698 | 42.2713 |  | 2007-01-01 | 13:35 | 48900 | 39.567 | 0.2374 | 43.324
| 2029-09-01 | 13:36 | 48960 | 305.25 | 1.8315 | 328.7027 |  | 2029-09-01 | 13:36 | 48960 | 186.313 | 1.1179 | 226.4216 |  | 2006-09-01 | 13:36 | 48960 | 174.569 | 1.0474 | 206.6997 |  | 2029-09-01 | 13:36 | 48960 | 116.969 | 0.70181 | 153.6113 |  | 2006-09-01 | 13:36 | 48960 | 102.383 | 0.6143 | 106.807 |  | 2028-01-01 | 13:36 | 48960 | 189.205 | 1.1352 | 227.6423 |  | 2007-01-01 | 13:36 | 48960 | 178.364 | 1.0702 | 208.356 |  | 2028-01-01 | 13:36 | 48960 | 82.6468 | 0.49588 | 83.5236 |  | 2007-01-01 | 13:36 | 48960 | 82.9163 | 0.4975 | 86.9606 |  | 2029-09-01 | 13:36 | 48960 | 186.032 | 1.1162 | 218.0498 |  | 2006-09-01 | 13:36 | 48960 | 174.569 | 1.0474 | 204.7693 |  | 2029-09-01 | 13:36 | 48960 | 81.1848 | 0.48711 | 114.4408 |  | 2006-09-01 | 13:36 | 48960 | 68.2103 | 0.40926 | 70.4667 |  | 2028-01-01 | 13:36 | 48960 | 187.625 | 1.1258 | 216.5142 |  | 2007-01-01 | 13:36 | 48960 | 178.363 | 1.0702 | 207.226 |  | 2028-01-01 | 13:36 | 48960 | 48.8605 | 0.29316 | 50.2547 |  | 2007-01-01 | 13:36 | 48960 | 50.5728 | 0.30344 | 54.0514 |  | 2029-09-01 | 13:36 | 48960 | 186.027 | 1.1162 | 216.379 |  | 2006-09-01 | 13:36 | 48960 | 174.569 | 1.0474 | 204.5799 |  | 2029-09-01 | 13:36 | 48960 | 60.5706 | 0.36342 | 92.2271 |  | 2006-09-01 | 13:36 | 48960 | 49.811 | 0.29887 | 52.4588 |  | 2028-01-01 | 13:36 | 48960 | 187.583 | 1.1255 | 213.952 |  | 2007-01-01 | 13:36 | 48960 | 178.363 | 1.0702 | 207.1429 |  | 2028-01-01 | 13:36 | 48960 | 34.0608 | 0.20436 | 35.9493 |  | 2007-01-01 | 13:36 | 48960 | 35.7215 | 0.21433 | 39.0831 |  | 2029-09-01 | 13:36 | 48960 | 91.2993 | 0.5478 | 99.5878 |  | 2029-09-01 | 13:36 | 48960 | 63.9463 | 0.38368 | 68.9782 |  | 2029-09-01 | 13:36 | 48960 | 43.3941 | 0.26036 | 47.7133 |  | 2006-09-01 | 13:36 | 48960 | 42.432 | 0.25459 | 46.988 |  | 2028-01-01 | 13:36 | 48960 | 82.6468 | 0.49588 | 83.5236 |  | 2007-01-01 | 13:36 | 48960 | 82.9163 | 0.4975 | 86.9606 |  | 2028-01-01 | 13:36 | 48960 | 39.5318 | 0.23719 | 42.5085 |  | 2007-01-01 | 13:36 | 48960 | 39.5996 | 0.2376 | 43.5616
| 2029-09-01 | 13:37 | 49020 | 307.59 | 1.8455 | 330.5482 |  | 2029-09-01 | 13:37 | 49020 | 190.253 | 1.1415 | 227.5631 |  | 2006-09-01 | 13:37 | 49020 | 178.12 | 1.0687 | 207.7684 |  | 2029-09-01 | 13:37 | 49020 | 118.202 | 0.70921 | 154.3205 |  | 2006-09-01 | 13:37 | 49020 | 103.184 | 0.6191 | 107.4261 |  | 2028-01-01 | 13:37 | 49020 | 193.253 | 1.1595 | 228.8018 |  | 2007-01-01 | 13:37 | 49020 | 182 | 1.092 | 209.448 |  | 2028-01-01 | 13:37 | 49020 | 83.1554 | 0.49893 | 84.0225 |  | 2007-01-01 | 13:37 | 49020 | 83.4238 | 0.50054 | 87.4611 |  | 2029-09-01 | 13:37 | 49020 | 189.975 | 1.1399 | 219.1897 |  | 2006-09-01 | 13:37 | 49020 | 178.12 | 1.0687 | 205.838 |  | 2029-09-01 | 13:37 | 49020 | 81.5499 | 0.4893 | 114.9301 |  | 2006-09-01 | 13:37 | 49020 | 68.3112 | 0.40987 | 70.8766 |  | 2028-01-01 | 13:37 | 49020 | 191.692 | 1.1502 | 217.6644 |  | 2007-01-01 | 13:37 | 49020 | 181.998 | 1.092 | 208.318 |  | 2028-01-01 | 13:37 | 49020 | 48.9499 | 0.2937 | 50.5484 |  | 2007-01-01 | 13:37 | 49020 | 50.671 | 0.30403 | 54.3555 |  | 2029-09-01 | 13:37 | 49020 | 189.97 | 1.1398 | 217.5188 |  | 2006-09-01 | 13:37 | 49020 | 178.12 | 1.0687 | 205.6486 |  | 2029-09-01 | 13:37 | 49020 | 60.6479 | 0.36389 | 92.591 |  | 2006-09-01 | 13:37 | 49020 | 49.7399 | 0.29844 | 52.7572 |  | 2028-01-01 | 13:37 | 49020 | 191.651 | 1.1499 | 215.1019 |  | 2007-01-01 | 13:37 | 49020 | 181.998 | 1.092 | 208.2349 |  | 2028-01-01 | 13:37 | 49020 | 34.089 | 0.20453 | 36.1538 |  | 2007-01-01 | 13:37 | 49020 | 35.7534 | 0.21452 | 39.2976 |  | 2029-09-01 | 13:37 | 49020 | 91.9121 | 0.55147 | 100.1393 |  | 2029-09-01 | 13:37 | 49020 | 64.1302 | 0.38478 | 69.363 |  | 2029-09-01 | 13:37 | 49020 | 43.4232 | 0.26054 | 47.9738 |  | 2006-09-01 | 13:37 | 49020 | 42.4733 | 0.25484 | 47.2428 |  | 2028-01-01 | 13:37 | 49020 | 83.1554 | 0.49893 | 84.0225 |  | 2007-01-01 | 13:37 | 49020 | 83.4238 | 0.50054 | 87.4611 |  | 2028-01-01 | 13:37 | 49020 | 39.5634 | 0.23738 | 42.7458 |  | 2007-01-01 | 13:37 | 49020 | 39.6286 | 0.23777 | 43.7994
| 2029-09-01 | 13:38 | 49080 | 309.889 | 1.8593 | 332.4076 |  | 2029-09-01 | 13:38 | 49080 | 194.133 | 1.1648 | 228.7279 |  | 2006-09-01 | 13:38 | 49080 | 181.618 | 1.0897 | 208.8581 |  | 2029-09-01 | 13:38 | 49080 | 119.374 | 0.71624 | 155.0367 |  | 2006-09-01 | 13:38 | 49080 | 103.931 | 0.62359 | 108.0497 |  | 2028-01-01 | 13:38 | 49080 | 197.248 | 1.1835 | 229.9853 |  | 2007-01-01 | 13:38 | 49080 | 185.579 | 1.1135 | 210.5615 |  | 2028-01-01 | 13:38 | 49080 | 83.6326 | 0.5018 | 84.5243 |  | 2007-01-01 | 13:38 | 49080 | 83.8996 | 0.5034 | 87.9645 |  | 2029-09-01 | 13:38 | 49080 | 193.859 | 1.1632 | 220.3528 |  | 2006-09-01 | 13:38 | 49080 | 181.618 | 1.0897 | 206.9277 |  | 2029-09-01 | 13:38 | 49080 | 81.8797 | 0.49128 | 115.4214 |  | 2006-09-01 | 13:38 | 49080 | 68.387 | 0.41032 | 71.2869 |  | 2028-01-01 | 13:38 | 49080 | 195.707 | 1.1742 | 218.8386 |  | 2007-01-01 | 13:38 | 49080 | 185.578 | 1.1135 | 209.4315 |  | 2028-01-01 | 13:38 | 49080 | 49.032 | 0.29419 | 50.8425 |  | 2007-01-01 | 13:38 | 49080 | 50.7613 | 0.30457 | 54.66 |  | 2029-09-01 | 13:38 | 49080 | 193.854 | 1.1631 | 218.682 |  | 2006-09-01 | 13:38 | 49080 | 181.618 | 1.0897 | 206.7383 |  | 2029-09-01 | 13:38 | 49080 | 60.7079 | 0.36425 | 92.9553 |  | 2006-09-01 | 13:38 | 49080 | 49.6593 | 0.29796 | 53.0552 |  | 2028-01-01 | 13:38 | 49080 | 195.667 | 1.174 | 216.2759 |  | 2007-01-01 | 13:38 | 49080 | 185.578 | 1.1135 | 209.3484 |  | 2028-01-01 | 13:38 | 49080 | 34.1158 | 0.20469 | 36.3585 |  | 2007-01-01 | 13:38 | 49080 | 35.7835 | 0.2147 | 39.5123 |  | 2029-09-01 | 13:38 | 49080 | 92.485 | 0.55491 | 100.6942 |  | 2029-09-01 | 13:38 | 49080 | 64.2957 | 0.38577 | 69.7487 |  | 2029-09-01 | 13:38 | 49080 | 43.4474 | 0.26068 | 48.2345 |  | 2006-09-01 | 13:38 | 49080 | 42.5102 | 0.25506 | 47.4979 |  | 2028-01-01 | 13:38 | 49080 | 83.6326 | 0.5018 | 84.5243 |  | 2007-01-01 | 13:38 | 49080 | 83.8996 | 0.5034 | 87.9645 |  | 2028-01-01 | 13:38 | 49080 | 39.5918 | 0.23755 | 42.9834 |  | 2007-01-01 | 13:38 | 49080 | 39.6545 | 0.23793 | 44.0373
| 2029-09-01 | 13:39 | 49140 | 312.148 | 1.8729 | 334.2805 |  | 2029-09-01 | 13:39 | 49140 | 197.955 | 1.1877 | 229.9156 |  | 2006-09-01 | 13:39 | 49140 | 185.064 | 1.1104 | 209.9685 |  | 2029-09-01 | 13:39 | 49140 | 120.486 | 0.72292 | 155.7597 |  | 2006-09-01 | 13:39 | 49140 | 104.627 | 0.62776 | 108.6774 |  | 2028-01-01 | 13:39 | 49140 | 201.191 | 1.2071 | 231.1924 |  | 2007-01-01 | 13:39 | 49140 | 189.103 | 1.1346 | 211.6961 |  | 2028-01-01 | 13:39 | 49140 | 84.0805 | 0.50448 | 85.0288 |  | 2007-01-01 | 13:39 | 49140 | 84.3458 | 0.50607 | 88.4706 |  | 2029-09-01 | 13:39 | 49140 | 197.685 | 1.1861 | 221.5389 |  | 2006-09-01 | 13:39 | 49140 | 185.064 | 1.1104 | 208.0381 |  | 2029-09-01 | 13:39 | 49140 | 82.1766 | 0.49306 | 115.9145 |  | 2006-09-01 | 13:39 | 49140 | 68.4401 | 0.41064 | 71.6975 |  | 2028-01-01 | 13:39 | 49140 | 199.671 | 1.198 | 220.0367 |  | 2007-01-01 | 13:39 | 49140 | 189.102 | 1.1346 | 210.5661 |  | 2028-01-01 | 13:39 | 49140 | 49.1077 | 0.29465 | 51.1372 |  | 2007-01-01 | 13:39 | 49140 | 50.8445 | 0.30507 | 54.9651 |  | 2029-09-01 | 13:39 | 49140 | 197.68 | 1.1861 | 219.868 |  | 2006-09-01 | 13:39 | 49140 | 185.064 | 1.1104 | 207.8487 |  | 2029-09-01 | 13:39 | 49140 | 60.7523 | 0.36451 | 93.3198 |  | 2006-09-01 | 13:39 | 49140 | 49.5704 | 0.29742 | 53.3526 |  | 2028-01-01 | 13:39 | 49140 | 199.631 | 1.1978 | 217.4737 |  | 2007-01-01 | 13:39 | 49140 | 189.102 | 1.1346 | 210.483 |  | 2028-01-01 | 13:39 | 49140 | 34.1413 | 0.20485 | 36.5634 |  | 2007-01-01 | 13:39 | 49140 | 35.8122 | 0.21487 | 39.7272 |  | 2029-09-01 | 13:39 | 49140 | 93.0204 | 0.55812 | 101.2523 |  | 2029-09-01 | 13:39 | 49140 | 64.4444 | 0.38667 | 70.1354 |  | 2029-09-01 | 13:39 | 49140 | 43.4671 | 0.2608 | 48.4953 |  | 2006-09-01 | 13:39 | 49140 | 42.5434 | 0.25526 | 47.7531 |  | 2028-01-01 | 13:39 | 49140 | 84.0805 | 0.50448 | 85.0288 |  | 2007-01-01 | 13:39 | 49140 | 84.3458 | 0.50607 | 88.4706 |  | 2028-01-01 | 13:39 | 49140 | 39.6174 | 0.2377 | 43.2211 |  | 2007-01-01 | 13:39 | 49140 | 39.6779 | 0.23807 | 44.2754
| 2029-09-01 | 13:40 | 49200 | 314.366 | 1.8862 | 336.1667 |  | 2029-09-01 | 13:40 | 49200 | 201.719 | 1.2103 | 231.1259 |  | 2006-09-01 | 13:40 | 49200 | 188.458 | 1.1307 | 211.0992 |  | 2029-09-01 | 13:40 | 49200 | 121.542 | 0.72925 | 156.4889 |  | 2006-09-01 | 13:40 | 49200 | 105.276 | 0.63166 | 109.3091 |  | 2028-01-01 | 13:40 | 49200 | 205.084 | 1.2305 | 232.423 |  | 2007-01-01 | 13:40 | 49200 | 192.574 | 1.1554 | 212.8516 |  | 2028-01-01 | 13:40 | 49200 | 84.501 | 0.50701 | 85.5358 |  | 2007-01-01 | 13:40 | 49200 | 84.7646 | 0.50859 | 88.9792 |  | 2029-09-01 | 13:40 | 49200 | 201.452 | 1.2087 | 222.7477 |  | 2006-09-01 | 13:40 | 49200 | 188.458 | 1.1307 | 209.1688 |  | 2029-09-01 | 13:40 | 49200 | 82.443 | 0.49466 | 116.4091 |  | 2006-09-01 | 13:40 | 49200 | 68.4724 | 0.41083 | 72.1084 |  | 2028-01-01 | 13:40 | 49200 | 203.583 | 1.2215 | 221.2582 |  | 2007-01-01 | 13:40 | 49200 | 192.573 | 1.1554 | 211.7215 |  | 2028-01-01 | 13:40 | 49200 | 49.1777 | 0.29507 | 51.4323 |  | 2007-01-01 | 13:40 | 49200 | 50.9215 | 0.30553 | 55.2706 |  | 2029-09-01 | 13:40 | 49200 | 201.448 | 1.2087 | 221.0767 |  | 2006-09-01 | 13:40 | 49200 | 188.458 | 1.1307 | 208.9795 |  | 2029-09-01 | 13:40 | 49200 | 60.7825 | 0.36469 | 93.6845 |  | 2006-09-01 | 13:40 | 49200 | 49.4744 | 0.29685 | 53.6495 |  | 2028-01-01 | 13:40 | 49200 | 203.543 | 1.2213 | 218.695 |  | 2007-01-01 | 13:40 | 49200 | 192.573 | 1.1554 | 211.6384 |  | 2028-01-01 | 13:40 | 49200 | 34.1659 | 0.205 | 36.7684 |  | 2007-01-01 | 13:40 | 49200 | 35.8397 | 0.21504 | 39.9422 |  | 2029-09-01 | 13:40 | 49200 | 93.5206 | 0.56112 | 101.8134 |  | 2029-09-01 | 13:40 | 49200 | 64.5778 | 0.38747 | 70.5229 |  | 2029-09-01 | 13:40 | 49200 | 43.4831 | 0.2609 | 48.7562 |  | 2006-09-01 | 13:40 | 49200 | 42.5732 | 0.25544 | 48.0086 |  | 2028-01-01 | 13:40 | 49200 | 84.501 | 0.50701 | 85.5358 |  | 2007-01-01 | 13:40 | 49200 | 84.7646 | 0.50859 | 88.9792 |  | 2028-01-01 | 13:40 | 49200 | 39.6408 | 0.23784 | 43.4589 |  | 2007-01-01 | 13:40 | 49200 | 39.6992 | 0.2382 | 44.5135
| 2029-09-01 | 13:41 | 49260 | 316.544 | 1.8993 | 338.0659 |  | 2029-09-01 | 13:41 | 49260 | 205.425 | 1.2326 | 232.3585 |  | 2006-09-01 | 13:41 | 49260 | 191.803 | 1.1508 | 212.2501 |  | 2029-09-01 | 13:41 | 49260 | 122.545 | 0.73527 | 157.2242 |  | 2006-09-01 | 13:41 | 49260 | 105.878 | 0.63527 | 109.9444 |  | 2028-01-01 | 13:41 | 49260 | 208.926 | 1.2536 | 233.6765 |  | 2007-01-01 | 13:41 | 49260 | 195.993 | 1.176 | 214.0275 |  | 2028-01-01 | 13:41 | 49260 | 84.8961 | 0.50938 | 86.0452 |  | 2007-01-01 | 13:41 | 49260 | 85.1579 | 0.51095 | 89.4901 |  | 2029-09-01 | 13:41 | 49260 | 205.162 | 1.231 | 223.9786 |  | 2006-09-01 | 13:41 | 49260 | 191.803 | 1.1508 | 210.3197 |  | 2029-09-01 | 13:41 | 49260 | 82.6808 | 0.49608 | 116.9052 |  | 2006-09-01 | 13:41 | 49260 | 68.4857 | 0.41091 | 72.5193 |  | 2028-01-01 | 13:41 | 49260 | 207.444 | 1.2447 | 222.5028 |  | 2007-01-01 | 13:41 | 49260 | 195.992 | 1.176 | 212.8975 |  | 2028-01-01 | 13:41 | 49260 | 49.2427 | 0.29546 | 51.7277 |  | 2007-01-01 | 13:41 | 49260 | 50.9931 | 0.30596 | 55.5766 |  | 2029-09-01 | 13:41 | 49260 | 205.157 | 1.2309 | 222.3077 |  | 2006-09-01 | 13:41 | 49260 | 191.803 | 1.1508 | 210.1303 |  | 2029-09-01 | 13:41 | 49260 | 60.8 | 0.3648 | 94.0493 |  | 2006-09-01 | 13:41 | 49260 | 49.3721 | 0.29623 | 53.9457 |  | 2028-01-01 | 13:41 | 49260 | 207.405 | 1.2444 | 219.9394 |  | 2007-01-01 | 13:41 | 49260 | 195.992 | 1.176 | 212.8144 |  | 2028-01-01 | 13:41 | 49260 | 34.1895 | 0.20514 | 36.9735 |  | 2007-01-01 | 13:41 | 49260 | 35.8663 | 0.2152 | 40.1574 |  | 2029-09-01 | 13:41 | 49260 | 93.9874 | 0.56392 | 102.3773 |  | 2029-09-01 | 13:41 | 49260 | 64.6972 | 0.38818 | 70.9111 |  | 2029-09-01 | 13:41 | 49260 | 43.4958 | 0.26097 | 49.0172 |  | 2006-09-01 | 13:41 | 49260 | 42.6003 | 0.2556 | 48.2642 |  | 2028-01-01 | 13:41 | 49260 | 84.8961 | 0.50938 | 86.0452 |  | 2007-01-01 | 13:41 | 49260 | 85.1579 | 0.51095 | 89.4901 |  | 2028-01-01 | 13:41 | 49260 | 39.6621 | 0.23797 | 43.6969 |  | 2007-01-01 | 13:41 | 49260 | 39.7186 | 0.23831 | 44.7519
| 2029-09-01 | 13:42 | 49320 | 318.68 | 1.9121 | 339.978 |  | 2029-09-01 | 13:42 | 49320 | 209.073 | 1.2544 | 233.6129 |  | 2006-09-01 | 13:42 | 49320 | 195.098 | 1.1706 | 213.4207 |  | 2029-09-01 | 13:42 | 49320 | 123.495 | 0.74097 | 157.9651 |  | 2006-09-01 | 13:42 | 49320 | 106.438 | 0.63863 | 110.583 |  | 2028-01-01 | 13:42 | 49320 | 212.719 | 1.2763 | 234.9528 |  | 2007-01-01 | 13:42 | 49320 | 199.362 | 1.1962 | 215.2237 |  | 2028-01-01 | 13:42 | 49320 | 85.2676 | 0.51161 | 86.5568 |  | 2007-01-01 | 13:42 | 49320 | 85.5276 | 0.51317 | 90.0033 |  | 2029-09-01 | 13:42 | 49320 | 208.814 | 1.2529 | 225.2315 |  | 2006-09-01 | 13:42 | 49320 | 195.098 | 1.1706 | 211.4902 |  | 2029-09-01 | 13:42 | 49320 | 82.8921 | 0.49735 | 117.4026 |  | 2006-09-01 | 13:42 | 49320 | 68.4817 | 0.41089 | 72.9302 |  | 2028-01-01 | 13:42 | 49320 | 211.255 | 1.2675 | 223.7704 |  | 2007-01-01 | 13:42 | 49320 | 199.361 | 1.1962 | 214.0936 |  | 2028-01-01 | 13:42 | 49320 | 49.3033 | 0.29582 | 52.0235 |  | 2007-01-01 | 13:42 | 49320 | 51.0599 | 0.30636 | 55.8829 |  | 2029-09-01 | 13:42 | 49320 | 208.809 | 1.2529 | 223.5605 |  | 2006-09-01 | 13:42 | 49320 | 195.098 | 1.1706 | 211.3009 |  | 2029-09-01 | 13:42 | 49320 | 60.8059 | 0.36484 | 94.4141 |  | 2006-09-01 | 13:42 | 49320 | 49.2646 | 0.29559 | 54.2413 |  | 2028-01-01 | 13:42 | 49320 | 211.217 | 1.2673 | 221.2067 |  | 2007-01-01 | 13:42 | 49320 | 199.361 | 1.1962 | 214.0106 |  | 2028-01-01 | 13:42 | 49320 | 34.2125 | 0.20528 | 37.1788 |  | 2007-01-01 | 13:42 | 49320 | 35.8922 | 0.21535 | 40.3728 |  | 2029-09-01 | 13:42 | 49320 | 94.4227 | 0.56654 | 102.9439 |  | 2029-09-01 | 13:42 | 49320 | 64.8036 | 0.38882 | 71.2999 |  | 2029-09-01 | 13:42 | 49320 | 43.5053 | 0.26103 | 49.2782 |  | 2006-09-01 | 13:42 | 49320 | 42.6248 | 0.25575 | 48.5199 |  | 2028-01-01 | 13:42 | 49320 | 85.2676 | 0.51161 | 86.5568 |  | 2007-01-01 | 13:42 | 49320 | 85.5276 | 0.51317 | 90.0033 |  | 2028-01-01 | 13:42 | 49320 | 39.6817 | 0.23809 | 43.935 |  | 2007-01-01 | 13:42 | 49320 | 39.7365 | 0.23842 | 44.9903
| 2029-09-01 | 13:43 | 49380 | 320.776 | 1.9247 | 341.9027 |  | 2029-09-01 | 13:43 | 49380 | 212.664 | 1.276 | 234.8889 |  | 2006-09-01 | 13:43 | 49380 | 198.345 | 1.1901 | 214.6107 |  | 2029-09-01 | 13:43 | 49380 | 124.396 | 0.74638 | 158.7115 |  | 2006-09-01 | 13:43 | 49380 | 106.956 | 0.64174 | 111.2247 |  | 2028-01-01 | 13:43 | 49380 | 216.462 | 1.2988 | 236.2516 |  | 2007-01-01 | 13:43 | 49380 | 202.68 | 1.2161 | 216.4398 |  | 2028-01-01 | 13:43 | 49380 | 85.617 | 0.5137 | 87.0705 |  | 2007-01-01 | 13:43 | 49380 | 85.8753 | 0.51525 | 90.5185 |  | 2029-09-01 | 13:43 | 49380 | 212.408 | 1.2744 | 226.506 |  | 2006-09-01 | 13:43 | 49380 | 198.345 | 1.1901 | 212.6803 |  | 2029-09-01 | 13:43 | 49380 | 83.0788 | 0.49847 | 117.901 |  | 2006-09-01 | 13:43 | 49380 | 68.4621 | 0.41077 | 73.341 |  | 2028-01-01 | 13:43 | 49380 | 215.017 | 1.2901 | 225.0605 |  | 2007-01-01 | 13:43 | 49380 | 202.679 | 1.2161 | 215.3097 |  | 2028-01-01 | 13:43 | 49380 | 49.3601 | 0.29616 | 52.3197 |  | 2007-01-01 | 13:43 | 49380 | 51.1226 | 0.30674 | 56.1897 |  | 2029-09-01 | 13:43 | 49380 | 212.403 | 1.2744 | 224.8349 |  | 2006-09-01 | 13:43 | 49380 | 198.345 | 1.1901 | 212.4909 |  | 2029-09-01 | 13:43 | 49380 | 60.8015 | 0.36481 | 94.7789 |  | 2006-09-01 | 13:43 | 49380 | 49.1524 | 0.29491 | 54.5362 |  | 2028-01-01 | 13:43 | 49380 | 214.979 | 1.2899 | 222.4966 |  | 2007-01-01 | 13:43 | 49380 | 202.679 | 1.2161 | 215.2266 |  | 2028-01-01 | 13:43 | 49380 | 34.2348 | 0.20541 | 37.3842 |  | 2007-01-01 | 13:43 | 49380 | 35.9174 | 0.2155 | 40.5883 |  | 2029-09-01 | 13:43 | 49380 | 94.8283 | 0.56897 | 103.5128 |  | 2029-09-01 | 13:43 | 49380 | 64.8983 | 0.38939 | 71.6893 |  | 2029-09-01 | 13:43 | 49380 | 43.5123 | 0.26107 | 49.5393 |  | 2006-09-01 | 13:43 | 49380 | 42.6472 | 0.25588 | 48.7758 |  | 2028-01-01 | 13:43 | 49380 | 85.617 | 0.5137 | 87.0705 |  | 2007-01-01 | 13:43 | 49380 | 85.8753 | 0.51525 | 90.5185 |  | 2028-01-01 | 13:43 | 49380 | 39.6998 | 0.2382 | 44.1732 |  | 2007-01-01 | 13:43 | 49380 | 39.7531 | 0.23852 | 45.2288
| 2029-09-01 | 13:44 | 49440 | 322.833 | 1.937 | 343.8397 |  | 2029-09-01 | 13:44 | 49440 | 216.198 | 1.2972 | 236.1861 |  | 2006-09-01 | 13:44 | 49440 | 201.545 | 1.2093 | 215.82 |  | 2029-09-01 | 13:44 | 49440 | 125.249 | 0.75149 | 159.463 |  | 2006-09-01 | 13:44 | 49440 | 107.435 | 0.64461 | 111.8693 |  | 2028-01-01 | 13:44 | 49440 | 220.157 | 1.3209 | 237.5725 |  | 2007-01-01 | 13:44 | 49440 | 205.95 | 1.2357 | 217.6755 |  | 2028-01-01 | 13:44 | 49440 | 85.9458 | 0.51567 | 87.5862 |  | 2007-01-01 | 13:44 | 49440 | 86.2027 | 0.51722 | 91.0357 |  | 2029-09-01 | 13:44 | 49440 | 215.946 | 1.2957 | 227.8016 |  | 2006-09-01 | 13:44 | 49440 | 201.545 | 1.2093 | 213.8896 |  | 2029-09-01 | 13:44 | 49440 | 83.2426 | 0.49946 | 118.4005 |  | 2006-09-01 | 13:44 | 49440 | 68.4281 | 0.41057 | 73.7515 |  | 2028-01-01 | 13:44 | 49440 | 218.73 | 1.3124 | 226.3728 |  | 2007-01-01 | 13:44 | 49440 | 205.949 | 1.2357 | 216.5454 |  | 2028-01-01 | 13:44 | 49440 | 49.4134 | 0.29648 | 52.6162 |  | 2007-01-01 | 13:44 | 49440 | 51.1817 | 0.30709 | 56.4968 |  | 2029-09-01 | 13:44 | 49440 | 215.941 | 1.2956 | 226.1306 |  | 2006-09-01 | 13:44 | 49440 | 201.545 | 1.2093 | 213.7002 |  | 2029-09-01 | 13:44 | 49440 | 60.7878 | 0.36473 | 95.1437 |  | 2006-09-01 | 13:44 | 49440 | 49.0364 | 0.29422 | 54.8304 |  | 2028-01-01 | 13:44 | 49440 | 218.693 | 1.3122 | 223.8087 |  | 2007-01-01 | 13:44 | 49440 | 205.949 | 1.2357 | 216.4623 |  | 2028-01-01 | 13:44 | 49440 | 34.2567 | 0.20554 | 37.5897 |  | 2007-01-01 | 13:44 | 49440 | 35.9422 | 0.21565 | 40.8039 |  | 2029-09-01 | 13:44 | 49440 | 95.2064 | 0.57124 | 104.0841 |  | 2029-09-01 | 13:44 | 49440 | 64.9825 | 0.38989 | 72.0792 |  | 2029-09-01 | 13:44 | 49440 | 43.5171 | 0.2611 | 49.8004 |  | 2006-09-01 | 13:44 | 49440 | 42.6677 | 0.25601 | 49.0318 |  | 2028-01-01 | 13:44 | 49440 | 85.9458 | 0.51567 | 87.5862 |  | 2007-01-01 | 13:44 | 49440 | 86.2027 | 0.51722 | 91.0357 |  | 2028-01-01 | 13:44 | 49440 | 39.7166 | 0.2383 | 44.4115 |  | 2007-01-01 | 13:44 | 49440 | 39.7687 | 0.23861 | 45.4674
| 2029-09-01 | 13:45 | 49500 | 324.851 | 1.9491 | 345.7888 |  | 2029-09-01 | 13:45 | 49500 | 219.678 | 1.3181 | 237.5041 |  | 2006-09-01 | 13:45 | 49500 | 204.699 | 1.2282 | 217.0482 |  | 2029-09-01 | 13:45 | 49500 | 126.056 | 0.75634 | 160.2193 |  | 2006-09-01 | 13:45 | 49500 | 107.877 | 0.64726 | 112.5166 |  | 2028-01-01 | 13:45 | 49500 | 223.804 | 1.3428 | 238.9154 |  | 2007-01-01 | 13:45 | 49500 | 209.174 | 1.255 | 218.9305 |  | 2028-01-01 | 13:45 | 49500 | 86.2556 | 0.51753 | 88.1037 |  | 2007-01-01 | 13:45 | 49500 | 86.5113 | 0.51907 | 91.5548 |  | 2029-09-01 | 13:45 | 49500 | 219.429 | 1.3166 | 229.1182 |  | 2006-09-01 | 13:45 | 49500 | 204.699 | 1.2282 | 215.1178 |  | 2029-09-01 | 13:45 | 49500 | 83.385 | 0.50031 | 118.9008 |  | 2006-09-01 | 13:45 | 49500 | 68.3813 | 0.41029 | 74.1618 |  | 2028-01-01 | 13:45 | 49500 | 222.395 | 1.3344 | 227.7072 |  | 2007-01-01 | 13:45 | 49500 | 209.173 | 1.255 | 217.8004 |  | 2028-01-01 | 13:45 | 49500 | 49.4637 | 0.29678 | 52.913 |  | 2007-01-01 | 13:45 | 49500 | 51.2375 | 0.30743 | 56.8042 |  | 2029-09-01 | 13:45 | 49500 | 219.424 | 1.3165 | 227.4471 |  | 2006-09-01 | 13:45 | 49500 | 204.699 | 1.2282 | 214.9284 |  | 2029-09-01 | 13:45 | 49500 | 60.7656 | 0.36459 | 95.5082 |  | 2006-09-01 | 13:45 | 49500 | 48.9171 | 0.2935 | 55.1239 |  | 2028-01-01 | 13:45 | 49500 | 222.358 | 1.3341 | 225.1429 |  | 2007-01-01 | 13:45 | 49500 | 209.173 | 1.255 | 217.7174 |  | 2028-01-01 | 13:45 | 49500 | 34.2781 | 0.20567 | 37.7954 |  | 2007-01-01 | 13:45 | 49500 | 35.9666 | 0.2158 | 41.0197 |  | 2029-09-01 | 13:45 | 49500 | 95.5586 | 0.57335 | 104.6574 |  | 2029-09-01 | 13:45 | 49500 | 65.0572 | 0.39034 | 72.4695 |  | 2029-09-01 | 13:45 | 49500 | 43.5201 | 0.26112 | 50.0615 |  | 2006-09-01 | 13:45 | 49500 | 42.6866 | 0.25612 | 49.2879 |  | 2028-01-01 | 13:45 | 49500 | 86.2556 | 0.51753 | 88.1037 |  | 2007-01-01 | 13:45 | 49500 | 86.5113 | 0.51907 | 91.5548 |  | 2028-01-01 | 13:45 | 49500 | 39.7324 | 0.23839 | 44.6499 |  | 2007-01-01 | 13:45 | 49500 | 39.7834 | 0.2387 | 45.7061
| 2029-09-01 | 13:46 | 49560 | 326.832 | 1.961 | 347.7498 |  | 2029-09-01 | 13:46 | 49560 | 223.103 | 1.3386 | 238.8428 |  | 2006-09-01 | 13:46 | 49560 | 207.808 | 1.2468 | 218.295 |  | 2029-09-01 | 13:46 | 49560 | 126.819 | 0.76091 | 160.9803 |  | 2006-09-01 | 13:46 | 49560 | 108.285 | 0.64971 | 113.1663 |  | 2028-01-01 | 13:46 | 49560 | 227.403 | 1.3644 | 240.2798 |  | 2007-01-01 | 13:46 | 49560 | 212.351 | 1.2741 | 220.2046 |  | 2028-01-01 | 13:46 | 49560 | 86.5475 | 0.51928 | 88.623 |  | 2007-01-01 | 13:46 | 49560 | 86.8025 | 0.52081 | 92.0756 |  | 2029-09-01 | 13:46 | 49560 | 222.857 | 1.3371 | 230.4553 |  | 2006-09-01 | 13:46 | 49560 | 207.808 | 1.2468 | 216.3646 |  | 2029-09-01 | 13:46 | 49560 | 83.5076 | 0.50105 | 119.4018 |  | 2006-09-01 | 13:46 | 49560 | 68.3227 | 0.40994 | 74.5718 |  | 2028-01-01 | 13:46 | 49560 | 226.013 | 1.3561 | 229.0633 |  | 2007-01-01 | 13:46 | 49560 | 212.35 | 1.2741 | 219.0745 |  | 2028-01-01 | 13:46 | 49560 | 49.5113 | 0.29707 | 53.21 |  | 2007-01-01 | 13:46 | 49560 | 51.2907 | 0.30774 | 57.1119 |  | 2029-09-01 | 13:46 | 49560 | 222.853 | 1.3371 | 228.7843 |  | 2006-09-01 | 13:46 | 49560 | 207.808 | 1.2468 | 216.1752 |  | 2029-09-01 | 13:46 | 49560 | 60.7358 | 0.36441 | 95.8727 |  | 2006-09-01 | 13:46 | 49560 | 48.7951 | 0.29277 | 55.4167 |  | 2028-01-01 | 13:46 | 49560 | 225.976 | 1.3559 | 226.4987 |  | 2007-01-01 | 13:46 | 49560 | 212.35 | 1.2741 | 218.9915 |  | 2028-01-01 | 13:46 | 49560 | 34.2992 | 0.2058 | 38.0012 |  | 2007-01-01 | 13:46 | 49560 | 35.9908 | 0.21594 | 41.2357 |  | 2029-09-01 | 13:46 | 49560 | 95.8866 | 0.57532 | 105.2328 |  | 2029-09-01 | 13:46 | 49560 | 65.1234 | 0.39074 | 72.8602 |  | 2029-09-01 | 13:46 | 49560 | 43.5215 | 0.26113 | 50.3226 |  | 2006-09-01 | 13:46 | 49560 | 42.704 | 0.25622 | 49.5442 |  | 2028-01-01 | 13:46 | 49560 | 86.5475 | 0.51928 | 88.623 |  | 2007-01-01 | 13:46 | 49560 | 86.8025 | 0.52081 | 92.0756 |  | 2028-01-01 | 13:46 | 49560 | 39.7472 | 0.23848 | 44.8884 |  | 2007-01-01 | 13:46 | 49560 | 39.7974 | 0.23878 | 45.9449
| 2029-09-01 | 13:47 | 49620 | 328.776 | 1.9727 | 349.7224 |  | 2029-09-01 | 13:47 | 49620 | 226.474 | 1.3588 | 240.2016 |  | 2006-09-01 | 13:47 | 49620 | 210.873 | 1.2652 | 219.5603 |  | 2029-09-01 | 13:47 | 49620 | 127.541 | 0.76525 | 161.7455 |  | 2006-09-01 | 13:47 | 49620 | 108.659 | 0.65195 | 113.8183 |  | 2028-01-01 | 13:47 | 49620 | 230.956 | 1.3857 | 241.6655 |  | 2007-01-01 | 13:47 | 49620 | 215.485 | 1.2929 | 221.4975 |  | 2028-01-01 | 13:47 | 49620 | 86.8228 | 0.52094 | 89.1439 |  | 2007-01-01 | 13:47 | 49620 | 87.0774 | 0.52246 | 92.5981 |  | 2029-09-01 | 13:47 | 49620 | 226.232 | 1.3574 | 231.8127 |  | 2006-09-01 | 13:47 | 49620 | 210.873 | 1.2652 | 217.6299 |  | 2029-09-01 | 13:47 | 49620 | 83.6116 | 0.50167 | 119.9035 |  | 2006-09-01 | 13:47 | 49620 | 68.2536 | 0.40952 | 74.9813 |  | 2028-01-01 | 13:47 | 49620 | 229.583 | 1.3775 | 230.4408 |  | 2007-01-01 | 13:47 | 49620 | 215.484 | 1.2929 | 220.3674 |  | 2028-01-01 | 13:47 | 49620 | 49.5566 | 0.29734 | 53.5074 |  | 2007-01-01 | 13:47 | 49620 | 51.3415 | 0.30805 | 57.42 |  | 2029-09-01 | 13:47 | 49620 | 226.227 | 1.3574 | 230.1416 |  | 2006-09-01 | 13:47 | 49620 | 210.873 | 1.2652 | 217.4405 |  | 2029-09-01 | 13:47 | 49620 | 60.6992 | 0.3642 | 96.2369 |  | 2006-09-01 | 13:47 | 49620 | 48.6708 | 0.29202 | 55.7087 |  | 2028-01-01 | 13:47 | 49620 | 229.547 | 1.3773 | 227.876 |  | 2007-01-01 | 13:47 | 49620 | 215.484 | 1.2929 | 220.2844 |  | 2028-01-01 | 13:47 | 49620 | 34.3201 | 0.20592 | 38.2071 |  | 2007-01-01 | 13:47 | 49620 | 36.0148 | 0.21609 | 41.4518 |  | 2029-09-01 | 13:47 | 49620 | 96.192 | 0.57715 | 105.8099 |  | 2029-09-01 | 13:47 | 49620 | 65.1818 | 0.39109 | 73.2513 |  | 2029-09-01 | 13:47 | 49620 | 43.5216 | 0.26113 | 50.5837 |  | 2006-09-01 | 13:47 | 49620 | 42.7203 | 0.25632 | 49.8005 |  | 2028-01-01 | 13:47 | 49620 | 86.8228 | 0.52094 | 89.1439 |  | 2007-01-01 | 13:47 | 49620 | 87.0774 | 0.52246 | 92.5981 |  | 2028-01-01 | 13:47 | 49620 | 39.7612 | 0.23857 | 45.1269 |  | 2007-01-01 | 13:47 | 49620 | 39.8109 | 0.23887 | 46.1838
| 2029-09-01 | 13:48 | 49680 | 330.684 | 1.9841 | 351.7065 |  | 2029-09-01 | 13:48 | 49680 | 229.792 | 1.3788 | 241.5804 |  | 2006-09-01 | 13:48 | 49680 | 213.894 | 1.2834 | 220.8436 |  | 2029-09-01 | 13:48 | 49680 | 128.222 | 0.76933 | 162.5148 |  | 2006-09-01 | 13:48 | 49680 | 109.001 | 0.65401 | 114.4723 |  | 2028-01-01 | 13:48 | 49680 | 234.463 | 1.4068 | 243.0723 |  | 2007-01-01 | 13:48 | 49680 | 218.562 | 1.3114 | 222.8089 |  | 2028-01-01 | 13:48 | 49680 | 87.0827 | 0.5225 | 89.6664 |  | 2007-01-01 | 13:48 | 49680 | 87.3375 | 0.52403 | 93.1221 |  | 2029-09-01 | 13:48 | 49680 | 229.553 | 1.3773 | 233.1901 |  | 2006-09-01 | 13:48 | 49680 | 213.894 | 1.2834 | 218.9132 |  | 2029-09-01 | 13:48 | 49680 | 83.6986 | 0.50219 | 120.4057 |  | 2006-09-01 | 13:48 | 49680 | 68.1748 | 0.40905 | 75.3903 |  | 2028-01-01 | 13:48 | 49680 | 233.108 | 1.3986 | 231.8394 |  | 2007-01-01 | 13:48 | 49680 | 218.561 | 1.3114 | 221.6788 |  | 2028-01-01 | 13:48 | 49680 | 49.5998 | 0.2976 | 53.805 |  | 2007-01-01 | 13:48 | 49680 | 51.3902 | 0.30834 | 57.7283 |  | 2029-09-01 | 13:48 | 49680 | 229.548 | 1.3773 | 231.5189 |  | 2006-09-01 | 13:48 | 49680 | 213.894 | 1.2834 | 218.7238 |  | 2029-09-01 | 13:48 | 49680 | 60.6564 | 0.36394 | 96.6008 |  | 2006-09-01 | 13:48 | 49680 | 48.5446 | 0.29127 | 56 |  | 2028-01-01 | 13:48 | 49680 | 233.072 | 1.3984 | 229.2745 |  | 2007-01-01 | 13:48 | 49680 | 218.561 | 1.3114 | 221.5957 |  | 2028-01-01 | 13:48 | 49680 | 34.3407 | 0.20604 | 38.4132 |  | 2007-01-01 | 13:48 | 49680 | 36.0387 | 0.21623 | 41.668 |  | 2029-09-01 | 13:48 | 49680 | 96.4761 | 0.57886 | 106.3888 |  | 2029-09-01 | 13:48 | 49680 | 65.2331 | 0.3914 | 73.6427 |  | 2029-09-01 | 13:48 | 49680 | 43.5205 | 0.26112 | 50.8449 |  | 2006-09-01 | 13:48 | 49680 | 42.7355 | 0.25641 | 50.0569 |  | 2028-01-01 | 13:48 | 49680 | 87.0827 | 0.5225 | 89.6664 |  | 2007-01-01 | 13:48 | 49680 | 87.3375 | 0.52403 | 93.1221 |  | 2028-01-01 | 13:48 | 49680 | 39.7745 | 0.23865 | 45.3656 |  | 2007-01-01 | 13:48 | 49680 | 39.824 | 0.23894 | 46.4227
| 2029-09-01 | 13:49 | 49740 | 332.555 | 1.9953 | 353.7018 |  | 2029-09-01 | 13:49 | 49740 | 233.057 | 1.3983 | 242.9787 |  | 2006-09-01 | 13:49 | 49740 | 216.872 | 1.3012 | 222.1449 |  | 2029-09-01 | 13:49 | 49740 | 128.864 | 0.77318 | 163.288 |  | 2006-09-01 | 13:49 | 49740 | 109.314 | 0.65588 | 115.1282 |  | 2028-01-01 | 13:49 | 49740 | 237.924 | 1.4275 | 244.4998 |  | 2007-01-01 | 13:49 | 49740 | 221.583 | 1.3295 | 224.1384 |  | 2028-01-01 | 13:49 | 49740 | 87.3281 | 0.52397 | 90.1904 |  | 2007-01-01 | 13:49 | 49740 | 87.5837 | 0.5255 | 93.6476 |  | 2029-09-01 | 13:49 | 49740 | 232.821 | 1.3969 | 234.587 |  | 2006-09-01 | 13:49 | 49740 | 216.872 | 1.3012 | 220.2145 |  | 2029-09-01 | 13:49 | 49740 | 83.7696 | 0.50262 | 120.9083 |  | 2006-09-01 | 13:49 | 49740 | 68.0874 | 0.40852 | 75.7988 |  | 2028-01-01 | 13:49 | 49740 | 236.586 | 1.4195 | 233.2589 |  | 2007-01-01 | 13:49 | 49740 | 221.582 | 1.3295 | 223.0083 |  | 2028-01-01 | 13:49 | 49740 | 49.6413 | 0.29785 | 54.1028 |  | 2007-01-01 | 13:49 | 49740 | 51.4372 | 0.30862 | 58.037 |  | 2029-09-01 | 13:49 | 49740 | 232.817 | 1.3969 | 232.9158 |  | 2006-09-01 | 13:49 | 49740 | 216.872 | 1.3012 | 220.0251 |  | 2029-09-01 | 13:49 | 49740 | 60.6081 | 0.36365 | 96.9644 |  | 2006-09-01 | 13:49 | 49740 | 48.4169 | 0.2905 | 56.2905 |  | 2028-01-01 | 13:49 | 49740 | 236.551 | 1.4193 | 230.6938 |  | 2007-01-01 | 13:49 | 49740 | 221.582 | 1.3295 | 222.9252 |  | 2028-01-01 | 13:49 | 49740 | 34.3611 | 0.20617 | 38.6193 |  | 2007-01-01 | 13:49 | 49740 | 36.0625 | 0.21638 | 41.8844 |  | 2029-09-01 | 13:49 | 49740 | 96.7401 | 0.58044 | 106.9692 |  | 2029-09-01 | 13:49 | 49740 | 65.278 | 0.39167 | 74.0344 |  | 2029-09-01 | 13:49 | 49740 | 43.5185 | 0.26111 | 51.106 |  | 2006-09-01 | 13:49 | 49740 | 42.7498 | 0.2565 | 50.3134 |  | 2028-01-01 | 13:49 | 49740 | 87.3281 | 0.52397 | 90.1904 |  | 2007-01-01 | 13:49 | 49740 | 87.5837 | 0.5255 | 93.6476 |  | 2028-01-01 | 13:49 | 49740 | 39.7873 | 0.23872 | 45.6043 |  | 2007-01-01 | 13:49 | 49740 | 39.8367 | 0.23902 | 46.6617
| 2029-09-01 | 13:50 | 49800 | 334.391 | 2.0063 | 355.7082 |  | 2029-09-01 | 13:50 | 49800 | 236.27 | 1.4176 | 244.3963 |  | 2006-09-01 | 13:50 | 49800 | 219.809 | 1.3189 | 223.4637 |  | 2029-09-01 | 13:50 | 49800 | 129.47 | 0.77682 | 164.0648 |  | 2006-09-01 | 13:50 | 49800 | 109.599 | 0.65759 | 115.7857 |  | 2028-01-01 | 13:50 | 49800 | 241.34 | 1.448 | 245.9479 |  | 2007-01-01 | 13:50 | 49800 | 224.55 | 1.3473 | 225.4857 |  | 2028-01-01 | 13:50 | 49800 | 87.5602 | 0.52536 | 90.7158 |  | 2007-01-01 | 13:50 | 49800 | 87.8172 | 0.5269 | 94.1745 |  | 2029-09-01 | 13:50 | 49800 | 236.038 | 1.4162 | 236.0032 |  | 2006-09-01 | 13:50 | 49800 | 219.809 | 1.3189 | 221.5333 |  | 2029-09-01 | 13:50 | 49800 | 83.826 | 0.50296 | 121.4113 |  | 2006-09-01 | 13:50 | 49800 | 67.9922 | 0.40795 | 76.2068 |  | 2028-01-01 | 13:50 | 49800 | 240.019 | 1.4401 | 234.6991 |  | 2007-01-01 | 13:50 | 49800 | 224.549 | 1.3473 | 224.3556 |  | 2028-01-01 | 13:50 | 49800 | 49.6811 | 0.29809 | 54.4009 |  | 2007-01-01 | 13:50 | 49800 | 51.4827 | 0.3089 | 58.3459 |  | 2029-09-01 | 13:50 | 49800 | 236.033 | 1.4162 | 234.332 |  | 2006-09-01 | 13:50 | 49800 | 219.809 | 1.3189 | 221.3439 |  | 2029-09-01 | 13:50 | 49800 | 60.5549 | 0.36333 | 97.3278 |  | 2006-09-01 | 13:50 | 49800 | 48.2881 | 0.28973 | 56.5802 |  | 2028-01-01 | 13:50 | 49800 | 239.984 | 1.4399 | 232.1337 |  | 2007-01-01 | 13:50 | 49800 | 224.549 | 1.3473 | 224.2725 |  | 2028-01-01 | 13:50 | 49800 | 34.3814 | 0.20629 | 38.8256 |  | 2007-01-01 | 13:50 | 49800 | 36.0864 | 0.21652 | 42.1009 |  | 2029-09-01 | 13:50 | 49800 | 96.9855 | 0.58191 | 107.5511 |  | 2029-09-01 | 13:50 | 49800 | 65.3171 | 0.3919 | 74.4263 |  | 2029-09-01 | 13:50 | 49800 | 43.5156 | 0.26109 | 51.3671 |  | 2006-09-01 | 13:50 | 49800 | 42.7633 | 0.25658 | 50.57 |  | 2028-01-01 | 13:50 | 49800 | 87.5602 | 0.52536 | 90.7158 |  | 2007-01-01 | 13:50 | 49800 | 87.8172 | 0.5269 | 94.1745 |  | 2028-01-01 | 13:50 | 49800 | 39.7995 | 0.2388 | 45.8431 |  | 2007-01-01 | 13:50 | 49800 | 39.8492 | 0.2391 | 46.9008
| 2029-09-01 | 13:51 | 49860 | 336.196 | 2.0172 | 357.7254 |  | 2029-09-01 | 13:51 | 49860 | 239.435 | 1.4366 | 245.8329 |  | 2006-09-01 | 13:51 | 49860 | 222.704 | 1.3362 | 224.7999 |  | 2029-09-01 | 13:51 | 49860 | 130.044 | 0.78026 | 164.8451 |  | 2006-09-01 | 13:51 | 49860 | 109.856 | 0.65914 | 116.4449 |  | 2028-01-01 | 13:51 | 49860 | 244.711 | 1.4683 | 247.4161 |  | 2007-01-01 | 13:51 | 49860 | 227.465 | 1.3648 | 226.8505 |  | 2028-01-01 | 13:51 | 49860 | 87.7798 | 0.52668 | 91.2424 |  | 2007-01-01 | 13:51 | 49860 | 88.0391 | 0.52823 | 94.7027 |  | 2029-09-01 | 13:51 | 49860 | 239.206 | 1.4352 | 237.4384 |  | 2006-09-01 | 13:51 | 49860 | 222.704 | 1.3362 | 222.8695 |  | 2029-09-01 | 13:51 | 49860 | 83.8706 | 0.50322 | 121.9145 |  | 2006-09-01 | 13:51 | 49860 | 67.89 | 0.40734 | 76.6141 |  | 2028-01-01 | 13:51 | 49860 | 243.408 | 1.4604 | 236.1595 |  | 2007-01-01 | 13:51 | 49860 | 227.464 | 1.3648 | 225.7204 |  | 2028-01-01 | 13:51 | 49860 | 49.7195 | 0.29832 | 54.6992 |  | 2007-01-01 | 13:51 | 49860 | 51.5271 | 0.30916 | 58.655 |  | 2029-09-01 | 13:51 | 49860 | 239.202 | 1.4352 | 235.7672 |  | 2006-09-01 | 13:51 | 49860 | 222.704 | 1.3362 | 222.6802 |  | 2029-09-01 | 13:51 | 49860 | 60.4986 | 0.36299 | 97.6908 |  | 2006-09-01 | 13:51 | 49860 | 48.1583 | 0.28895 | 56.8691 |  | 2028-01-01 | 13:51 | 49860 | 243.373 | 1.4602 | 233.5939 |  | 2007-01-01 | 13:51 | 49860 | 227.464 | 1.3648 | 225.6373 |  | 2028-01-01 | 13:51 | 49860 | 34.4016 | 0.20641 | 39.032 |  | 2007-01-01 | 13:51 | 49860 | 36.1104 | 0.21666 | 42.3176 |  | 2029-09-01 | 13:51 | 49860 | 97.2144 | 0.58329 | 108.1344 |  | 2029-09-01 | 13:51 | 49860 | 65.3518 | 0.39211 | 74.8184 |  | 2029-09-01 | 13:51 | 49860 | 43.5125 | 0.26108 | 51.6281 |  | 2006-09-01 | 13:51 | 49860 | 42.7761 | 0.25666 | 50.8266 |  | 2028-01-01 | 13:51 | 49860 | 87.7798 | 0.52668 | 91.2424 |  | 2007-01-01 | 13:51 | 49860 | 88.0391 | 0.52823 | 94.7027 |  | 2028-01-01 | 13:51 | 49860 | 39.8114 | 0.23887 | 46.082 |  | 2007-01-01 | 13:51 | 49860 | 39.8617 | 0.23917 | 47.14
| 2029-09-01 | 13:52 | 49920 | 337.971 | 2.0278 | 359.7532 |  | 2029-09-01 | 13:52 | 49920 | 242.552 | 1.4553 | 247.2882 |  | 2006-09-01 | 13:52 | 49920 | 225.56 | 1.3534 | 226.1533 |  | 2029-09-01 | 13:52 | 49920 | 130.586 | 0.78352 | 165.6286 |  | 2006-09-01 | 13:52 | 49920 | 110.089 | 0.66053 | 117.1054 |  | 2028-01-01 | 13:52 | 49920 | 248.039 | 1.4882 | 248.9044 |  | 2007-01-01 | 13:52 | 49920 | 230.328 | 1.382 | 228.2325 |  | 2028-01-01 | 13:52 | 49920 | 87.9877 | 0.52793 | 91.7704 |  | 2007-01-01 | 13:52 | 49920 | 88.2502 | 0.5295 | 95.2323 |  | 2029-09-01 | 13:52 | 49920 | 242.326 | 1.454 | 238.8924 |  | 2006-09-01 | 13:52 | 49920 | 225.56 | 1.3534 | 224.2229 |  | 2029-09-01 | 13:52 | 49920 | 83.9042 | 0.50343 | 122.4179 |  | 2006-09-01 | 13:52 | 49920 | 67.7815 | 0.40669 | 77.0208 |  | 2028-01-01 | 13:52 | 49920 | 246.752 | 1.4805 | 237.64 |  | 2007-01-01 | 13:52 | 49920 | 230.327 | 1.382 | 227.1023 |  | 2028-01-01 | 13:52 | 49920 | 49.7567 | 0.29854 | 54.9978 |  | 2007-01-01 | 13:52 | 49920 | 51.5705 | 0.30942 | 58.9644 |  | 2029-09-01 | 13:52 | 49920 | 242.322 | 1.4539 | 237.2211 |  | 2006-09-01 | 13:52 | 49920 | 225.56 | 1.3534 | 224.0335 |  | 2029-09-01 | 13:52 | 49920 | 60.4396 | 0.36264 | 98.0534 |  | 2006-09-01 | 13:52 | 49920 | 48.0279 | 0.28817 | 57.1573 |  | 2028-01-01 | 13:52 | 49920 | 246.718 | 1.4803 | 235.0742 |  | 2007-01-01 | 13:52 | 49920 | 230.327 | 1.382 | 227.0193 |  | 2028-01-01 | 13:52 | 49920 | 34.4216 | 0.20653 | 39.2386 |  | 2007-01-01 | 13:52 | 49920 | 36.1345 | 0.21681 | 42.5344 |  | 2029-09-01 | 13:52 | 49920 | 97.4281 | 0.58457 | 108.719 |  | 2029-09-01 | 13:52 | 49920 | 65.3824 | 0.39229 | 75.2107 |  | 2029-09-01 | 13:52 | 49920 | 43.5092 | 0.26106 | 51.8892 |  | 2006-09-01 | 13:52 | 49920 | 42.7883 | 0.25673 | 51.0834 |  | 2028-01-01 | 13:52 | 49920 | 87.9877 | 0.52793 | 91.7704 |  | 2007-01-01 | 13:52 | 49920 | 88.2502 | 0.5295 | 95.2323 |  | 2028-01-01 | 13:52 | 49920 | 39.8228 | 0.23894 | 46.3209 |  | 2007-01-01 | 13:52 | 49920 | 39.874 | 0.23924 | 47.3792
| 2029-09-01 | 13:53 | 49980 | 339.717 | 2.0383 | 361.7915 |  | 2029-09-01 | 13:53 | 49980 | 245.623 | 1.4737 | 248.762 |  | 2006-09-01 | 13:53 | 49980 | 228.376 | 1.3703 | 227.5236 |  | 2029-09-01 | 13:53 | 49980 | 131.099 | 0.78659 | 166.4152 |  | 2006-09-01 | 13:53 | 49980 | 110.298 | 0.66179 | 117.7672 |  | 2028-01-01 | 13:53 | 49980 | 251.324 | 1.5079 | 250.4123 |  | 2007-01-01 | 13:53 | 49980 | 233.14 | 1.3988 | 229.6313 |  | 2028-01-01 | 13:53 | 49980 | 88.1849 | 0.52911 | 92.2995 |  | 2007-01-01 | 13:53 | 49980 | 88.4513 | 0.53071 | 95.763 |  | 2029-09-01 | 13:53 | 49980 | 245.4 | 1.4724 | 240.3648 |  | 2006-09-01 | 13:53 | 49980 | 228.376 | 1.3703 | 225.5932 |  | 2029-09-01 | 13:53 | 49980 | 83.9279 | 0.50357 | 122.9215 |  | 2006-09-01 | 13:53 | 49980 | 67.6673 | 0.406 | 77.4268 |  | 2028-01-01 | 13:53 | 49980 | 250.053 | 1.5003 | 239.1403 |  | 2007-01-01 | 13:53 | 49980 | 233.139 | 1.3988 | 228.5012 |  | 2028-01-01 | 13:53 | 49980 | 49.7927 | 0.29876 | 55.2965 |  | 2007-01-01 | 13:53 | 49980 | 51.613 | 0.30968 | 59.2741 |  | 2029-09-01 | 13:53 | 49980 | 245.396 | 1.4724 | 238.6935 |  | 2006-09-01 | 13:53 | 49980 | 228.376 | 1.3703 | 225.4038 |  | 2029-09-01 | 13:53 | 49980 | 60.3781 | 0.36227 | 98.4157 |  | 2006-09-01 | 13:53 | 49980 | 47.8971 | 0.28738 | 57.4447 |  | 2028-01-01 | 13:53 | 49980 | 250.019 | 1.5001 | 236.5743 |  | 2007-01-01 | 13:53 | 49980 | 233.139 | 1.3988 | 228.4181 |  | 2028-01-01 | 13:53 | 49980 | 34.4416 | 0.20665 | 39.4452 |  | 2007-01-01 | 13:53 | 49980 | 36.1587 | 0.21695 | 42.7513 |  | 2029-09-01 | 13:53 | 49980 | 97.6274 | 0.58576 | 109.3047 |  | 2029-09-01 | 13:53 | 49980 | 65.4094 | 0.39246 | 75.6032 |  | 2029-09-01 | 13:53 | 49980 | 43.5058 | 0.26103 | 52.1502 |  | 2006-09-01 | 13:53 | 49980 | 42.8 | 0.2568 | 51.3402 |  | 2028-01-01 | 13:53 | 49980 | 88.1849 | 0.52911 | 92.2995 |  | 2007-01-01 | 13:53 | 49980 | 88.4513 | 0.53071 | 95.763 |  | 2028-01-01 | 13:53 | 49980 | 39.834 | 0.239 | 46.5599 |  | 2007-01-01 | 13:53 | 49980 | 39.8864 | 0.23932 | 47.6186
| 2029-09-01 | 13:54 | 50040 | 341.434 | 2.0486 | 363.8401 |  | 2029-09-01 | 13:54 | 50040 | 248.647 | 1.4919 | 250.2539 |  | 2006-09-01 | 13:54 | 50040 | 231.154 | 1.3869 | 228.9105 |  | 2029-09-01 | 13:54 | 50040 | 131.584 | 0.7895 | 167.2047 |  | 2006-09-01 | 13:54 | 50040 | 110.484 | 0.6629 | 118.4301 |  | 2028-01-01 | 13:54 | 50040 | 254.565 | 1.5274 | 251.9397 |  | 2007-01-01 | 13:54 | 50040 | 235.901 | 1.4154 | 231.0467 |  | 2028-01-01 | 13:54 | 50040 | 88.3719 | 0.53023 | 92.8297 |  | 2007-01-01 | 13:54 | 50040 | 88.6432 | 0.53186 | 96.2948 |  | 2029-09-01 | 13:54 | 50040 | 248.428 | 1.4906 | 241.8554 |  | 2006-09-01 | 13:54 | 50040 | 231.154 | 1.3869 | 226.9801 |  | 2029-09-01 | 13:54 | 50040 | 83.9425 | 0.50365 | 123.4252 |  | 2006-09-01 | 13:54 | 50040 | 67.5482 | 0.40529 | 77.8321 |  | 2028-01-01 | 13:54 | 50040 | 253.31 | 1.5199 | 240.6602 |  | 2007-01-01 | 13:54 | 50040 | 235.9 | 1.4154 | 229.9166 |  | 2028-01-01 | 13:54 | 50040 | 49.8279 | 0.29897 | 55.5955 |  | 2007-01-01 | 13:54 | 50040 | 51.6548 | 0.30993 | 59.584 |  | 2029-09-01 | 13:54 | 50040 | 248.424 | 1.4905 | 240.1841 |  | 2006-09-01 | 13:54 | 50040 | 231.154 | 1.3869 | 226.7907 |  | 2029-09-01 | 13:54 | 50040 | 60.3146 | 0.36189 | 98.7776 |  | 2006-09-01 | 13:54 | 50040 | 47.766 | 0.2866 | 57.7313 |  | 2028-01-01 | 13:54 | 50040 | 253.277 | 1.5197 | 238.094 |  | 2007-01-01 | 13:54 | 50040 | 235.9 | 1.4154 | 229.8335 |  | 2028-01-01 | 13:54 | 50040 | 34.4615 | 0.20677 | 39.652 |  | 2007-01-01 | 13:54 | 50040 | 36.183 | 0.2171 | 42.9684 |  | 2029-09-01 | 13:54 | 50040 | 97.8133 | 0.58688 | 109.8916 |  | 2029-09-01 | 13:54 | 50040 | 65.4332 | 0.3926 | 75.9958 |  | 2029-09-01 | 13:54 | 50040 | 43.5024 | 0.26101 | 52.4113 |  | 2006-09-01 | 13:54 | 50040 | 42.8112 | 0.25687 | 51.597 |  | 2028-01-01 | 13:54 | 50040 | 88.3719 | 0.53023 | 92.8297 |  | 2007-01-01 | 13:54 | 50040 | 88.6432 | 0.53186 | 96.2948 |  | 2028-01-01 | 13:54 | 50040 | 39.8448 | 0.23907 | 46.799 |  | 2007-01-01 | 13:54 | 50040 | 39.8988 | 0.23939 | 47.8579
| 2029-09-01 | 13:55 | 50100 | 343.122 | 2.0587 | 365.8988 |  | 2029-09-01 | 13:55 | 50100 | 251.626 | 1.5098 | 251.7636 |  | 2006-09-01 | 13:55 | 50100 | 233.894 | 1.4034 | 230.3138 |  | 2029-09-01 | 13:55 | 50100 | 132.043 | 0.79226 | 167.997 |  | 2006-09-01 | 13:55 | 50100 | 110.648 | 0.66389 | 119.094 |  | 2028-01-01 | 13:55 | 50100 | 257.764 | 1.5466 | 253.4863 |  | 2007-01-01 | 13:55 | 50100 | 238.614 | 1.4317 | 232.4784 |  | 2028-01-01 | 13:55 | 50100 | 88.5496 | 0.5313 | 93.361 |  | 2007-01-01 | 13:55 | 50100 | 88.8266 | 0.53296 | 96.8278 |  | 2029-09-01 | 13:55 | 50100 | 251.41 | 1.5085 | 243.3638 |  | 2006-09-01 | 13:55 | 50100 | 233.894 | 1.4034 | 228.3834 |  | 2029-09-01 | 13:55 | 50100 | 83.9487 | 0.50369 | 123.9288 |  | 2006-09-01 | 13:55 | 50100 | 67.4245 | 0.40455 | 78.2367 |  | 2028-01-01 | 13:55 | 50100 | 256.526 | 1.5392 | 242.1994 |  | 2007-01-01 | 13:55 | 50100 | 238.613 | 1.4317 | 231.3483 |  | 2028-01-01 | 13:55 | 50100 | 49.8622 | 0.29917 | 55.8947 |  | 2007-01-01 | 13:55 | 50100 | 51.696 | 0.31018 | 59.8942 |  | 2029-09-01 | 13:55 | 50100 | 251.406 | 1.5084 | 241.6925 |  | 2006-09-01 | 13:55 | 50100 | 233.894 | 1.4034 | 228.1941 |  | 2029-09-01 | 13:55 | 50100 | 60.2494 | 0.3615 | 99.1391 |  | 2006-09-01 | 13:55 | 50100 | 47.6349 | 0.28581 | 58.0171 |  | 2028-01-01 | 13:55 | 50100 | 256.493 | 1.539 | 239.6329 |  | 2007-01-01 | 13:55 | 50100 | 238.613 | 1.4317 | 231.2652 |  | 2028-01-01 | 13:55 | 50100 | 34.4814 | 0.20689 | 39.8589 |  | 2007-01-01 | 13:55 | 50100 | 36.2075 | 0.21725 | 43.1857 |  | 2029-09-01 | 13:55 | 50100 | 97.9865 | 0.58792 | 110.4795 |  | 2029-09-01 | 13:55 | 50100 | 65.4539 | 0.39272 | 76.3885 |  | 2029-09-01 | 13:55 | 50100 | 43.4988 | 0.26099 | 52.6722 |  | 2006-09-01 | 13:55 | 50100 | 42.822 | 0.25693 | 51.8539 |  | 2028-01-01 | 13:55 | 50100 | 88.5496 | 0.5313 | 93.361 |  | 2007-01-01 | 13:55 | 50100 | 88.8266 | 0.53296 | 96.8278 |  | 2028-01-01 | 13:55 | 50100 | 39.8555 | 0.23913 | 47.0381 |  | 2007-01-01 | 13:55 | 50100 | 39.9112 | 0.23947 | 48.0974
| 2029-09-01 | 13:56 | 50160 | 344.782 | 2.0687 | 367.9675 |  | 2029-09-01 | 13:56 | 50160 | 254.56 | 1.5274 | 253.291 |  | 2006-09-01 | 13:56 | 50160 | 236.597 | 1.4196 | 231.7334 |  | 2029-09-01 | 13:56 | 50160 | 132.477 | 0.79486 | 168.7918 |  | 2006-09-01 | 13:56 | 50160 | 110.793 | 0.66476 | 119.7588 |  | 2028-01-01 | 13:56 | 50160 | 260.922 | 1.5655 | 255.0518 |  | 2007-01-01 | 13:56 | 50160 | 241.277 | 1.4477 | 233.9261 |  | 2028-01-01 | 13:56 | 50160 | 88.7185 | 0.53231 | 93.8933 |  | 2007-01-01 | 13:56 | 50160 | 89.0023 | 0.53401 | 97.3618 |  | 2029-09-01 | 13:56 | 50160 | 254.347 | 1.5261 | 244.8899 |  | 2006-09-01 | 13:56 | 50160 | 236.597 | 1.4196 | 229.803 |  | 2029-09-01 | 13:56 | 50160 | 83.9473 | 0.50368 | 124.4325 |  | 2006-09-01 | 13:56 | 50160 | 67.2969 | 0.40378 | 78.6404 |  | 2028-01-01 | 13:56 | 50160 | 259.699 | 1.5582 | 243.7576 |  | 2007-01-01 | 13:56 | 50160 | 241.276 | 1.4477 | 232.7959 |  | 2028-01-01 | 13:56 | 50160 | 49.8957 | 0.29937 | 56.194 |  | 2007-01-01 | 13:56 | 50160 | 51.7369 | 0.31042 | 60.2046 |  | 2029-09-01 | 13:56 | 50160 | 254.343 | 1.5261 | 243.2186 |  | 2006-09-01 | 13:56 | 50160 | 236.597 | 1.4196 | 229.6136 |  | 2029-09-01 | 13:56 | 50160 | 60.1827 | 0.3611 | 99.5001 |  | 2006-09-01 | 13:56 | 50160 | 47.5039 | 0.28502 | 58.3021 |  | 2028-01-01 | 13:56 | 50160 | 259.667 | 1.558 | 241.1909 |  | 2007-01-01 | 13:56 | 50160 | 241.276 | 1.4477 | 232.7128 |  | 2028-01-01 | 13:56 | 50160 | 34.5012 | 0.20701 | 40.0659 |  | 2007-01-01 | 13:56 | 50160 | 36.2322 | 0.21739 | 43.4031 |  | 2029-09-01 | 13:56 | 50160 | 98.1479 | 0.58889 | 111.0684 |  | 2029-09-01 | 13:56 | 50160 | 65.472 | 0.39283 | 76.7813 |  | 2029-09-01 | 13:56 | 50160 | 43.4952 | 0.26097 | 52.9332 |  | 2006-09-01 | 13:56 | 50160 | 42.8325 | 0.257 | 52.1109 |  | 2028-01-01 | 13:56 | 50160 | 88.7185 | 0.53231 | 93.8933 |  | 2007-01-01 | 13:56 | 50160 | 89.0023 | 0.53401 | 97.3618 |  | 2028-01-01 | 13:56 | 50160 | 39.8659 | 0.2392 | 47.2773 |  | 2007-01-01 | 13:56 | 50160 | 39.9237 | 0.23954 | 48.337
| 2029-09-01 | 13:57 | 50220 | 346.414 | 2.0785 | 370.046 |  | 2029-09-01 | 13:57 | 50220 | 257.45 | 1.5447 | 254.8357 |  | 2006-09-01 | 13:57 | 50220 | 239.263 | 1.4356 | 233.169 |  | 2029-09-01 | 13:57 | 50220 | 132.886 | 0.79732 | 169.5892 |  | 2006-09-01 | 13:57 | 50220 | 110.918 | 0.66551 | 120.4243 |  | 2028-01-01 | 13:57 | 50220 | 264.038 | 1.5842 | 256.6361 |  | 2007-01-01 | 13:57 | 50220 | 243.893 | 1.4634 | 235.3894 |  | 2028-01-01 | 13:57 | 50220 | 88.8793 | 0.53328 | 94.4266 |  | 2007-01-01 | 13:57 | 50220 | 89.1708 | 0.53502 | 97.8968 |  | 2029-09-01 | 13:57 | 50220 | 257.24 | 1.5434 | 246.4334 |  | 2006-09-01 | 13:57 | 50220 | 239.263 | 1.4356 | 231.2386 |  | 2029-09-01 | 13:57 | 50220 | 83.9389 | 0.50363 | 124.9362 |  | 2006-09-01 | 13:57 | 50220 | 67.1658 | 0.40299 | 79.0434 |  | 2028-01-01 | 13:57 | 50220 | 262.831 | 1.577 | 245.3345 |  | 2007-01-01 | 13:57 | 50220 | 243.892 | 1.4634 | 234.2593 |  | 2028-01-01 | 13:57 | 50220 | 49.9287 | 0.29957 | 56.4936 |  | 2007-01-01 | 13:57 | 50220 | 51.7774 | 0.31066 | 60.5153 |  | 2029-09-01 | 13:57 | 50220 | 257.236 | 1.5434 | 244.762 |  | 2006-09-01 | 13:57 | 50220 | 239.263 | 1.4356 | 231.0492 |  | 2029-09-01 | 13:57 | 50220 | 60.1149 | 0.36069 | 99.8608 |  | 2006-09-01 | 13:57 | 50220 | 47.373 | 0.28424 | 58.5864 |  | 2028-01-01 | 13:57 | 50220 | 262.799 | 1.5768 | 242.7677 |  | 2007-01-01 | 13:57 | 50220 | 243.892 | 1.4634 | 234.1762 |  | 2028-01-01 | 13:57 | 50220 | 34.5211 | 0.20713 | 40.273 |  | 2007-01-01 | 13:57 | 50220 | 36.2571 | 0.21754 | 43.6206 |  | 2029-09-01 | 13:57 | 50220 | 98.2983 | 0.58979 | 111.6582 |  | 2029-09-01 | 13:57 | 50220 | 65.4877 | 0.39293 | 77.1743 |  | 2029-09-01 | 13:57 | 50220 | 43.4916 | 0.26095 | 53.1942 |  | 2006-09-01 | 13:57 | 50220 | 42.8426 | 0.25706 | 52.368 |  | 2028-01-01 | 13:57 | 50220 | 88.8793 | 0.53328 | 94.4266 |  | 2007-01-01 | 13:57 | 50220 | 89.1708 | 0.53502 | 97.8968 |  | 2028-01-01 | 13:57 | 50220 | 39.8762 | 0.23926 | 47.5166 |  | 2007-01-01 | 13:57 | 50220 | 39.9364 | 0.23962 | 48.5766
| 2029-09-01 | 13:58 | 50280 | 348.019 | 2.0881 | 372.1341 |  | 2029-09-01 | 13:58 | 50280 | 260.296 | 1.5618 | 256.3975 |  | 2006-09-01 | 13:58 | 50280 | 241.895 | 1.4514 | 234.6204 |  | 2029-09-01 | 13:58 | 50280 | 133.274 | 0.79964 | 170.3888 |  | 2006-09-01 | 13:58 | 50280 | 111.025 | 0.66615 | 121.0904 |  | 2028-01-01 | 13:58 | 50280 | 267.114 | 1.6027 | 258.2387 |  | 2007-01-01 | 13:58 | 50280 | 246.461 | 1.4788 | 236.8682 |  | 2028-01-01 | 13:58 | 50280 | 89.0325 | 0.53419 | 94.9608 |  | 2007-01-01 | 13:58 | 50280 | 89.3329 | 0.536 | 98.4328 |  | 2029-09-01 | 13:58 | 50280 | 260.089 | 1.5605 | 247.9939 |  | 2006-09-01 | 13:58 | 50280 | 241.895 | 1.4514 | 232.69 |  | 2029-09-01 | 13:58 | 50280 | 83.9245 | 0.50355 | 125.4397 |  | 2006-09-01 | 13:58 | 50280 | 67.0316 | 0.40219 | 79.4456 |  | 2028-01-01 | 13:58 | 50280 | 265.922 | 1.5955 | 246.9301 |  | 2007-01-01 | 13:58 | 50280 | 246.46 | 1.4788 | 235.738 |  | 2028-01-01 | 13:58 | 50280 | 49.961 | 0.29977 | 56.7934 |  | 2007-01-01 | 13:58 | 50280 | 51.8177 | 0.31091 | 60.8262 |  | 2029-09-01 | 13:58 | 50280 | 260.085 | 1.5605 | 246.3225 |  | 2006-09-01 | 13:58 | 50280 | 241.895 | 1.4514 | 232.5006 |  | 2029-09-01 | 13:58 | 50280 | 60.0462 | 0.36028 | 100.2211 |  | 2006-09-01 | 13:58 | 50280 | 47.2425 | 0.28345 | 58.8698 |  | 2028-01-01 | 13:58 | 50280 | 265.891 | 1.5953 | 244.3631 |  | 2007-01-01 | 13:58 | 50280 | 246.46 | 1.4788 | 235.655 |  | 2028-01-01 | 13:58 | 50280 | 34.5409 | 0.20725 | 40.4803 |  | 2007-01-01 | 13:58 | 50280 | 36.2823 | 0.21769 | 43.8383 |  | 2029-09-01 | 13:58 | 50280 | 98.4383 | 0.59063 | 112.2488 |  | 2029-09-01 | 13:58 | 50280 | 65.5011 | 0.39301 | 77.5673 |  | 2029-09-01 | 13:58 | 50280 | 43.488 | 0.26093 | 53.4551 |  | 2006-09-01 | 13:58 | 50280 | 42.8526 | 0.25712 | 52.6251 |  | 2028-01-01 | 13:58 | 50280 | 89.0325 | 0.53419 | 94.9608 |  | 2007-01-01 | 13:58 | 50280 | 89.3329 | 0.536 | 98.4328 |  | 2028-01-01 | 13:58 | 50280 | 39.8864 | 0.23932 | 47.7559 |  | 2007-01-01 | 13:58 | 50280 | 39.9492 | 0.2397 | 48.8163
| 2029-09-01 | 13:59 | 50340 | 349.598 | 2.0976 | 374.2317 |  | 2029-09-01 | 13:59 | 50340 | 263.099 | 1.5786 | 257.976 |  | 2006-09-01 | 13:59 | 50340 | 244.491 | 1.4669 | 236.0873 |  | 2029-09-01 | 13:59 | 50340 | 133.64 | 0.80184 | 171.1906 |  | 2006-09-01 | 13:59 | 50340 | 111.116 | 0.6667 | 121.7571 |  | 2028-01-01 | 13:59 | 50340 | 270.149 | 1.6209 | 259.8596 |  | 2007-01-01 | 13:59 | 50340 | 248.983 | 1.4939 | 238.3621 |  | 2028-01-01 | 13:59 | 50340 | 89.1786 | 0.53507 | 95.4959 |  | 2007-01-01 | 13:59 | 50340 | 89.489 | 0.53693 | 98.9697 |  | 2029-09-01 | 13:59 | 50340 | 262.895 | 1.5774 | 249.5713 |  | 2006-09-01 | 13:59 | 50340 | 244.491 | 1.4669 | 234.1569 |  | 2029-09-01 | 13:59 | 50340 | 83.9046 | 0.50343 | 125.9431 |  | 2006-09-01 | 13:59 | 50340 | 66.8947 | 0.40137 | 79.847 |  | 2028-01-01 | 13:59 | 50340 | 268.973 | 1.6138 | 248.5439 |  | 2007-01-01 | 13:59 | 50340 | 248.982 | 1.4939 | 237.2319 |  | 2028-01-01 | 13:59 | 50340 | 49.9929 | 0.29996 | 57.0933 |  | 2007-01-01 | 13:59 | 50340 | 51.8579 | 0.31115 | 61.1374 |  | 2029-09-01 | 13:59 | 50340 | 262.891 | 1.5773 | 247.8998 |  | 2006-09-01 | 13:59 | 50340 | 244.491 | 1.4669 | 233.9675 |  | 2029-09-01 | 13:59 | 50340 | 59.977 | 0.35986 | 100.581 |  | 2006-09-01 | 13:59 | 50340 | 47.1123 | 0.28267 | 59.1525 |  | 2028-01-01 | 13:59 | 50340 | 268.942 | 1.6137 | 245.9767 |  | 2007-01-01 | 13:59 | 50340 | 248.982 | 1.4939 | 237.1488 |  | 2028-01-01 | 13:59 | 50340 | 34.5607 | 0.20736 | 40.6876 |  | 2007-01-01 | 13:59 | 50340 | 36.3076 | 0.21785 | 44.0561 |  | 2029-09-01 | 13:59 | 50340 | 98.5687 | 0.59141 | 112.8403 |  | 2029-09-01 | 13:59 | 50340 | 65.5127 | 0.39308 | 77.9603 |  | 2029-09-01 | 13:59 | 50340 | 43.4843 | 0.26091 | 53.716 |  | 2006-09-01 | 13:59 | 50340 | 42.8622 | 0.25717 | 52.8823 |  | 2028-01-01 | 13:59 | 50340 | 89.1786 | 0.53507 | 95.4959 |  | 2007-01-01 | 13:59 | 50340 | 89.489 | 0.53693 | 98.9697 |  | 2028-01-01 | 13:59 | 50340 | 39.8964 | 0.23938 | 47.9953 |  | 2007-01-01 | 13:59 | 50340 | 39.9622 | 0.23977 | 49.056
5 | 2029-09-01 | 14:00 | 50400 | 351.15 | 2.1069 | 376.3386 |  | 2029-09-01 | 14:00 | 50400 | 265.86 | 1.5952 | 259.5712 |  | 2006-09-01 | 14:00 | 50400 | 247.053 | 1.4823 | 237.5696 |  | 2029-09-01 | 14:00 | 50400 | 133.987 | 0.80392 | 171.9946 |  | 2006-09-01 | 14:00 | 50400 | 111.19 | 0.66714 | 122.4242 |  | 2028-01-01 | 14:00 | 50400 | 273.145 | 1.6389 | 261.4985 |  | 2007-01-01 | 14:00 | 50400 | 251.459 | 1.5088 | 239.8708 |  | 2028-01-01 | 14:00 | 50400 | 89.3182 | 0.53591 | 96.0318 |  | 2007-01-01 | 14:00 | 50400 | 89.6398 | 0.53784 | 99.5076 |  | 2029-09-01 | 14:00 | 50400 | 265.658 | 1.5939 | 251.1652 |  | 2006-09-01 | 14:00 | 50400 | 247.053 | 1.4823 | 235.6392 |  | 2029-09-01 | 14:00 | 50400 | 83.8801 | 0.50328 | 126.4464 |  | 2006-09-01 | 14:00 | 50400 | 66.7555 | 0.40053 | 80.2475 |  | 2028-01-01 | 14:00 | 50400 | 271.983 | 1.6319 | 250.1758 |  | 2007-01-01 | 14:00 | 50400 | 251.458 | 1.5087 | 238.7407 |  | 2028-01-01 | 14:00 | 50400 | 50.0243 | 0.30015 | 57.3935 |  | 2007-01-01 | 14:00 | 50400 | 51.8981 | 0.31139 | 61.4487 |  | 2029-09-01 | 14:00 | 50400 | 265.655 | 1.5939 | 249.4938 |  | 2006-09-01 | 14:00 | 50400 | 247.053 | 1.4823 | 235.4499 |  | 2029-09-01 | 14:00 | 50400 | 59.9075 | 0.35945 | 100.9404 |  | 2006-09-01 | 14:00 | 50400 | 46.9827 | 0.2819 | 59.4344 |  | 2028-01-01 | 14:00 | 50400 | 271.953 | 1.6317 | 247.6085 |  | 2007-01-01 | 14:00 | 50400 | 251.458 | 1.5087 | 238.6576 |  | 2028-01-01 | 14:00 | 50400 | 34.5805 | 0.20748 | 40.8951 |  | 2007-01-01 | 14:00 | 50400 | 36.3332 | 0.218 | 44.2741 |  | 2029-09-01 | 14:00 | 50400 | 98.6899 | 0.59214 | 113.4324 |  | 2029-09-01 | 14:00 | 50400 | 65.5224 | 0.39313 | 78.3535 |  | 2029-09-01 | 14:00 | 50400 | 43.4807 | 0.26088 | 53.9769 |  | 2006-09-01 | 14:00 | 50400 | 42.8717 | 0.25723 | 53.1395 |  | 2028-01-01 | 14:00 | 50400 | 89.3182 | 0.53591 | 96.0318 |  | 2007-01-01 | 14:00 | 50400 | 89.6398 | 0.53784 | 99.5076 |  | 2028-01-01 | 14:00 | 50400 | 39.9064 | 0.23944 | 48.2347 |  | 2007-01-01 | 14:00 | 50400 | 39.9755 | 0.23985 | 49.2959
| 2029-09-01 | 14:01 | 50460 | 346.165 | 0 | 376.3386 |  | 2029-09-01 | 14:01 | 50460 | 223.665 | 0 | 259.5712 |  | 2006-09-01 | 14:01 | 50460 | 189.026 | 0 | 237.5696 |  | 2029-09-01 | 14:01 | 50460 | 112.722 | 0 | 171.9946 |  | 2006-09-01 | 14:01 | 50460 | 85.074 | 0 | 122.4242 |  | 2028-01-01 | 14:01 | 50460 | 251.462 | 0 | 261.4985 |  | 2007-01-01 | 14:01 | 50460 | 186.436 | 0 | 239.8708 |  | 2028-01-01 | 14:01 | 50460 | 82.2269 | 0 | 96.0318 |  | 2007-01-01 | 14:01 | 50460 | 66.4603 | 0 | 99.5076 |  | 2029-09-01 | 14:01 | 50460 | 201.82 | 0 | 251.1652 |  | 2006-09-01 | 14:01 | 50460 | 162.613 | 0 | 235.6392 |  | 2029-09-01 | 14:01 | 50460 | 63.7236 | 0 | 126.4464 |  | 2006-09-01 | 14:01 | 50460 | 43.9393 | 0 | 80.2475 |  | 2028-01-01 | 14:01 | 50460 | 234.91 | 0 | 250.1758 |  | 2007-01-01 | 14:01 | 50460 | 157.668 | 0 | 238.7407 |  | 2028-01-01 | 14:01 | 50460 | 43.2057 | 0 | 57.3935 |  | 2007-01-01 | 14:01 | 50460 | 32.5409 | 0 | 61.4487 |  | 2029-09-01 | 14:01 | 50460 | 190.458 | 0 | 249.4938 |  | 2006-09-01 | 14:01 | 50460 | 149.72 | 0 | 235.4499 |  | 2029-09-01 | 14:01 | 50460 | 42.95 | 0 | 100.9404 |  | 2006-09-01 | 14:01 | 50460 | 28.4726 | 0 | 59.4344 |  | 2028-01-01 | 14:01 | 50460 | 221.63 | 0 | 247.6085 |  | 2007-01-01 | 14:01 | 50460 | 144.033 | 0 | 238.6576 |  | 2028-01-01 | 14:01 | 50460 | 28.1816 | 0 | 40.8951 |  | 2007-01-01 | 14:01 | 50460 | 20.8113 | 0 | 44.2741 |  | 2029-09-01 | 14:01 | 50460 | 92.6494 | 0 | 113.4324 |  | 2029-09-01 | 14:01 | 50460 | 59.5767 | 0 | 78.3535 |  | 2029-09-01 | 14:01 | 50460 | 37.7897 | 0 | 53.9769 |  | 2006-09-01 | 14:01 | 50460 | 37.1928 | 0 | 53.1395 |  | 2028-01-01 | 14:01 | 50460 | 82.2269 | 0 | 96.0318 |  | 2007-01-01 | 14:01 | 50460 | 66.4603 | 0 | 99.5076 |  | 2028-01-01 | 14:01 | 50460 | 33.8683 | 0 | 48.2347 |  | 2007-01-01 | 14:01 | 50460 | 27.7456 | 0 | 49.2959
| 2029-09-01 | 14:02 | 50520 | 341.25 | 0 | 376.3386 |  | 2029-09-01 | 14:02 | 50520 | 188.161 | 0 | 259.5712 |  | 2006-09-01 | 14:02 | 50520 | 144.523 | 0 | 237.5696 |  | 2029-09-01 | 14:02 | 50520 | 94.8284 | 0 | 171.9946 |  | 2006-09-01 | 14:02 | 50520 | 65.0447 | 0 | 122.4242 |  | 2028-01-01 | 14:02 | 50520 | 231.491 | 0 | 261.4985 |  | 2007-01-01 | 14:02 | 50520 | 138.522 | 0 | 239.8708 |  | 2028-01-01 | 14:02 | 50520 | 75.6954 | 0 | 96.0318 |  | 2007-01-01 | 14:02 | 50520 | 49.3803 | 0 | 99.5076 |  | 2029-09-01 | 14:02 | 50520 | 153.314 | 0 | 251.1652 |  | 2006-09-01 | 14:02 | 50520 | 106.919 | 0 | 235.6392 |  | 2029-09-01 | 14:02 | 50520 | 48.4081 | 0 | 126.4464 |  | 2006-09-01 | 14:02 | 50520 | 28.8902 | 0 | 80.2475 |  | 2028-01-01 | 14:02 | 50520 | 202.875 | 0 | 250.1758 |  | 2007-01-01 | 14:02 | 50520 | 99.1741 | 0 | 238.7407 |  | 2028-01-01 | 14:02 | 50520 | 37.3136 | 0 | 57.3935 |  | 2007-01-01 | 14:02 | 50520 | 20.4684 | 0 | 61.4487 |  | 2029-09-01 | 14:02 | 50520 | 136.538 | 0 | 249.4938 |  | 2006-09-01 | 14:02 | 50520 | 90.6198 | 0 | 235.4499 |  | 2029-09-01 | 14:02 | 50520 | 30.7905 | 0 | 100.9404 |  | 2006-09-01 | 14:02 | 50520 | 17.2334 | 0 | 59.4344 |  | 2028-01-01 | 14:02 | 50520 | 180.6 | 0 | 247.6085 |  | 2007-01-01 | 14:02 | 50520 | 82.8029 | 0 | 238.6576 |  | 2028-01-01 | 14:02 | 50520 | 22.9644 | 0 | 40.8951 |  | 2007-01-01 | 14:02 | 50520 | 11.9642 | 0 | 44.2741 |  | 2029-09-01 | 14:02 | 50520 | 86.9786 | 0 | 113.4324 |  | 2029-09-01 | 14:02 | 50520 | 54.1705 | 0 | 78.3535 |  | 2029-09-01 | 14:02 | 50520 | 32.8436 | 0 | 53.9769 |  | 2006-09-01 | 14:02 | 50520 | 32.2656 | 0 | 53.1395 |  | 2028-01-01 | 14:02 | 50520 | 75.6954 | 0 | 96.0318 |  | 2007-01-01 | 14:02 | 50520 | 49.3803 | 0 | 99.5076 |  | 2028-01-01 | 14:02 | 50520 | 28.7428 | 0 | 48.2347 |  | 2007-01-01 | 14:02 | 50520 | 19.2958 | 0 | 49.2959
| 2029-09-01 | 14:03 | 50580 | 336.406 | 0 | 376.3386 |  | 2029-09-01 | 14:03 | 50580 | 158.286 | 0 | 259.5712 |  | 2006-09-01 | 14:03 | 50580 | 110.417 | 0 | 237.5696 |  | 2029-09-01 | 14:03 | 50580 | 79.7725 | 0 | 171.9946 |  | 2006-09-01 | 14:03 | 50580 | 49.6949 | 0 | 122.4242 |  | 2028-01-01 | 14:03 | 50580 | 213.096 | 0 | 261.4985 |  | 2007-01-01 | 14:03 | 50580 | 103.146 | 0 | 239.8708 |  | 2028-01-01 | 14:03 | 50580 | 69.6798 | 0 | 96.0318 |  | 2007-01-01 | 14:03 | 50580 | 36.7694 | 0 | 99.5076 |  | 2029-09-01 | 14:03 | 50580 | 116.46 | 0 | 251.1652 |  | 2006-09-01 | 14:03 | 50580 | 70.2234 | 0 | 235.6392 |  | 2029-09-01 | 14:03 | 50580 | 36.7716 | 0 | 126.4464 |  | 2006-09-01 | 14:03 | 50580 | 18.9749 | 0 | 80.2475 |  | 2028-01-01 | 14:03 | 50580 | 175.195 | 0 | 250.1758 |  | 2007-01-01 | 14:03 | 50580 | 62.5818 | 0 | 238.7407 |  | 2028-01-01 | 14:03 | 50580 | 32.2226 | 0 | 57.3935 |  | 2007-01-01 | 14:03 | 50580 | 12.9162 | 0 | 61.4487 |  | 2029-09-01 | 14:03 | 50580 | 97.8765 | 0 | 249.4938 |  | 2006-09-01 | 14:03 | 50580 | 54.78 | 0 | 235.4499 |  | 2029-09-01 | 14:03 | 50580 | 22.072 | 0 | 100.9404 |  | 2006-09-01 | 14:03 | 50580 | 10.4176 | 0 | 59.4344 |  | 2028-01-01 | 14:03 | 50580 | 147.15 | 0 | 247.6085 |  | 2007-01-01 | 14:03 | 50580 | 47.7792 | 0 | 238.6576 |  | 2028-01-01 | 14:03 | 50580 | 18.7111 | 0 | 40.8951 |  | 2007-01-01 | 14:03 | 50580 | 6.9036 | 0 | 44.2741 |  | 2029-09-01 | 14:03 | 50580 | 81.6549 | 0 | 113.4324 |  | 2029-09-01 | 14:03 | 50580 | 49.2549 | 0 | 78.3535 |  | 2029-09-01 | 14:03 | 50580 | 28.5449 | 0 | 53.9769 |  | 2006-09-01 | 14:03 | 50580 | 27.9907 | 0 | 53.1395 |  | 2028-01-01 | 14:03 | 50580 | 69.6798 | 0 | 96.0318 |  | 2007-01-01 | 14:03 | 50580 | 36.7694 | 0 | 99.5076 |  | 2028-01-01 | 14:03 | 50580 | 24.3919 | 0 | 48.2347 |  | 2007-01-01 | 14:03 | 50580 | 13.4467 | 0 | 49.2959
| 2029-09-01 | 14:04 | 50640 | 331.63 | 0 | 376.3386 |  | 2029-09-01 | 14:04 | 50640 | 133.15 | 0 | 259.5712 |  | 2006-09-01 | 14:04 | 50640 | 84.2985 | 0 | 237.5696 |  | 2029-09-01 | 14:04 | 50640 | 67.1046 | 0 | 171.9946 |  | 2006-09-01 | 14:04 | 50640 | 37.9399 | 0 | 122.4242 |  | 2028-01-01 | 14:04 | 50640 | 196.155 | 0 | 261.4985 |  | 2007-01-01 | 14:04 | 50640 | 76.9727 | 0 | 239.8708 |  | 2028-01-01 | 14:04 | 50640 | 64.1394 | 0 | 96.0318 |  | 2007-01-01 | 14:04 | 50640 | 27.4391 | 0 | 99.5076 |  | 2029-09-01 | 14:04 | 50640 | 88.4601 | 0 | 251.1652 |  | 2006-09-01 | 14:04 | 50640 | 46.0726 | 0 | 235.6392 |  | 2029-09-01 | 14:04 | 50640 | 27.9307 | 0 | 126.4464 |  | 2006-09-01 | 14:04 | 50640 | 12.4492 | 0 | 80.2475 |  | 2028-01-01 | 14:04 | 50640 | 151.281 | 0 | 250.1758 |  | 2007-01-01 | 14:04 | 50640 | 39.6195 | 0 | 238.7407 |  | 2028-01-01 | 14:04 | 50640 | 27.8241 | 0 | 57.3935 |  | 2007-01-01 | 14:04 | 50640 | 8.177 | 0 | 61.4487 |  | 2029-09-01 | 14:04 | 50640 | 70.1576 | 0 | 249.4938 |  | 2006-09-01 | 14:04 | 50640 | 33.0732 | 0 | 235.4499 |  | 2029-09-01 | 14:04 | 50640 | 15.8212 | 0 | 100.9404 |  | 2006-09-01 | 14:04 | 50640 | 6.2896 | 0 | 59.4344 |  | 2028-01-01 | 14:04 | 50640 | 119.884 | 0 | 247.6085 |  | 2007-01-01 | 14:04 | 50640 | 27.6734 | 0 | 238.6576 |  | 2028-01-01 | 14:04 | 50640 | 15.244 | 0 | 40.8951 |  | 2007-01-01 | 14:04 | 50640 | 3.9985 | 0 | 44.2741 |  | 2029-09-01 | 14:04 | 50640 | 76.6571 | 0 | 113.4324 |  | 2029-09-01 | 14:04 | 50640 | 44.7853 | 0 | 78.3535 |  | 2029-09-01 | 14:04 | 50640 | 24.8088 | 0 | 53.9769 |  | 2006-09-01 | 14:04 | 50640 | 24.2819 | 0 | 53.1395 |  | 2028-01-01 | 14:04 | 50640 | 64.1394 | 0 | 96.0318 |  | 2007-01-01 | 14:04 | 50640 | 27.4391 | 0 | 99.5076 |  | 2028-01-01 | 14:04 | 50640 | 20.6989 | 0 | 48.2347 |  | 2007-01-01 | 14:04 | 50640 | 9.3898 | 0 | 49.2959
| 2029-09-01 | 14:05 | 50700 | 326.922 | 0 | 376.3386 |  | 2029-09-01 | 14:05 | 50700 | 112.002 | 0 | 259.5712 |  | 2006-09-01 | 14:05 | 50700 | 64.3115 | 0 | 237.5696 |  | 2029-09-01 | 14:05 | 50700 | 56.4464 | 0 | 171.9946 |  | 2006-09-01 | 14:05 | 50700 | 28.9445 | 0 | 122.4242 |  | 2028-01-01 | 14:05 | 50700 | 180.553 | 0 | 261.4985 |  | 2007-01-01 | 14:05 | 50700 | 57.5685 | 0 | 239.8708 |  | 2028-01-01 | 14:05 | 50700 | 59.037 | 0 | 96.0318 |  | 2007-01-01 | 14:05 | 50700 | 20.5219 | 0 | 99.5076 |  | 2029-09-01 | 14:05 | 50700 | 67.1883 | 0 | 251.1652 |  | 2006-09-01 | 14:05 | 50700 | 30.1951 | 0 | 235.6392 |  | 2029-09-01 | 14:05 | 50700 | 21.2143 | 0 | 126.4464 |  | 2006-09-01 | 14:05 | 50700 | 8.1589 | 0 | 80.2475 |  | 2028-01-01 | 14:05 | 50700 | 130.621 | 0 | 250.1758 |  | 2007-01-01 | 14:05 | 50700 | 25.1653 | 0 | 238.7407 |  | 2028-01-01 | 14:05 | 50700 | 24.0243 | 0 | 57.3935 |  | 2007-01-01 | 14:05 | 50700 | 5.1938 | 0 | 61.4487 |  | 2029-09-01 | 14:05 | 50700 | 50.2855 | 0 | 249.4938 |  | 2006-09-01 | 14:05 | 50700 | 19.9428 | 0 | 235.4499 |  | 2029-09-01 | 14:05 | 50700 | 11.3398 | 0 | 100.9404 |  | 2006-09-01 | 14:05 | 50700 | 3.7926 | 0 | 59.4344 |  | 2028-01-01 | 14:05 | 50700 | 97.6594 | 0 | 247.6085 |  | 2007-01-01 | 14:05 | 50700 | 16.0894 | 0 | 238.6576 |  | 2028-01-01 | 14:05 | 50700 | 12.418 | 0 | 40.8951 |  | 2007-01-01 | 14:05 | 50700 | 2.3248 | 0 | 44.2741 |  | 2029-09-01 | 14:05 | 50700 | 71.9651 | 0 | 113.4324 |  | 2029-09-01 | 14:05 | 50700 | 40.7214 | 0 | 78.3535 |  | 2029-09-01 | 14:05 | 50700 | 21.5617 | 0 | 53.9769 |  | 2006-09-01 | 14:05 | 50700 | 21.0642 | 0 | 53.1395 |  | 2028-01-01 | 14:05 | 50700 | 59.037 | 0 | 96.0318 |  | 2007-01-01 | 14:05 | 50700 | 20.5219 | 0 | 99.5076 |  | 2028-01-01 | 14:05 | 50700 | 17.5643 | 0 | 48.2347 |  | 2007-01-01 | 14:05 | 50700 | 6.5705 | 0 | 49.2959
| 2029-09-01 | 14:06 | 50760 | 322.28 | 0 | 376.3386 |  | 2029-09-01 | 14:06 | 50760 | 94.2096 | 0 | 259.5712 |  | 2006-09-01 | 14:06 | 50760 | 49.0279 | 0 | 237.5696 |  | 2029-09-01 | 14:06 | 50760 | 47.4794 | 0 | 171.9946 |  | 2006-09-01 | 14:06 | 50760 | 22.0658 | 0 | 122.4242 |  | 2028-01-01 | 14:06 | 50760 | 166.186 | 0 | 261.4985 |  | 2007-01-01 | 14:06 | 50760 | 43.1527 | 0 | 239.8708 |  | 2028-01-01 | 14:06 | 50760 | 54.3382 | 0 | 96.0318 |  | 2007-01-01 | 14:06 | 50760 | 15.383 | 0 | 99.5076 |  | 2029-09-01 | 14:06 | 50760 | 51.0288 | 0 | 251.1652 |  | 2006-09-01 | 14:06 | 50760 | 19.768 | 0 | 235.6392 |  | 2029-09-01 | 14:06 | 50760 | 16.1121 | 0 | 126.4464 |  | 2006-09-01 | 14:06 | 50760 | 5.3415 | 0 | 80.2475 |  | 2028-01-01 | 14:06 | 50760 | 112.774 | 0 | 250.1758 |  | 2007-01-01 | 14:06 | 50760 | 16.0377 | 0 | 238.7407 |  | 2028-01-01 | 14:06 | 50760 | 20.7417 | 0 | 57.3935 |  | 2007-01-01 | 14:06 | 50760 | 3.31 | 0 | 61.4487 |  | 2029-09-01 | 14:06 | 50760 | 36.0398 | 0 | 249.4938 |  | 2006-09-01 | 14:06 | 50760 | 12.0103 | 0 | 235.4499 |  | 2029-09-01 | 14:06 | 50760 | 8.1273 | 0 | 100.9404 |  | 2006-09-01 | 14:06 | 50760 | 2.284 | 0 | 59.4344 |  | 2028-01-01 | 14:06 | 50760 | 79.5468 | 0 | 247.6085 |  | 2007-01-01 | 14:06 | 50760 | 9.3905 | 0 | 238.6576 |  | 2028-01-01 | 14:06 | 50760 | 10.1149 | 0 | 40.8951 |  | 2007-01-01 | 14:06 | 50760 | 1.3568 | 0 | 44.2741 |  | 2029-09-01 | 14:06 | 50760 | 67.5603 | 0 | 113.4324 |  | 2029-09-01 | 14:06 | 50760 | 37.0262 | 0 | 78.3535 |  | 2029-09-01 | 14:06 | 50760 | 18.7396 | 0 | 53.9769 |  | 2006-09-01 | 14:06 | 50760 | 18.2726 | 0 | 53.1395 |  | 2028-01-01 | 14:06 | 50760 | 54.3382 | 0 | 96.0318 |  | 2007-01-01 | 14:06 | 50760 | 15.383 | 0 | 99.5076 |  | 2028-01-01 | 14:06 | 50760 | 14.9038 | 0 | 48.2347 |  | 2007-01-01 | 14:06 | 50760 | 4.6074 | 0 | 49.2959
| 2029-09-01 | 14:07 | 50820 | 317.705 | 0 | 376.3386 |  | 2029-09-01 | 14:07 | 50820 | 79.2408 | 0 | 259.5712 |  | 2006-09-01 | 14:07 | 50820 | 37.3493 | 0 | 237.5696 |  | 2029-09-01 | 14:07 | 50820 | 39.9354 | 0 | 171.9946 |  | 2006-09-01 | 14:07 | 50820 | 16.8097 | 0 | 122.4242 |  | 2028-01-01 | 14:07 | 50820 | 152.955 | 0 | 261.4985 |  | 2007-01-01 | 14:07 | 50820 | 32.4204 | 0 | 239.8708 |  | 2028-01-01 | 14:07 | 50820 | 50.0112 | 0 | 96.0318 |  | 2007-01-01 | 14:07 | 50820 | 11.5572 | 0 | 99.5076 |  | 2029-09-01 | 14:07 | 50820 | 38.7538 | 0 | 251.1652 |  | 2006-09-01 | 14:07 | 50820 | 12.9277 | 0 | 235.6392 |  | 2029-09-01 | 14:07 | 50820 | 12.2363 | 0 | 126.4464 |  | 2006-09-01 | 14:07 | 50820 | 3.4932 | 0 | 80.2475 |  | 2028-01-01 | 14:07 | 50820 | 97.3578 | 0 | 250.1758 |  | 2007-01-01 | 14:07 | 50820 | 10.2554 | 0 | 238.7407 |  | 2028-01-01 | 14:07 | 50820 | 17.9064 | 0 | 57.3935 |  | 2007-01-01 | 14:07 | 50820 | 2.1166 | 0 | 61.4487 |  | 2029-09-01 | 14:07 | 50820 | 25.8282 | 0 | 249.4938 |  | 2006-09-01 | 14:07 | 50820 | 7.224 | 0 | 235.4499 |  | 2029-09-01 | 14:07 | 50820 | 5.8245 | 0 | 100.9404 |  | 2006-09-01 | 14:07 | 50820 | 1.3738 | 0 | 59.4344 |  | 2028-01-01 | 14:07 | 50820 | 64.7868 | 0 | 247.6085 |  | 2007-01-01 | 14:07 | 50820 | 5.5023 | 0 | 238.6576 |  | 2028-01-01 | 14:07 | 50820 | 8.238 | 0 | 40.8951 |  | 2007-01-01 | 14:07 | 50820 | 0.79502 | 0 | 44.2741 |  | 2029-09-01 | 14:07 | 50820 | 63.4251 | 0 | 113.4324 |  | 2029-09-01 | 14:07 | 50820 | 33.6663 | 0 | 78.3535 |  | 2029-09-01 | 14:07 | 50820 | 16.2868 | 0 | 53.9769 |  | 2006-09-01 | 14:07 | 50820 | 15.8507 | 0 | 53.1395 |  | 2028-01-01 | 14:07 | 50820 | 50.0112 | 0 | 96.0318 |  | 2007-01-01 | 14:07 | 50820 | 11.5572 | 0 | 99.5076 |  | 2028-01-01 | 14:07 | 50820 | 12.6458 | 0 | 48.2347 |  | 2007-01-01 | 14:07 | 50820 | 3.2377 | 0 | 49.2959
| 2029-09-01 | 14:08 | 50880 | 313.195 | 0 | 376.3386 |  | 2029-09-01 | 14:08 | 50880 | 66.6479 | 0 | 259.5712 |  | 2006-09-01 | 14:08 | 50880 | 28.432 | 0 | 237.5696 |  | 2029-09-01 | 14:08 | 50880 | 33.5889 | 0 | 171.9946 |  | 2006-09-01 | 14:08 | 50880 | 12.7963 | 0 | 122.4242 |  | 2028-01-01 | 14:08 | 50880 | 140.771 | 0 | 261.4985 |  | 2007-01-01 | 14:08 | 50880 | 24.4133 | 0 | 239.8708 |  | 2028-01-01 | 14:08 | 50880 | 46.0269 | 0 | 96.0318 |  | 2007-01-01 | 14:08 | 50880 | 8.7028 | 0 | 99.5076 |  | 2029-09-01 | 14:08 | 50880 | 29.4299 | 0 | 251.1652 |  | 2006-09-01 | 14:08 | 50880 | 8.4453 | 0 | 235.6392 |  | 2029-09-01 | 14:08 | 50880 | 9.2923 | 0 | 126.4464 |  | 2006-09-01 | 14:08 | 50880 | 2.282 | 0 | 80.2475 |  | 2028-01-01 | 14:08 | 50880 | 84.0429 | 0 | 250.1758 |  | 2007-01-01 | 14:08 | 50880 | 6.5804 | 0 | 238.7407 |  | 2028-01-01 | 14:08 | 50880 | 15.4574 | 0 | 57.3935 |  | 2007-01-01 | 14:08 | 50880 | 1.3581 | 0 | 61.4487 |  | 2029-09-01 | 14:08 | 50880 | 18.5088 | 0 | 249.4938 |  | 2006-09-01 | 14:08 | 50880 | 4.3397 | 0 | 235.4499 |  | 2029-09-01 | 14:08 | 50880 | 4.1739 | 0 | 100.9404 |  | 2006-09-01 | 14:08 | 50880 | 0.8253 | 0 | 59.4344 |  | 2028-01-01 | 14:08 | 50880 | 52.76 | 0 | 247.6085 |  | 2007-01-01 | 14:08 | 50880 | 3.2368 | 0 | 238.6576 |  | 2028-01-01 | 14:08 | 50880 | 6.7088 | 0 | 40.8951 |  | 2007-01-01 | 14:08 | 50880 | 0.46769 | 0 | 44.2741 |  | 2029-09-01 | 14:08 | 50880 | 59.5431 | 0 | 113.4324 |  | 2029-09-01 | 14:08 | 50880 | 30.6113 | 0 | 78.3535 |  | 2029-09-01 | 14:08 | 50880 | 14.1551 | 0 | 53.9769 |  | 2006-09-01 | 14:08 | 50880 | 13.7497 | 0 | 53.1395 |  | 2028-01-01 | 14:08 | 50880 | 46.0269 | 0 | 96.0318 |  | 2007-01-01 | 14:08 | 50880 | 8.7028 | 0 | 99.5076 |  | 2028-01-01 | 14:08 | 50880 | 10.7295 | 0 | 48.2347 |  | 2007-01-01 | 14:08 | 50880 | 2.2801 | 0 | 49.2959
| 2029-09-01 | 14:09 | 50940 | 308.748 | 0 | 376.3386 |  | 2029-09-01 | 14:09 | 50940 | 56.0544 | 0 | 259.5712 |  | 2006-09-01 | 14:09 | 50940 | 21.6281 | 0 | 237.5696 |  | 2029-09-01 | 14:09 | 50940 | 28.25 | 0 | 171.9946 |  | 2006-09-01 | 14:09 | 50940 | 9.7341 | 0 | 122.4242 |  | 2028-01-01 | 14:09 | 50940 | 129.553 | 0 | 261.4985 |  | 2007-01-01 | 14:09 | 50940 | 18.4267 | 0 | 239.8708 |  | 2028-01-01 | 14:09 | 50940 | 42.3581 | 0 | 96.0318 |  | 2007-01-01 | 14:09 | 50940 | 6.5687 | 0 | 99.5076 |  | 2029-09-01 | 14:09 | 50940 | 22.348 | 0 | 251.1652 |  | 2006-09-01 | 14:09 | 50940 | 5.5112 | 0 | 235.6392 |  | 2029-09-01 | 14:09 | 50940 | 7.0563 | 0 | 126.4464 |  | 2006-09-01 | 14:09 | 50940 | 1.4892 | 0 | 80.2475 |  | 2028-01-01 | 14:09 | 50940 | 72.5435 | 0 | 250.1758 |  | 2007-01-01 | 14:09 | 50940 | 4.2371 | 0 | 238.7407 |  | 2028-01-01 | 14:09 | 50940 | 13.3424 | 0 | 57.3935 |  | 2007-01-01 | 14:09 | 50940 | 0.87449 | 0 | 61.4487 |  | 2029-09-01 | 14:09 | 50940 | 13.2628 | 0 | 249.4938 |  | 2006-09-01 | 14:09 | 50940 | 2.6038 | 0 | 235.4499 |  | 2029-09-01 | 14:09 | 50940 | 2.9909 | 0 | 100.9404 |  | 2006-09-01 | 14:09 | 50940 | 0.49517 | 0 | 59.4344 |  | 2028-01-01 | 14:09 | 50940 | 42.9614 | 0 | 247.6085 |  | 2007-01-01 | 14:09 | 50940 | 1.9118 | 0 | 238.6576 |  | 2028-01-01 | 14:09 | 50940 | 5.4628 | 0 | 40.8951 |  | 2007-01-01 | 14:09 | 50940 | 0.27623 | 0 | 44.2741 |  | 2029-09-01 | 14:09 | 50940 | 55.8986 | 0 | 113.4324 |  | 2029-09-01 | 14:09 | 50940 | 27.8335 | 0 | 78.3535 |  | 2029-09-01 | 14:09 | 50940 | 12.3024 | 0 | 53.9769 |  | 2006-09-01 | 14:09 | 50940 | 11.9269 | 0 | 53.1395 |  | 2028-01-01 | 14:09 | 50940 | 42.3581 | 0 | 96.0318 |  | 2007-01-01 | 14:09 | 50940 | 6.5687 | 0 | 99.5076 |  | 2028-01-01 | 14:09 | 50940 | 9.1032 | 0 | 48.2347 |  | 2007-01-01 | 14:09 | 50940 | 1.6092 | 0 | 49.2959
| 2029-09-01 | 14:10 | 51000 | 304.365 | 0 | 376.3386 |  | 2029-09-01 | 14:10 | 51000 | 47.143 | 0 | 259.5712 |  | 2006-09-01 | 14:10 | 51000 | 16.4405 | 0 | 237.5696 |  | 2029-09-01 | 14:10 | 51000 | 23.7589 | 0 | 171.9946 |  | 2006-09-01 | 14:10 | 51000 | 7.3994 | 0 | 122.4242 |  | 2028-01-01 | 14:10 | 51000 | 119.223 | 0 | 261.4985 |  | 2007-01-01 | 14:10 | 51000 | 13.941 | 0 | 239.8708 |  | 2028-01-01 | 14:10 | 51000 | 38.9801 | 0 | 96.0318 |  | 2007-01-01 | 14:10 | 51000 | 4.9697 | 0 | 99.5076 |  | 2029-09-01 | 14:10 | 51000 | 16.9694 | 0 | 251.1652 |  | 2006-09-01 | 14:10 | 51000 | 3.5926 | 0 | 235.6392 |  | 2029-09-01 | 14:10 | 51000 | 5.358 | 0 | 126.4464 |  | 2006-09-01 | 14:10 | 51000 | 0.97075 | 0 | 80.2475 |  | 2028-01-01 | 14:10 | 51000 | 62.6128 | 0 | 250.1758 |  | 2007-01-01 | 14:10 | 51000 | 2.7379 | 0 | 238.7407 |  | 2028-01-01 | 14:10 | 51000 | 11.5159 | 0 | 57.3935 |  | 2007-01-01 | 14:10 | 51000 | 0.56508 | 0 | 61.4487 |  | 2029-09-01 | 14:10 | 51000 | 9.503 | 0 | 249.4938 |  | 2006-09-01 | 14:10 | 51000 | 1.5603 | 0 | 235.4499 |  | 2029-09-01 | 14:10 | 51000 | 2.143 | 0 | 100.9404 |  | 2006-09-01 | 14:10 | 51000 | 0.29673 | 0 | 59.4344 |  | 2028-01-01 | 14:10 | 51000 | 34.9789 | 0 | 247.6085 |  | 2007-01-01 | 14:10 | 51000 | 1.1338 | 0 | 238.6576 |  | 2028-01-01 | 14:10 | 51000 | 4.4478 | 0 | 40.8951 |  | 2007-01-01 | 14:10 | 51000 | 0.16382 | 0 | 44.2741 |  | 2029-09-01 | 14:10 | 51000 | 52.4772 | 0 | 113.4324 |  | 2029-09-01 | 14:10 | 51000 | 25.3078 | 0 | 78.3535 |  | 2029-09-01 | 14:10 | 51000 | 10.6922 | 0 | 53.9769 |  | 2006-09-01 | 14:10 | 51000 | 10.3457 | 0 | 53.1395 |  | 2028-01-01 | 14:10 | 51000 | 38.9801 | 0 | 96.0318 |  | 2007-01-01 | 14:10 | 51000 | 4.9697 | 0 | 99.5076 |  | 2028-01-01 | 14:10 | 51000 | 7.7231 | 0 | 48.2347 |  | 2007-01-01 | 14:10 | 51000 | 1.1382 | 0 | 49.2959
| 2029-09-01 | 14:11 | 51060 | 300.044 | 0 | 376.3386 |  | 2029-09-01 | 14:11 | 51060 | 39.647 | 0 | 259.5712 |  | 2006-09-01 | 14:11 | 51060 | 12.4882 | 0 | 237.5696 |  | 2029-09-01 | 14:11 | 51060 | 19.9811 | 0 | 171.9946 |  | 2006-09-01 | 14:11 | 51060 | 5.6206 | 0 | 122.4242 |  | 2028-01-01 | 14:11 | 51060 | 109.713 | 0 | 261.4985 |  | 2007-01-01 | 14:11 | 51060 | 10.5725 | 0 | 239.8708 |  | 2028-01-01 | 14:11 | 51060 | 35.87 | 0 | 96.0318 |  | 2007-01-01 | 14:11 | 51060 | 3.7689 | 0 | 99.5076 |  | 2029-09-01 | 14:11 | 51060 | 12.8846 | 0 | 251.1652 |  | 2006-09-01 | 14:11 | 51060 | 2.3394 | 0 | 235.6392 |  | 2029-09-01 | 14:11 | 51060 | 4.0682 | 0 | 126.4464 |  | 2006-09-01 | 14:11 | 51060 | 0.63213 | 0 | 80.2475 |  | 2028-01-01 | 14:11 | 51060 | 54.0375 | 0 | 250.1758 |  | 2007-01-01 | 14:11 | 51060 | 1.7755 | 0 | 238.7407 |  | 2028-01-01 | 14:11 | 51060 | 9.9387 | 0 | 57.3935 |  | 2007-01-01 | 14:11 | 51060 | 0.36644 | 0 | 61.4487 |  | 2029-09-01 | 14:11 | 51060 | 6.8087 | 0 | 249.4938 |  | 2006-09-01 | 14:11 | 51060 | 0.93385 | 0 | 235.4499 |  | 2029-09-01 | 14:11 | 51060 | 1.5354 | 0 | 100.9404 |  | 2006-09-01 | 14:11 | 51060 | 0.17759 | 0 | 59.4344 |  | 2028-01-01 | 14:11 | 51060 | 28.4767 | 0 | 247.6085 |  | 2007-01-01 | 14:11 | 51060 | 0.6752 | 0 | 238.6576 |  | 2028-01-01 | 14:11 | 51060 | 3.621 | 0 | 40.8951 |  | 2007-01-01 | 14:11 | 51060 | 0.09756 | 0 | 44.2741 |  | 2029-09-01 | 14:11 | 51060 | 49.2653 | 0 | 113.4324 |  | 2029-09-01 | 14:11 | 51060 | 23.0113 | 0 | 78.3535 |  | 2029-09-01 | 14:11 | 51060 | 9.2928 | 0 | 53.9769 |  | 2006-09-01 | 14:11 | 51060 | 8.9739 | 0 | 53.1395 |  | 2028-01-01 | 14:11 | 51060 | 35.87 | 0 | 96.0318 |  | 2007-01-01 | 14:11 | 51060 | 3.7689 | 0 | 99.5076 |  | 2028-01-01 | 14:11 | 51060 | 6.552 | 0 | 48.2347 |  | 2007-01-01 | 14:11 | 51060 | 0.80689 | 0 | 49.2959
| 2029-09-01 | 14:12 | 51120 | 295.785 | 0 | 376.3386 |  | 2029-09-01 | 14:12 | 51120 | 33.3417 | 0 | 259.5712 |  | 2006-09-01 | 14:12 | 51120 | 9.4792 | 0 | 237.5696 |  | 2029-09-01 | 14:12 | 51120 | 16.8034 | 0 | 171.9946 |  | 2006-09-01 | 14:12 | 51120 | 4.2663 | 0 | 122.4242 |  | 2028-01-01 | 14:12 | 51120 | 100.957 | 0 | 261.4985 |  | 2007-01-01 | 14:12 | 51120 | 8.0374 | 0 | 239.8708 |  | 2028-01-01 | 14:12 | 51120 | 33.0066 | 0 | 96.0318 |  | 2007-01-01 | 14:12 | 51120 | 2.8652 | 0 | 99.5076 |  | 2029-09-01 | 14:12 | 51120 | 9.7825 | 0 | 251.1652 |  | 2006-09-01 | 14:12 | 51120 | 1.5218 | 0 | 235.6392 |  | 2029-09-01 | 14:12 | 51120 | 3.0888 | 0 | 126.4464 |  | 2006-09-01 | 14:12 | 51120 | 0.41119 | 0 | 80.2475 |  | 2028-01-01 | 14:12 | 51120 | 46.6332 | 0 | 250.1758 |  | 2007-01-01 | 14:12 | 51120 | 1.1555 | 0 | 238.7407 |  | 2028-01-01 | 14:12 | 51120 | 8.5769 | 0 | 57.3935 |  | 2007-01-01 | 14:12 | 51120 | 0.23848 | 0 | 61.4487 |  | 2029-09-01 | 14:12 | 51120 | 4.8779 | 0 | 249.4938 |  | 2006-09-01 | 14:12 | 51120 | 0.55822 | 0 | 235.4499 |  | 2029-09-01 | 14:12 | 51120 | 1.1 | 0 | 100.9404 |  | 2006-09-01 | 14:12 | 51120 | 0.10616 | 0 | 59.4344 |  | 2028-01-01 | 14:12 | 51120 | 23.1808 | 0 | 247.6085 |  | 2007-01-01 | 14:12 | 51120 | 0.4038 | 0 | 238.6576 |  | 2028-01-01 | 14:12 | 51120 | 2.9476 | 0 | 40.8951 |  | 2007-01-01 | 14:12 | 51120 | 0.058345 | 0 | 44.2741 |  | 2029-09-01 | 14:12 | 51120 | 46.2499 | 0 | 113.4324 |  | 2029-09-01 | 14:12 | 51120 | 20.9232 | 0 | 78.3535 |  | 2029-09-01 | 14:12 | 51120 | 8.0765 | 0 | 53.9769 |  | 2006-09-01 | 14:12 | 51120 | 7.7839 | 0 | 53.1395 |  | 2028-01-01 | 14:12 | 51120 | 33.0066 | 0 | 96.0318 |  | 2007-01-01 | 14:12 | 51120 | 2.8652 | 0 | 99.5076 |  | 2028-01-01 | 14:12 | 51120 | 5.5583 | 0 | 48.2347 |  | 2007-01-01 | 14:12 | 51120 | 0.57331 | 0 | 49.2959
| 2029-09-01 | 14:13 | 51180 | 291.586 | 0 | 376.3386 |  | 2029-09-01 | 14:13 | 51180 | 28.0382 | 0 | 259.5712 |  | 2006-09-01 | 14:13 | 51180 | 7.19 | 0 | 237.5696 |  | 2029-09-01 | 14:13 | 51180 | 14.1306 | 0 | 171.9946 |  | 2006-09-01 | 14:13 | 51180 | 3.236 | 0 | 122.4242 |  | 2028-01-01 | 14:13 | 51180 | 92.8954 | 0 | 261.4985 |  | 2007-01-01 | 14:13 | 51180 | 6.1252 | 0 | 239.8708 |  | 2028-01-01 | 14:13 | 51180 | 30.3705 | 0 | 96.0318 |  | 2007-01-01 | 14:13 | 51180 | 2.1835 | 0 | 99.5076 |  | 2029-09-01 | 14:13 | 51180 | 7.4269 | 0 | 251.1652 |  | 2006-09-01 | 14:13 | 51180 | 0.98883 | 0 | 235.6392 |  | 2029-09-01 | 14:13 | 51180 | 2.345 | 0 | 126.4464 |  | 2006-09-01 | 14:13 | 51180 | 0.26719 | 0 | 80.2475 |  | 2028-01-01 | 14:13 | 51180 | 40.2404 | 0 | 250.1758 |  | 2007-01-01 | 14:13 | 51180 | 0.75473 | 0 | 238.7407 |  | 2028-01-01 | 14:13 | 51180 | 7.4011 | 0 | 57.3935 |  | 2007-01-01 | 14:13 | 51180 | 0.15577 | 0 | 61.4487 |  | 2029-09-01 | 14:13 | 51180 | 3.4945 | 0 | 249.4938 |  | 2006-09-01 | 14:13 | 51180 | 0.33327 | 0 | 235.4499 |  | 2029-09-01 | 14:13 | 51180 | 0.78803 | 0 | 100.9404 |  | 2006-09-01 | 14:13 | 51180 | 0.063378 | 0 | 59.4344 |  | 2028-01-01 | 14:13 | 51180 | 18.8678 | 0 | 247.6085 |  | 2007-01-01 | 14:13 | 51180 | 0.24252 | 0 | 238.6576 |  | 2028-01-01 | 14:13 | 51180 | 2.3992 | 0 | 40.8951 |  | 2007-01-01 | 14:13 | 51180 | 0.035042 | 0 | 44.2741 |  | 2029-09-01 | 14:13 | 51180 | 43.4192 | 0 | 113.4324 |  | 2029-09-01 | 14:13 | 51180 | 19.0246 | 0 | 78.3535 |  | 2029-09-01 | 14:13 | 51180 | 7.0194 | 0 | 53.9769 |  | 2006-09-01 | 14:13 | 51180 | 6.7517 | 0 | 53.1395 |  | 2028-01-01 | 14:13 | 51180 | 30.3705 | 0 | 96.0318 |  | 2007-01-01 | 14:13 | 51180 | 2.1835 | 0 | 99.5076 |  | 2028-01-01 | 14:13 | 51180 | 4.7151 | 0 | 48.2347 |  | 2007-01-01 | 14:13 | 51180 | 0.40828 | 0 | 49.2959
| 2029-09-01 | 14:14 | 51240 | 287.447 | 0 | 376.3386 |  | 2029-09-01 | 14:14 | 51240 | 23.5775 | 0 | 259.5712 |  | 2006-09-01 | 14:14 | 51240 | 5.4497 | 0 | 237.5696 |  | 2029-09-01 | 14:14 | 51240 | 11.8825 | 0 | 171.9946 |  | 2006-09-01 | 14:14 | 51240 | 2.4528 | 0 | 122.4242 |  | 2028-01-01 | 14:14 | 51240 | 85.4743 | 0 | 261.4985 |  | 2007-01-01 | 14:14 | 51240 | 4.6796 | 0 | 239.8708 |  | 2028-01-01 | 14:14 | 51240 | 27.9437 | 0 | 96.0318 |  | 2007-01-01 | 14:14 | 51240 | 1.6682 | 0 | 99.5076 |  | 2029-09-01 | 14:14 | 51240 | 5.6382 | 0 | 251.1652 |  | 2006-09-01 | 14:14 | 51240 | 0.64185 | 0 | 235.6392 |  | 2029-09-01 | 14:14 | 51240 | 1.7802 | 0 | 126.4464 |  | 2006-09-01 | 14:14 | 51240 | 0.17343 | 0 | 80.2475 |  | 2028-01-01 | 14:14 | 51240 | 34.7214 | 0 | 250.1758 |  | 2007-01-01 | 14:14 | 51240 | 0.49479 | 0 | 238.7407 |  | 2028-01-01 | 14:14 | 51240 | 6.386 | 0 | 57.3935 |  | 2007-01-01 | 14:14 | 51240 | 0.10212 | 0 | 61.4487 |  | 2029-09-01 | 14:14 | 51240 | 2.5032 | 0 | 249.4938 |  | 2006-09-01 | 14:14 | 51240 | 0.19872 | 0 | 235.4499 |  | 2029-09-01 | 14:14 | 51240 | 0.56449 | 0 | 100.9404 |  | 2006-09-01 | 14:14 | 51240 | 0.037791 | 0 | 59.4344 |  | 2028-01-01 | 14:14 | 51240 | 15.3557 | 0 | 247.6085 |  | 2007-01-01 | 14:14 | 51240 | 0.1463 | 0 | 238.6576 |  | 2028-01-01 | 14:14 | 51240 | 1.9526 | 0 | 40.8951 |  | 2007-01-01 | 14:14 | 51240 | 0.021138 | 0 | 44.2741 |  | 2029-09-01 | 14:14 | 51240 | 40.7617 | 0 | 113.4324 |  | 2029-09-01 | 14:14 | 51240 | 17.2982 | 0 | 78.3535 |  | 2029-09-01 | 14:14 | 51240 | 6.1007 | 0 | 53.9769 |  | 2006-09-01 | 14:14 | 51240 | 5.8562 | 0 | 53.1395 |  | 2028-01-01 | 14:14 | 51240 | 27.9437 | 0 | 96.0318 |  | 2007-01-01 | 14:14 | 51240 | 1.6682 | 0 | 99.5076 |  | 2028-01-01 | 14:14 | 51240 | 3.9996 | 0 | 48.2347 |  | 2007-01-01 | 14:14 | 51240 | 0.29143 | 0 | 49.2959
| 2029-09-01 | 14:15 | 51300 | 283.366 | 1.7002 | 378.0388 |  | 2029-09-01 | 14:15 | 51300 | 19.8258 | 0.11895 | 259.6902 |  | 2006-09-01 | 14:15 | 51300 | 4.1277 | 0.024766 | 237.5944 |  | 2029-09-01 | 14:15 | 51300 | 9.9917 | 0.05995 | 172.0545 |  | 2006-09-01 | 14:15 | 51300 | 1.8578 | 0.011147 | 122.4354 |  | 2028-01-01 | 14:15 | 51300 | 78.6428 | 0.47186 | 261.9704 |  | 2007-01-01 | 14:15 | 51300 | 3.5842 | 0.021505 | 239.8923 |  | 2028-01-01 | 14:15 | 51300 | 25.7098 | 0.15426 | 96.186 |  | 2007-01-01 | 14:15 | 51300 | 1.2777 | 0.007666 | 99.5153 |  | 2029-09-01 | 14:15 | 51300 | 4.2801 | 0.02568 | 251.1909 |  | 2006-09-01 | 14:15 | 51300 | 0.41618 | 0.0024971 | 235.6417 |  | 2029-09-01 | 14:15 | 51300 | 1.3514 | 0.0081084 | 126.4545 |  | 2006-09-01 | 14:15 | 51300 | 0.11246 | 0.00067474 | 80.2482 |  | 2028-01-01 | 14:15 | 51300 | 29.957 | 0.17974 | 250.3555 |  | 2007-01-01 | 14:15 | 51300 | 0.3256 | 0.0019536 | 238.7426 |  | 2028-01-01 | 14:15 | 51300 | 5.5098 | 0.033059 | 57.4265 |  | 2007-01-01 | 14:15 | 51300 | 0.067199 | 0.0004032 | 61.4491 |  | 2029-09-01 | 14:15 | 51300 | 1.793 | 0.010758 | 249.5045 |  | 2006-09-01 | 14:15 | 51300 | 0.11835 | 0.00071009 | 235.4506 |  | 2029-09-01 | 14:15 | 51300 | 0.40434 | 0.002426 | 100.9428 |  | 2006-09-01 | 14:15 | 51300 | 0.022507 | 0.00013504 | 59.4345 |  | 2028-01-01 | 14:15 | 51300 | 12.4961 | 0.074977 | 247.6834 |  | 2007-01-01 | 14:15 | 51300 | 0.088641 | 0.00053185 | 238.6581 |  | 2028-01-01 | 14:15 | 51300 | 1.589 | 0.0095337 | 40.9046 |  | 2007-01-01 | 14:15 | 51300 | 0.012808 | 7.6847e-05 | 44.2742 |  | 2029-09-01 | 14:15 | 51300 | 38.2668 | 0.2296 | 113.662 |  | 2029-09-01 | 14:15 | 51300 | 15.7286 | 0.094372 | 78.4478 |  | 2029-09-01 | 14:15 | 51300 | 5.3022 | 0.031813 | 54.0087 |  | 2006-09-01 | 14:15 | 51300 | 5.0794 | 0.030476 | 53.17 |  | 2028-01-01 | 14:15 | 51300 | 25.7098 | 0.15426 | 96.186 |  | 2007-01-01 | 14:15 | 51300 | 1.2777 | 0.007666 | 99.5153 |  | 2028-01-01 | 14:15 | 51300 | 3.3926 | 0.020356 | 48.2551 |  | 2007-01-01 | 14:15 | 51300 | 0.20852 | 0.0012511 | 49.2971
| 2029-09-01 | 14:16 | 51360 | 285.845 | 1.7151 | 379.7539 |  | 2029-09-01 | 14:16 | 51360 | 25.9922 | 0.15595 | 259.8461 |  | 2006-09-01 | 14:16 | 51360 | 10.4925 | 0.062955 | 237.6574 |  | 2029-09-01 | 14:16 | 51360 | 15.795 | 0.09477 | 172.1493 |  | 2006-09-01 | 14:16 | 51360 | 7.9364 | 0.047619 | 122.483 |  | 2028-01-01 | 14:16 | 51360 | 84.1015 | 0.50461 | 262.475 |  | 2007-01-01 | 14:16 | 51360 | 9.9666 | 0.0598 | 239.9521 |  | 2028-01-01 | 14:16 | 51360 | 30.0777 | 0.18047 | 96.3665 |  | 2007-01-01 | 14:16 | 51360 | 7.3023 | 0.043814 | 99.5591 |  | 2029-09-01 | 14:16 | 51360 | 10.6642 | 0.063985 | 251.2549 |  | 2006-09-01 | 14:16 | 51360 | 6.8406 | 0.041044 | 235.6828 |  | 2029-09-01 | 14:16 | 51360 | 7.3137 | 0.043882 | 126.4984 |  | 2006-09-01 | 14:16 | 51360 | 6.0509 | 0.036305 | 80.2845 |  | 2028-01-01 | 14:16 | 51360 | 36.0359 | 0.21622 | 250.5718 |  | 2007-01-01 | 14:16 | 51360 | 6.7594 | 0.040556 | 238.7832 |  | 2028-01-01 | 14:16 | 51360 | 10.6538 | 0.063923 | 57.4905 |  | 2007-01-01 | 14:16 | 51360 | 5.8725 | 0.035235 | 61.4844 |  | 2029-09-01 | 14:16 | 51360 | 8.212 | 0.049272 | 249.5538 |  | 2006-09-01 | 14:16 | 51360 | 6.5476 | 0.039285 | 235.4898 |  | 2029-09-01 | 14:16 | 51360 | 6.2498 | 0.037499 | 100.9803 |  | 2006-09-01 | 14:16 | 51360 | 5.7536 | 0.034521 | 59.469 |  | 2028-01-01 | 14:16 | 51360 | 18.7973 | 0.11278 | 247.7962 |  | 2007-01-01 | 14:16 | 51360 | 6.5261 | 0.039157 | 238.6973 |  | 2028-01-01 | 14:16 | 51360 | 6.8318 | 0.040991 | 40.9456 |  | 2007-01-01 | 14:16 | 51360 | 5.5544 | 0.033326 | 44.3075 |  | 2029-09-01 | 14:16 | 51360 | 42.0681 | 0.25241 | 113.9144 |  | 2029-09-01 | 14:16 | 51360 | 20.2475 | 0.12148 | 78.5693 |  | 2029-09-01 | 14:16 | 51360 | 10.2902 | 0.061741 | 54.0704 |  | 2006-09-01 | 14:16 | 51360 | 10.0787 | 0.060472 | 53.2305 |  | 2028-01-01 | 14:16 | 51360 | 30.0777 | 0.18047 | 96.3665 |  | 2007-01-01 | 14:16 | 51360 | 7.3023 | 0.043814 | 99.5591 |  | 2028-01-01 | 14:16 | 51360 | 8.5337 | 0.051202 | 48.3063 |  | 2007-01-01 | 14:16 | 51360 | 5.8051 | 0.03483 | 49.332
| 2029-09-01 | 14:17 | 51420 | 288.288 | 1.7297 | 381.4836 |  | 2029-09-01 | 14:17 | 51420 | 32.0724 | 0.19243 | 260.0385 |  | 2006-09-01 | 14:17 | 51420 | 16.7548 | 0.10053 | 237.7579 |  | 2029-09-01 | 14:17 | 51420 | 21.341 | 0.12805 | 172.2773 |  | 2006-09-01 | 14:17 | 51420 | 13.6842 | 0.082105 | 122.5651 |  | 2028-01-01 | 14:17 | 51420 | 89.4912 | 0.53695 | 263.0119 |  | 2007-01-01 | 14:17 | 51420 | 16.2488 | 0.097493 | 240.0496 |  | 2028-01-01 | 14:17 | 51420 | 34.1496 | 0.2049 | 96.5714 |  | 2007-01-01 | 14:17 | 51420 | 12.929 | 0.077574 | 99.6366 |  | 2029-09-01 | 14:17 | 51420 | 16.959 | 0.10175 | 251.3566 |  | 2006-09-01 | 14:17 | 51420 | 13.1617 | 0.07897 | 235.7618 |  | 2029-09-01 | 14:17 | 51420 | 12.8426 | 0.077056 | 126.5755 |  | 2006-09-01 | 14:17 | 51420 | 11.4562 | 0.068737 | 80.3533 |  | 2028-01-01 | 14:17 | 51420 | 42.0375 | 0.25222 | 250.824 |  | 2007-01-01 | 14:17 | 51420 | 13.092 | 0.078552 | 238.8617 |  | 2028-01-01 | 14:17 | 51420 | 15.1995 | 0.091197 | 57.5816 |  | 2007-01-01 | 14:17 | 51420 | 11.0309 | 0.066185 | 61.5506 |  | 2029-09-01 | 14:17 | 51420 | 14.5411 | 0.087247 | 249.641 |  | 2006-09-01 | 14:17 | 51420 | 12.8733 | 0.07724 | 235.5671 |  | 2029-09-01 | 14:17 | 51420 | 11.514 | 0.069084 | 101.0494 |  | 2006-09-01 | 14:17 | 51420 | 10.7823 | 0.064694 | 59.5337 |  | 2028-01-01 | 14:17 | 51420 | 25.0184 | 0.15011 | 247.9463 |  | 2007-01-01 | 14:17 | 51420 | 12.8624 | 0.077174 | 238.7745 |  | 2028-01-01 | 14:17 | 51420 | 11.2351 | 0.067411 | 41.013 |  | 2007-01-01 | 14:17 | 51420 | 10.2499 | 0.061499 | 44.369 |  | 2029-09-01 | 14:17 | 51420 | 45.6374 | 0.27382 | 114.1882 |  | 2029-09-01 | 14:17 | 51420 | 24.3572 | 0.14614 | 78.7155 |  | 2029-09-01 | 14:17 | 51420 | 14.6261 | 0.087757 | 54.1582 |  | 2006-09-01 | 14:17 | 51420 | 14.4164 | 0.086498 | 53.317 |  | 2028-01-01 | 14:17 | 51420 | 34.1496 | 0.2049 | 96.5714 |  | 2007-01-01 | 14:17 | 51420 | 12.929 | 0.077574 | 99.6366 |  | 2028-01-01 | 14:17 | 51420 | 12.9486 | 0.077692 | 48.384 |  | 2007-01-01 | 14:17 | 51420 | 10.6182 | 0.063709 | 49.3957
| 2029-09-01 | 14:18 | 51480 | 290.698 | 1.7442 | 383.2278 |  | 2029-09-01 | 14:18 | 51480 | 38.0674 | 0.2284 | 260.267 |  | 2006-09-01 | 14:18 | 51480 | 22.9161 | 0.1375 | 237.8954 |  | 2029-09-01 | 14:18 | 51480 | 26.641 | 0.15985 | 172.4372 |  | 2006-09-01 | 14:18 | 51480 | 19.1195 | 0.11472 | 122.6798 |  | 2028-01-01 | 14:18 | 51480 | 94.8129 | 0.56888 | 263.5808 |  | 2007-01-01 | 14:18 | 51480 | 22.4324 | 0.13459 | 240.1842 |  | 2028-01-01 | 14:18 | 51480 | 37.9453 | 0.22767 | 96.7991 |  | 2007-01-01 | 14:18 | 51480 | 18.1842 | 0.10911 | 99.7457 |  | 2029-09-01 | 14:18 | 51480 | 23.1656 | 0.13899 | 251.4956 |  | 2006-09-01 | 14:18 | 51480 | 19.3808 | 0.11628 | 235.878 |  | 2029-09-01 | 14:18 | 51480 | 17.9695 | 0.10782 | 126.6833 |  | 2006-09-01 | 14:18 | 51480 | 16.3771 | 0.098263 | 80.4515 |  | 2028-01-01 | 14:18 | 51480 | 47.963 | 0.28778 | 251.1118 |  | 2007-01-01 | 14:18 | 51480 | 19.3252 | 0.11595 | 238.9777 |  | 2028-01-01 | 14:18 | 51480 | 19.2159 | 0.1153 | 57.6969 |  | 2007-01-01 | 14:18 | 51480 | 15.6143 | 0.093686 | 61.6443 |  | 2029-09-01 | 14:18 | 51480 | 20.7816 | 0.12469 | 249.7657 |  | 2006-09-01 | 14:18 | 51480 | 19.0971 | 0.11458 | 235.6817 |  | 2029-09-01 | 14:18 | 51480 | 16.2545 | 0.097527 | 101.147 |  | 2006-09-01 | 14:18 | 51480 | 15.1959 | 0.091175 | 59.6249 |  | 2028-01-01 | 14:18 | 51480 | 31.1605 | 0.18696 | 248.1333 |  | 2007-01-01 | 14:18 | 51480 | 19.0993 | 0.1146 | 238.889 |  | 2028-01-01 | 14:18 | 51480 | 14.9323 | 0.089594 | 41.1026 |  | 2007-01-01 | 14:18 | 51480 | 14.2283 | 0.08537 | 44.4544 |  | 2029-09-01 | 14:18 | 51480 | 48.9888 | 0.29393 | 114.4822 |  | 2029-09-01 | 14:18 | 51480 | 28.0946 | 0.16857 | 78.884 |  | 2029-09-01 | 14:18 | 51480 | 18.3951 | 0.11037 | 54.2686 |  | 2006-09-01 | 14:18 | 51480 | 18.18 | 0.10908 | 53.426 |  | 2028-01-01 | 14:18 | 51480 | 37.9453 | 0.22767 | 96.7991 |  | 2007-01-01 | 14:18 | 51480 | 18.1842 | 0.10911 | 99.7457 |  | 2028-01-01 | 14:18 | 51480 | 16.7396 | 0.10044 | 48.4844 |  | 2007-01-01 | 14:18 | 51480 | 14.758 | 0.088548 | 49.4842
| 2029-09-01 | 14:19 | 51540 | 293.073 | 1.7584 | 384.9862 |  | 2029-09-01 | 14:19 | 51540 | 43.9785 | 0.26387 | 260.5308 |  | 2006-09-01 | 14:19 | 51540 | 28.9778 | 0.17387 | 238.0693 |  | 2029-09-01 | 14:19 | 51540 | 31.7058 | 0.19023 | 172.6274 |  | 2006-09-01 | 14:19 | 51540 | 24.2596 | 0.14556 | 122.8254 |  | 2028-01-01 | 14:19 | 51540 | 100.067 | 0.6004 | 264.1812 |  | 2007-01-01 | 14:19 | 51540 | 28.5191 | 0.17111 | 240.3553 |  | 2028-01-01 | 14:19 | 51540 | 41.4831 | 0.2489 | 97.048 |  | 2007-01-01 | 14:19 | 51540 | 23.0931 | 0.13856 | 99.8843 |  | 2029-09-01 | 14:19 | 51540 | 29.2853 | 0.17571 | 251.6713 |  | 2006-09-01 | 14:19 | 51540 | 25.4994 | 0.153 | 236.031 |  | 2029-09-01 | 14:19 | 51540 | 22.7234 | 0.13634 | 126.8196 |  | 2006-09-01 | 14:19 | 51540 | 20.8577 | 0.12515 | 80.5767 |  | 2028-01-01 | 14:19 | 51540 | 53.8134 | 0.32288 | 251.4346 |  | 2007-01-01 | 14:19 | 51540 | 25.4608 | 0.15276 | 239.1304 |  | 2028-01-01 | 14:19 | 51540 | 22.7639 | 0.13658 | 57.8335 |  | 2007-01-01 | 14:19 | 51540 | 19.687 | 0.11812 | 61.7624 |  | 2029-09-01 | 14:19 | 51540 | 26.9347 | 0.16161 | 249.9273 |  | 2006-09-01 | 14:19 | 51540 | 25.2203 | 0.15132 | 235.833 |  | 2029-09-01 | 14:19 | 51540 | 20.5234 | 0.12314 | 101.2701 |  | 2006-09-01 | 14:19 | 51540 | 19.0706 | 0.11442 | 59.7393 |  | 2028-01-01 | 14:19 | 51540 | 37.2247 | 0.22335 | 248.3566 |  | 2007-01-01 | 14:19 | 51540 | 25.2384 | 0.15143 | 239.0405 |  | 2028-01-01 | 14:19 | 51540 | 18.0359 | 0.10822 | 41.2108 |  | 2007-01-01 | 14:19 | 51540 | 17.5987 | 0.10559 | 44.56 |  | 2029-09-01 | 14:19 | 51540 | 52.1358 | 0.31281 | 114.795 |  | 2029-09-01 | 14:19 | 51540 | 31.4935 | 0.18896 | 79.073 |  | 2029-09-01 | 14:19 | 51540 | 21.6715 | 0.13003 | 54.3986 |  | 2006-09-01 | 14:19 | 51540 | 21.4452 | 0.12867 | 53.5547 |  | 2028-01-01 | 14:19 | 51540 | 41.4831 | 0.2489 | 97.048 |  | 2007-01-01 | 14:19 | 51540 | 23.0931 | 0.13856 | 99.8843 |  | 2028-01-01 | 14:19 | 51540 | 19.9945 | 0.11997 | 48.6044 |  | 2007-01-01 | 14:19 | 51540 | 18.3189 | 0.10991 | 49.5941
| 2029-09-01 | 14:20 | 51600 | 295.416 | 1.7725 | 386.7587 |  | 2029-09-01 | 14:20 | 51600 | 49.8068 | 0.29884 | 260.8297 |  | 2006-09-01 | 14:20 | 51600 | 34.9413 | 0.20965 | 238.2789 |  | 2029-09-01 | 14:20 | 51600 | 36.5458 | 0.21927 | 172.8467 |  | 2006-09-01 | 14:20 | 51600 | 29.1208 | 0.17472 | 123.0001 |  | 2028-01-01 | 14:20 | 51600 | 105.256 | 0.63154 | 264.8127 |  | 2007-01-01 | 14:20 | 51600 | 34.5107 | 0.20706 | 240.5624 |  | 2028-01-01 | 14:20 | 51600 | 44.7803 | 0.26868 | 97.3166 |  | 2007-01-01 | 14:20 | 51600 | 27.6789 | 0.16607 | 100.0504 |  | 2029-09-01 | 14:20 | 51600 | 35.3194 | 0.21192 | 251.8832 |  | 2006-09-01 | 14:20 | 51600 | 31.519 | 0.18911 | 236.2201 |  | 2029-09-01 | 14:20 | 51600 | 27.1315 | 0.16279 | 126.9824 |  | 2006-09-01 | 14:20 | 51600 | 24.9381 | 0.14963 | 80.7263 |  | 2028-01-01 | 14:20 | 51600 | 59.5898 | 0.35754 | 251.7922 |  | 2007-01-01 | 14:20 | 51600 | 31.5004 | 0.189 | 239.3194 |  | 2028-01-01 | 14:20 | 51600 | 25.8976 | 0.15539 | 57.9889 |  | 2007-01-01 | 14:20 | 51600 | 23.3058 | 0.13983 | 61.9022 |  | 2029-09-01 | 14:20 | 51600 | 33.0016 | 0.19801 | 250.1253 |  | 2006-09-01 | 14:20 | 51600 | 31.2444 | 0.18747 | 236.0205 |  | 2029-09-01 | 14:20 | 51600 | 24.3675 | 0.14621 | 101.4163 |  | 2006-09-01 | 14:20 | 51600 | 22.4732 | 0.13484 | 59.8742 |  | 2028-01-01 | 14:20 | 51600 | 43.212 | 0.25927 | 248.6159 |  | 2007-01-01 | 14:20 | 51600 | 31.2815 | 0.18769 | 239.2282 |  | 2028-01-01 | 14:20 | 51600 | 20.6405 | 0.12384 | 41.3347 |  | 2007-01-01 | 14:20 | 51600 | 20.454 | 0.12272 | 44.6827 |  | 2029-09-01 | 14:20 | 51600 | 55.0907 | 0.33054 | 115.1255 |  | 2029-09-01 | 14:20 | 51600 | 34.5845 | 0.20751 | 79.2805 |  | 2029-09-01 | 14:20 | 51600 | 24.5195 | 0.14712 | 54.5457 |  | 2006-09-01 | 14:20 | 51600 | 24.2779 | 0.14567 | 53.7004 |  | 2028-01-01 | 14:20 | 51600 | 44.7803 | 0.26868 | 97.3166 |  | 2007-01-01 | 14:20 | 51600 | 27.6789 | 0.16607 | 100.0504 |  | 2028-01-01 | 14:20 | 51600 | 22.7889 | 0.13673 | 48.7411 |  | 2007-01-01 | 14:20 | 51600 | 21.3821 | 0.12829 | 49.7224
| 2029-09-01 | 14:21 | 51660 | 297.726 | 1.7864 | 388.5451 |  | 2029-09-01 | 14:21 | 51660 | 55.5536 | 0.33332 | 261.163 |  | 2006-09-01 | 14:21 | 51660 | 40.8081 | 0.24485 | 238.5238 |  | 2029-09-01 | 14:21 | 51660 | 41.1709 | 0.24703 | 173.0937 |  | 2006-09-01 | 14:21 | 51660 | 33.7185 | 0.20231 | 123.2024 |  | 2028-01-01 | 14:21 | 51660 | 110.379 | 0.66227 | 265.475 |  | 2007-01-01 | 14:21 | 51660 | 40.4089 | 0.24245 | 240.8049 |  | 2028-01-01 | 14:21 | 51660 | 47.8527 | 0.28712 | 97.6038 |  | 2007-01-01 | 14:21 | 51660 | 31.9632 | 0.19178 | 100.2422 |  | 2029-09-01 | 14:21 | 51660 | 41.269 | 0.24761 | 252.1309 |  | 2006-09-01 | 14:21 | 51660 | 37.441 | 0.22465 | 236.4448 |  | 2029-09-01 | 14:21 | 51660 | 31.2189 | 0.18731 | 127.1697 |  | 2006-09-01 | 14:21 | 51660 | 28.6547 | 0.17193 | 80.8982 |  | 2028-01-01 | 14:21 | 51660 | 65.2932 | 0.39176 | 252.1839 |  | 2007-01-01 | 14:21 | 51660 | 37.4457 | 0.22467 | 239.5441 |  | 2028-01-01 | 14:21 | 51660 | 28.6647 | 0.17199 | 58.1609 |  | 2007-01-01 | 14:21 | 51660 | 26.5215 | 0.15913 | 62.0613 |  | 2029-09-01 | 14:21 | 51660 | 38.9837 | 0.2339 | 250.3592 |  | 2006-09-01 | 14:21 | 51660 | 37.1708 | 0.22302 | 236.2435 |  | 2029-09-01 | 14:21 | 51660 | 27.8291 | 0.16697 | 101.5833 |  | 2006-09-01 | 14:21 | 51660 | 25.4622 | 0.15277 | 60.027 |  | 2028-01-01 | 14:21 | 51660 | 49.1234 | 0.29474 | 248.9106 |  | 2007-01-01 | 14:21 | 51660 | 37.2302 | 0.22338 | 239.4515 |  | 2028-01-01 | 14:21 | 51660 | 22.8256 | 0.13695 | 41.4716 |  | 2007-01-01 | 14:21 | 51660 | 22.8725 | 0.13723 | 44.82 |  | 2029-09-01 | 14:21 | 51660 | 57.8653 | 0.34719 | 115.4727 |  | 2029-09-01 | 14:21 | 51660 | 37.3956 | 0.22437 | 79.5049 |  | 2029-09-01 | 14:21 | 51660 | 26.9951 | 0.16197 | 54.7077 |  | 2006-09-01 | 14:21 | 51660 | 26.7354 | 0.16041 | 53.8608 |  | 2028-01-01 | 14:21 | 51660 | 47.8527 | 0.28712 | 97.6038 |  | 2007-01-01 | 14:21 | 51660 | 31.9632 | 0.19178 | 100.2422 |  | 2028-01-01 | 14:21 | 51660 | 25.1876 | 0.15113 | 48.8922 |  | 2007-01-01 | 14:21 | 51660 | 24.0177 | 0.14411 | 49.8665
| 2029-09-01 | 14:22 | 51720 | 300.003 | 1.8 | 390.3451 |  | 2029-09-01 | 14:22 | 51720 | 61.2199 | 0.36732 | 261.5303 |  | 2006-09-01 | 14:22 | 51720 | 46.5794 | 0.27948 | 238.8032 |  | 2029-09-01 | 14:22 | 51720 | 45.5905 | 0.27354 | 173.3673 |  | 2006-09-01 | 14:22 | 51720 | 38.0674 | 0.2284 | 123.4308 |  | 2028-01-01 | 14:22 | 51720 | 115.438 | 0.69263 | 266.1676 |  | 2007-01-01 | 14:22 | 51720 | 46.2152 | 0.27729 | 241.0821 |  | 2028-01-01 | 14:22 | 51720 | 50.7155 | 0.30429 | 97.9081 |  | 2007-01-01 | 14:22 | 51720 | 35.9663 | 0.2158 | 100.458 |  | 2029-09-01 | 14:22 | 51720 | 47.1353 | 0.28281 | 252.4137 |  | 2006-09-01 | 14:22 | 51720 | 43.2668 | 0.2596 | 236.7044 |  | 2029-09-01 | 14:22 | 51720 | 35.0088 | 0.21005 | 127.3798 |  | 2006-09-01 | 14:22 | 51720 | 32.0406 | 0.19224 | 81.0905 |  | 2028-01-01 | 14:22 | 51720 | 70.9245 | 0.42555 | 252.6095 |  | 2007-01-01 | 14:22 | 51720 | 43.2985 | 0.25979 | 239.8039 |  | 2028-01-01 | 14:22 | 51720 | 31.1077 | 0.18665 | 58.3475 |  | 2007-01-01 | 14:22 | 51720 | 29.3789 | 0.17627 | 62.2376 |  | 2029-09-01 | 14:22 | 51720 | 44.882 | 0.26929 | 250.6285 |  | 2006-09-01 | 14:22 | 51720 | 43.0009 | 0.25801 | 236.5015 |  | 2029-09-01 | 14:22 | 51720 | 30.9461 | 0.18568 | 101.769 |  | 2006-09-01 | 14:22 | 51720 | 28.0888 | 0.16853 | 60.1955 |  | 2028-01-01 | 14:22 | 51720 | 54.9601 | 0.32976 | 249.2404 |  | 2007-01-01 | 14:22 | 51720 | 43.0864 | 0.25852 | 239.7101 |  | 2028-01-01 | 14:22 | 51720 | 24.6581 | 0.14795 | 41.6196 |  | 2007-01-01 | 14:22 | 51720 | 24.9209 | 0.14953 | 44.9695 |  | 2029-09-01 | 14:22 | 51720 | 60.4706 | 0.36282 | 115.8355 |  | 2029-09-01 | 14:22 | 51720 | 39.952 | 0.23971 | 79.7446 |  | 2029-09-01 | 14:22 | 51720 | 29.1472 | 0.17488 | 54.8826 |  | 2006-09-01 | 14:22 | 51720 | 28.8673 | 0.1732 | 54.034 |  | 2028-01-01 | 14:22 | 51720 | 50.7155 | 0.30429 | 97.9081 |  | 2007-01-01 | 14:22 | 51720 | 35.9663 | 0.2158 | 100.458 |  | 2028-01-01 | 14:22 | 51720 | 27.2465 | 0.16348 | 49.0557 |  | 2007-01-01 | 14:22 | 51720 | 26.2855 | 0.15771 | 50.0243
| 2029-09-01 | 14:23 | 51780 | 302.249 | 1.8135 | 392.1586 |  | 2029-09-01 | 14:23 | 51780 | 66.8069 | 0.40084 | 261.9311 |  | 2006-09-01 | 14:23 | 51780 | 52.2568 | 0.31354 | 239.1168 |  | 2029-09-01 | 14:23 | 51780 | 49.8138 | 0.29888 | 173.6661 |  | 2006-09-01 | 14:23 | 51780 | 42.1813 | 0.25309 | 123.6839 |  | 2028-01-01 | 14:23 | 51780 | 120.433 | 0.7226 | 266.8902 |  | 2007-01-01 | 14:23 | 51780 | 51.9313 | 0.31159 | 241.3937 |  | 2028-01-01 | 14:23 | 51780 | 53.3826 | 0.3203 | 98.2283 |  | 2007-01-01 | 14:23 | 51780 | 39.7073 | 0.23824 | 100.6962 |  | 2029-09-01 | 14:23 | 51780 | 52.9195 | 0.31752 | 252.7312 |  | 2006-09-01 | 14:23 | 51780 | 48.9977 | 0.29399 | 236.9984 |  | 2029-09-01 | 14:23 | 51780 | 38.5227 | 0.23114 | 127.6109 |  | 2006-09-01 | 14:23 | 51780 | 35.1259 | 0.21076 | 81.3012 |  | 2028-01-01 | 14:23 | 51780 | 76.4848 | 0.45891 | 253.0684 |  | 2007-01-01 | 14:23 | 51780 | 49.0602 | 0.29436 | 240.0983 |  | 2028-01-01 | 14:23 | 51780 | 33.264 | 0.19958 | 58.5471 |  | 2007-01-01 | 14:23 | 51780 | 31.9181 | 0.19151 | 62.4291 |  | 2029-09-01 | 14:23 | 51780 | 50.6977 | 0.30419 | 250.9327 |  | 2006-09-01 | 14:23 | 51780 | 48.7362 | 0.29242 | 236.7939 |  | 2029-09-01 | 14:23 | 51780 | 33.7528 | 0.20252 | 101.9715 |  | 2006-09-01 | 14:23 | 51780 | 30.3977 | 0.18239 | 60.3779 |  | 2028-01-01 | 14:23 | 51780 | 60.7231 | 0.36434 | 249.6047 |  | 2007-01-01 | 14:23 | 51780 | 48.8515 | 0.29311 | 240.0032 |  | 2028-01-01 | 14:23 | 51780 | 26.1942 | 0.15717 | 41.7768 |  | 2007-01-01 | 14:23 | 51780 | 26.6558 | 0.15993 | 45.1294 |  | 2029-09-01 | 14:23 | 51780 | 62.9169 | 0.3775 | 116.213 |  | 2029-09-01 | 14:23 | 51780 | 42.277 | 0.25366 | 79.9983 |  | 2029-09-01 | 14:23 | 51780 | 31.0179 | 0.18611 | 55.0687 |  | 2006-09-01 | 14:23 | 51780 | 30.7165 | 0.1843 | 54.2183 |  | 2028-01-01 | 14:23 | 51780 | 53.3826 | 0.3203 | 98.2283 |  | 2007-01-01 | 14:23 | 51780 | 39.7073 | 0.23824 | 100.6962 |  | 2028-01-01 | 14:23 | 51780 | 29.0133 | 0.17408 | 49.2298 |  | 2007-01-01 | 14:23 | 51780 | 28.2373 | 0.16942 | 50.1937
| 2029-09-01 | 14:24 | 51840 | 304.464 | 1.8268 | 393.9854 |  | 2029-09-01 | 14:24 | 51840 | 72.3158 | 0.43389 | 262.365 |  | 2006-09-01 | 14:24 | 51840 | 57.8415 | 0.34705 | 239.4638 |  | 2029-09-01 | 14:24 | 51840 | 53.8492 | 0.3231 | 173.9892 |  | 2006-09-01 | 14:24 | 51840 | 46.073 | 0.27644 | 123.9604 |  | 2028-01-01 | 14:24 | 51840 | 125.365 | 0.75219 | 267.6424 |  | 2007-01-01 | 14:24 | 51840 | 57.5589 | 0.34535 | 241.7391 |  | 2028-01-01 | 14:24 | 51840 | 55.867 | 0.3352 | 98.5635 |  | 2007-01-01 | 14:24 | 51840 | 43.2037 | 0.25922 | 100.9554 |  | 2029-09-01 | 14:24 | 51840 | 58.6228 | 0.35174 | 253.0829 |  | 2006-09-01 | 14:24 | 51840 | 54.6351 | 0.32781 | 237.3262 |  | 2029-09-01 | 14:24 | 51840 | 41.7808 | 0.25068 | 127.8616 |  | 2006-09-01 | 14:24 | 51840 | 37.9379 | 0.22763 | 81.5288 |  | 2028-01-01 | 14:24 | 51840 | 81.9751 | 0.49185 | 253.5602 |  | 2007-01-01 | 14:24 | 51840 | 54.7327 | 0.3284 | 240.4267 |  | 2028-01-01 | 14:24 | 51840 | 35.1668 | 0.211 | 58.7581 |  | 2007-01-01 | 14:24 | 51840 | 34.1747 | 0.20505 | 62.6342 |  | 2029-09-01 | 14:24 | 51840 | 56.4321 | 0.33859 | 251.2713 |  | 2006-09-01 | 14:24 | 51840 | 54.3778 | 0.32627 | 237.1202 |  | 2029-09-01 | 14:24 | 51840 | 36.28 | 0.21768 | 102.1892 |  | 2006-09-01 | 14:24 | 51840 | 32.4283 | 0.19457 | 60.5724 |  | 2028-01-01 | 14:24 | 51840 | 66.4134 | 0.39848 | 250.0032 |  | 2007-01-01 | 14:24 | 51840 | 54.5272 | 0.32716 | 240.3303 |  | 2028-01-01 | 14:24 | 51840 | 27.4813 | 0.16489 | 41.9416 |  | 2007-01-01 | 14:24 | 51840 | 28.1249 | 0.16875 | 45.2982 |  | 2029-09-01 | 14:24 | 51840 | 65.2139 | 0.39128 | 116.6043 |  | 2029-09-01 | 14:24 | 51840 | 44.3913 | 0.26635 | 80.2646 |  | 2029-09-01 | 14:24 | 51840 | 32.644 | 0.19586 | 55.2645 |  | 2006-09-01 | 14:24 | 51840 | 32.3205 | 0.19392 | 54.4122 |  | 2028-01-01 | 14:24 | 51840 | 55.867 | 0.3352 | 98.5635 |  | 2007-01-01 | 14:24 | 51840 | 43.2037 | 0.25922 | 100.9554 |  | 2028-01-01 | 14:24 | 51840 | 30.5294 | 0.18318 | 49.413 |  | 2007-01-01 | 14:24 | 51840 | 29.9174 | 0.1795 | 50.3732
| 2029-09-01 | 14:25 | 51900 | 306.647 | 1.8399 | 395.8253 |  | 2029-09-01 | 14:25 | 51900 | 77.7476 | 0.46649 | 262.8315 |  | 2006-09-01 | 14:25 | 51900 | 63.3349 | 0.38001 | 239.8438 |  | 2029-09-01 | 14:25 | 51900 | 57.7052 | 0.34623 | 174.3355 |  | 2006-09-01 | 14:25 | 51900 | 49.7549 | 0.29853 | 124.2589 |  | 2028-01-01 | 14:25 | 51900 | 130.237 | 0.78142 | 268.4238 |  | 2007-01-01 | 14:25 | 51900 | 63.0996 | 0.3786 | 242.1177 |  | 2028-01-01 | 14:25 | 51900 | 58.181 | 0.34909 | 98.9126 |  | 2007-01-01 | 14:25 | 51900 | 46.4721 | 0.27883 | 101.2343 |  | 2029-09-01 | 14:25 | 51900 | 64.2462 | 0.38548 | 253.4684 |  | 2006-09-01 | 14:25 | 51900 | 60.1805 | 0.36108 | 237.6873 |  | 2029-09-01 | 14:25 | 51900 | 44.8016 | 0.26881 | 128.1304 |  | 2006-09-01 | 14:25 | 51900 | 40.5014 | 0.24301 | 81.7719 |  | 2028-01-01 | 14:25 | 51900 | 87.3963 | 0.52438 | 254.0846 |  | 2007-01-01 | 14:25 | 51900 | 60.3176 | 0.36191 | 240.7886 |  | 2028-01-01 | 14:25 | 51900 | 36.8452 | 0.22107 | 58.9792 |  | 2007-01-01 | 14:25 | 51900 | 36.1803 | 0.21708 | 62.8513 |  | 2029-09-01 | 14:25 | 51900 | 62.0862 | 0.37252 | 251.6438 |  | 2006-09-01 | 14:25 | 51900 | 59.9273 | 0.35956 | 237.4797 |  | 2029-09-01 | 14:25 | 51900 | 38.5556 | 0.23133 | 102.4205 |  | 2006-09-01 | 14:25 | 51900 | 34.2149 | 0.20529 | 60.7777 |  | 2028-01-01 | 14:25 | 51900 | 72.032 | 0.43219 | 250.4354 |  | 2007-01-01 | 14:25 | 51900 | 60.1153 | 0.36069 | 240.691 |  | 2028-01-01 | 14:25 | 51900 | 28.5592 | 0.17136 | 42.113 |  | 2007-01-01 | 14:25 | 51900 | 29.3689 | 0.17621 | 45.4744 |  | 2029-09-01 | 14:25 | 51900 | 67.3708 | 0.40422 | 117.0085 |  | 2029-09-01 | 14:25 | 51900 | 46.3142 | 0.27789 | 80.5425 |  | 2029-09-01 | 14:25 | 51900 | 34.0576 | 0.20435 | 55.4689 |  | 2006-09-01 | 14:25 | 51900 | 33.7116 | 0.20227 | 54.6145 |  | 2028-01-01 | 14:25 | 51900 | 58.181 | 0.34909 | 98.9126 |  | 2007-01-01 | 14:25 | 51900 | 46.4721 | 0.27883 | 101.2343 |  | 2028-01-01 | 14:25 | 51900 | 31.83 | 0.19098 | 49.6039 |  | 2007-01-01 | 14:25 | 51900 | 31.3641 | 0.18818 | 50.5614
| 2029-09-01 | 14:26 | 51960 | 308.801 | 1.8528 | 397.6781 |  | 2029-09-01 | 14:26 | 51960 | 83.1033 | 0.49862 | 263.3301 |  | 2006-09-01 | 14:26 | 51960 | 68.7383 | 0.41243 | 240.2563 |  | 2029-09-01 | 14:26 | 51960 | 61.3897 | 0.36834 | 174.7038 |  | 2006-09-01 | 14:26 | 51960 | 53.2386 | 0.31943 | 124.5783 |  | 2028-01-01 | 14:26 | 51960 | 135.047 | 0.81028 | 269.2341 |  | 2007-01-01 | 14:26 | 51960 | 68.5551 | 0.41133 | 242.529 |  | 2028-01-01 | 14:26 | 51960 | 60.3359 | 0.36202 | 99.2747 |  | 2007-01-01 | 14:26 | 51960 | 49.528 | 0.29717 | 101.5314 |  | 2029-09-01 | 14:26 | 51960 | 69.791 | 0.41875 | 253.8871 |  | 2006-09-01 | 14:26 | 51960 | 65.635 | 0.39381 | 238.0811 |  | 2029-09-01 | 14:26 | 51960 | 47.6022 | 0.28561 | 128.416 |  | 2006-09-01 | 14:26 | 51960 | 42.8389 | 0.25703 | 82.0289 |  | 2028-01-01 | 14:26 | 51960 | 92.7495 | 0.5565 | 254.6411 |  | 2007-01-01 | 14:26 | 51960 | 65.8165 | 0.3949 | 241.1835 |  | 2028-01-01 | 14:26 | 51960 | 38.3254 | 0.22995 | 59.2092 |  | 2007-01-01 | 14:26 | 51960 | 37.9629 | 0.22778 | 63.079 |  | 2029-09-01 | 14:26 | 51960 | 67.6612 | 0.40597 | 252.0498 |  | 2006-09-01 | 14:26 | 51960 | 65.3859 | 0.39232 | 237.8721 |  | 2029-09-01 | 14:26 | 51960 | 40.6044 | 0.24363 | 102.6641 |  | 2006-09-01 | 14:26 | 51960 | 35.7877 | 0.21473 | 60.9925 |  | 2028-01-01 | 14:26 | 51960 | 77.5798 | 0.46548 | 250.9009 |  | 2007-01-01 | 14:26 | 51960 | 65.6173 | 0.3937 | 241.0847 |  | 2028-01-01 | 14:26 | 51960 | 29.4612 | 0.17677 | 42.2898 |  | 2007-01-01 | 14:26 | 51960 | 30.4223 | 0.18253 | 45.6569 |  | 2029-09-01 | 14:26 | 51960 | 69.3961 | 0.41638 | 117.4249 |  | 2029-09-01 | 14:26 | 51960 | 48.063 | 0.28838 | 80.8309 |  | 2029-09-01 | 14:26 | 51960 | 35.2864 | 0.21172 | 55.6806 |  | 2006-09-01 | 14:26 | 51960 | 34.9181 | 0.20951 | 54.824 |  | 2028-01-01 | 14:26 | 51960 | 60.3359 | 0.36202 | 99.2747 |  | 2007-01-01 | 14:26 | 51960 | 49.528 | 0.29717 | 101.5314 |  | 2028-01-01 | 14:26 | 51960 | 32.9455 | 0.19767 | 49.8016 |  | 2007-01-01 | 14:26 | 51960 | 32.6102 | 0.19566 | 50.757
| 2029-09-01 | 14:27 | 52020 | 310.924 | 1.8655 | 399.5436 |  | 2029-09-01 | 14:27 | 52020 | 88.3842 | 0.53031 | 263.8605 |  | 2006-09-01 | 14:27 | 52020 | 74.0529 | 0.44432 | 240.7006 |  | 2029-09-01 | 14:27 | 52020 | 64.9101 | 0.38946 | 175.0933 |  | 2006-09-01 | 14:27 | 52020 | 56.5351 | 0.33921 | 124.9175 |  | 2028-01-01 | 14:27 | 52020 | 139.797 | 0.83878 | 270.0729 |  | 2007-01-01 | 14:27 | 52020 | 73.9273 | 0.44356 | 242.9726 |  | 2028-01-01 | 14:27 | 52020 | 62.3424 | 0.37405 | 99.6487 |  | 2007-01-01 | 14:27 | 52020 | 52.3859 | 0.31432 | 101.8457 |  | 2029-09-01 | 14:27 | 52020 | 75.2582 | 0.45155 | 254.3387 |  | 2006-09-01 | 14:27 | 52020 | 71 | 0.426 | 238.5071 |  | 2029-09-01 | 14:27 | 52020 | 50.1988 | 0.30119 | 128.7172 |  | 2006-09-01 | 14:27 | 52020 | 44.9709 | 0.26983 | 82.2987 |  | 2028-01-01 | 14:27 | 52020 | 98.0355 | 0.58821 | 255.2293 |  | 2007-01-01 | 14:27 | 52020 | 71.2313 | 0.42739 | 241.6109 |  | 2028-01-01 | 14:27 | 52020 | 39.6303 | 0.23778 | 59.4469 |  | 2007-01-01 | 14:27 | 52020 | 39.5477 | 0.23729 | 63.3163 |  | 2029-09-01 | 14:27 | 52020 | 73.1583 | 0.43895 | 252.4888 |  | 2006-09-01 | 14:27 | 52020 | 70.755 | 0.42453 | 238.2966 |  | 2029-09-01 | 14:27 | 52020 | 42.4491 | 0.25469 | 102.9188 |  | 2006-09-01 | 14:27 | 52020 | 37.1729 | 0.22304 | 61.2155 |  | 2028-01-01 | 14:27 | 52020 | 83.058 | 0.49835 | 251.3992 |  | 2007-01-01 | 14:27 | 52020 | 71.0352 | 0.42621 | 241.5109 |  | 2028-01-01 | 14:27 | 52020 | 30.2155 | 0.18129 | 42.4711 |  | 2007-01-01 | 14:27 | 52020 | 31.3142 | 0.18789 | 45.8448 |  | 2029-09-01 | 14:27 | 52020 | 71.2979 | 0.42779 | 117.8527 |  | 2029-09-01 | 14:27 | 52020 | 49.6534 | 0.29792 | 81.1288 |  | 2029-09-01 | 14:27 | 52020 | 36.3546 | 0.21813 | 55.8987 |  | 2006-09-01 | 14:27 | 52020 | 35.9644 | 0.21579 | 55.0398 |  | 2028-01-01 | 14:27 | 52020 | 62.3424 | 0.37405 | 99.6487 |  | 2007-01-01 | 14:27 | 52020 | 52.3859 | 0.31432 | 101.8457 |  | 2028-01-01 | 14:27 | 52020 | 33.9021 | 0.20341 | 50.005 |  | 2007-01-01 | 14:27 | 52020 | 33.6839 | 0.2021 | 50.9591
| 2029-09-01 | 14:28 | 52080 | 313.018 | 1.8781 | 401.4217 |  | 2029-09-01 | 14:28 | 52080 | 93.5912 | 0.56155 | 264.422 |  | 2006-09-01 | 14:28 | 52080 | 79.2802 | 0.47568 | 241.1763 |  | 2029-09-01 | 14:28 | 52080 | 68.2738 | 0.40964 | 175.5029 |  | 2006-09-01 | 14:28 | 52080 | 59.6546 | 0.35793 | 125.2755 |  | 2028-01-01 | 14:28 | 52080 | 144.488 | 0.86693 | 270.9398 |  | 2007-01-01 | 14:28 | 52080 | 79.217 | 0.4753 | 243.4479 |  | 2028-01-01 | 14:28 | 52080 | 64.2105 | 0.38526 | 100.034 |  | 2007-01-01 | 14:28 | 52080 | 55.0593 | 0.33036 | 102.1761 |  | 2029-09-01 | 14:28 | 52080 | 80.6489 | 0.48389 | 254.8226 |  | 2006-09-01 | 14:28 | 52080 | 76.2768 | 0.45766 | 238.9647 |  | 2029-09-01 | 14:28 | 52080 | 52.6061 | 0.31564 | 129.0328 |  | 2006-09-01 | 14:28 | 52080 | 46.916 | 0.2815 | 82.5802 |  | 2028-01-01 | 14:28 | 52080 | 103.255 | 0.61953 | 255.8489 |  | 2007-01-01 | 14:28 | 52080 | 76.5629 | 0.45938 | 242.0702 |  | 2028-01-01 | 14:28 | 52080 | 40.7802 | 0.24468 | 59.6916 |  | 2007-01-01 | 14:28 | 52080 | 40.9569 | 0.24574 | 63.5621 |  | 2029-09-01 | 14:28 | 52080 | 78.5784 | 0.47147 | 252.9602 |  | 2006-09-01 | 14:28 | 52080 | 76.0358 | 0.45621 | 238.7528 |  | 2029-09-01 | 14:28 | 52080 | 44.11 | 0.26466 | 103.1835 |  | 2006-09-01 | 14:28 | 52080 | 38.3937 | 0.23036 | 61.4459 |  | 2028-01-01 | 14:28 | 52080 | 88.4674 | 0.5308 | 251.93 |  | 2007-01-01 | 14:28 | 52080 | 76.3699 | 0.45822 | 241.9692 |  | 2028-01-01 | 14:28 | 52080 | 30.8457 | 0.18507 | 42.6561 |  | 2007-01-01 | 14:28 | 52080 | 32.0694 | 0.19242 | 46.0372 |  | 2029-09-01 | 14:28 | 52080 | 73.0836 | 0.4385 | 118.2912 |  | 2029-09-01 | 14:28 | 52080 | 51.0997 | 0.3066 | 81.4354 |  | 2029-09-01 | 14:28 | 52080 | 37.2832 | 0.2237 | 56.1224 |  | 2006-09-01 | 14:28 | 52080 | 36.8716 | 0.22123 | 55.261 |  | 2028-01-01 | 14:28 | 52080 | 64.2105 | 0.38526 | 100.034 |  | 2007-01-01 | 14:28 | 52080 | 55.0593 | 0.33036 | 102.1761 |  | 2028-01-01 | 14:28 | 52080 | 34.7222 | 0.20833 | 50.2134 |  | 2007-01-01 | 14:28 | 52080 | 34.6095 | 0.20766 | 51.1668
| 2029-09-01 | 14:29 | 52140 | 315.082 | 1.8905 | 403.3122 |  | 2029-09-01 | 14:29 | 52140 | 98.7254 | 0.59235 | 265.0144 |  | 2006-09-01 | 14:29 | 52140 | 84.4212 | 0.50653 | 241.6828 |  | 2029-09-01 | 14:29 | 52140 | 71.4877 | 0.42893 | 175.9318 |  | 2006-09-01 | 14:29 | 52140 | 62.6069 | 0.37564 | 125.6511 |  | 2028-01-01 | 14:29 | 52140 | 149.121 | 0.89473 | 271.8346 |  | 2007-01-01 | 14:29 | 52140 | 84.4233 | 0.50654 | 243.9544 |  | 2028-01-01 | 14:29 | 52140 | 65.9493 | 0.3957 | 100.4297 |  | 2007-01-01 | 14:29 | 52140 | 57.5612 | 0.34537 | 102.5215 |  | 2029-09-01 | 14:29 | 52140 | 85.9643 | 0.51579 | 255.3384 |  | 2006-09-01 | 14:29 | 52140 | 81.4667 | 0.4888 | 239.4535 |  | 2029-09-01 | 14:29 | 52140 | 54.8378 | 0.32903 | 129.3619 |  | 2006-09-01 | 14:29 | 52140 | 48.6913 | 0.29215 | 82.8724 |  | 2028-01-01 | 14:29 | 52140 | 108.41 | 0.65046 | 256.4993 |  | 2007-01-01 | 14:29 | 52140 | 81.8104 | 0.49086 | 242.5611 |  | 2028-01-01 | 14:29 | 52140 | 41.793 | 0.25076 | 59.9424 |  | 2007-01-01 | 14:29 | 52140 | 42.2105 | 0.25326 | 63.8153 |  | 2029-09-01 | 14:29 | 52140 | 83.9227 | 0.50354 | 253.4638 |  | 2006-09-01 | 14:29 | 52140 | 81.2296 | 0.48738 | 239.2402 |  | 2029-09-01 | 14:29 | 52140 | 45.6053 | 0.27363 | 103.4571 |  | 2006-09-01 | 14:29 | 52140 | 39.4704 | 0.23682 | 61.6827 |  | 2028-01-01 | 14:29 | 52140 | 93.809 | 0.56285 | 252.4929 |  | 2007-01-01 | 14:29 | 52140 | 81.6204 | 0.48972 | 242.4589 |  | 2028-01-01 | 14:29 | 52140 | 31.3716 | 0.18823 | 42.8444 |  | 2007-01-01 | 14:29 | 52140 | 32.7091 | 0.19625 | 46.2335 |  | 2029-09-01 | 14:29 | 52140 | 74.7605 | 0.44856 | 118.7398 |  | 2029-09-01 | 14:29 | 52140 | 52.4151 | 0.31449 | 81.7499 |  | 2029-09-01 | 14:29 | 52140 | 38.0904 | 0.22854 | 56.351 |  | 2006-09-01 | 14:29 | 52140 | 37.6581 | 0.22595 | 55.487 |  | 2028-01-01 | 14:29 | 52140 | 65.9493 | 0.3957 | 100.4297 |  | 2007-01-01 | 14:29 | 52140 | 57.5612 | 0.34537 | 102.5215 |  | 2028-01-01 | 14:29 | 52140 | 35.425 | 0.21255 | 50.4259 |  | 2007-01-01 | 14:29 | 52140 | 35.4082 | 0.21245 | 51.3792
| 2029-09-01 | 14:30 | 52200 | 317.118 | 1.9027 | 405.2149 |  | 2029-09-01 | 14:30 | 52200 | 103.788 | 0.62273 | 265.6371 |  | 2006-09-01 | 14:30 | 52200 | 89.4773 | 0.53686 | 242.2196 |  | 2029-09-01 | 14:30 | 52200 | 74.5583 | 0.44735 | 176.3792 |  | 2006-09-01 | 14:30 | 52200 | 65.4012 | 0.39241 | 126.0435 |  | 2028-01-01 | 14:30 | 52200 | 153.696 | 0.92218 | 272.7567 |  | 2007-01-01 | 14:30 | 52200 | 89.5472 | 0.53728 | 244.4917 |  | 2028-01-01 | 14:30 | 52200 | 67.5675 | 0.4054 | 100.8351 |  | 2007-01-01 | 14:30 | 52200 | 59.904 | 0.35942 | 102.8809 |  | 2029-09-01 | 14:30 | 52200 | 91.2053 | 0.54723 | 255.8856 |  | 2006-09-01 | 14:30 | 52200 | 86.5709 | 0.51943 | 239.973 |  | 2029-09-01 | 14:30 | 52200 | 56.9068 | 0.34144 | 129.7033 |  | 2006-09-01 | 14:30 | 52200 | 50.312 | 0.30187 | 83.1742 |  | 2028-01-01 | 14:30 | 52200 | 113.5 | 0.681 | 257.1803 |  | 2007-01-01 | 14:30 | 52200 | 86.9748 | 0.52185 | 243.0829 |  | 2028-01-01 | 14:30 | 52200 | 42.6846 | 0.25611 | 60.1985 |  | 2007-01-01 | 14:30 | 52200 | 43.3263 | 0.25996 | 64.0753 |  | 2029-09-01 | 14:30 | 52200 | 89.1923 | 0.53515 | 253.9989 |  | 2006-09-01 | 14:30 | 52200 | 86.3376 | 0.51803 | 239.7582 |  | 2029-09-01 | 14:30 | 52200 | 46.9515 | 0.28171 | 103.7388 |  | 2006-09-01 | 14:30 | 52200 | 40.4207 | 0.24252 | 61.9252 |  | 2028-01-01 | 14:30 | 52200 | 99.0837 | 0.5945 | 253.0874 |  | 2007-01-01 | 14:30 | 52200 | 86.7877 | 0.52073 | 242.9796 |  | 2028-01-01 | 14:30 | 52200 | 31.81 | 0.19086 | 43.0352 |  | 2007-01-01 | 14:30 | 52200 | 33.2512 | 0.19951 | 46.433 |  | 2029-09-01 | 14:30 | 52200 | 76.335 | 0.45801 | 119.1978 |  | 2029-09-01 | 14:30 | 52200 | 53.6115 | 0.32167 | 82.0715 |  | 2029-09-01 | 14:30 | 52200 | 38.7921 | 0.23275 | 56.5837 |  | 2006-09-01 | 14:30 | 52200 | 38.34 | 0.23004 | 55.717 |  | 2028-01-01 | 14:30 | 52200 | 67.5675 | 0.4054 | 100.8351 |  | 2007-01-01 | 14:30 | 52200 | 59.904 | 0.35942 | 102.8809 |  | 2028-01-01 | 14:30 | 52200 | 36.0271 | 0.21616 | 50.6421 |  | 2007-01-01 | 14:30 | 52200 | 36.0982 | 0.21659 | 51.5958
| 2029-09-01 | 14:31 | 52260 | 319.128 | 1.9148 | 407.1297 |  | 2029-09-01 | 14:31 | 52260 | 108.78 | 0.65268 | 266.2898 |  | 2006-09-01 | 14:31 | 52260 | 94.4498 | 0.5667 | 242.7863 |  | 2029-09-01 | 14:31 | 52260 | 77.4927 | 0.46496 | 176.8441 |  | 2006-09-01 | 14:31 | 52260 | 68.0463 | 0.40828 | 126.4518 |  | 2028-01-01 | 14:31 | 52260 | 158.215 | 0.94929 | 273.706 |  | 2007-01-01 | 14:31 | 52260 | 94.59 | 0.56754 | 245.0592 |  | 2028-01-01 | 14:31 | 52260 | 69.0732 | 0.41444 | 101.2495 |  | 2007-01-01 | 14:31 | 52260 | 62.1005 | 0.3726 | 103.2535 |  | 2029-09-01 | 14:31 | 52260 | 96.3736 | 0.57824 | 256.4639 |  | 2006-09-01 | 14:31 | 52260 | 91.5906 | 0.54954 | 240.5225 |  | 2029-09-01 | 14:31 | 52260 | 58.8252 | 0.35295 | 130.0563 |  | 2006-09-01 | 14:31 | 52260 | 51.792 | 0.31075 | 83.485 |  | 2028-01-01 | 14:31 | 52260 | 118.527 | 0.71116 | 257.8915 |  | 2007-01-01 | 14:31 | 52260 | 92.0573 | 0.55234 | 243.6353 |  | 2028-01-01 | 14:31 | 52260 | 43.4692 | 0.26082 | 60.4593 |  | 2007-01-01 | 14:31 | 52260 | 44.322 | 0.26593 | 64.3412 |  | 2029-09-01 | 14:31 | 52260 | 94.3887 | 0.56633 | 254.5652 |  | 2006-09-01 | 14:31 | 52260 | 91.3612 | 0.54817 | 240.3064 |  | 2029-09-01 | 14:31 | 52260 | 48.1637 | 0.28898 | 104.0278 |  | 2006-09-01 | 14:31 | 52260 | 41.2601 | 0.24756 | 62.1728 |  | 2028-01-01 | 14:31 | 52260 | 104.293 | 0.62576 | 253.7132 |  | 2007-01-01 | 14:31 | 52260 | 91.8731 | 0.55124 | 243.5309 |  | 2028-01-01 | 14:31 | 52260 | 32.1749 | 0.19305 | 43.2283 |  | 2007-01-01 | 14:31 | 52260 | 33.7122 | 0.20227 | 46.6353 |  | 2029-09-01 | 14:31 | 52260 | 77.8139 | 0.46688 | 119.6647 |  | 2029-09-01 | 14:31 | 52260 | 54.6997 | 0.3282 | 82.3997 |  | 2029-09-01 | 14:31 | 52260 | 39.4023 | 0.23641 | 56.8201 |  | 2006-09-01 | 14:31 | 52260 | 38.931 | 0.23359 | 55.9506 |  | 2028-01-01 | 14:31 | 52260 | 69.0732 | 0.41444 | 101.2495 |  | 2007-01-01 | 14:31 | 52260 | 62.1005 | 0.3726 | 103.2535 |  | 2028-01-01 | 14:31 | 52260 | 36.5428 | 0.21926 | 50.8613 |  | 2007-01-01 | 14:31 | 52260 | 36.6959 | 0.22018 | 51.816
| 2029-09-01 | 14:32 | 52320 | 321.111 | 1.9267 | 409.0564 |  | 2029-09-01 | 14:32 | 52320 | 113.703 | 0.68222 | 266.972 |  | 2006-09-01 | 14:32 | 52320 | 99.3397 | 0.59604 | 243.3824 |  | 2029-09-01 | 14:32 | 52320 | 80.2968 | 0.48178 | 177.3259 |  | 2006-09-01 | 14:32 | 52320 | 70.5504 | 0.4233 | 126.8751 |  | 2028-01-01 | 14:32 | 52320 | 162.678 | 0.97607 | 274.6821 |  | 2007-01-01 | 14:32 | 52320 | 99.5526 | 0.59732 | 245.6566 |  | 2028-01-01 | 14:32 | 52320 | 70.474 | 0.42284 | 101.6724 |  | 2007-01-01 | 14:32 | 52320 | 64.1493 | 0.3849 | 103.6384 |  | 2029-09-01 | 14:32 | 52320 | 101.47 | 0.60882 | 257.0727 |  | 2006-09-01 | 14:32 | 52320 | 96.5272 | 0.57916 | 241.1017 |  | 2029-09-01 | 14:32 | 52320 | 60.6041 | 0.36362 | 130.4199 |  | 2006-09-01 | 14:32 | 52320 | 53.1443 | 0.31887 | 83.8038 |  | 2028-01-01 | 14:32 | 52320 | 123.491 | 0.74095 | 258.6324 |  | 2007-01-01 | 14:32 | 52320 | 97.059 | 0.58235 | 244.2176 |  | 2028-01-01 | 14:32 | 52320 | 44.1591 | 0.26495 | 60.7243 |  | 2007-01-01 | 14:32 | 52320 | 45.202 | 0.27121 | 64.6124 |  | 2029-09-01 | 14:32 | 52320 | 99.5131 | 0.59708 | 255.1623 |  | 2006-09-01 | 14:32 | 52320 | 96.3015 | 0.57781 | 240.8842 |  | 2029-09-01 | 14:32 | 52320 | 49.2554 | 0.29553 | 104.3233 |  | 2006-09-01 | 14:32 | 52320 | 42.0023 | 0.25201 | 62.4248 |  | 2028-01-01 | 14:32 | 52320 | 109.437 | 0.65662 | 254.3698 |  | 2007-01-01 | 14:32 | 52320 | 96.8777 | 0.58127 | 244.1121 |  | 2028-01-01 | 14:32 | 52320 | 32.4781 | 0.19487 | 43.4231 |  | 2007-01-01 | 14:32 | 52320 | 34.0984 | 0.20459 | 46.8399 |  | 2029-09-01 | 14:32 | 52320 | 79.203 | 0.47522 | 120.1399 |  | 2029-09-01 | 14:32 | 52320 | 55.6897 | 0.33414 | 82.7339 |  | 2029-09-01 | 14:32 | 52320 | 39.9329 | 0.2396 | 57.0597 |  | 2006-09-01 | 14:32 | 52320 | 39.4432 | 0.23666 | 56.1873 |  | 2028-01-01 | 14:32 | 52320 | 70.474 | 0.42284 | 101.6724 |  | 2007-01-01 | 14:32 | 52320 | 64.1493 | 0.3849 | 103.6384 |  | 2028-01-01 | 14:32 | 52320 | 36.9842 | 0.22191 | 51.0832 |  | 2007-01-01 | 14:32 | 52320 | 37.208 | 0.22325 | 52.0393
| 2029-09-01 | 14:33 | 52380 | 323.068 | 1.9384 | 410.9948 |  | 2029-09-01 | 14:33 | 52380 | 118.558 | 0.71135 | 267.6833 |  | 2006-09-01 | 14:33 | 52380 | 104.148 | 0.62489 | 244.0073 |  | 2029-09-01 | 14:33 | 52380 | 82.9765 | 0.49786 | 177.8238 |  | 2006-09-01 | 14:33 | 52380 | 72.9213 | 0.43753 | 127.3126 |  | 2028-01-01 | 14:33 | 52380 | 167.086 | 1.0025 | 275.6846 |  | 2007-01-01 | 14:33 | 52380 | 104.436 | 0.62662 | 246.2832 |  | 2028-01-01 | 14:33 | 52380 | 71.7769 | 0.43066 | 102.103 |  | 2007-01-01 | 14:33 | 52380 | 66.0615 | 0.39637 | 104.0348 |  | 2029-09-01 | 14:33 | 52380 | 106.496 | 0.63898 | 257.7116 |  | 2006-09-01 | 14:33 | 52380 | 101.382 | 0.60829 | 241.71 |  | 2029-09-01 | 14:33 | 52380 | 62.2536 | 0.37352 | 130.7934 |  | 2006-09-01 | 14:33 | 52380 | 54.3802 | 0.32628 | 84.1301 |  | 2028-01-01 | 14:33 | 52380 | 128.393 | 0.77036 | 259.4028 |  | 2007-01-01 | 14:33 | 52380 | 101.981 | 0.61189 | 244.8295 |  | 2028-01-01 | 14:33 | 52380 | 44.7653 | 0.26859 | 60.9928 |  | 2007-01-01 | 14:33 | 52380 | 45.9808 | 0.27588 | 64.8883 |  | 2029-09-01 | 14:33 | 52380 | 104.566 | 0.6274 | 255.7897 |  | 2006-09-01 | 14:33 | 52380 | 101.16 | 0.60696 | 241.4911 |  | 2029-09-01 | 14:33 | 52380 | 50.2384 | 0.30143 | 104.6248 |  | 2006-09-01 | 14:33 | 52380 | 42.6593 | 0.25596 | 62.6807 |  | 2028-01-01 | 14:33 | 52380 | 114.516 | 0.6871 | 255.0569 |  | 2007-01-01 | 14:33 | 52380 | 101.803 | 0.61082 | 244.7229 |  | 2028-01-01 | 14:33 | 52380 | 32.7295 | 0.19638 | 43.6195 |  | 2007-01-01 | 14:33 | 52380 | 34.4221 | 0.20653 | 47.0464 |  | 2029-09-01 | 14:33 | 52380 | 80.5079 | 0.48305 | 120.6229 |  | 2029-09-01 | 14:33 | 52380 | 56.5904 | 0.33954 | 83.0734 |  | 2029-09-01 | 14:33 | 52380 | 40.3944 | 0.24237 | 57.3021 |  | 2006-09-01 | 14:33 | 52380 | 39.887 | 0.23932 | 56.4266 |  | 2028-01-01 | 14:33 | 52380 | 71.7769 | 0.43066 | 102.103 |  | 2007-01-01 | 14:33 | 52380 | 66.0615 | 0.39637 | 104.0348 |  | 2028-01-01 | 14:33 | 52380 | 37.3618 | 0.22417 | 51.3074 |  | 2007-01-01 | 14:33 | 52380 | 37.6475 | 0.22589 | 52.2651
| 2029-09-01 | 14:34 | 52440 | 325 | 1.95 | 412.9448 |  | 2029-09-01 | 14:34 | 52440 | 123.346 | 0.74008 | 268.4234 |  | 2006-09-01 | 14:34 | 52440 | 108.877 | 0.65326 | 244.6605 |  | 2029-09-01 | 14:34 | 52440 | 85.5373 | 0.51322 | 178.337 |  | 2006-09-01 | 14:34 | 52440 | 75.1662 | 0.451 | 127.7636 |  | 2028-01-01 | 14:34 | 52440 | 171.44 | 1.0286 | 276.7133 |  | 2007-01-01 | 14:34 | 52440 | 109.242 | 0.65545 | 246.9386 |  | 2028-01-01 | 14:34 | 52440 | 72.9885 | 0.43793 | 102.5409 |  | 2007-01-01 | 14:34 | 52440 | 67.8464 | 0.40708 | 104.4418 |  | 2029-09-01 | 14:34 | 52440 | 111.452 | 0.66871 | 258.3804 |  | 2006-09-01 | 14:34 | 52440 | 106.155 | 0.63693 | 242.3469 |  | 2029-09-01 | 14:34 | 52440 | 63.7831 | 0.3827 | 131.1761 |  | 2006-09-01 | 14:34 | 52440 | 55.5103 | 0.33306 | 84.4632 |  | 2028-01-01 | 14:34 | 52440 | 133.235 | 0.79941 | 260.2022 |  | 2007-01-01 | 14:34 | 52440 | 106.825 | 0.64095 | 245.4705 |  | 2028-01-01 | 14:34 | 52440 | 45.2976 | 0.27179 | 61.2646 |  | 2007-01-01 | 14:34 | 52440 | 46.6698 | 0.28002 | 65.1683 |  | 2029-09-01 | 14:34 | 52440 | 109.55 | 0.6573 | 256.447 |  | 2006-09-01 | 14:34 | 52440 | 105.937 | 0.63562 | 242.1268 |  | 2029-09-01 | 14:34 | 52440 | 51.1237 | 0.30674 | 104.9315 |  | 2006-09-01 | 14:34 | 52440 | 43.2414 | 0.25945 | 62.9402 |  | 2028-01-01 | 14:34 | 52440 | 119.533 | 0.7172 | 255.7741 |  | 2007-01-01 | 14:34 | 52440 | 106.649 | 0.63989 | 245.3628 |  | 2028-01-01 | 14:34 | 52440 | 32.9373 | 0.19762 | 43.8171 |  | 2007-01-01 | 14:34 | 52440 | 34.6931 | 0.20816 | 47.2545 |  | 2029-09-01 | 14:34 | 52440 | 81.7335 | 0.4904 | 121.1133 |  | 2029-09-01 | 14:34 | 52440 | 57.4098 | 0.34446 | 83.4179 |  | 2029-09-01 | 14:34 | 52440 | 40.7957 | 0.24477 | 57.5469 |  | 2006-09-01 | 14:34 | 52440 | 40.2714 | 0.24163 | 56.6682 |  | 2028-01-01 | 14:34 | 52440 | 72.9885 | 0.43793 | 102.5409 |  | 2007-01-01 | 14:34 | 52440 | 67.8464 | 0.40708 | 104.4418 |  | 2028-01-01 | 14:34 | 52440 | 37.6846 | 0.22611 | 51.5335 |  | 2007-01-01 | 14:34 | 52440 | 38.0245 | 0.22815 | 52.4933
| 2029-09-01 | 14:35 | 52500 | 326.907 | 1.9614 | 414.9062 |  | 2029-09-01 | 14:35 | 52500 | 128.068 | 0.76841 | 269.1918 |  | 2006-09-01 | 14:35 | 52500 | 113.527 | 0.68116 | 245.3417 |  | 2029-09-01 | 14:35 | 52500 | 87.9845 | 0.52791 | 178.8649 |  | 2006-09-01 | 14:35 | 52500 | 77.2921 | 0.46375 | 128.2274 |  | 2028-01-01 | 14:35 | 52500 | 175.74 | 1.0544 | 277.7677 |  | 2007-01-01 | 14:35 | 52500 | 113.971 | 0.68383 | 247.6225 |  | 2028-01-01 | 14:35 | 52500 | 74.1148 | 0.44469 | 102.9856 |  | 2007-01-01 | 14:35 | 52500 | 69.5126 | 0.41708 | 104.8589 |  | 2029-09-01 | 14:35 | 52500 | 116.34 | 0.69804 | 259.0784 |  | 2006-09-01 | 14:35 | 52500 | 110.85 | 0.6651 | 243.012 |  | 2029-09-01 | 14:35 | 52500 | 65.2014 | 0.39121 | 131.5673 |  | 2006-09-01 | 14:35 | 52500 | 56.5441 | 0.33926 | 84.8025 |  | 2028-01-01 | 14:35 | 52500 | 138.017 | 0.8281 | 261.0303 |  | 2007-01-01 | 14:35 | 52500 | 111.591 | 0.66955 | 246.14 |  | 2028-01-01 | 14:35 | 52500 | 45.7646 | 0.27459 | 61.5392 |  | 2007-01-01 | 14:35 | 52500 | 47.2794 | 0.28368 | 65.452 |  | 2029-09-01 | 14:35 | 52500 | 114.464 | 0.68678 | 257.1338 |  | 2006-09-01 | 14:35 | 52500 | 110.635 | 0.66381 | 242.7906 |  | 2029-09-01 | 14:35 | 52500 | 51.9209 | 0.31153 | 105.243 |  | 2006-09-01 | 14:35 | 52500 | 43.7578 | 0.26255 | 63.2027 |  | 2028-01-01 | 14:35 | 52500 | 124.488 | 0.74693 | 256.521 |  | 2007-01-01 | 14:35 | 52500 | 111.418 | 0.66851 | 246.0313 |  | 2028-01-01 | 14:35 | 52500 | 33.1086 | 0.19865 | 44.0158 |  | 2007-01-01 | 14:35 | 52500 | 34.9196 | 0.20952 | 47.4641 |  | 2029-09-01 | 14:35 | 52500 | 82.8849 | 0.49731 | 121.6106 |  | 2029-09-01 | 14:35 | 52500 | 58.1553 | 0.34893 | 83.7668 |  | 2029-09-01 | 14:35 | 52500 | 41.1448 | 0.24687 | 57.7937 |  | 2006-09-01 | 14:35 | 52500 | 40.6044 | 0.24363 | 56.9118 |  | 2028-01-01 | 14:35 | 52500 | 74.1148 | 0.44469 | 102.9856 |  | 2007-01-01 | 14:35 | 52500 | 69.5126 | 0.41708 | 104.8589 |  | 2028-01-01 | 14:35 | 52500 | 37.9605 | 0.22776 | 51.7613 |  | 2007-01-01 | 14:35 | 52500 | 38.3481 | 0.23009 | 52.7234
| 2029-09-01 | 14:36 | 52560 | 328.789 | 1.9727 | 416.8789 |  | 2029-09-01 | 14:36 | 52560 | 132.724 | 0.79634 | 269.9882 |  | 2006-09-01 | 14:36 | 52560 | 118.098 | 0.70859 | 246.0503 |  | 2029-09-01 | 14:36 | 52560 | 90.3232 | 0.54194 | 179.4068 |  | 2006-09-01 | 14:36 | 52560 | 79.3055 | 0.47583 | 128.7032 |  | 2028-01-01 | 14:36 | 52560 | 179.988 | 1.0799 | 278.8476 |  | 2007-01-01 | 14:36 | 52560 | 118.624 | 0.71174 | 248.3342 |  | 2028-01-01 | 14:36 | 52560 | 75.1617 | 0.45097 | 103.4366 |  | 2007-01-01 | 14:36 | 52560 | 71.068 | 0.42641 | 105.2853 |  | 2029-09-01 | 14:36 | 52560 | 121.16 | 0.72696 | 259.8054 |  | 2006-09-01 | 14:36 | 52560 | 115.465 | 0.69279 | 243.7048 |  | 2029-09-01 | 14:36 | 52560 | 66.5165 | 0.3991 | 131.9664 |  | 2006-09-01 | 14:36 | 52560 | 57.4904 | 0.34494 | 85.1474 |  | 2028-01-01 | 14:36 | 52560 | 142.74 | 0.85644 | 261.8867 |  | 2007-01-01 | 14:36 | 52560 | 116.281 | 0.69769 | 246.8377 |  | 2028-01-01 | 14:36 | 52560 | 46.1738 | 0.27704 | 61.8163 |  | 2007-01-01 | 14:36 | 52560 | 47.8184 | 0.28691 | 65.7389 |  | 2029-09-01 | 14:36 | 52560 | 119.31 | 0.71586 | 257.8497 |  | 2006-09-01 | 14:36 | 52560 | 115.254 | 0.69152 | 243.4821 |  | 2029-09-01 | 14:36 | 52560 | 52.6388 | 0.31583 | 105.5589 |  | 2006-09-01 | 14:36 | 52560 | 44.2167 | 0.2653 | 63.468 |  | 2028-01-01 | 14:36 | 52560 | 129.381 | 0.77629 | 257.2973 |  | 2007-01-01 | 14:36 | 52560 | 116.11 | 0.69666 | 246.728 |  | 2028-01-01 | 14:36 | 52560 | 33.2492 | 0.1995 | 44.2153 |  | 2007-01-01 | 14:36 | 52560 | 35.1085 | 0.21065 | 47.6747 |  | 2029-09-01 | 14:36 | 52560 | 83.9665 | 0.5038 | 122.1144 |  | 2029-09-01 | 14:36 | 52560 | 58.8337 | 0.353 | 84.1198 |  | 2029-09-01 | 14:36 | 52560 | 41.4486 | 0.24869 | 58.0424 |  | 2006-09-01 | 14:36 | 52560 | 40.8927 | 0.24536 | 57.1572 |  | 2028-01-01 | 14:36 | 52560 | 75.1617 | 0.45097 | 103.4366 |  | 2007-01-01 | 14:36 | 52560 | 71.068 | 0.42641 | 105.2853 |  | 2028-01-01 | 14:36 | 52560 | 38.1959 | 0.22918 | 51.9905 |  | 2007-01-01 | 14:36 | 52560 | 38.6258 | 0.23175 | 52.9551
| 2029-09-01 | 14:37 | 52620 | 330.647 | 1.9839 | 418.8628 |  | 2029-09-01 | 14:37 | 52620 | 137.317 | 0.8239 | 270.8121 |  | 2006-09-01 | 14:37 | 52620 | 122.594 | 0.73556 | 246.7858 |  | 2029-09-01 | 14:37 | 52620 | 92.5581 | 0.55535 | 179.9622 |  | 2006-09-01 | 14:37 | 52620 | 81.2127 | 0.48728 | 129.1905 |  | 2028-01-01 | 14:37 | 52620 | 184.184 | 1.1051 | 279.9527 |  | 2007-01-01 | 14:37 | 52620 | 123.203 | 0.73922 | 249.0734 |  | 2028-01-01 | 14:37 | 52620 | 76.1345 | 0.45681 | 103.8934 |  | 2007-01-01 | 14:37 | 52620 | 72.5201 | 0.43512 | 105.7204 |  | 2029-09-01 | 14:37 | 52620 | 125.914 | 0.75548 | 260.5608 |  | 2006-09-01 | 14:37 | 52620 | 120.004 | 0.72002 | 244.4248 |  | 2029-09-01 | 14:37 | 52620 | 67.736 | 0.40642 | 132.3728 |  | 2006-09-01 | 14:37 | 52620 | 58.3569 | 0.35014 | 85.4975 |  | 2028-01-01 | 14:37 | 52620 | 147.405 | 0.88443 | 262.7712 |  | 2007-01-01 | 14:37 | 52620 | 120.895 | 0.72537 | 247.5631 |  | 2028-01-01 | 14:37 | 52620 | 46.532 | 0.27919 | 62.0955 |  | 2007-01-01 | 14:37 | 52620 | 48.2949 | 0.28977 | 66.0287 |  | 2029-09-01 | 14:37 | 52620 | 124.09 | 0.74454 | 258.5942 |  | 2006-09-01 | 14:37 | 52620 | 119.796 | 0.71878 | 244.2009 |  | 2029-09-01 | 14:37 | 52620 | 53.2853 | 0.31971 | 105.8786 |  | 2006-09-01 | 14:37 | 52620 | 44.6251 | 0.26775 | 63.7358 |  | 2028-01-01 | 14:37 | 52620 | 134.215 | 0.80529 | 258.1026 |  | 2007-01-01 | 14:37 | 52620 | 120.727 | 0.72436 | 247.4524 |  | 2028-01-01 | 14:37 | 52620 | 33.3642 | 0.20019 | 44.4155 |  | 2007-01-01 | 14:37 | 52620 | 35.2656 | 0.21159 | 47.8863 |  | 2029-09-01 | 14:37 | 52620 | 84.9827 | 0.5099 | 122.6243 |  | 2029-09-01 | 14:37 | 52620 | 59.4509 | 0.35671 | 84.4765 |  | 2029-09-01 | 14:37 | 52620 | 41.7128 | 0.25028 | 58.2927 |  | 2006-09-01 | 14:37 | 52620 | 41.1422 | 0.24685 | 57.404 |  | 2028-01-01 | 14:37 | 52620 | 76.1345 | 0.45681 | 103.8934 |  | 2007-01-01 | 14:37 | 52620 | 72.5201 | 0.43512 | 105.7204 |  | 2028-01-01 | 14:37 | 52620 | 38.3967 | 0.23038 | 52.2208 |  | 2007-01-01 | 14:37 | 52620 | 38.864 | 0.23318 | 53.1883
| 2029-09-01 | 14:38 | 52680 | 332.481 | 1.9949 | 420.8577 |  | 2029-09-01 | 14:38 | 52680 | 141.846 | 0.85108 | 271.6631 |  | 2006-09-01 | 14:38 | 52680 | 127.013 | 0.76208 | 247.5479 |  | 2029-09-01 | 14:38 | 52680 | 94.694 | 0.56816 | 180.5304 |  | 2006-09-01 | 14:38 | 52680 | 83.0195 | 0.49812 | 129.6886 |  | 2028-01-01 | 14:38 | 52680 | 188.331 | 1.13 | 281.0827 |  | 2007-01-01 | 14:38 | 52680 | 127.708 | 0.76625 | 249.8397 |  | 2028-01-01 | 14:38 | 52680 | 77.0381 | 0.46223 | 104.3556 |  | 2007-01-01 | 14:38 | 52680 | 73.8757 | 0.44325 | 106.1637 |  | 2029-09-01 | 14:38 | 52680 | 130.602 | 0.78361 | 261.3445 |  | 2006-09-01 | 14:38 | 52680 | 124.466 | 0.7468 | 245.1716 |  | 2029-09-01 | 14:38 | 52680 | 68.8669 | 0.4132 | 132.786 |  | 2006-09-01 | 14:38 | 52680 | 59.151 | 0.35491 | 85.8524 |  | 2028-01-01 | 14:38 | 52680 | 152.014 | 0.91208 | 263.6833 |  | 2007-01-01 | 14:38 | 52680 | 125.435 | 0.75261 | 248.3157 |  | 2028-01-01 | 14:38 | 52680 | 46.8452 | 0.28107 | 62.3765 |  | 2007-01-01 | 14:38 | 52680 | 48.7159 | 0.2923 | 66.321 |  | 2029-09-01 | 14:38 | 52680 | 128.804 | 0.77282 | 259.367 |  | 2006-09-01 | 14:38 | 52680 | 124.261 | 0.74557 | 244.9464 |  | 2029-09-01 | 14:38 | 52680 | 53.8675 | 0.32321 | 106.2018 |  | 2006-09-01 | 14:38 | 52680 | 44.9891 | 0.26993 | 64.0057 |  | 2028-01-01 | 14:38 | 52680 | 138.989 | 0.83393 | 258.9365 |  | 2007-01-01 | 14:38 | 52680 | 125.27 | 0.75162 | 248.204 |  | 2028-01-01 | 14:38 | 52680 | 33.4575 | 0.20075 | 44.6162 |  | 2007-01-01 | 14:38 | 52680 | 35.3959 | 0.21238 | 48.0987 |  | 2029-09-01 | 14:38 | 52680 | 85.9374 | 0.51562 | 123.14 |  | 2029-09-01 | 14:38 | 52680 | 60.0127 | 0.36008 | 84.8366 |  | 2029-09-01 | 14:38 | 52680 | 41.9427 | 0.25166 | 58.5444 |  | 2006-09-01 | 14:38 | 52680 | 41.3581 | 0.24815 | 57.6522 |  | 2028-01-01 | 14:38 | 52680 | 77.0381 | 0.46223 | 104.3556 |  | 2007-01-01 | 14:38 | 52680 | 73.8757 | 0.44325 | 106.1637 |  | 2028-01-01 | 14:38 | 52680 | 38.5678 | 0.23141 | 52.4522 |  | 2007-01-01 | 14:38 | 52680 | 39.0684 | 0.23441 | 53.4227
| 2029-09-01 | 14:39 | 52740 | 334.292 | 2.0058 | 422.8635 |  | 2029-09-01 | 14:39 | 52740 | 146.313 | 0.87788 | 272.541 |  | 2006-09-01 | 14:39 | 52740 | 131.358 | 0.78815 | 248.3361 |  | 2029-09-01 | 14:39 | 52740 | 96.7352 | 0.58041 | 181.1108 |  | 2006-09-01 | 14:39 | 52740 | 84.7314 | 0.50839 | 130.197 |  | 2028-01-01 | 14:39 | 52740 | 192.428 | 1.1546 | 282.2373 |  | 2007-01-01 | 14:39 | 52740 | 132.14 | 0.79284 | 250.6325 |  | 2028-01-01 | 14:39 | 52740 | 77.8772 | 0.46726 | 104.8229 |  | 2007-01-01 | 14:39 | 52740 | 75.1414 | 0.45085 | 106.6145 |  | 2029-09-01 | 14:39 | 52740 | 135.226 | 0.81136 | 262.1558 |  | 2006-09-01 | 14:39 | 52740 | 128.853 | 0.77312 | 245.9447 |  | 2029-09-01 | 14:39 | 52740 | 69.9156 | 0.41949 | 133.2055 |  | 2006-09-01 | 14:39 | 52740 | 59.8791 | 0.35927 | 86.2117 |  | 2028-01-01 | 14:39 | 52740 | 156.567 | 0.9394 | 264.6227 |  | 2007-01-01 | 14:39 | 52740 | 129.903 | 0.77942 | 249.0951 |  | 2028-01-01 | 14:39 | 52740 | 47.1185 | 0.28271 | 62.6592 |  | 2007-01-01 | 14:39 | 52740 | 49.0877 | 0.29453 | 66.6155 |  | 2029-09-01 | 14:39 | 52740 | 133.452 | 0.80071 | 260.1677 |  | 2006-09-01 | 14:39 | 52740 | 128.652 | 0.77191 | 245.7183 |  | 2029-09-01 | 14:39 | 52740 | 54.3919 | 0.32635 | 106.5281 |  | 2006-09-01 | 14:39 | 52740 | 45.3142 | 0.27189 | 64.2776 |  | 2028-01-01 | 14:39 | 52740 | 143.706 | 0.86224 | 259.7988 |  | 2007-01-01 | 14:39 | 52740 | 129.74 | 0.77844 | 248.9824 |  | 2028-01-01 | 14:39 | 52740 | 33.5327 | 0.2012 | 44.8174 |  | 2007-01-01 | 14:39 | 52740 | 35.5034 | 0.21302 | 48.3117 |  | 2029-09-01 | 14:39 | 52740 | 86.8344 | 0.52101 | 123.661 |  | 2029-09-01 | 14:39 | 52740 | 60.5239 | 0.36314 | 85.1997 |  | 2029-09-01 | 14:39 | 52740 | 42.1429 | 0.25286 | 58.7972 |  | 2006-09-01 | 14:39 | 52740 | 41.5448 | 0.24927 | 57.9015 |  | 2028-01-01 | 14:39 | 52740 | 77.8772 | 0.46726 | 104.8229 |  | 2007-01-01 | 14:39 | 52740 | 75.1414 | 0.45085 | 106.6145 |  | 2028-01-01 | 14:39 | 52740 | 38.7133 | 0.23228 | 52.6845 |  | 2007-01-01 | 14:39 | 52740 | 39.2438 | 0.23546 | 53.6582
| 2029-09-01 | 14:40 | 52800 | 336.079 | 2.0165 | 424.8799 |  | 2029-09-01 | 14:40 | 52800 | 150.718 | 0.90431 | 273.4453 |  | 2006-09-01 | 14:40 | 52800 | 135.63 | 0.81378 | 249.1499 |  | 2029-09-01 | 14:40 | 52800 | 98.6859 | 0.59212 | 181.7029 |  | 2006-09-01 | 14:40 | 52800 | 86.3536 | 0.51812 | 130.7151 |  | 2028-01-01 | 14:40 | 52800 | 196.475 | 1.1788 | 283.4161 |  | 2007-01-01 | 14:40 | 52800 | 136.5 | 0.819 | 251.4515 |  | 2028-01-01 | 14:40 | 52800 | 78.6562 | 0.47194 | 105.2948 |  | 2007-01-01 | 14:40 | 52800 | 76.323 | 0.45794 | 107.0725 |  | 2029-09-01 | 14:40 | 52800 | 139.786 | 0.83872 | 262.9945 |  | 2006-09-01 | 14:40 | 52800 | 133.166 | 0.799 | 246.7437 |  | 2029-09-01 | 14:40 | 52800 | 70.8881 | 0.42533 | 133.6309 |  | 2006-09-01 | 14:40 | 52800 | 60.5471 | 0.36328 | 86.575 |  | 2028-01-01 | 14:40 | 52800 | 161.064 | 0.96638 | 265.589 |  | 2007-01-01 | 14:40 | 52800 | 134.297 | 0.80578 | 249.9009 |  | 2028-01-01 | 14:40 | 52800 | 47.3567 | 0.28414 | 62.9434 |  | 2007-01-01 | 14:40 | 52800 | 49.4157 | 0.29649 | 66.912 |  | 2029-09-01 | 14:40 | 52800 | 138.037 | 0.82822 | 260.996 |  | 2006-09-01 | 14:40 | 52800 | 132.968 | 0.79781 | 246.5162 |  | 2029-09-01 | 14:40 | 52800 | 54.8642 | 0.32919 | 106.8573 |  | 2006-09-01 | 14:40 | 52800 | 45.6052 | 0.27363 | 64.5512 |  | 2028-01-01 | 14:40 | 52800 | 148.364 | 0.89018 | 260.6889 |  | 2007-01-01 | 14:40 | 52800 | 134.137 | 0.80482 | 249.7872 |  | 2028-01-01 | 14:40 | 52800 | 33.5927 | 0.20156 | 45.019 |  | 2007-01-01 | 14:40 | 52800 | 35.5919 | 0.21355 | 48.5253 |  | 2029-09-01 | 14:40 | 52800 | 87.6773 | 0.52606 | 124.187 |  | 2029-09-01 | 14:40 | 52800 | 60.9892 | 0.36594 | 85.5657 |  | 2029-09-01 | 14:40 | 52800 | 42.3171 | 0.2539 | 59.0511 |  | 2006-09-01 | 14:40 | 52800 | 41.7062 | 0.25024 | 58.1517 |  | 2028-01-01 | 14:40 | 52800 | 78.6562 | 0.47194 | 105.2948 |  | 2007-01-01 | 14:40 | 52800 | 76.323 | 0.45794 | 107.0725 |  | 2028-01-01 | 14:40 | 52800 | 38.8368 | 0.23302 | 52.9175 |  | 2007-01-01 | 14:40 | 52800 | 39.3942 | 0.23637 | 53.8946
| 2029-09-01 | 14:41 | 52860 | 337.844 | 2.0271 | 426.907 |  | 2029-09-01 | 14:41 | 52860 | 155.064 | 0.93038 | 274.3757 |  | 2006-09-01 | 14:41 | 52860 | 139.83 | 0.83898 | 249.9888 |  | 2029-09-01 | 14:41 | 52860 | 100.55 | 0.6033 | 182.3062 |  | 2006-09-01 | 14:41 | 52860 | 87.891 | 0.52735 | 131.2424 |  | 2028-01-01 | 14:41 | 52860 | 200.471 | 1.2028 | 284.619 |  | 2007-01-01 | 14:41 | 52860 | 140.79 | 0.84474 | 252.2962 |  | 2028-01-01 | 14:41 | 52860 | 79.3791 | 0.47627 | 105.7711 |  | 2007-01-01 | 14:41 | 52860 | 77.4263 | 0.46456 | 107.537 |  | 2029-09-01 | 14:41 | 52860 | 144.284 | 0.8657 | 263.8602 |  | 2006-09-01 | 14:41 | 52860 | 137.406 | 0.82444 | 247.5682 |  | 2029-09-01 | 14:41 | 52860 | 71.7899 | 0.43074 | 134.0616 |  | 2006-09-01 | 14:41 | 52860 | 61.1605 | 0.36696 | 86.942 |  | 2028-01-01 | 14:41 | 52860 | 165.504 | 0.99302 | 266.5821 |  | 2007-01-01 | 14:41 | 52860 | 138.621 | 0.83173 | 250.7326 |  | 2028-01-01 | 14:41 | 52860 | 47.5638 | 0.28538 | 63.2288 |  | 2007-01-01 | 14:41 | 52860 | 49.705 | 0.29823 | 67.2102 |  | 2029-09-01 | 14:41 | 52860 | 142.559 | 0.85535 | 261.8513 |  | 2006-09-01 | 14:41 | 52860 | 137.211 | 0.82327 | 247.3394 |  | 2029-09-01 | 14:41 | 52860 | 55.2896 | 0.33174 | 107.189 |  | 2006-09-01 | 14:41 | 52860 | 45.8662 | 0.2752 | 64.8264 |  | 2028-01-01 | 14:41 | 52860 | 152.964 | 0.91778 | 261.6067 |  | 2007-01-01 | 14:41 | 52860 | 138.463 | 0.83078 | 250.618 |  | 2028-01-01 | 14:41 | 52860 | 33.64 | 0.20184 | 45.2208 |  | 2007-01-01 | 14:41 | 52860 | 35.6641 | 0.21398 | 48.7392 |  | 2029-09-01 | 14:41 | 52860 | 88.4693 | 0.53082 | 124.7178 |  | 2029-09-01 | 14:41 | 52860 | 61.4128 | 0.36848 | 85.9341 |  | 2029-09-01 | 14:41 | 52860 | 42.4688 | 0.25481 | 59.3059 |  | 2006-09-01 | 14:41 | 52860 | 41.8456 | 0.25107 | 58.4028 |  | 2028-01-01 | 14:41 | 52860 | 79.3791 | 0.47627 | 105.7711 |  | 2007-01-01 | 14:41 | 52860 | 77.4263 | 0.46456 | 107.537 |  | 2028-01-01 | 14:41 | 52860 | 38.9415 | 0.23365 | 53.1512 |  | 2007-01-01 | 14:41 | 52860 | 39.5233 | 0.23714 | 54.1317
| 2029-09-01 | 14:42 | 52920 | 339.586 | 2.0375 | 428.9445 |  | 2029-09-01 | 14:42 | 52920 | 159.349 | 0.95609 | 275.3318 |  | 2006-09-01 | 14:42 | 52920 | 143.958 | 0.86375 | 250.8526 |  | 2029-09-01 | 14:42 | 52920 | 102.332 | 0.61399 | 182.9202 |  | 2006-09-01 | 14:42 | 52920 | 89.3483 | 0.53609 | 131.7785 |  | 2028-01-01 | 14:42 | 52920 | 204.417 | 1.2265 | 285.8455 |  | 2007-01-01 | 14:42 | 52920 | 145.011 | 0.87007 | 253.1663 |  | 2028-01-01 | 14:42 | 52920 | 80.0497 | 0.4803 | 106.2514 |  | 2007-01-01 | 14:42 | 52920 | 78.4565 | 0.47074 | 108.0078 |  | 2029-09-01 | 14:42 | 52920 | 148.72 | 0.89232 | 264.7526 |  | 2006-09-01 | 14:42 | 52920 | 141.574 | 0.84944 | 248.4176 |  | 2029-09-01 | 14:42 | 52920 | 72.6263 | 0.43576 | 134.4974 |  | 2006-09-01 | 14:42 | 52920 | 61.7242 | 0.37035 | 87.3123 |  | 2028-01-01 | 14:42 | 52920 | 169.889 | 1.0193 | 267.6014 |  | 2007-01-01 | 14:42 | 52920 | 142.875 | 0.85725 | 251.5899 |  | 2028-01-01 | 14:42 | 52920 | 47.7435 | 0.28646 | 63.5152 |  | 2007-01-01 | 14:42 | 52920 | 49.9599 | 0.29976 | 67.51 |  | 2029-09-01 | 14:42 | 52920 | 147.019 | 0.88211 | 262.7334 |  | 2006-09-01 | 14:42 | 52920 | 141.383 | 0.8483 | 248.1877 |  | 2029-09-01 | 14:42 | 52920 | 55.6727 | 0.33404 | 107.5231 |  | 2006-09-01 | 14:42 | 52920 | 46.1009 | 0.27661 | 65.103 |  | 2028-01-01 | 14:42 | 52920 | 157.506 | 0.94504 | 262.5518 |  | 2007-01-01 | 14:42 | 52920 | 142.719 | 0.85631 | 251.4743 |  | 2028-01-01 | 14:42 | 52920 | 33.6766 | 0.20206 | 45.4229 |  | 2007-01-01 | 14:42 | 52920 | 35.7224 | 0.21433 | 48.9536 |  | 2029-09-01 | 14:42 | 52920 | 89.2136 | 0.53528 | 125.2531 |  | 2029-09-01 | 14:42 | 52920 | 61.7984 | 0.37079 | 86.3049 |  | 2029-09-01 | 14:42 | 52920 | 42.6009 | 0.25561 | 59.5615 |  | 2006-09-01 | 14:42 | 52920 | 41.966 | 0.2518 | 58.6546 |  | 2028-01-01 | 14:42 | 52920 | 80.0497 | 0.4803 | 106.2514 |  | 2007-01-01 | 14:42 | 52920 | 78.4565 | 0.47074 | 108.0078 |  | 2028-01-01 | 14:42 | 52920 | 39.0301 | 0.23418 | 53.3854 |  | 2007-01-01 | 14:42 | 52920 | 39.634 | 0.2378 | 54.3695
| 2029-09-01 | 14:43 | 52980 | 341.307 | 2.0478 | 430.9924 |  | 2029-09-01 | 14:43 | 52980 | 163.577 | 0.98146 | 276.3133 |  | 2006-09-01 | 14:43 | 52980 | 148.016 | 0.8881 | 251.7407 |  | 2029-09-01 | 14:43 | 52980 | 104.035 | 0.62421 | 183.5444 |  | 2006-09-01 | 14:43 | 52980 | 90.7299 | 0.54438 | 132.3229 |  | 2028-01-01 | 14:43 | 52980 | 208.312 | 1.2499 | 287.0953 |  | 2007-01-01 | 14:43 | 52980 | 149.162 | 0.89497 | 254.0613 |  | 2028-01-01 | 14:43 | 52980 | 80.6715 | 0.48403 | 106.7354 |  | 2007-01-01 | 14:43 | 52980 | 79.4185 | 0.47651 | 108.4843 |  | 2029-09-01 | 14:43 | 52980 | 153.095 | 0.91857 | 265.6711 |  | 2006-09-01 | 14:43 | 52980 | 145.671 | 0.87403 | 249.2916 |  | 2029-09-01 | 14:43 | 52980 | 73.4019 | 0.44041 | 134.9378 |  | 2006-09-01 | 14:43 | 52980 | 62.2426 | 0.37346 | 87.6858 |  | 2028-01-01 | 14:43 | 52980 | 174.218 | 1.0453 | 268.6467 |  | 2007-01-01 | 14:43 | 52980 | 147.059 | 0.88235 | 252.4722 |  | 2028-01-01 | 14:43 | 52980 | 47.8989 | 0.28739 | 63.8026 |  | 2007-01-01 | 14:43 | 52980 | 50.1844 | 0.30111 | 67.8111 |  | 2029-09-01 | 14:43 | 52980 | 151.418 | 0.90851 | 263.6419 |  | 2006-09-01 | 14:43 | 52980 | 145.483 | 0.8729 | 249.0606 |  | 2029-09-01 | 14:43 | 52980 | 56.0177 | 0.33611 | 107.8592 |  | 2006-09-01 | 14:43 | 52980 | 46.3126 | 0.27788 | 65.3809 |  | 2028-01-01 | 14:43 | 52980 | 161.99 | 0.97194 | 263.5237 |  | 2007-01-01 | 14:43 | 52980 | 146.906 | 0.88144 | 252.3558 |  | 2028-01-01 | 14:43 | 52980 | 33.7042 | 0.20223 | 45.6251 |  | 2007-01-01 | 14:43 | 52980 | 35.7689 | 0.21461 | 49.1682 |  | 2029-09-01 | 14:43 | 52980 | 89.9132 | 0.53948 | 125.7926 |  | 2029-09-01 | 14:43 | 52980 | 62.1495 | 0.3729 | 86.6778 |  | 2029-09-01 | 14:43 | 52980 | 42.716 | 0.2563 | 59.8178 |  | 2006-09-01 | 14:43 | 52980 | 42.0699 | 0.25242 | 58.907 |  | 2028-01-01 | 14:43 | 52980 | 80.6715 | 0.48403 | 106.7354 |  | 2007-01-01 | 14:43 | 52980 | 79.4185 | 0.47651 | 108.4843 |  | 2028-01-01 | 14:43 | 52980 | 39.1048 | 0.23463 | 53.62 |  | 2007-01-01 | 14:43 | 52980 | 39.7291 | 0.23837 | 54.6079
| 2029-09-01 | 14:44 | 53040 | 343.006 | 2.058 | 433.0504 |  | 2029-09-01 | 14:44 | 53040 | 167.746 | 1.0065 | 277.3197 |  | 2006-09-01 | 14:44 | 53040 | 152.005 | 0.91203 | 252.6527 |  | 2029-09-01 | 14:44 | 53040 | 105.662 | 0.63397 | 184.1784 |  | 2006-09-01 | 14:44 | 53040 | 92.0399 | 0.55224 | 132.8752 |  | 2028-01-01 | 14:44 | 53040 | 212.159 | 1.273 | 288.3683 |  | 2007-01-01 | 14:44 | 53040 | 153.246 | 0.91948 | 254.9808 |  | 2028-01-01 | 14:44 | 53040 | 81.2478 | 0.48749 | 107.2229 |  | 2007-01-01 | 14:44 | 53040 | 80.317 | 0.4819 | 108.9662 |  | 2029-09-01 | 14:44 | 53040 | 157.41 | 0.94446 | 266.6156 |  | 2006-09-01 | 14:44 | 53040 | 149.699 | 0.89819 | 250.1898 |  | 2029-09-01 | 14:44 | 53040 | 74.1211 | 0.44473 | 135.3825 |  | 2006-09-01 | 14:44 | 53040 | 62.7198 | 0.37632 | 88.0621 |  | 2028-01-01 | 14:44 | 53040 | 178.493 | 1.071 | 269.7177 |  | 2007-01-01 | 14:44 | 53040 | 151.175 | 0.90705 | 253.3793 |  | 2028-01-01 | 14:44 | 53040 | 48.033 | 0.2882 | 64.0908 |  | 2007-01-01 | 14:44 | 53040 | 50.3818 | 0.30229 | 68.1134 |  | 2029-09-01 | 14:44 | 53040 | 155.757 | 0.93454 | 264.5765 |  | 2006-09-01 | 14:44 | 53040 | 149.514 | 0.89708 | 249.9577 |  | 2029-09-01 | 14:44 | 53040 | 56.3285 | 0.33797 | 108.1972 |  | 2006-09-01 | 14:44 | 53040 | 46.504 | 0.27902 | 65.6599 |  | 2028-01-01 | 14:44 | 53040 | 166.418 | 0.99851 | 264.5222 |  | 2007-01-01 | 14:44 | 53040 | 151.024 | 0.90614 | 253.2619 |  | 2028-01-01 | 14:44 | 53040 | 33.7244 | 0.20235 | 45.8274 |  | 2007-01-01 | 14:44 | 53040 | 35.8053 | 0.21483 | 49.383 |  | 2029-09-01 | 14:44 | 53040 | 90.5706 | 0.54342 | 126.336 |  | 2029-09-01 | 14:44 | 53040 | 62.4692 | 0.37482 | 87.0527 |  | 2029-09-01 | 14:44 | 53040 | 42.8163 | 0.2569 | 60.0747 |  | 2006-09-01 | 14:44 | 53040 | 42.1594 | 0.25296 | 59.1599 |  | 2028-01-01 | 14:44 | 53040 | 81.2478 | 0.48749 | 107.2229 |  | 2007-01-01 | 14:44 | 53040 | 80.317 | 0.4819 | 108.9662 |  | 2028-01-01 | 14:44 | 53040 | 39.1675 | 0.235 | 53.855 |  | 2007-01-01 | 14:44 | 53040 | 39.8106 | 0.23886 | 54.8467
| 2029-09-01 | 14:45 | 53100 | 344.683 | 2.0681 | 435.1185 |  | 2029-09-01 | 14:45 | 53100 | 171.859 | 1.0312 | 278.3509 |  | 2006-09-01 | 14:45 | 53100 | 155.926 | 0.93556 | 253.5883 |  | 2029-09-01 | 14:45 | 53100 | 107.217 | 0.6433 | 184.8217 |  | 2006-09-01 | 14:45 | 53100 | 93.2823 | 0.55969 | 133.4348 |  | 2028-01-01 | 14:45 | 53100 | 215.957 | 1.2957 | 289.664 |  | 2007-01-01 | 14:45 | 53100 | 157.262 | 0.94357 | 255.9243 |  | 2028-01-01 | 14:45 | 53100 | 81.7818 | 0.49069 | 107.7136 |  | 2007-01-01 | 14:45 | 53100 | 81.1563 | 0.48694 | 109.4531 |  | 2029-09-01 | 14:45 | 53100 | 161.667 | 0.97 | 267.5856 |  | 2006-09-01 | 14:45 | 53100 | 153.658 | 0.92195 | 251.1118 |  | 2029-09-01 | 14:45 | 53100 | 74.7881 | 0.44873 | 135.8312 |  | 2006-09-01 | 14:45 | 53100 | 63.1595 | 0.37896 | 88.441 |  | 2028-01-01 | 14:45 | 53100 | 182.713 | 1.0963 | 270.8139 |  | 2007-01-01 | 14:45 | 53100 | 155.223 | 0.93134 | 254.3106 |  | 2028-01-01 | 14:45 | 53100 | 48.1482 | 0.28889 | 64.3797 |  | 2007-01-01 | 14:45 | 53100 | 50.5553 | 0.30333 | 68.4167 |  | 2029-09-01 | 14:45 | 53100 | 160.036 | 0.96022 | 265.5367 |  | 2006-09-01 | 14:45 | 53100 | 153.476 | 0.92086 | 250.8786 |  | 2029-09-01 | 14:45 | 53100 | 56.6084 | 0.33965 | 108.5368 |  | 2006-09-01 | 14:45 | 53100 | 46.6776 | 0.28007 | 65.94 |  | 2028-01-01 | 14:45 | 53100 | 170.791 | 1.0247 | 265.547 |  | 2007-01-01 | 14:45 | 53100 | 155.075 | 0.93045 | 254.1924 |  | 2028-01-01 | 14:45 | 53100 | 33.7382 | 0.20243 | 46.0299 |  | 2007-01-01 | 14:45 | 53100 | 35.8333 | 0.215 | 49.598 |  | 2029-09-01 | 14:45 | 53100 | 91.1886 | 0.54713 | 126.8832 |  | 2029-09-01 | 14:45 | 53100 | 62.7604 | 0.37656 | 87.4292 |  | 2029-09-01 | 14:45 | 53100 | 42.9038 | 0.25742 | 60.3322 |  | 2006-09-01 | 14:45 | 53100 | 42.2365 | 0.25342 | 59.4134 |  | 2028-01-01 | 14:45 | 53100 | 81.7818 | 0.49069 | 107.7136 |  | 2007-01-01 | 14:45 | 53100 | 81.1563 | 0.48694 | 109.4531 |  | 2028-01-01 | 14:45 | 53100 | 39.2201 | 0.23532 | 54.0903 |  | 2007-01-01 | 14:45 | 53100 | 39.8807 | 0.23928 | 55.086
| 2029-09-01 | 14:46 | 53160 | 346.34 | 2.078 | 437.1965 |  | 2029-09-01 | 14:46 | 53160 | 175.916 | 1.0555 | 279.4064 |  | 2006-09-01 | 14:46 | 53160 | 159.78 | 0.95868 | 254.5469 |  | 2029-09-01 | 14:46 | 53160 | 108.704 | 0.65222 | 185.4739 |  | 2006-09-01 | 14:46 | 53160 | 94.4608 | 0.56676 | 134.0016 |  | 2028-01-01 | 14:46 | 53160 | 219.708 | 1.3182 | 290.9823 |  | 2007-01-01 | 14:46 | 53160 | 161.213 | 0.96728 | 256.8916 |  | 2028-01-01 | 14:46 | 53160 | 82.2762 | 0.49366 | 108.2073 |  | 2007-01-01 | 14:46 | 53160 | 81.9404 | 0.49164 | 109.9448 |  | 2029-09-01 | 14:46 | 53160 | 165.865 | 0.99519 | 268.5808 |  | 2006-09-01 | 14:46 | 53160 | 157.549 | 0.94529 | 252.0571 |  | 2029-09-01 | 14:46 | 53160 | 75.4066 | 0.45244 | 136.2837 |  | 2006-09-01 | 14:46 | 53160 | 63.5651 | 0.38139 | 88.8224 |  | 2028-01-01 | 14:46 | 53160 | 186.881 | 1.1213 | 271.9352 |  | 2007-01-01 | 14:46 | 53160 | 159.206 | 0.95524 | 255.2658 |  | 2028-01-01 | 14:46 | 53160 | 48.2467 | 0.28948 | 64.6692 |  | 2007-01-01 | 14:46 | 53160 | 50.7074 | 0.30424 | 68.721 |  | 2029-09-01 | 14:46 | 53160 | 164.257 | 0.98554 | 266.5222 |  | 2006-09-01 | 14:46 | 53160 | 157.37 | 0.94422 | 251.8228 |  | 2029-09-01 | 14:46 | 53160 | 56.8605 | 0.34116 | 108.878 |  | 2006-09-01 | 14:46 | 53160 | 46.8356 | 0.28101 | 66.221 |  | 2028-01-01 | 14:46 | 53160 | 175.108 | 1.0506 | 266.5976 |  | 2007-01-01 | 14:46 | 53160 | 159.059 | 0.95435 | 255.1467 |  | 2028-01-01 | 14:46 | 53160 | 33.7467 | 0.20248 | 46.2323 |  | 2007-01-01 | 14:46 | 53160 | 35.8543 | 0.21513 | 49.8131 |  | 2029-09-01 | 14:46 | 53160 | 91.7696 | 0.55062 | 127.4338 |  | 2029-09-01 | 14:46 | 53160 | 63.0257 | 0.37815 | 87.8074 |  | 2029-09-01 | 14:46 | 53160 | 42.9801 | 0.25788 | 60.59 |  | 2006-09-01 | 14:46 | 53160 | 42.3027 | 0.25382 | 59.6672 |  | 2028-01-01 | 14:46 | 53160 | 82.2762 | 0.49366 | 108.2073 |  | 2007-01-01 | 14:46 | 53160 | 81.9404 | 0.49164 | 109.9448 |  | 2028-01-01 | 14:46 | 53160 | 39.2639 | 0.23558 | 54.3259 |  | 2007-01-01 | 14:46 | 53160 | 39.9411 | 0.23965 | 55.3257
| 2029-09-01 | 14:47 | 53220 | 347.976 | 2.0879 | 439.2844 |  | 2029-09-01 | 14:47 | 53220 | 179.918 | 1.0795 | 280.4859 |  | 2006-09-01 | 14:47 | 53220 | 163.568 | 0.98141 | 255.5284 |  | 2029-09-01 | 14:47 | 53220 | 110.124 | 0.66074 | 186.1346 |  | 2006-09-01 | 14:47 | 53220 | 95.5788 | 0.57347 | 134.5751 |  | 2028-01-01 | 14:47 | 53220 | 223.411 | 1.3405 | 292.3227 |  | 2007-01-01 | 14:47 | 53220 | 165.099 | 0.99059 | 257.8822 |  | 2028-01-01 | 14:47 | 53220 | 82.7337 | 0.4964 | 108.7037 |  | 2007-01-01 | 14:47 | 53220 | 82.6732 | 0.49604 | 110.4408 |  | 2029-09-01 | 14:47 | 53220 | 170.007 | 1.02 | 269.6008 |  | 2006-09-01 | 14:47 | 53220 | 161.374 | 0.96824 | 253.0253 |  | 2029-09-01 | 14:47 | 53220 | 75.9803 | 0.45588 | 136.7395 |  | 2006-09-01 | 14:47 | 53220 | 63.9396 | 0.38364 | 89.2061 |  | 2028-01-01 | 14:47 | 53220 | 190.996 | 1.146 | 273.0812 |  | 2007-01-01 | 14:47 | 53220 | 163.122 | 0.97873 | 256.2446 |  | 2028-01-01 | 14:47 | 53220 | 48.3304 | 0.28998 | 64.9592 |  | 2007-01-01 | 14:47 | 53220 | 50.84 | 0.30504 | 69.026 |  | 2029-09-01 | 14:47 | 53220 | 168.421 | 1.0105 | 267.5328 |  | 2006-09-01 | 14:47 | 53220 | 161.198 | 0.96719 | 252.79 |  | 2029-09-01 | 14:47 | 53220 | 57.0876 | 0.34253 | 109.2205 |  | 2006-09-01 | 14:47 | 53220 | 46.9799 | 0.28188 | 66.5029 |  | 2028-01-01 | 14:47 | 53220 | 179.371 | 1.0762 | 267.6738 |  | 2007-01-01 | 14:47 | 53220 | 162.979 | 0.97787 | 256.1246 |  | 2028-01-01 | 14:47 | 53220 | 33.7509 | 0.20251 | 46.4349 |  | 2007-01-01 | 14:47 | 53220 | 35.8694 | 0.21522 | 50.0284 |  | 2029-09-01 | 14:47 | 53220 | 92.3158 | 0.55389 | 127.9877 |  | 2029-09-01 | 14:47 | 53220 | 63.2673 | 0.3796 | 88.187 |  | 2029-09-01 | 14:47 | 53220 | 43.0468 | 0.25828 | 60.8483 |  | 2006-09-01 | 14:47 | 53220 | 42.3596 | 0.25416 | 59.9213 |  | 2028-01-01 | 14:47 | 53220 | 82.7337 | 0.4964 | 108.7037 |  | 2007-01-01 | 14:47 | 53220 | 82.6732 | 0.49604 | 110.4408 |  | 2028-01-01 | 14:47 | 53220 | 39.3001 | 0.2358 | 54.5617 |  | 2007-01-01 | 14:47 | 53220 | 39.993 | 0.23996 | 55.5656
| 2029-09-01 | 14:48 | 53280 | 349.592 | 2.0976 | 441.3819 |  | 2029-09-01 | 14:48 | 53280 | 183.865 | 1.1032 | 281.5891 |  | 2006-09-01 | 14:48 | 53280 | 167.29 | 1.0037 | 256.5321 |  | 2029-09-01 | 14:48 | 53280 | 111.482 | 0.66889 | 186.8035 |  | 2006-09-01 | 14:48 | 53280 | 96.6396 | 0.57984 | 135.1549 |  | 2028-01-01 | 14:48 | 53280 | 227.067 | 1.3624 | 293.6851 |  | 2007-01-01 | 14:48 | 53280 | 168.921 | 1.0135 | 258.8957 |  | 2028-01-01 | 14:48 | 53280 | 83.1569 | 0.49894 | 109.2026 |  | 2007-01-01 | 14:48 | 53280 | 83.3582 | 0.50015 | 110.941 |  | 2029-09-01 | 14:48 | 53280 | 174.092 | 1.0446 | 270.6454 |  | 2006-09-01 | 14:48 | 53280 | 165.133 | 0.9908 | 254.0161 |  | 2029-09-01 | 14:48 | 53280 | 76.5123 | 0.45907 | 137.1986 |  | 2006-09-01 | 14:48 | 53280 | 64.2859 | 0.38572 | 89.5918 |  | 2028-01-01 | 14:48 | 53280 | 195.06 | 1.1704 | 274.2516 |  | 2007-01-01 | 14:48 | 53280 | 166.975 | 1.0018 | 257.2464 |  | 2028-01-01 | 14:48 | 53280 | 48.4012 | 0.29041 | 65.2496 |  | 2007-01-01 | 14:48 | 53280 | 50.9555 | 0.30573 | 69.3317 |  | 2029-09-01 | 14:48 | 53280 | 172.528 | 1.0352 | 268.5679 |  | 2006-09-01 | 14:48 | 53280 | 164.96 | 0.98976 | 253.7797 |  | 2029-09-01 | 14:48 | 53280 | 57.2921 | 0.34375 | 109.5642 |  | 2006-09-01 | 14:48 | 53280 | 47.1121 | 0.28267 | 66.7856 |  | 2028-01-01 | 14:48 | 53280 | 183.581 | 1.1015 | 268.7753 |  | 2007-01-01 | 14:48 | 53280 | 166.833 | 1.001 | 257.1256 |  | 2028-01-01 | 14:48 | 53280 | 33.7513 | 0.20251 | 46.6374 |  | 2007-01-01 | 14:48 | 53280 | 35.8796 | 0.21528 | 50.2436 |  | 2029-09-01 | 14:48 | 53280 | 92.8294 | 0.55698 | 128.5447 |  | 2029-09-01 | 14:48 | 53280 | 63.4876 | 0.38093 | 88.5679 |  | 2029-09-01 | 14:48 | 53280 | 43.105 | 0.25863 | 61.107 |  | 2006-09-01 | 14:48 | 53280 | 42.4084 | 0.25445 | 60.1758 |  | 2028-01-01 | 14:48 | 53280 | 83.1569 | 0.49894 | 109.2026 |  | 2007-01-01 | 14:48 | 53280 | 83.3582 | 0.50015 | 110.941 |  | 2028-01-01 | 14:48 | 53280 | 39.3299 | 0.23598 | 54.7977 |  | 2007-01-01 | 14:48 | 53280 | 40.0379 | 0.24023 | 55.8059
| 2029-09-01 | 14:49 | 53340 | 351.188 | 2.1071 | 443.4891 |  | 2029-09-01 | 14:49 | 53340 | 187.76 | 1.1266 | 282.7156 |  | 2006-09-01 | 14:49 | 53340 | 170.949 | 1.0257 | 257.5578 |  | 2029-09-01 | 14:49 | 53340 | 112.779 | 0.67667 | 187.4802 |  | 2006-09-01 | 14:49 | 53340 | 97.6465 | 0.58588 | 135.7408 |  | 2028-01-01 | 14:49 | 53340 | 230.676 | 1.3841 | 295.0692 |  | 2007-01-01 | 14:49 | 53340 | 172.68 | 1.0361 | 259.9318 |  | 2028-01-01 | 14:49 | 53340 | 83.548 | 0.50129 | 109.7039 |  | 2007-01-01 | 14:49 | 53340 | 83.9987 | 0.50399 | 111.4449 |  | 2029-09-01 | 14:49 | 53340 | 178.122 | 1.0687 | 271.7141 |  | 2006-09-01 | 14:49 | 53340 | 168.827 | 1.013 | 255.0291 |  | 2029-09-01 | 14:49 | 53340 | 77.0057 | 0.46203 | 137.6607 |  | 2006-09-01 | 14:49 | 53340 | 64.6064 | 0.38764 | 89.9794 |  | 2028-01-01 | 14:49 | 53340 | 199.071 | 1.1944 | 275.446 |  | 2007-01-01 | 14:49 | 53340 | 170.764 | 1.0246 | 258.271 |  | 2028-01-01 | 14:49 | 53340 | 48.4605 | 0.29076 | 65.5403 |  | 2007-01-01 | 14:49 | 53340 | 51.0558 | 0.30633 | 69.6381 |  | 2029-09-01 | 14:49 | 53340 | 176.58 | 1.0595 | 269.6274 |  | 2006-09-01 | 14:49 | 53340 | 168.657 | 1.0119 | 254.7917 |  | 2029-09-01 | 14:49 | 53340 | 57.4764 | 0.34486 | 109.9091 |  | 2006-09-01 | 14:49 | 53340 | 47.2339 | 0.2834 | 67.069 |  | 2028-01-01 | 14:49 | 53340 | 187.736 | 1.1264 | 269.9017 |  | 2007-01-01 | 14:49 | 53340 | 170.624 | 1.0237 | 258.1493 |  | 2028-01-01 | 14:49 | 53340 | 33.7486 | 0.20249 | 46.8399 |  | 2007-01-01 | 14:49 | 53340 | 35.8857 | 0.21531 | 50.459 |  | 2029-09-01 | 14:49 | 53340 | 93.3123 | 0.55987 | 129.1045 |  | 2029-09-01 | 14:49 | 53340 | 63.6884 | 0.38213 | 88.95 |  | 2029-09-01 | 14:49 | 53340 | 43.1559 | 0.25894 | 61.3659 |  | 2006-09-01 | 14:49 | 53340 | 42.4501 | 0.2547 | 60.4305 |  | 2028-01-01 | 14:49 | 53340 | 83.548 | 0.50129 | 109.7039 |  | 2007-01-01 | 14:49 | 53340 | 83.9987 | 0.50399 | 111.4449 |  | 2028-01-01 | 14:49 | 53340 | 39.3542 | 0.23613 | 55.0338 |  | 2007-01-01 | 14:49 | 53340 | 40.0766 | 0.24046 | 56.0463
| 2029-09-01 | 14:50 | 53400 | 352.765 | 2.1166 | 445.6057 |  | 2029-09-01 | 14:50 | 53400 | 191.601 | 1.1496 | 283.8652 |  | 2006-09-01 | 14:50 | 53400 | 174.544 | 1.0473 | 258.6051 |  | 2029-09-01 | 14:50 | 53400 | 114.02 | 0.68412 | 188.1643 |  | 2006-09-01 | 14:50 | 53400 | 98.6024 | 0.59161 | 136.3324 |  | 2028-01-01 | 14:50 | 53400 | 234.238 | 1.4054 | 296.4746 |  | 2007-01-01 | 14:50 | 53400 | 176.377 | 1.0583 | 260.9901 |  | 2028-01-01 | 14:50 | 53400 | 83.9092 | 0.50346 | 110.2074 |  | 2007-01-01 | 14:50 | 53400 | 84.5978 | 0.50759 | 111.9525 |  | 2029-09-01 | 14:50 | 53400 | 182.097 | 1.0926 | 272.8067 |  | 2006-09-01 | 14:50 | 53400 | 172.457 | 1.0347 | 256.0638 |  | 2029-09-01 | 14:50 | 53400 | 77.4632 | 0.46478 | 138.1254 |  | 2006-09-01 | 14:50 | 53400 | 64.9035 | 0.38942 | 90.3688 |  | 2028-01-01 | 14:50 | 53400 | 203.03 | 1.2182 | 276.6642 |  | 2007-01-01 | 14:50 | 53400 | 174.49 | 1.0469 | 259.318 |  | 2028-01-01 | 14:50 | 53400 | 48.5097 | 0.29106 | 65.8314 |  | 2007-01-01 | 14:50 | 53400 | 51.1429 | 0.30686 | 69.9449 |  | 2029-09-01 | 14:50 | 53400 | 180.576 | 1.0835 | 270.7109 |  | 2006-09-01 | 14:50 | 53400 | 172.29 | 1.0337 | 255.8254 |  | 2029-09-01 | 14:50 | 53400 | 57.6423 | 0.34585 | 110.255 |  | 2006-09-01 | 14:50 | 53400 | 47.3464 | 0.28408 | 67.353 |  | 2028-01-01 | 14:50 | 53400 | 191.838 | 1.151 | 271.0528 |  | 2007-01-01 | 14:50 | 53400 | 174.352 | 1.0461 | 259.1954 |  | 2028-01-01 | 14:50 | 53400 | 33.7434 | 0.20246 | 47.0423 |  | 2007-01-01 | 14:50 | 53400 | 35.8885 | 0.21533 | 50.6743 |  | 2029-09-01 | 14:50 | 53400 | 93.7666 | 0.5626 | 129.6671 |  | 2029-09-01 | 14:50 | 53400 | 63.8714 | 0.38323 | 89.3333 |  | 2029-09-01 | 14:50 | 53400 | 43.2004 | 0.2592 | 61.6251 |  | 2006-09-01 | 14:50 | 53400 | 42.4858 | 0.25491 | 60.6854 |  | 2028-01-01 | 14:50 | 53400 | 83.9092 | 0.50346 | 110.2074 |  | 2007-01-01 | 14:50 | 53400 | 84.5978 | 0.50759 | 111.9525 |  | 2028-01-01 | 14:50 | 53400 | 39.3737 | 0.23624 | 55.2701 |  | 2007-01-01 | 14:50 | 53400 | 40.1103 | 0.24066 | 56.287
| 2029-09-01 | 14:51 | 53460 | 354.323 | 2.1259 | 447.7316 |  | 2029-09-01 | 14:51 | 53460 | 195.391 | 1.1723 | 285.0376 |  | 2006-09-01 | 14:51 | 53460 | 178.077 | 1.0685 | 259.6735 |  | 2029-09-01 | 14:51 | 53460 | 115.205 | 0.69123 | 188.8555 |  | 2006-09-01 | 14:51 | 53460 | 99.51 | 0.59706 | 136.9295 |  | 2028-01-01 | 14:51 | 53460 | 237.754 | 1.4265 | 297.9011 |  | 2007-01-01 | 14:51 | 53460 | 180.013 | 1.0801 | 262.0701 |  | 2028-01-01 | 14:51 | 53460 | 84.2427 | 0.50546 | 110.7128 |  | 2007-01-01 | 14:51 | 53460 | 85.1585 | 0.51095 | 112.4635 |  | 2029-09-01 | 14:51 | 53460 | 186.019 | 1.1161 | 273.9228 |  | 2006-09-01 | 14:51 | 53460 | 176.025 | 1.0561 | 257.12 |  | 2029-09-01 | 14:51 | 53460 | 77.8876 | 0.46733 | 138.5928 |  | 2006-09-01 | 14:51 | 53460 | 65.1793 | 0.39108 | 90.7599 |  | 2028-01-01 | 14:51 | 53460 | 206.938 | 1.2416 | 277.9058 |  | 2007-01-01 | 14:51 | 53460 | 178.154 | 1.0689 | 260.3869 |  | 2028-01-01 | 14:51 | 53460 | 48.55 | 0.2913 | 66.1227 |  | 2007-01-01 | 14:51 | 53460 | 51.2184 | 0.30731 | 70.2522 |  | 2029-09-01 | 14:51 | 53460 | 184.519 | 1.1071 | 271.818 |  | 2006-09-01 | 14:51 | 53460 | 175.86 | 1.0552 | 256.8806 |  | 2029-09-01 | 14:51 | 53460 | 57.7918 | 0.34675 | 110.6017 |  | 2006-09-01 | 14:51 | 53460 | 47.4508 | 0.2847 | 67.6378 |  | 2028-01-01 | 14:51 | 53460 | 195.886 | 1.1753 | 272.2281 |  | 2007-01-01 | 14:51 | 53460 | 178.019 | 1.0681 | 260.2636 |  | 2028-01-01 | 14:51 | 53460 | 33.7359 | 0.20242 | 47.2447 |  | 2007-01-01 | 14:51 | 53460 | 35.8885 | 0.21533 | 50.8896 |  | 2029-09-01 | 14:51 | 53460 | 94.1939 | 0.56516 | 130.2323 |  | 2029-09-01 | 14:51 | 53460 | 64.0384 | 0.38423 | 89.7175 |  | 2029-09-01 | 14:51 | 53460 | 43.2394 | 0.25944 | 61.8845 |  | 2006-09-01 | 14:51 | 53460 | 42.5161 | 0.2551 | 60.9405 |  | 2028-01-01 | 14:51 | 53460 | 84.2427 | 0.50546 | 110.7128 |  | 2007-01-01 | 14:51 | 53460 | 85.1585 | 0.51095 | 112.4635 |  | 2028-01-01 | 14:51 | 53460 | 39.3891 | 0.23633 | 55.5064 |  | 2007-01-01 | 14:51 | 53460 | 40.1397 | 0.24084 | 56.5278
| 2029-09-01 | 14:52 | 53520 | 355.862 | 2.1352 | 449.8668 |  | 2029-09-01 | 14:52 | 53520 | 199.131 | 1.1948 | 286.2324 |  | 2006-09-01 | 14:52 | 53520 | 181.548 | 1.0893 | 260.7628 |  | 2029-09-01 | 14:52 | 53520 | 116.337 | 0.69802 | 189.5536 |  | 2006-09-01 | 14:52 | 53520 | 100.372 | 0.60223 | 137.5317 |  | 2028-01-01 | 14:52 | 53520 | 241.224 | 1.4473 | 299.3485 |  | 2007-01-01 | 14:52 | 53520 | 183.588 | 1.1015 | 263.1717 |  | 2028-01-01 | 14:52 | 53520 | 84.5501 | 0.5073 | 111.2201 |  | 2007-01-01 | 14:52 | 53520 | 85.6835 | 0.5141 | 112.9776 |  | 2029-09-01 | 14:52 | 53520 | 189.888 | 1.1393 | 275.0621 |  | 2006-09-01 | 14:52 | 53520 | 179.53 | 1.0772 | 258.1971 |  | 2029-09-01 | 14:52 | 53520 | 78.2812 | 0.46969 | 139.0624 |  | 2006-09-01 | 14:52 | 53520 | 65.4356 | 0.39261 | 91.1525 |  | 2028-01-01 | 14:52 | 53520 | 210.796 | 1.2648 | 279.1706 |  | 2007-01-01 | 14:52 | 53520 | 181.758 | 1.0905 | 261.4774 |  | 2028-01-01 | 14:52 | 53520 | 48.5823 | 0.29149 | 66.4142 |  | 2007-01-01 | 14:52 | 53520 | 51.2836 | 0.3077 | 70.5599 |  | 2029-09-01 | 14:52 | 53520 | 188.409 | 1.1305 | 272.9484 |  | 2006-09-01 | 14:52 | 53520 | 179.368 | 1.0762 | 257.9568 |  | 2029-09-01 | 14:52 | 53520 | 57.9265 | 0.34756 | 110.9493 |  | 2006-09-01 | 14:52 | 53520 | 47.548 | 0.28529 | 67.923 |  | 2028-01-01 | 14:52 | 53520 | 199.883 | 1.1993 | 273.4274 |  | 2007-01-01 | 14:52 | 53520 | 181.624 | 1.0897 | 261.3533 |  | 2028-01-01 | 14:52 | 53520 | 33.7267 | 0.20236 | 47.4471 |  | 2007-01-01 | 14:52 | 53520 | 35.8863 | 0.21532 | 51.1049 |  | 2029-09-01 | 14:52 | 53520 | 94.596 | 0.56758 | 130.7999 |  | 2029-09-01 | 14:52 | 53520 | 64.1908 | 0.38514 | 90.1026 |  | 2029-09-01 | 14:52 | 53520 | 43.2737 | 0.25964 | 62.1442 |  | 2006-09-01 | 14:52 | 53520 | 42.5418 | 0.25525 | 61.1957 |  | 2028-01-01 | 14:52 | 53520 | 84.5501 | 0.5073 | 111.2201 |  | 2007-01-01 | 14:52 | 53520 | 85.6835 | 0.5141 | 112.9776 |  | 2028-01-01 | 14:52 | 53520 | 39.401 | 0.23641 | 55.7428 |  | 2007-01-01 | 14:52 | 53520 | 40.1654 | 0.24099 | 56.7688
| 2029-09-01 | 14:53 | 53580 | 357.383 | 2.1443 | 452.0111 |  | 2029-09-01 | 14:53 | 53580 | 202.82 | 1.2169 | 287.4493 |  | 2006-09-01 | 14:53 | 53580 | 184.959 | 1.1098 | 261.8726 |  | 2029-09-01 | 14:53 | 53580 | 117.42 | 0.70452 | 190.2581 |  | 2006-09-01 | 14:53 | 53580 | 101.191 | 0.60715 | 138.1389 |  | 2028-01-01 | 14:53 | 53580 | 244.648 | 1.4679 | 300.8164 |  | 2007-01-01 | 14:53 | 53580 | 187.103 | 1.1226 | 264.2943 |  | 2028-01-01 | 14:53 | 53580 | 84.8334 | 0.509 | 111.7291 |  | 2007-01-01 | 14:53 | 53580 | 86.1755 | 0.51705 | 113.4946 |  | 2029-09-01 | 14:53 | 53580 | 193.705 | 1.1622 | 276.2244 |  | 2006-09-01 | 14:53 | 53580 | 182.975 | 1.0978 | 259.295 |  | 2029-09-01 | 14:53 | 53580 | 78.6462 | 0.47188 | 139.5343 |  | 2006-09-01 | 14:53 | 53580 | 65.6743 | 0.39405 | 91.5466 |  | 2028-01-01 | 14:53 | 53580 | 214.603 | 1.2876 | 280.4582 |  | 2007-01-01 | 14:53 | 53580 | 185.301 | 1.1118 | 262.5892 |  | 2028-01-01 | 14:53 | 53580 | 48.6078 | 0.29165 | 66.7058 |  | 2007-01-01 | 14:53 | 53580 | 51.3399 | 0.30804 | 70.868 |  | 2029-09-01 | 14:53 | 53580 | 192.247 | 1.1535 | 274.1019 |  | 2006-09-01 | 14:53 | 53580 | 182.815 | 1.0969 | 259.0537 |  | 2029-09-01 | 14:53 | 53580 | 58.0479 | 0.34829 | 111.2976 |  | 2006-09-01 | 14:53 | 53580 | 47.639 | 0.28583 | 68.2089 |  | 2028-01-01 | 14:53 | 53580 | 203.828 | 1.223 | 274.6503 |  | 2007-01-01 | 14:53 | 53580 | 185.17 | 1.111 | 262.4643 |  | 2028-01-01 | 14:53 | 53580 | 33.7159 | 0.2023 | 47.6494 |  | 2007-01-01 | 14:53 | 53580 | 35.8823 | 0.21529 | 51.3202 |  | 2029-09-01 | 14:53 | 53580 | 94.9743 | 0.56985 | 131.3697 |  | 2029-09-01 | 14:53 | 53580 | 64.3299 | 0.38598 | 90.4886 |  | 2029-09-01 | 14:53 | 53580 | 43.3038 | 0.25982 | 62.404 |  | 2006-09-01 | 14:53 | 53580 | 42.5635 | 0.25538 | 61.4511 |  | 2028-01-01 | 14:53 | 53580 | 84.8334 | 0.509 | 111.7291 |  | 2007-01-01 | 14:53 | 53580 | 86.1755 | 0.51705 | 113.4946 |  | 2028-01-01 | 14:53 | 53580 | 39.4099 | 0.23646 | 55.9793 |  | 2007-01-01 | 14:53 | 53580 | 40.1882 | 0.24113 | 57.0099
| 2029-09-01 | 14:54 | 53640 | 358.887 | 2.1533 | 454.1644 |  | 2029-09-01 | 14:54 | 53640 | 206.46 | 1.2388 | 288.6881 |  | 2006-09-01 | 14:54 | 53640 | 188.311 | 1.1299 | 263.0024 |  | 2029-09-01 | 14:54 | 53640 | 118.455 | 0.71073 | 190.9688 |  | 2006-09-01 | 14:54 | 53640 | 101.969 | 0.61181 | 138.7507 |  | 2028-01-01 | 14:54 | 53640 | 248.028 | 1.4882 | 302.3045 |  | 2007-01-01 | 14:54 | 53640 | 190.56 | 1.1434 | 265.4377 |  | 2028-01-01 | 14:54 | 53640 | 85.0942 | 0.51057 | 112.2397 |  | 2007-01-01 | 14:54 | 53640 | 86.6371 | 0.51982 | 114.0145 |  | 2029-09-01 | 14:54 | 53640 | 197.471 | 1.1848 | 277.4092 |  | 2006-09-01 | 14:54 | 53640 | 186.359 | 1.1182 | 260.4131 |  | 2029-09-01 | 14:54 | 53640 | 78.9848 | 0.47391 | 140.0082 |  | 2006-09-01 | 14:54 | 53640 | 65.8969 | 0.39538 | 91.942 |  | 2028-01-01 | 14:54 | 53640 | 218.362 | 1.3102 | 281.7684 |  | 2007-01-01 | 14:54 | 53640 | 188.786 | 1.1327 | 263.7219 |  | 2028-01-01 | 14:54 | 53640 | 48.6271 | 0.29176 | 66.9976 |  | 2007-01-01 | 14:54 | 53640 | 51.3886 | 0.30833 | 71.1763 |  | 2029-09-01 | 14:54 | 53640 | 196.033 | 1.1762 | 275.2781 |  | 2006-09-01 | 14:54 | 53640 | 186.202 | 1.1172 | 260.1709 |  | 2029-09-01 | 14:54 | 53640 | 58.1572 | 0.34894 | 111.6465 |  | 2006-09-01 | 14:54 | 53640 | 47.7246 | 0.28635 | 68.4952 |  | 2028-01-01 | 14:54 | 53640 | 207.722 | 1.2463 | 275.8967 |  | 2007-01-01 | 14:54 | 53640 | 188.657 | 1.1319 | 263.5963 |  | 2028-01-01 | 14:54 | 53640 | 33.7039 | 0.20222 | 47.8516 |  | 2007-01-01 | 14:54 | 53640 | 35.877 | 0.21526 | 51.5355 |  | 2029-09-01 | 14:54 | 53640 | 95.3307 | 0.57198 | 131.9417 |  | 2029-09-01 | 14:54 | 53640 | 64.4571 | 0.38674 | 90.8754 |  | 2029-09-01 | 14:54 | 53640 | 43.3304 | 0.25998 | 62.664 |  | 2006-09-01 | 14:54 | 53640 | 42.5818 | 0.25549 | 61.7066 |  | 2028-01-01 | 14:54 | 53640 | 85.0942 | 0.51057 | 112.2397 |  | 2007-01-01 | 14:54 | 53640 | 86.6371 | 0.51982 | 114.0145 |  | 2028-01-01 | 14:54 | 53640 | 39.4163 | 0.2365 | 56.2158 |  | 2007-01-01 | 14:54 | 53640 | 40.2086 | 0.24125 | 57.2512
| 2029-09-01 | 14:55 | 53700 | 360.374 | 2.1622 | 456.3266 |  | 2029-09-01 | 14:55 | 53700 | 210.053 | 1.2603 | 289.9484 |  | 2006-09-01 | 14:55 | 53700 | 191.603 | 1.1496 | 264.152 |  | 2029-09-01 | 14:55 | 53700 | 119.444 | 0.71666 | 191.6855 |  | 2006-09-01 | 14:55 | 53700 | 102.708 | 0.61625 | 139.3669 |  | 2028-01-01 | 14:55 | 53700 | 251.364 | 1.5082 | 303.8127 |  | 2007-01-01 | 14:55 | 53700 | 193.96 | 1.1638 | 266.6014 |  | 2028-01-01 | 14:55 | 53700 | 85.3339 | 0.512 | 112.7517 |  | 2007-01-01 | 14:55 | 53700 | 87.0707 | 0.52242 | 114.5369 |  | 2029-09-01 | 14:55 | 53700 | 201.188 | 1.2071 | 278.6163 |  | 2006-09-01 | 14:55 | 53700 | 189.684 | 1.1381 | 261.5512 |  | 2029-09-01 | 14:55 | 53700 | 79.2989 | 0.47579 | 140.484 |  | 2006-09-01 | 14:55 | 53700 | 66.1048 | 0.39663 | 92.3386 |  | 2028-01-01 | 14:55 | 53700 | 222.071 | 1.3324 | 283.1008 |  | 2007-01-01 | 14:55 | 53700 | 192.212 | 1.1533 | 264.8752 |  | 2028-01-01 | 14:55 | 53700 | 48.641 | 0.29185 | 67.2894 |  | 2007-01-01 | 14:55 | 53700 | 51.4307 | 0.30858 | 71.4849 |  | 2029-09-01 | 14:55 | 53700 | 199.77 | 1.1986 | 276.4767 |  | 2006-09-01 | 14:55 | 53700 | 189.53 | 1.1372 | 261.3081 |  | 2029-09-01 | 14:55 | 53700 | 58.2558 | 0.34953 | 111.996 |  | 2006-09-01 | 14:55 | 53700 | 47.8053 | 0.28683 | 68.7821 |  | 2028-01-01 | 14:55 | 53700 | 211.566 | 1.2694 | 277.1661 |  | 2007-01-01 | 14:55 | 53700 | 192.085 | 1.1525 | 264.7488 |  | 2028-01-01 | 14:55 | 53700 | 33.6908 | 0.20214 | 48.0538 |  | 2007-01-01 | 14:55 | 53700 | 35.8707 | 0.21522 | 51.7507 |  | 2029-09-01 | 14:55 | 53700 | 95.6663 | 0.574 | 132.5157 |  | 2029-09-01 | 14:55 | 53700 | 64.5734 | 0.38744 | 91.2628 |  | 2029-09-01 | 14:55 | 53700 | 43.3539 | 0.26012 | 62.9241 |  | 2006-09-01 | 14:55 | 53700 | 42.597 | 0.25558 | 61.9622 |  | 2028-01-01 | 14:55 | 53700 | 85.3339 | 0.512 | 112.7517 |  | 2007-01-01 | 14:55 | 53700 | 87.0707 | 0.52242 | 114.5369 |  | 2028-01-01 | 14:55 | 53700 | 39.4204 | 0.23652 | 56.4523 |  | 2007-01-01 | 14:55 | 53700 | 40.2271 | 0.24136 | 57.4925
| 2029-09-01 | 14:56 | 53760 | 361.844 | 2.1711 | 458.4977 |  | 2029-09-01 | 14:56 | 53760 | 213.597 | 1.2816 | 291.23 |  | 2006-09-01 | 14:56 | 53760 | 194.838 | 1.169 | 265.3211 |  | 2029-09-01 | 14:56 | 53760 | 120.389 | 0.72233 | 192.4078 |  | 2006-09-01 | 14:56 | 53760 | 103.412 | 0.62047 | 139.9874 |  | 2028-01-01 | 14:56 | 53760 | 254.656 | 1.5279 | 305.3407 |  | 2007-01-01 | 14:56 | 53760 | 197.302 | 1.1838 | 267.7852 |  | 2028-01-01 | 14:56 | 53760 | 85.5541 | 0.51332 | 113.265 |  | 2007-01-01 | 14:56 | 53760 | 87.4781 | 0.52487 | 115.0618 |  | 2029-09-01 | 14:56 | 53760 | 204.855 | 1.2291 | 279.8454 |  | 2006-09-01 | 14:56 | 53760 | 192.951 | 1.1577 | 262.709 |  | 2029-09-01 | 14:56 | 53760 | 79.5902 | 0.47754 | 140.9616 |  | 2006-09-01 | 14:56 | 53760 | 66.2994 | 0.3978 | 92.7364 |  | 2028-01-01 | 14:56 | 53760 | 225.732 | 1.3544 | 284.4552 |  | 2007-01-01 | 14:56 | 53760 | 195.582 | 1.1735 | 266.0487 |  | 2028-01-01 | 14:56 | 53760 | 48.6501 | 0.2919 | 67.5813 |  | 2007-01-01 | 14:56 | 53760 | 51.4673 | 0.3088 | 71.7937 |  | 2029-09-01 | 14:56 | 53760 | 203.456 | 1.2207 | 277.6975 |  | 2006-09-01 | 14:56 | 53760 | 192.8 | 1.1568 | 262.4649 |  | 2029-09-01 | 14:56 | 53760 | 58.3445 | 0.35007 | 112.3461 |  | 2006-09-01 | 14:56 | 53760 | 47.8818 | 0.28729 | 69.0693 |  | 2028-01-01 | 14:56 | 53760 | 215.359 | 1.2922 | 278.4582 |  | 2007-01-01 | 14:56 | 53760 | 195.456 | 1.1727 | 265.9215 |  | 2028-01-01 | 14:56 | 53760 | 33.6769 | 0.20206 | 48.2558 |  | 2007-01-01 | 14:56 | 53760 | 35.8638 | 0.21518 | 51.9659 |  | 2029-09-01 | 14:56 | 53760 | 95.9824 | 0.57589 | 133.0916 |  | 2029-09-01 | 14:56 | 53760 | 64.6798 | 0.38808 | 91.6509 |  | 2029-09-01 | 14:56 | 53760 | 43.3748 | 0.26025 | 63.1843 |  | 2006-09-01 | 14:56 | 53760 | 42.6097 | 0.25566 | 62.2179 |  | 2028-01-01 | 14:56 | 53760 | 85.5541 | 0.51332 | 113.265 |  | 2007-01-01 | 14:56 | 53760 | 87.4781 | 0.52487 | 115.0618 |  | 2028-01-01 | 14:56 | 53760 | 39.4227 | 0.23654 | 56.6888 |  | 2007-01-01 | 14:56 | 53760 | 40.244 | 0.24146 | 57.734
| 2029-09-01 | 14:57 | 53820 | 363.297 | 2.1798 | 460.6775 |  | 2029-09-01 | 14:57 | 53820 | 217.095 | 1.3026 | 292.5325 |  | 2006-09-01 | 14:57 | 53820 | 198.016 | 1.1881 | 266.5092 |  | 2029-09-01 | 14:57 | 53820 | 121.293 | 0.72776 | 193.1356 |  | 2006-09-01 | 14:57 | 53820 | 104.08 | 0.62448 | 140.6119 |  | 2028-01-01 | 14:57 | 53820 | 257.905 | 1.5474 | 306.8881 |  | 2007-01-01 | 14:57 | 53820 | 200.589 | 1.2035 | 268.9888 |  | 2028-01-01 | 14:57 | 53820 | 85.756 | 0.51454 | 113.7795 |  | 2007-01-01 | 14:57 | 53820 | 87.8614 | 0.52717 | 115.5889 |  | 2029-09-01 | 14:57 | 53820 | 208.474 | 1.2508 | 281.0963 |  | 2006-09-01 | 14:57 | 53820 | 196.161 | 1.177 | 263.8859 |  | 2029-09-01 | 14:57 | 53820 | 79.8604 | 0.47916 | 141.4407 |  | 2006-09-01 | 14:57 | 53820 | 66.4819 | 0.39889 | 93.1353 |  | 2028-01-01 | 14:57 | 53820 | 229.346 | 1.3761 | 285.8313 |  | 2007-01-01 | 14:57 | 53820 | 198.894 | 1.1934 | 267.2421 |  | 2028-01-01 | 14:57 | 53820 | 48.6551 | 0.29193 | 67.8733 |  | 2007-01-01 | 14:57 | 53820 | 51.4997 | 0.309 | 72.1027 |  | 2029-09-01 | 14:57 | 53820 | 207.094 | 1.2426 | 278.94 |  | 2006-09-01 | 14:57 | 53820 | 196.012 | 1.1761 | 263.6409 |  | 2029-09-01 | 14:57 | 53820 | 58.4245 | 0.35055 | 112.6967 |  | 2006-09-01 | 14:57 | 53820 | 47.9547 | 0.28773 | 69.3571 |  | 2028-01-01 | 14:57 | 53820 | 219.104 | 1.3146 | 279.7728 |  | 2007-01-01 | 14:57 | 53820 | 198.771 | 1.1926 | 267.1141 |  | 2028-01-01 | 14:57 | 53820 | 33.6622 | 0.20197 | 48.4578 |  | 2007-01-01 | 14:57 | 53820 | 35.8568 | 0.21514 | 52.181 |  | 2029-09-01 | 14:57 | 53820 | 96.28 | 0.57768 | 133.6693 |  | 2029-09-01 | 14:57 | 53820 | 64.7771 | 0.38866 | 92.0395 |  | 2029-09-01 | 14:57 | 53820 | 43.3933 | 0.26036 | 63.4447 |  | 2006-09-01 | 14:57 | 53820 | 42.6201 | 0.25572 | 62.4736 |  | 2028-01-01 | 14:57 | 53820 | 85.756 | 0.51454 | 113.7795 |  | 2007-01-01 | 14:57 | 53820 | 87.8614 | 0.52717 | 115.5889 |  | 2028-01-01 | 14:57 | 53820 | 39.4233 | 0.23654 | 56.9254 |  | 2007-01-01 | 14:57 | 53820 | 40.2596 | 0.24156 | 57.9756
| 2029-09-01 | 14:58 | 53880 | 364.733 | 2.1884 | 462.8659 |  | 2029-09-01 | 14:58 | 53880 | 220.547 | 1.3233 | 293.8558 |  | 2006-09-01 | 14:58 | 53880 | 201.138 | 1.2068 | 267.716 |  | 2029-09-01 | 14:58 | 53880 | 122.156 | 0.73294 | 193.8685 |  | 2006-09-01 | 14:58 | 53880 | 104.716 | 0.6283 | 141.2402 |  | 2028-01-01 | 14:58 | 53880 | 261.111 | 1.5667 | 308.4548 |  | 2007-01-01 | 14:58 | 53880 | 203.82 | 1.2229 | 270.2117 |  | 2028-01-01 | 14:58 | 53880 | 85.9412 | 0.51565 | 114.2952 |  | 2007-01-01 | 14:58 | 53880 | 88.2245 | 0.52935 | 116.1183 |  | 2029-09-01 | 14:58 | 53880 | 212.044 | 1.2723 | 282.3685 |  | 2006-09-01 | 14:58 | 53880 | 199.313 | 1.1959 | 265.0818 |  | 2029-09-01 | 14:58 | 53880 | 80.1111 | 0.48067 | 141.9214 |  | 2006-09-01 | 14:58 | 53880 | 66.6533 | 0.39992 | 93.5352 |  | 2028-01-01 | 14:58 | 53880 | 232.913 | 1.3975 | 287.2287 |  | 2007-01-01 | 14:58 | 53880 | 202.152 | 1.2129 | 268.455 |  | 2028-01-01 | 14:58 | 53880 | 48.6565 | 0.29194 | 68.1652 |  | 2007-01-01 | 14:58 | 53880 | 51.5293 | 0.30918 | 72.4119 |  | 2029-09-01 | 14:58 | 53880 | 210.684 | 1.2641 | 280.2041 |  | 2006-09-01 | 14:58 | 53880 | 199.167 | 1.195 | 264.8359 |  | 2029-09-01 | 14:58 | 53880 | 58.4967 | 0.35098 | 113.0476 |  | 2006-09-01 | 14:58 | 53880 | 48.0243 | 0.28815 | 69.6452 |  | 2028-01-01 | 14:58 | 53880 | 222.8 | 1.3368 | 281.1096 |  | 2007-01-01 | 14:58 | 53880 | 202.03 | 1.2122 | 268.3263 |  | 2028-01-01 | 14:58 | 53880 | 33.647 | 0.20188 | 48.6597 |  | 2007-01-01 | 14:58 | 53880 | 35.8504 | 0.2151 | 52.3961 |  | 2029-09-01 | 14:58 | 53880 | 96.5604 | 0.57936 | 134.2486 |  | 2029-09-01 | 14:58 | 53880 | 64.8662 | 0.3892 | 92.4287 |  | 2029-09-01 | 14:58 | 53880 | 43.4096 | 0.26046 | 63.7052 |  | 2006-09-01 | 14:58 | 53880 | 42.6285 | 0.25577 | 62.7293 |  | 2028-01-01 | 14:58 | 53880 | 85.9412 | 0.51565 | 114.2952 |  | 2007-01-01 | 14:58 | 53880 | 88.2245 | 0.52935 | 116.1183 |  | 2028-01-01 | 14:58 | 53880 | 39.4226 | 0.23654 | 57.1619 |  | 2007-01-01 | 14:58 | 53880 | 40.2752 | 0.24165 | 58.2172
| 2029-09-01 | 14:59 | 53940 | 366.153 | 2.1969 | 465.0628 |  | 2029-09-01 | 14:59 | 53940 | 223.952 | 1.3437 | 295.1995 |  | 2006-09-01 | 14:59 | 53940 | 204.205 | 1.2252 | 268.9412 |  | 2029-09-01 | 14:59 | 53940 | 122.982 | 0.73789 | 194.6064 |  | 2006-09-01 | 14:59 | 53940 | 105.322 | 0.63193 | 141.8721 |  | 2028-01-01 | 14:59 | 53940 | 264.277 | 1.5857 | 310.0404 |  | 2007-01-01 | 14:59 | 53940 | 206.997 | 1.242 | 271.4537 |  | 2028-01-01 | 14:59 | 53940 | 86.1108 | 0.51666 | 114.8119 |  | 2007-01-01 | 14:59 | 53940 | 88.5526 | 0.53132 | 116.6496 |  | 2029-09-01 | 14:59 | 53940 | 215.567 | 1.2934 | 283.6619 |  | 2006-09-01 | 14:59 | 53940 | 202.411 | 1.2145 | 266.2963 |  | 2029-09-01 | 14:59 | 53940 | 80.3436 | 0.48206 | 142.4035 |  | 2006-09-01 | 14:59 | 53940 | 66.8147 | 0.40089 | 93.9361 |  | 2028-01-01 | 14:59 | 53940 | 236.435 | 1.4186 | 288.6474 |  | 2007-01-01 | 14:59 | 53940 | 205.354 | 1.2321 | 269.6871 |  | 2028-01-01 | 14:59 | 53940 | 48.6547 | 0.29193 | 68.4571 |  | 2007-01-01 | 14:59 | 53940 | 51.5495 | 0.3093 | 72.7212 |  | 2029-09-01 | 14:59 | 53940 | 214.225 | 1.2853 | 281.4895 |  | 2006-09-01 | 14:59 | 53940 | 202.267 | 1.2136 | 266.0495 |  | 2029-09-01 | 14:59 | 53940 | 58.5616 | 0.35137 | 113.399 |  | 2006-09-01 | 14:59 | 53940 | 48.0911 | 0.28855 | 69.9338 |  | 2028-01-01 | 14:59 | 53940 | 226.449 | 1.3587 | 282.4683 |  | 2007-01-01 | 14:59 | 53940 | 205.234 | 1.2314 | 269.5577 |  | 2028-01-01 | 14:59 | 53940 | 33.6313 | 0.20179 | 48.8615 |  | 2007-01-01 | 14:59 | 53940 | 35.8402 | 0.21504 | 52.6112 |  | 2029-09-01 | 14:59 | 53940 | 96.8245 | 0.58095 | 134.8296 |  | 2029-09-01 | 14:59 | 53940 | 64.9477 | 0.38969 | 92.8184 |  | 2029-09-01 | 14:59 | 53940 | 43.4242 | 0.26055 | 63.9657 |  | 2006-09-01 | 14:59 | 53940 | 42.6352 | 0.25581 | 62.9852 |  | 2028-01-01 | 14:59 | 53940 | 86.1108 | 0.51666 | 114.8119 |  | 2007-01-01 | 14:59 | 53940 | 88.5526 | 0.53132 | 116.6496 |  | 2028-01-01 | 14:59 | 53940 | 39.4209 | 0.23653 | 57.3984 |  | 2007-01-01 | 14:59 | 53940 | 40.2841 | 0.2417 | 58.4589
6 | 2029-09-01 | 15:00 | 54000 | 367.555 | 2.2053 | 467.2681 |  | 2029-09-01 | 15:00 | 54000 | 227.313 | 1.3639 | 296.5634 |  | 2006-09-01 | 15:00 | 54000 | 207.217 | 1.2433 | 270.1845 |  | 2029-09-01 | 15:00 | 54000 | 123.771 | 0.74263 | 195.349 |  | 2006-09-01 | 15:00 | 54000 | 105.898 | 0.63539 | 142.5075 |  | 2028-01-01 | 15:00 | 54000 | 267.401 | 1.6044 | 311.6448 |  | 2007-01-01 | 15:00 | 54000 | 210.12 | 1.2607 | 272.7144 |  | 2028-01-01 | 15:00 | 54000 | 86.266 | 0.5176 | 115.3295 |  | 2007-01-01 | 15:00 | 54000 | 88.847 | 0.53308 | 117.1827 |  | 2029-09-01 | 15:00 | 54000 | 219.043 | 1.3143 | 284.9762 |  | 2006-09-01 | 15:00 | 54000 | 205.453 | 1.2327 | 267.529 |  | 2029-09-01 | 15:00 | 54000 | 80.5593 | 0.48336 | 142.8868 |  | 2006-09-01 | 15:00 | 54000 | 66.9669 | 0.4018 | 94.3379 |  | 2028-01-01 | 15:00 | 54000 | 239.91 | 1.4395 | 290.0868 |  | 2007-01-01 | 15:00 | 54000 | 208.502 | 1.251 | 270.9381 |  | 2028-01-01 | 15:00 | 54000 | 48.6502 | 0.2919 | 68.749 |  | 2007-01-01 | 15:00 | 54000 | 51.559 | 0.30935 | 73.0305 |  | 2029-09-01 | 15:00 | 54000 | 217.72 | 1.3063 | 282.7958 |  | 2006-09-01 | 15:00 | 54000 | 205.311 | 1.2319 | 267.2814 |  | 2029-09-01 | 15:00 | 54000 | 58.6202 | 0.35172 | 113.7507 |  | 2006-09-01 | 15:00 | 54000 | 48.1555 | 0.28893 | 70.2227 |  | 2028-01-01 | 15:00 | 54000 | 230.051 | 1.3803 | 283.8486 |  | 2007-01-01 | 15:00 | 54000 | 208.385 | 1.2503 | 270.808 |  | 2028-01-01 | 15:00 | 54000 | 33.6154 | 0.20169 | 49.0632 |  | 2007-01-01 | 15:00 | 54000 | 35.8252 | 0.21495 | 52.8261 |  | 2029-09-01 | 15:00 | 54000 | 97.0734 | 0.58244 | 135.412 |  | 2029-09-01 | 15:00 | 54000 | 65.0223 | 0.39013 | 93.2086 |  | 2029-09-01 | 15:00 | 54000 | 43.4372 | 0.26062 | 64.2263 |  | 2006-09-01 | 15:00 | 54000 | 42.6405 | 0.25584 | 63.241 |  | 2028-01-01 | 15:00 | 54000 | 86.266 | 0.5176 | 115.3295 |  | 2007-01-01 | 15:00 | 54000 | 88.847 | 0.53308 | 117.1827 |  | 2028-01-01 | 15:00 | 54000 | 39.4182 | 0.23651 | 57.6349 |  | 2007-01-01 | 15:00 | 54000 | 40.287 | 0.24172 | 58.7006
| 2029-09-01 | 15:01 | 54060 | 368.939 | 2.2136 | 469.4818 |  | 2029-09-01 | 15:01 | 54060 | 230.628 | 1.3838 | 297.9472 |  | 2006-09-01 | 15:01 | 54060 | 210.176 | 1.2611 | 271.4456 |  | 2029-09-01 | 15:01 | 54060 | 124.525 | 0.74715 | 196.0962 |  | 2006-09-01 | 15:01 | 54060 | 106.447 | 0.63868 | 143.1462 |  | 2028-01-01 | 15:01 | 54060 | 270.484 | 1.6229 | 313.2677 |  | 2007-01-01 | 15:01 | 54060 | 213.191 | 1.2791 | 273.9935 |  | 2028-01-01 | 15:01 | 54060 | 86.4134 | 0.51848 | 115.8479 |  | 2007-01-01 | 15:01 | 54060 | 89.1144 | 0.53469 | 117.7174 |  | 2029-09-01 | 15:01 | 54060 | 222.471 | 1.3348 | 286.311 |  | 2006-09-01 | 15:01 | 54060 | 208.441 | 1.2506 | 268.7796 |  | 2029-09-01 | 15:01 | 54060 | 80.7596 | 0.48456 | 143.3714 |  | 2006-09-01 | 15:01 | 54060 | 67.1109 | 0.40267 | 94.7406 |  | 2028-01-01 | 15:01 | 54060 | 243.34 | 1.46 | 291.5469 |  | 2007-01-01 | 15:01 | 54060 | 211.598 | 1.2696 | 272.2077 |  | 2028-01-01 | 15:01 | 54060 | 48.6494 | 0.2919 | 69.0409 |  | 2007-01-01 | 15:01 | 54060 | 51.5636 | 0.30938 | 73.3399 |  | 2029-09-01 | 15:01 | 54060 | 221.167 | 1.327 | 284.1228 |  | 2006-09-01 | 15:01 | 54060 | 208.302 | 1.2498 | 268.5312 |  | 2029-09-01 | 15:01 | 54060 | 58.6732 | 0.35204 | 114.1028 |  | 2006-09-01 | 15:01 | 54060 | 48.2177 | 0.28931 | 70.512 |  | 2028-01-01 | 15:01 | 54060 | 233.606 | 1.4016 | 285.2503 |  | 2007-01-01 | 15:01 | 54060 | 211.482 | 1.2689 | 272.0769 |  | 2028-01-01 | 15:01 | 54060 | 33.605 | 0.20163 | 49.2648 |  | 2007-01-01 | 15:01 | 54060 | 35.81 | 0.21486 | 53.041 |  | 2029-09-01 | 15:01 | 54060 | 97.307 | 0.58384 | 135.9959 |  | 2029-09-01 | 15:01 | 54060 | 65.0902 | 0.39054 | 93.5991 |  | 2029-09-01 | 15:01 | 54060 | 43.4485 | 0.26069 | 64.487 |  | 2006-09-01 | 15:01 | 54060 | 42.6445 | 0.25587 | 63.4969 |  | 2028-01-01 | 15:01 | 54060 | 86.4134 | 0.51848 | 115.8479 |  | 2007-01-01 | 15:01 | 54060 | 89.1144 | 0.53469 | 117.7174 |  | 2028-01-01 | 15:01 | 54060 | 39.4172 | 0.2365 | 57.8714 |  | 2007-01-01 | 15:01 | 54060 | 40.2866 | 0.24172 | 58.9424
| 2029-09-01 | 15:02 | 54120 | 370.303 | 2.2218 | 471.7036 |  | 2029-09-01 | 15:02 | 54120 | 233.896 | 1.4034 | 299.3505 |  | 2006-09-01 | 15:02 | 54120 | 213.082 | 1.2785 | 272.7241 |  | 2029-09-01 | 15:02 | 54120 | 125.247 | 0.75148 | 196.8477 |  | 2006-09-01 | 15:02 | 54120 | 106.97 | 0.64182 | 143.788 |  | 2028-01-01 | 15:02 | 54120 | 273.526 | 1.6412 | 314.9089 |  | 2007-01-01 | 15:02 | 54120 | 216.211 | 1.2973 | 275.2908 |  | 2028-01-01 | 15:02 | 54120 | 86.5537 | 0.51932 | 116.3673 |  | 2007-01-01 | 15:02 | 54120 | 89.356 | 0.53614 | 118.2535 |  | 2029-09-01 | 15:02 | 54120 | 225.852 | 1.3551 | 287.6661 |  | 2006-09-01 | 15:02 | 54120 | 211.376 | 1.2683 | 270.0479 |  | 2029-09-01 | 15:02 | 54120 | 80.9457 | 0.48567 | 143.857 |  | 2006-09-01 | 15:02 | 54120 | 67.2473 | 0.40348 | 95.144 |  | 2028-01-01 | 15:02 | 54120 | 246.726 | 1.4804 | 293.0272 |  | 2007-01-01 | 15:02 | 54120 | 214.643 | 1.2879 | 273.4956 |  | 2028-01-01 | 15:02 | 54120 | 48.6517 | 0.29191 | 69.3328 |  | 2007-01-01 | 15:02 | 54120 | 51.5633 | 0.30938 | 73.6493 |  | 2029-09-01 | 15:02 | 54120 | 224.566 | 1.3474 | 285.4702 |  | 2006-09-01 | 15:02 | 54120 | 211.24 | 1.2674 | 269.7987 |  | 2029-09-01 | 15:02 | 54120 | 58.7211 | 0.35233 | 114.4551 |  | 2006-09-01 | 15:02 | 54120 | 48.2782 | 0.28967 | 70.8017 |  | 2028-01-01 | 15:02 | 54120 | 237.114 | 1.4227 | 286.673 |  | 2007-01-01 | 15:02 | 54120 | 214.529 | 1.2872 | 273.3641 |  | 2028-01-01 | 15:02 | 54120 | 33.5993 | 0.2016 | 49.4664 |  | 2007-01-01 | 15:02 | 54120 | 35.7944 | 0.21477 | 53.2558 |  | 2029-09-01 | 15:02 | 54120 | 97.5264 | 0.58516 | 136.581 |  | 2029-09-01 | 15:02 | 54120 | 65.1519 | 0.39091 | 93.99 |  | 2029-09-01 | 15:02 | 54120 | 43.4583 | 0.26075 | 64.7478 |  | 2006-09-01 | 15:02 | 54120 | 42.6474 | 0.25588 | 63.7528 |  | 2028-01-01 | 15:02 | 54120 | 86.5537 | 0.51932 | 116.3673 |  | 2007-01-01 | 15:02 | 54120 | 89.356 | 0.53614 | 118.2535 |  | 2028-01-01 | 15:02 | 54120 | 39.4176 | 0.23651 | 58.1079 |  | 2007-01-01 | 15:02 | 54120 | 40.2831 | 0.2417 | 59.1841
| 2029-09-01 | 15:03 | 54180 | 371.648 | 2.2299 | 473.9335 |  | 2029-09-01 | 15:03 | 54180 | 237.12 | 1.4227 | 300.7733 |  | 2006-09-01 | 15:03 | 54180 | 215.936 | 1.2956 | 274.0197 |  | 2029-09-01 | 15:03 | 54180 | 125.937 | 0.75562 | 197.6033 |  | 2006-09-01 | 15:03 | 54180 | 107.468 | 0.64481 | 144.4328 |  | 2028-01-01 | 15:03 | 54180 | 276.528 | 1.6592 | 316.5681 |  | 2007-01-01 | 15:03 | 54180 | 219.181 | 1.3151 | 276.6059 |  | 2028-01-01 | 15:03 | 54180 | 86.6874 | 0.52012 | 116.8874 |  | 2007-01-01 | 15:03 | 54180 | 89.5747 | 0.53745 | 118.7909 |  | 2029-09-01 | 15:03 | 54180 | 229.187 | 1.3751 | 289.0413 |  | 2006-09-01 | 15:03 | 54180 | 214.259 | 1.2856 | 271.3334 |  | 2029-09-01 | 15:03 | 54180 | 81.1185 | 0.48671 | 144.3438 |  | 2006-09-01 | 15:03 | 54180 | 67.3769 | 0.40426 | 95.5483 |  | 2028-01-01 | 15:03 | 54180 | 250.067 | 1.5004 | 294.5276 |  | 2007-01-01 | 15:03 | 54180 | 217.636 | 1.3058 | 274.8014 |  | 2028-01-01 | 15:03 | 54180 | 48.6569 | 0.29194 | 69.6248 |  | 2007-01-01 | 15:03 | 54180 | 51.5595 | 0.30936 | 73.9586 |  | 2029-09-01 | 15:03 | 54180 | 227.918 | 1.3675 | 286.8377 |  | 2006-09-01 | 15:03 | 54180 | 214.125 | 1.2847 | 271.0834 |  | 2029-09-01 | 15:03 | 54180 | 58.7645 | 0.35259 | 114.8077 |  | 2006-09-01 | 15:03 | 54180 | 48.337 | 0.29002 | 71.0917 |  | 2028-01-01 | 15:03 | 54180 | 240.577 | 1.4435 | 288.1164 |  | 2007-01-01 | 15:03 | 54180 | 217.524 | 1.3051 | 274.6692 |  | 2028-01-01 | 15:03 | 54180 | 33.5976 | 0.20159 | 49.668 |  | 2007-01-01 | 15:03 | 54180 | 35.779 | 0.21467 | 53.4704 |  | 2029-09-01 | 15:03 | 54180 | 97.7324 | 0.58639 | 137.1674 |  | 2029-09-01 | 15:03 | 54180 | 65.208 | 0.39125 | 94.3813 |  | 2029-09-01 | 15:03 | 54180 | 43.4668 | 0.2608 | 65.0086 |  | 2006-09-01 | 15:03 | 54180 | 42.6494 | 0.2559 | 64.0086 |  | 2028-01-01 | 15:03 | 54180 | 86.6874 | 0.52012 | 116.8874 |  | 2007-01-01 | 15:03 | 54180 | 89.5747 | 0.53745 | 118.7909 |  | 2028-01-01 | 15:03 | 54180 | 39.4192 | 0.23652 | 58.3444 |  | 2007-01-01 | 15:03 | 54180 | 40.2774 | 0.24166 | 59.4257
| 2029-09-01 | 15:04 | 54240 | 372.975 | 2.2378 | 476.1713 |  | 2029-09-01 | 15:04 | 54240 | 240.299 | 1.4418 | 302.2151 |  | 2006-09-01 | 15:04 | 54240 | 218.74 | 1.3124 | 275.3321 |  | 2029-09-01 | 15:04 | 54240 | 126.596 | 0.75958 | 198.3629 |  | 2006-09-01 | 15:04 | 54240 | 107.944 | 0.64766 | 145.0805 |  | 2028-01-01 | 15:04 | 54240 | 279.49 | 1.6769 | 318.245 |  | 2007-01-01 | 15:04 | 54240 | 222.101 | 1.3326 | 277.9385 |  | 2028-01-01 | 15:04 | 54240 | 86.8149 | 0.52089 | 117.4083 |  | 2007-01-01 | 15:04 | 54240 | 89.7729 | 0.53864 | 119.3296 |  | 2029-09-01 | 15:04 | 54240 | 232.475 | 1.3948 | 290.4361 |  | 2006-09-01 | 15:04 | 54240 | 217.091 | 1.3025 | 272.636 |  | 2029-09-01 | 15:04 | 54240 | 81.2791 | 0.48767 | 144.8314 |  | 2006-09-01 | 15:04 | 54240 | 67.5003 | 0.405 | 95.9533 |  | 2028-01-01 | 15:04 | 54240 | 253.364 | 1.5202 | 296.0478 |  | 2007-01-01 | 15:04 | 54240 | 220.58 | 1.3235 | 276.1249 |  | 2028-01-01 | 15:04 | 54240 | 48.6645 | 0.29199 | 69.9168 |  | 2007-01-01 | 15:04 | 54240 | 51.5531 | 0.30932 | 74.268 |  | 2029-09-01 | 15:04 | 54240 | 231.223 | 1.3873 | 288.2251 |  | 2006-09-01 | 15:04 | 54240 | 216.959 | 1.3018 | 272.3852 |  | 2029-09-01 | 15:04 | 54240 | 58.8038 | 0.35282 | 115.1605 |  | 2006-09-01 | 15:04 | 54240 | 48.3944 | 0.29037 | 71.3821 |  | 2028-01-01 | 15:04 | 54240 | 243.993 | 1.464 | 289.5804 |  | 2007-01-01 | 15:04 | 54240 | 220.469 | 1.3228 | 275.9921 |  | 2028-01-01 | 15:04 | 54240 | 33.5991 | 0.20159 | 49.8696 |  | 2007-01-01 | 15:04 | 54240 | 35.764 | 0.21458 | 53.685 |  | 2029-09-01 | 15:04 | 54240 | 97.9259 | 0.58756 | 137.755 |  | 2029-09-01 | 15:04 | 54240 | 65.2591 | 0.39155 | 94.7728 |  | 2029-09-01 | 15:04 | 54240 | 43.4742 | 0.26085 | 65.2694 |  | 2006-09-01 | 15:04 | 54240 | 42.6506 | 0.2559 | 64.2646 |  | 2028-01-01 | 15:04 | 54240 | 86.8149 | 0.52089 | 117.4083 |  | 2007-01-01 | 15:04 | 54240 | 89.7729 | 0.53864 | 119.3296 |  | 2028-01-01 | 15:04 | 54240 | 39.4218 | 0.23653 | 58.581 |  | 2007-01-01 | 15:04 | 54240 | 40.2703 | 0.24162 | 59.6674
| 2029-09-01 | 15:05 | 54300 | 374.283 | 2.2457 | 478.417 |  | 2029-09-01 | 15:05 | 54300 | 243.434 | 1.4606 | 303.6757 |  | 2006-09-01 | 15:05 | 54300 | 221.493 | 1.329 | 276.6611 |  | 2029-09-01 | 15:05 | 54300 | 127.228 | 0.76337 | 199.1262 |  | 2006-09-01 | 15:05 | 54300 | 108.397 | 0.65038 | 145.7308 |  | 2028-01-01 | 15:05 | 54300 | 282.413 | 1.6945 | 319.9395 |  | 2007-01-01 | 15:05 | 54300 | 224.972 | 1.3498 | 279.2883 |  | 2028-01-01 | 15:05 | 54300 | 86.9367 | 0.52162 | 117.9299 |  | 2007-01-01 | 15:05 | 54300 | 89.9527 | 0.53972 | 119.8693 |  | 2029-09-01 | 15:05 | 54300 | 235.718 | 1.4143 | 291.8504 |  | 2006-09-01 | 15:05 | 54300 | 219.872 | 1.3192 | 273.9552 |  | 2029-09-01 | 15:05 | 54300 | 81.4283 | 0.48857 | 145.32 |  | 2006-09-01 | 15:05 | 54300 | 67.618 | 0.40571 | 96.359 |  | 2028-01-01 | 15:05 | 54300 | 256.617 | 1.5397 | 297.5875 |  | 2007-01-01 | 15:05 | 54300 | 223.475 | 1.3408 | 277.4657 |  | 2028-01-01 | 15:05 | 54300 | 48.6743 | 0.29205 | 70.2088 |  | 2007-01-01 | 15:05 | 54300 | 51.5446 | 0.30927 | 74.5772 |  | 2029-09-01 | 15:05 | 54300 | 234.484 | 1.4069 | 289.632 |  | 2006-09-01 | 15:05 | 54300 | 219.742 | 1.3185 | 273.7036 |  | 2029-09-01 | 15:05 | 54300 | 58.8393 | 0.35304 | 115.5135 |  | 2006-09-01 | 15:05 | 54300 | 48.4506 | 0.2907 | 71.6728 |  | 2028-01-01 | 15:05 | 54300 | 247.365 | 1.4842 | 291.0646 |  | 2007-01-01 | 15:05 | 54300 | 223.366 | 1.3402 | 277.3323 |  | 2028-01-01 | 15:05 | 54300 | 33.6033 | 0.20162 | 50.0712 |  | 2007-01-01 | 15:05 | 54300 | 35.7496 | 0.2145 | 53.8995 |  | 2029-09-01 | 15:05 | 54300 | 98.1075 | 0.58864 | 138.3436 |  | 2029-09-01 | 15:05 | 54300 | 65.3054 | 0.39183 | 95.1646 |  | 2029-09-01 | 15:05 | 54300 | 43.4806 | 0.26088 | 65.5303 |  | 2006-09-01 | 15:05 | 54300 | 42.6511 | 0.25591 | 64.5205 |  | 2028-01-01 | 15:05 | 54300 | 86.9367 | 0.52162 | 117.9299 |  | 2007-01-01 | 15:05 | 54300 | 89.9527 | 0.53972 | 119.8693 |  | 2028-01-01 | 15:05 | 54300 | 39.4253 | 0.23655 | 58.8175 |  | 2007-01-01 | 15:05 | 54300 | 40.2621 | 0.24157 | 59.9089
| 2029-09-01 | 15:06 | 54360 | 375.573 | 2.2534 | 480.6704 |  | 2029-09-01 | 15:06 | 54360 | 246.526 | 1.4792 | 305.1548 |  | 2006-09-01 | 15:06 | 54360 | 224.197 | 1.3452 | 278.0063 |  | 2029-09-01 | 15:06 | 54360 | 127.831 | 0.76699 | 199.8932 |  | 2006-09-01 | 15:06 | 54360 | 108.83 | 0.65298 | 146.3838 |  | 2028-01-01 | 15:06 | 54360 | 285.296 | 1.7118 | 321.6513 |  | 2007-01-01 | 15:06 | 54360 | 227.795 | 1.3668 | 280.6551 |  | 2028-01-01 | 15:06 | 54360 | 87.0531 | 0.52232 | 118.4522 |  | 2007-01-01 | 15:06 | 54360 | 90.1155 | 0.54069 | 120.41 |  | 2029-09-01 | 15:06 | 54360 | 238.916 | 1.4335 | 293.2839 |  | 2006-09-01 | 15:06 | 54360 | 222.603 | 1.3356 | 275.2908 |  | 2029-09-01 | 15:06 | 54360 | 81.5669 | 0.4894 | 145.8094 |  | 2006-09-01 | 15:06 | 54360 | 67.7306 | 0.40638 | 96.7654 |  | 2028-01-01 | 15:06 | 54360 | 259.827 | 1.559 | 299.1465 |  | 2007-01-01 | 15:06 | 54360 | 226.321 | 1.3579 | 278.8236 |  | 2028-01-01 | 15:06 | 54360 | 48.6861 | 0.29212 | 70.5009 |  | 2007-01-01 | 15:06 | 54360 | 51.5346 | 0.30921 | 74.8864 |  | 2029-09-01 | 15:06 | 54360 | 237.699 | 1.4262 | 291.0582 |  | 2006-09-01 | 15:06 | 54360 | 222.475 | 1.3348 | 275.0385 |  | 2029-09-01 | 15:06 | 54360 | 58.8716 | 0.35323 | 115.8668 |  | 2006-09-01 | 15:06 | 54360 | 48.5058 | 0.29103 | 71.9638 |  | 2028-01-01 | 15:06 | 54360 | 250.693 | 1.5042 | 292.5687 |  | 2007-01-01 | 15:06 | 54360 | 226.213 | 1.3573 | 278.6895 |  | 2028-01-01 | 15:06 | 54360 | 33.6099 | 0.20166 | 50.2728 |  | 2007-01-01 | 15:06 | 54360 | 35.7358 | 0.21441 | 54.1139 |  | 2029-09-01 | 15:06 | 54360 | 98.2781 | 0.58967 | 138.9333 |  | 2029-09-01 | 15:06 | 54360 | 65.3476 | 0.39209 | 95.5567 |  | 2029-09-01 | 15:06 | 54360 | 43.4861 | 0.26092 | 65.7912 |  | 2006-09-01 | 15:06 | 54360 | 42.6509 | 0.25591 | 64.7764 |  | 2028-01-01 | 15:06 | 54360 | 87.0531 | 0.52232 | 118.4522 |  | 2007-01-01 | 15:06 | 54360 | 90.1155 | 0.54069 | 120.41 |  | 2028-01-01 | 15:06 | 54360 | 39.4296 | 0.23658 | 59.0541 |  | 2007-01-01 | 15:06 | 54360 | 40.2531 | 0.24152 | 60.1504
| 2029-09-01 | 15:07 | 54420 | 376.845 | 2.2611 | 482.9315 |  | 2029-09-01 | 15:07 | 54420 | 249.575 | 1.4974 | 306.6523 |  | 2006-09-01 | 15:07 | 54420 | 226.852 | 1.3611 | 279.3674 |  | 2029-09-01 | 15:07 | 54420 | 128.408 | 0.77045 | 200.6637 |  | 2006-09-01 | 15:07 | 54420 | 109.243 | 0.65546 | 147.0393 |  | 2028-01-01 | 15:07 | 54420 | 288.14 | 1.7288 | 323.3801 |  | 2007-01-01 | 15:07 | 54420 | 230.571 | 1.3834 | 282.0385 |  | 2028-01-01 | 15:07 | 54420 | 87.1646 | 0.52299 | 118.9752 |  | 2007-01-01 | 15:07 | 54420 | 90.2627 | 0.54158 | 120.9516 |  | 2029-09-01 | 15:07 | 54420 | 242.07 | 1.4524 | 294.7363 |  | 2006-09-01 | 15:07 | 54420 | 225.284 | 1.3517 | 276.6425 |  | 2029-09-01 | 15:07 | 54420 | 81.6958 | 0.49017 | 146.2996 |  | 2006-09-01 | 15:07 | 54420 | 67.8386 | 0.40703 | 97.1724 |  | 2028-01-01 | 15:07 | 54420 | 262.993 | 1.578 | 300.7244 |  | 2007-01-01 | 15:07 | 54420 | 229.119 | 1.3747 | 280.1984 |  | 2028-01-01 | 15:07 | 54420 | 48.6995 | 0.2922 | 70.7931 |  | 2007-01-01 | 15:07 | 54420 | 51.5232 | 0.30914 | 75.1956 |  | 2029-09-01 | 15:07 | 54420 | 240.869 | 1.4452 | 292.5034 |  | 2006-09-01 | 15:07 | 54420 | 225.159 | 1.351 | 276.3894 |  | 2029-09-01 | 15:07 | 54420 | 58.9009 | 0.35341 | 116.2202 |  | 2006-09-01 | 15:07 | 54420 | 48.56 | 0.29136 | 72.2552 |  | 2028-01-01 | 15:07 | 54420 | 253.975 | 1.5239 | 294.0926 |  | 2007-01-01 | 15:07 | 54420 | 229.013 | 1.3741 | 280.0636 |  | 2028-01-01 | 15:07 | 54420 | 33.6184 | 0.20171 | 50.4745 |  | 2007-01-01 | 15:07 | 54420 | 35.7226 | 0.21434 | 54.3283 |  | 2029-09-01 | 15:07 | 54420 | 98.4382 | 0.59063 | 139.5239 |  | 2029-09-01 | 15:07 | 54420 | 65.3859 | 0.39232 | 95.949 |  | 2029-09-01 | 15:07 | 54420 | 43.4909 | 0.26095 | 66.0522 |  | 2006-09-01 | 15:07 | 54420 | 42.6503 | 0.2559 | 65.0323 |  | 2028-01-01 | 15:07 | 54420 | 87.1646 | 0.52299 | 118.9752 |  | 2007-01-01 | 15:07 | 54420 | 90.2627 | 0.54158 | 120.9516 |  | 2028-01-01 | 15:07 | 54420 | 39.4345 | 0.23661 | 59.2907 |  | 2007-01-01 | 15:07 | 54420 | 40.2434 | 0.24146 | 60.3919
| 2029-09-01 | 15:08 | 54480 | 378.099 | 2.2686 | 485.2001 |  | 2029-09-01 | 15:08 | 54480 | 252.582 | 1.5155 | 308.1678 |  | 2006-09-01 | 15:08 | 54480 | 229.459 | 1.3768 | 280.7441 |  | 2029-09-01 | 15:08 | 54480 | 128.961 | 0.77377 | 201.4374 |  | 2006-09-01 | 15:08 | 54480 | 109.638 | 0.65783 | 147.6971 |  | 2028-01-01 | 15:08 | 54480 | 290.945 | 1.7457 | 325.1258 |  | 2007-01-01 | 15:08 | 54480 | 233.3 | 1.3998 | 283.4383 |  | 2028-01-01 | 15:08 | 54480 | 87.2715 | 0.52363 | 119.4988 |  | 2007-01-01 | 15:08 | 54480 | 90.3954 | 0.54237 | 121.4939 |  | 2029-09-01 | 15:08 | 54480 | 245.18 | 1.4711 | 296.2074 |  | 2006-09-01 | 15:08 | 54480 | 227.918 | 1.3675 | 278.01 |  | 2029-09-01 | 15:08 | 54480 | 81.8156 | 0.49089 | 146.7905 |  | 2006-09-01 | 15:08 | 54480 | 67.9422 | 0.40765 | 97.5801 |  | 2028-01-01 | 15:08 | 54480 | 266.117 | 1.5967 | 302.3211 |  | 2007-01-01 | 15:08 | 54480 | 231.87 | 1.3912 | 281.5896 |  | 2028-01-01 | 15:08 | 54480 | 48.7145 | 0.29229 | 71.0854 |  | 2007-01-01 | 15:08 | 54480 | 51.5107 | 0.30906 | 75.5046 |  | 2029-09-01 | 15:08 | 54480 | 243.996 | 1.464 | 293.9673 |  | 2006-09-01 | 15:08 | 54480 | 227.794 | 1.3668 | 277.7562 |  | 2029-09-01 | 15:08 | 54480 | 58.9274 | 0.35356 | 116.5737 |  | 2006-09-01 | 15:08 | 54480 | 48.6135 | 0.29168 | 72.5468 |  | 2028-01-01 | 15:08 | 54480 | 257.213 | 1.5433 | 295.6359 |  | 2007-01-01 | 15:08 | 54480 | 231.766 | 1.3906 | 281.4542 |  | 2028-01-01 | 15:08 | 54480 | 33.6285 | 0.20177 | 50.6763 |  | 2007-01-01 | 15:08 | 54480 | 35.7099 | 0.21426 | 54.5425 |  | 2029-09-01 | 15:08 | 54480 | 98.5886 | 0.59153 | 140.1154 |  | 2029-09-01 | 15:08 | 54480 | 65.4207 | 0.39252 | 96.3416 |  | 2029-09-01 | 15:08 | 54480 | 43.4951 | 0.26097 | 66.3131 |  | 2006-09-01 | 15:08 | 54480 | 42.6492 | 0.2559 | 65.2882 |  | 2028-01-01 | 15:08 | 54480 | 87.2715 | 0.52363 | 119.4988 |  | 2007-01-01 | 15:08 | 54480 | 90.3954 | 0.54237 | 121.4939 |  | 2028-01-01 | 15:08 | 54480 | 39.44 | 0.23664 | 59.5274 |  | 2007-01-01 | 15:08 | 54480 | 40.2333 | 0.2414 | 60.6333
| 2029-09-01 | 15:09 | 54540 | 379.335 | 2.276 | 487.4761 |  | 2029-09-01 | 15:09 | 54540 | 255.547 | 1.5333 | 309.701 |  | 2006-09-01 | 15:09 | 54540 | 232.018 | 1.3921 | 282.1362 |  | 2029-09-01 | 15:09 | 54540 | 129.489 | 0.77693 | 202.2144 |  | 2006-09-01 | 15:09 | 54540 | 110.015 | 0.66009 | 148.3572 |  | 2028-01-01 | 15:09 | 54540 | 293.711 | 1.7623 | 326.888 |  | 2007-01-01 | 15:09 | 54540 | 235.983 | 1.4159 | 284.8542 |  | 2028-01-01 | 15:09 | 54540 | 87.3741 | 0.52424 | 120.0231 |  | 2007-01-01 | 15:09 | 54540 | 90.5149 | 0.54309 | 122.037 |  | 2029-09-01 | 15:09 | 54540 | 248.247 | 1.4895 | 297.6969 |  | 2006-09-01 | 15:09 | 54540 | 230.503 | 1.383 | 279.3931 |  | 2029-09-01 | 15:09 | 54540 | 81.927 | 0.49156 | 147.282 |  | 2006-09-01 | 15:09 | 54540 | 68.042 | 0.40825 | 97.9883 |  | 2028-01-01 | 15:09 | 54540 | 269.199 | 1.6152 | 303.9363 |  | 2007-01-01 | 15:09 | 54540 | 234.575 | 1.4074 | 282.997 |  | 2028-01-01 | 15:09 | 54540 | 48.7308 | 0.29238 | 71.3778 |  | 2007-01-01 | 15:09 | 54540 | 51.4973 | 0.30898 | 75.8136 |  | 2029-09-01 | 15:09 | 54540 | 247.08 | 1.4825 | 295.4498 |  | 2006-09-01 | 15:09 | 54540 | 230.382 | 1.3823 | 279.1385 |  | 2029-09-01 | 15:09 | 54540 | 58.9516 | 0.35371 | 116.9274 |  | 2006-09-01 | 15:09 | 54540 | 48.6663 | 0.292 | 72.8388 |  | 2028-01-01 | 15:09 | 54540 | 260.408 | 1.5624 | 297.1983 |  | 2007-01-01 | 15:09 | 54540 | 234.472 | 1.4068 | 282.861 |  | 2028-01-01 | 15:09 | 54540 | 33.64 | 0.20184 | 50.8782 |  | 2007-01-01 | 15:09 | 54540 | 35.6977 | 0.21419 | 54.7567 |  | 2029-09-01 | 15:09 | 54540 | 98.7296 | 0.59238 | 140.7078 |  | 2029-09-01 | 15:09 | 54540 | 65.4523 | 0.39271 | 96.7343 |  | 2029-09-01 | 15:09 | 54540 | 43.4987 | 0.26099 | 66.5741 |  | 2006-09-01 | 15:09 | 54540 | 42.6476 | 0.25589 | 65.544 |  | 2028-01-01 | 15:09 | 54540 | 87.3741 | 0.52424 | 120.0231 |  | 2007-01-01 | 15:09 | 54540 | 90.5149 | 0.54309 | 122.037 |  | 2028-01-01 | 15:09 | 54540 | 39.4461 | 0.23668 | 59.764 |  | 2007-01-01 | 15:09 | 54540 | 40.2229 | 0.24134 | 60.8746
| 2029-09-01 | 15:10 | 54600 | 380.554 | 2.2833 | 489.7594 |  | 2029-09-01 | 15:10 | 54600 | 258.471 | 1.5508 | 311.2519 |  | 2006-09-01 | 15:10 | 54600 | 234.531 | 1.4072 | 283.5434 |  | 2029-09-01 | 15:10 | 54600 | 129.994 | 0.77996 | 202.9943 |  | 2006-09-01 | 15:10 | 54600 | 110.375 | 0.66225 | 149.0194 |  | 2028-01-01 | 15:10 | 54600 | 296.44 | 1.7786 | 328.6667 |  | 2007-01-01 | 15:10 | 54600 | 238.62 | 1.4317 | 286.2859 |  | 2028-01-01 | 15:10 | 54600 | 87.4728 | 0.52484 | 120.5479 |  | 2007-01-01 | 15:10 | 54600 | 90.622 | 0.54373 | 122.5808 |  | 2029-09-01 | 15:10 | 54600 | 251.272 | 1.5076 | 299.2045 |  | 2006-09-01 | 15:10 | 54600 | 233.042 | 1.3983 | 280.7913 |  | 2029-09-01 | 15:10 | 54600 | 82.0306 | 0.49218 | 147.7742 |  | 2006-09-01 | 15:10 | 54600 | 68.1383 | 0.40883 | 98.3972 |  | 2028-01-01 | 15:10 | 54600 | 272.239 | 1.6334 | 305.5697 |  | 2007-01-01 | 15:10 | 54600 | 237.234 | 1.4234 | 284.4204 |  | 2028-01-01 | 15:10 | 54600 | 48.7483 | 0.29249 | 71.6703 |  | 2007-01-01 | 15:10 | 54600 | 51.4832 | 0.3089 | 76.1225 |  | 2029-09-01 | 15:10 | 54600 | 250.12 | 1.5007 | 296.9505 |  | 2006-09-01 | 15:10 | 54600 | 232.923 | 1.3975 | 280.536 |  | 2029-09-01 | 15:10 | 54600 | 58.9735 | 0.35384 | 117.2813 |  | 2006-09-01 | 15:10 | 54600 | 48.7186 | 0.29231 | 73.1311 |  | 2028-01-01 | 15:10 | 54600 | 263.56 | 1.5814 | 298.7797 |  | 2007-01-01 | 15:10 | 54600 | 237.133 | 1.4228 | 284.2838 |  | 2028-01-01 | 15:10 | 54600 | 33.6527 | 0.20192 | 51.0801 |  | 2007-01-01 | 15:10 | 54600 | 35.6859 | 0.21412 | 54.9708 |  | 2029-09-01 | 15:10 | 54600 | 98.862 | 0.59317 | 141.301 |  | 2029-09-01 | 15:10 | 54600 | 65.481 | 0.39289 | 97.1272 |  | 2029-09-01 | 15:10 | 54600 | 43.5017 | 0.26101 | 66.8351 |  | 2006-09-01 | 15:10 | 54600 | 42.6458 | 0.25587 | 65.7999 |  | 2028-01-01 | 15:10 | 54600 | 87.4728 | 0.52484 | 120.5479 |  | 2007-01-01 | 15:10 | 54600 | 90.622 | 0.54373 | 122.5808 |  | 2028-01-01 | 15:10 | 54600 | 39.4525 | 0.23672 | 60.0007 |  | 2007-01-01 | 15:10 | 54600 | 40.2122 | 0.24127 | 61.1159
| 2029-09-01 | 15:11 | 54660 | 381.756 | 2.2905 | 492.05 |  | 2029-09-01 | 15:11 | 54660 | 261.354 | 1.5681 | 312.82 |  | 2006-09-01 | 15:11 | 54660 | 236.999 | 1.422 | 284.9654 |  | 2029-09-01 | 15:11 | 54660 | 130.478 | 0.78287 | 203.7772 |  | 2006-09-01 | 15:11 | 54660 | 110.72 | 0.66432 | 149.6838 |  | 2028-01-01 | 15:11 | 54660 | 299.132 | 1.7948 | 330.4615 |  | 2007-01-01 | 15:11 | 54660 | 241.213 | 1.4473 | 287.7332 |  | 2028-01-01 | 15:11 | 54660 | 87.5677 | 0.52541 | 121.0733 |  | 2007-01-01 | 15:11 | 54660 | 90.7178 | 0.54431 | 123.1251 |  | 2029-09-01 | 15:11 | 54660 | 254.255 | 1.5255 | 300.7301 |  | 2006-09-01 | 15:11 | 54660 | 235.535 | 1.4132 | 282.2045 |  | 2029-09-01 | 15:11 | 54660 | 82.127 | 0.49276 | 148.267 |  | 2006-09-01 | 15:11 | 54660 | 68.2315 | 0.40939 | 98.8065 |  | 2028-01-01 | 15:11 | 54660 | 275.239 | 1.6514 | 307.2212 |  | 2007-01-01 | 15:11 | 54660 | 239.848 | 1.4391 | 285.8595 |  | 2028-01-01 | 15:11 | 54660 | 48.7669 | 0.2926 | 71.9629 |  | 2007-01-01 | 15:11 | 54660 | 51.4685 | 0.30881 | 76.4313 |  | 2029-09-01 | 15:11 | 54660 | 253.119 | 1.5187 | 298.4693 |  | 2006-09-01 | 15:11 | 54660 | 235.417 | 1.4125 | 281.9485 |  | 2029-09-01 | 15:11 | 54660 | 58.9935 | 0.35396 | 117.6352 |  | 2006-09-01 | 15:11 | 54660 | 48.7703 | 0.29262 | 73.4238 |  | 2028-01-01 | 15:11 | 54660 | 266.67 | 1.6 | 300.3797 |  | 2007-01-01 | 15:11 | 54660 | 239.748 | 1.4385 | 285.7223 |  | 2028-01-01 | 15:11 | 54660 | 33.6662 | 0.202 | 51.2821 |  | 2007-01-01 | 15:11 | 54660 | 35.6746 | 0.21405 | 55.1849 |  | 2029-09-01 | 15:11 | 54660 | 98.9862 | 0.59392 | 141.8949 |  | 2029-09-01 | 15:11 | 54660 | 65.507 | 0.39304 | 97.5202 |  | 2029-09-01 | 15:11 | 54660 | 43.5043 | 0.26103 | 67.0962 |  | 2006-09-01 | 15:11 | 54660 | 42.6436 | 0.25586 | 66.0558 |  | 2028-01-01 | 15:11 | 54660 | 87.5677 | 0.52541 | 121.0733 |  | 2007-01-01 | 15:11 | 54660 | 90.7178 | 0.54431 | 123.1251 |  | 2028-01-01 | 15:11 | 54660 | 39.4593 | 0.23676 | 60.2375 |  | 2007-01-01 | 15:11 | 54660 | 40.2014 | 0.24121 | 61.3571
| 2029-09-01 | 15:12 | 54720 | 382.941 | 2.2976 | 494.3476 |  | 2029-09-01 | 15:12 | 54720 | 264.198 | 1.5852 | 314.4052 |  | 2006-09-01 | 15:12 | 54720 | 239.421 | 1.4365 | 286.4019 |  | 2029-09-01 | 15:12 | 54720 | 130.94 | 0.78564 | 204.5628 |  | 2006-09-01 | 15:12 | 54720 | 111.05 | 0.6663 | 150.3501 |  | 2028-01-01 | 15:12 | 54720 | 301.788 | 1.8107 | 332.2722 |  | 2007-01-01 | 15:12 | 54720 | 243.762 | 1.4626 | 289.1958 |  | 2028-01-01 | 15:12 | 54720 | 87.6593 | 0.52596 | 121.5993 |  | 2007-01-01 | 15:12 | 54720 | 90.8031 | 0.54482 | 123.6699 |  | 2029-09-01 | 15:12 | 54720 | 257.196 | 1.5432 | 302.2732 |  | 2006-09-01 | 15:12 | 54720 | 237.981 | 1.4279 | 283.6324 |  | 2029-09-01 | 15:12 | 54720 | 82.2167 | 0.4933 | 148.7603 |  | 2006-09-01 | 15:12 | 54720 | 68.3217 | 0.40993 | 99.2165 |  | 2028-01-01 | 15:12 | 54720 | 278.198 | 1.6692 | 308.8904 |  | 2007-01-01 | 15:12 | 54720 | 242.417 | 1.4545 | 287.314 |  | 2028-01-01 | 15:12 | 54720 | 48.7864 | 0.29272 | 72.2556 |  | 2007-01-01 | 15:12 | 54720 | 51.4533 | 0.30872 | 76.7401 |  | 2029-09-01 | 15:12 | 54720 | 256.076 | 1.5365 | 300.0057 |  | 2006-09-01 | 15:12 | 54720 | 237.866 | 1.4272 | 283.3757 |  | 2029-09-01 | 15:12 | 54720 | 59.0118 | 0.35407 | 117.9893 |  | 2006-09-01 | 15:12 | 54720 | 48.8217 | 0.29293 | 73.7167 |  | 2028-01-01 | 15:12 | 54720 | 269.738 | 1.6184 | 301.9981 |  | 2007-01-01 | 15:12 | 54720 | 242.32 | 1.4539 | 287.1762 |  | 2028-01-01 | 15:12 | 54720 | 33.6806 | 0.20208 | 51.4842 |  | 2007-01-01 | 15:12 | 54720 | 35.6636 | 0.21398 | 55.3989 |  | 2029-09-01 | 15:12 | 54720 | 99.1028 | 0.59462 | 142.4895 |  | 2029-09-01 | 15:12 | 54720 | 65.5306 | 0.39318 | 97.9134 |  | 2029-09-01 | 15:12 | 54720 | 43.5065 | 0.26104 | 67.3572 |  | 2006-09-01 | 15:12 | 54720 | 42.6412 | 0.25585 | 66.3116 |  | 2028-01-01 | 15:12 | 54720 | 87.6593 | 0.52596 | 121.5993 |  | 2007-01-01 | 15:12 | 54720 | 90.8031 | 0.54482 | 123.6699 |  | 2028-01-01 | 15:12 | 54720 | 39.4664 | 0.2368 | 60.4743 |  | 2007-01-01 | 15:12 | 54720 | 40.1904 | 0.24114 | 61.5983
| 2029-09-01 | 15:13 | 54780 | 384.108 | 2.3046 | 496.6523 |  | 2029-09-01 | 15:13 | 54780 | 267.002 | 1.602 | 316.0072 |  | 2006-09-01 | 15:13 | 54780 | 241.799 | 1.4508 | 287.8527 |  | 2029-09-01 | 15:13 | 54780 | 131.383 | 0.7883 | 205.3511 |  | 2006-09-01 | 15:13 | 54780 | 111.367 | 0.6682 | 151.0183 |  | 2028-01-01 | 15:13 | 54780 | 304.408 | 1.8264 | 334.0986 |  | 2007-01-01 | 15:13 | 54780 | 246.267 | 1.4776 | 290.6734 |  | 2028-01-01 | 15:13 | 54780 | 87.7476 | 0.52649 | 122.1258 |  | 2007-01-01 | 15:13 | 54780 | 90.8786 | 0.54527 | 124.2151 |  | 2029-09-01 | 15:13 | 54780 | 260.096 | 1.5606 | 303.8338 |  | 2006-09-01 | 15:13 | 54780 | 240.384 | 1.4423 | 285.0747 |  | 2029-09-01 | 15:13 | 54780 | 82.3002 | 0.4938 | 149.2541 |  | 2006-09-01 | 15:13 | 54780 | 68.4093 | 0.41046 | 99.6269 |  | 2028-01-01 | 15:13 | 54780 | 281.119 | 1.6867 | 310.5771 |  | 2007-01-01 | 15:13 | 54780 | 244.944 | 1.4697 | 288.7837 |  | 2028-01-01 | 15:13 | 54780 | 48.8067 | 0.29284 | 72.5485 |  | 2007-01-01 | 15:13 | 54780 | 51.4377 | 0.30863 | 77.0487 |  | 2029-09-01 | 15:13 | 54780 | 258.992 | 1.554 | 301.5597 |  | 2006-09-01 | 15:13 | 54780 | 240.27 | 1.4416 | 284.8173 |  | 2029-09-01 | 15:13 | 54780 | 59.0284 | 0.35417 | 118.3435 |  | 2006-09-01 | 15:13 | 54780 | 48.8727 | 0.29324 | 74.0099 |  | 2028-01-01 | 15:13 | 54780 | 272.766 | 1.6366 | 303.6347 |  | 2007-01-01 | 15:13 | 54780 | 244.847 | 1.4691 | 288.6453 |  | 2028-01-01 | 15:13 | 54780 | 33.6957 | 0.20217 | 51.6863 |  | 2007-01-01 | 15:13 | 54780 | 35.653 | 0.21392 | 55.6128 |  | 2029-09-01 | 15:13 | 54780 | 99.2121 | 0.59527 | 143.0848 |  | 2029-09-01 | 15:13 | 54780 | 65.552 | 0.39331 | 98.3067 |  | 2029-09-01 | 15:13 | 54780 | 43.5084 | 0.26105 | 67.6183 |  | 2006-09-01 | 15:13 | 54780 | 42.6385 | 0.25583 | 66.5675 |  | 2028-01-01 | 15:13 | 54780 | 87.7476 | 0.52649 | 122.1258 |  | 2007-01-01 | 15:13 | 54780 | 90.8786 | 0.54527 | 124.2151 |  | 2028-01-01 | 15:13 | 54780 | 39.4737 | 0.23684 | 60.7111 |  | 2007-01-01 | 15:13 | 54780 | 40.1794 | 0.24108 | 61.8393
| 2029-09-01 | 15:14 | 54840 | 385.26 | 2.3116 | 498.9638 |  | 2029-09-01 | 15:14 | 54840 | 269.767 | 1.6186 | 317.6258 |  | 2006-09-01 | 15:14 | 54840 | 244.133 | 1.4648 | 289.3175 |  | 2029-09-01 | 15:14 | 54840 | 131.806 | 0.79084 | 206.142 |  | 2006-09-01 | 15:14 | 54840 | 111.67 | 0.67002 | 151.6883 |  | 2028-01-01 | 15:14 | 54840 | 306.992 | 1.842 | 335.9406 |  | 2007-01-01 | 15:14 | 54840 | 248.73 | 1.4924 | 292.1658 |  | 2028-01-01 | 15:14 | 54840 | 87.833 | 0.527 | 122.6528 |  | 2007-01-01 | 15:14 | 54840 | 90.945 | 0.54567 | 124.7608 |  | 2029-09-01 | 15:14 | 54840 | 262.956 | 1.5777 | 305.4116 |  | 2006-09-01 | 15:14 | 54840 | 242.742 | 1.4565 | 286.5312 |  | 2029-09-01 | 15:14 | 54840 | 82.3779 | 0.49427 | 149.7483 |  | 2006-09-01 | 15:14 | 54840 | 68.4946 | 0.41097 | 100.0379 |  | 2028-01-01 | 15:14 | 54840 | 284 | 1.704 | 312.2811 |  | 2007-01-01 | 15:14 | 54840 | 247.427 | 1.4846 | 290.2682 |  | 2028-01-01 | 15:14 | 54840 | 48.8277 | 0.29297 | 72.8414 |  | 2007-01-01 | 15:14 | 54840 | 51.4218 | 0.30853 | 77.3572 |  | 2029-09-01 | 15:14 | 54840 | 261.867 | 1.5712 | 303.1309 |  | 2006-09-01 | 15:14 | 54840 | 242.63 | 1.4558 | 286.2731 |  | 2029-09-01 | 15:14 | 54840 | 59.0436 | 0.35426 | 118.6977 |  | 2006-09-01 | 15:14 | 54840 | 48.9234 | 0.29354 | 74.3035 |  | 2028-01-01 | 15:14 | 54840 | 275.754 | 1.6545 | 305.2892 |  | 2007-01-01 | 15:14 | 54840 | 247.332 | 1.484 | 290.1293 |  | 2028-01-01 | 15:14 | 54840 | 33.7114 | 0.20227 | 51.8886 |  | 2007-01-01 | 15:14 | 54840 | 35.6427 | 0.21386 | 55.8266 |  | 2029-09-01 | 15:14 | 54840 | 99.3147 | 0.59589 | 143.6807 |  | 2029-09-01 | 15:14 | 54840 | 65.5714 | 0.39343 | 98.7001 |  | 2029-09-01 | 15:14 | 54840 | 43.51 | 0.26106 | 67.8793 |  | 2006-09-01 | 15:14 | 54840 | 42.6357 | 0.25581 | 66.8233 |  | 2028-01-01 | 15:14 | 54840 | 87.833 | 0.527 | 122.6528 |  | 2007-01-01 | 15:14 | 54840 | 90.945 | 0.54567 | 124.7608 |  | 2028-01-01 | 15:14 | 54840 | 39.4813 | 0.23689 | 60.948 |  | 2007-01-01 | 15:14 | 54840 | 40.1683 | 0.24101 | 62.0803
| 2029-09-01 | 15:15 | 54900 | 386.395 | 2.3184 | 501.2822 |  | 2029-09-01 | 15:15 | 54900 | 272.493 | 1.635 | 319.2608 |  | 2006-09-01 | 15:15 | 54900 | 246.424 | 1.4785 | 290.7961 |  | 2029-09-01 | 15:15 | 54900 | 132.211 | 0.79327 | 206.9352 |  | 2006-09-01 | 15:15 | 54900 | 111.96 | 0.67176 | 152.36 |  | 2028-01-01 | 15:15 | 54900 | 309.542 | 1.8573 | 337.7978 |  | 2007-01-01 | 15:15 | 54900 | 251.151 | 1.5069 | 293.6727 |  | 2028-01-01 | 15:15 | 54900 | 87.9157 | 0.52749 | 123.1803 |  | 2007-01-01 | 15:15 | 54900 | 91.0032 | 0.54602 | 125.3068 |  | 2029-09-01 | 15:15 | 54900 | 265.777 | 1.5947 | 307.0062 |  | 2006-09-01 | 15:15 | 54900 | 245.056 | 1.4703 | 288.0015 |  | 2029-09-01 | 15:15 | 54900 | 82.4503 | 0.4947 | 150.243 |  | 2006-09-01 | 15:15 | 54900 | 68.5777 | 0.41147 | 100.4494 |  | 2028-01-01 | 15:15 | 54900 | 286.842 | 1.7211 | 314.0021 |  | 2007-01-01 | 15:15 | 54900 | 249.868 | 1.4992 | 291.7675 |  | 2028-01-01 | 15:15 | 54900 | 48.8494 | 0.2931 | 73.1345 |  | 2007-01-01 | 15:15 | 54900 | 51.4058 | 0.30843 | 77.6656 |  | 2029-09-01 | 15:15 | 54900 | 264.703 | 1.5882 | 304.7191 |  | 2006-09-01 | 15:15 | 54900 | 244.946 | 1.4697 | 287.7428 |  | 2029-09-01 | 15:15 | 54900 | 59.0575 | 0.35434 | 119.0521 |  | 2006-09-01 | 15:15 | 54900 | 48.9739 | 0.29384 | 74.5973 |  | 2028-01-01 | 15:15 | 54900 | 278.701 | 1.6722 | 306.9614 |  | 2007-01-01 | 15:15 | 54900 | 249.774 | 1.4986 | 291.628 |  | 2028-01-01 | 15:15 | 54900 | 33.7275 | 0.20236 | 52.091 |  | 2007-01-01 | 15:15 | 54900 | 35.6327 | 0.2138 | 56.0404 |  | 2029-09-01 | 15:15 | 54900 | 99.411 | 0.59647 | 144.2772 |  | 2029-09-01 | 15:15 | 54900 | 65.589 | 0.39353 | 99.0937 |  | 2029-09-01 | 15:15 | 54900 | 43.5114 | 0.26107 | 68.1404 |  | 2006-09-01 | 15:15 | 54900 | 42.6326 | 0.2558 | 67.0791 |  | 2028-01-01 | 15:15 | 54900 | 87.9157 | 0.52749 | 123.1803 |  | 2007-01-01 | 15:15 | 54900 | 91.0032 | 0.54602 | 125.3068 |  | 2028-01-01 | 15:15 | 54900 | 39.4891 | 0.23693 | 61.185 |  | 2007-01-01 | 15:15 | 54900 | 40.1572 | 0.24094 | 62.3213

## Weather Data (Selected)
[13 empty] | Light breeze | Fresh Breeze
[12 empty] | Summer | 2029-09-01 | 2006-09-01
[12 empty] | Winter | 2028-01-01 | 2007-01-01
Summer | Light breeze | [12 empty] | Fresh Breeze
| 9/29 | [12 empty] | 9/6
| !Date | Time | Ta [K] | Pb [Pa] | Ws [m/s] | Wd [deg] | Hr [g/kg] | Ith [kJ/m^2] | Idn [kJ/m^2] | Ts [K] | Rn [-] | Sn [-] | T [C] | !Date | Time | Ta [K] | Pb [Pa] | Ws [m/s] | Wd [deg] | Hr [g/kg] | Ith [kJ/m^2] | Idn [kJ/m^2] | Ts [K] | Rn [-] | Sn [-] | T [C]
| 9/29 | 01:00:00 | 288.15 | 98867 | 3.6 | 150 | 9.6099 | 0 | 0 | 275.608 | 0 | 1 | 15 | 9/6 | 01:00:00 | 285.15 | 98841 | 6.7 | 220 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
| 9/29 | 02:00:00 | 288.15 | 98867 | 3.1 | 170 | 9.6099 | 0 | 0 | 275.608 | 0 | 1 | 15 | 9/6 | 02:00:00 | 286.15 | 98850 | 6.7 | 220 | 8.408 | 0 | 0 | 272.766 | 0 | 1 | 13
| 9/29 | 03:00:00 | 287.15 | 98858 | 3.6 | 160 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14 | 9/6 | 03:00:00 | 287.15 | 98858 | 9.8 | 220 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
| 9/29 | 04:00:00 | 287.15 | 98858 | 0 | 130 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14 | 9/6 | 04:00:00 | 286.15 | 98850 | 8.2 | 210 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
| 9/29 | 05:00:00 | 285.15 | 98841 | 3.6 | 140 | 8.9926 | 0 | 0 | 272.627 | 0 | 1 | 12 | 9/6 | 05:00:00 | 286.15 | 98850 | 7.7 | 210 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
| 9/29 | 06:00:00 | 285.15 | 98841 | 2.6 | 140 | 8.9926 | 0 | 0 | 271.77 | 0 | 1 | 12 | 9/6 | 06:00:00 | 286.15 | 98850 | 7.2 | 220 | 8.9918 | 3.6 | 0 | 273.473 | 0 | 1 | 13
| 9/29 | 07:00:00 | 285.15 | 98841 | 4.1 | 130 | 8.9926 | 61.2 | 0 | 271.336 | 0 | 1 | 12 | 9/6 | 07:00:00 | 286.15 | 98850 | 8.7 | 220 | 8.9918 | 129.6 | 0 | 273.473 | 0 | 1 | 13
8 | 9/29 | 08:00:00 | 286.15 | 98850 | 2.1 | 335 | 9.6116 | 403.2 | 669.6 | 272.509 | 0 | 1 | 13 | 9/6 | 08:00:00 | 287.15 | 98858 | 8.2 | 230 | 9.6108 | 687.6 | 835.2 | 274.167 | 0 | 1 | 14 | 8
9 | 9/29 | 09:00:00 | 289.15 | 98875 | 0.5 | 95 | 10.2668 | 882 | 1591.2 | 275.589 | 0 | 1 | 16 | 9/6 | 09:00:00 | 288.15 | 98867 | 7.2 | 260 | 9.6099 | 1188 | 1501.2 | 275.122 | 0 | 1 | 15 | 9
10 | 9/29 | 10:00:00 | 291.15 | 98892 | 2.6 | 140 | 10.9627 | 1324.8 | 2055.6 | 277.718 | 0 | 1 | 18 | 9/6 | 10:00:00 | 285.15 | 98841 | 8.2 | 270 | 8.4088 | 1638 | 1875.6 | 271.813 | 0 | 1 | 12 | 10
11 | 9/29 | 11:00:00 | 293.15 | 98908 | 3.6 | 140 | 10.9609 | 1652.4 | 2448 | 279.626 | 0 | 1 | 20 | 9/6 | 11:00:00 | 285.15 | 98841 | 9.8 | 250 | 7.8591 | 1972.8 | 2149.2 | 271.588 | 0 | 1 | 12 | 11
12 | 9/29 | 12:00:00 | 295.15 | 98924 | 2.1 | 150 | 11.6988 | 1818 | 2570.4 | 281.758 | 0 | 1 | 22 | 9/6 | 12:00:00 | 286.15 | 98850 | 9.8 | 250 | 8.408 | 2149.2 | 2062.8 | 272.766 | 0 | 1 | 13 | 12
13 | 9/29 | 13:00:00 | 297.15 | 98940 | 2.6 | 160 | 11.6968 | 1807.2 | 2566.8 | 283.667 | 0 | 1 | 24 | 9/6 | 13:00:00 | 288.15 | 98867 | 11.3 | 250 | 7.857 | 2167.2 | 2224.8 | 274.446 | 0 | 1 | 15 | 13
14 | 9/29 | 14:00:00 | 298.15 | 98948 | 4.1 | 220 | 9.602 | 1630.8 | 2397.6 | 284.245 | 0 | 1 | 25 | 9/6 | 14:00:00 | 285.15 | 98841 | 8.2 | 250 | 7.8591 | 2016 | 2170.8 | 271.588 | 0 | 1 | 12 | 14
15 | 9/29 | 15:00:00 | 298.15 | 98948 | 4.1 | 200 | 9.602 | 1288.8 | 2016 | 284.245 | 0 | 1 | 25 | 9/6 | 15:00:00 | 286.15 | 98850 | 9.8 | 250 | 7.3412 | 1713.6 | 1908 | 272.314 | 0 | 1 | 13 | 15
16 | 9/29 | 16:00:00 | 298.15 | 98948 | 3.6 | 210 | 9.602 | 838.8 | 1332 | 284.245 | 0 | 1 | 25 | 9/6 | 16:00:00 | 287.15 | 98858 | 11.3 | 250 | 6.854 | 1281.6 | 1508.4 | 273.038 | 0 | 1 | 14 | 16
| 9/29 | 17:00:00 | 297.15 | 98940 | 3.6 | 180 | 10.26 | 356.4 | 558 | 283.666 | 0 | 1 | 24 | 9/6 | 17:00:00 | 287.15 | 98858 | 12.9 | 240 | 6.854 | 781.2 | 1072.8 | 273.038 | 0 | 1 | 14
| 9/29 | 18:00:00 | 295.15 | 98924 | 2.6 | 170 | 10.2617 | 43.2 | 0 | 281.897 | 0 | 1 | 22 | 9/6 | 18:00:00 | 286.15 | 98850 | 12.3 | 240 | 6.8546 | 324 | 352.8 | 271.821 | 0 | 1 | 13
| 9/29 | 19:00:00 | 294.15 | 98916 | 2.6 | 160 | 10.2625 | 0 | 0 | 281.078 | 0 | 1 | 21 | 9/6 | 19:00:00 | 285.15 | 98841 | 11.8 | 250 | 6.3977 | 32.4 | 0 | 270.643 | 0 | 1 | 12
| 9/29 | 20:00:00 | 294.15 | 98916 | 2.6 | 190 | 9.6051 | 0 | 0 | 280.715 | 0 | 1 | 21 | 9/6 | 20:00:00 | 285.15 | 98841 | 10.3 | 250 | 6.8552 | 0 | 0 | 271.136 | 0 | 1 | 12
| 9/29 | 21:00:00 | 292.15 | 98900 | 2.1 | 200 | 9.6067 | 0 | 0 | 278.941 | 0 | 1 | 19 | 9/6 | 21:00:00 | 285.15 | 98841 | 9.3 | 250 | 7.3418 | 0 | 0 | 271.363 | 0 | 1 | 12
| 9/29 | 22:00:00 | 291.15 | 98892 | 1.5 | 200 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18 | 9/6 | 22:00:00 | 284.15 | 98833 | 11.8 | 260 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
| 9/29 | 23:00:00 | 291.15 | 98892 | 1 | 210 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18 | 9/6 | 23:00:00 | 284.15 | 98833 | 10.8 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
| 9/29 | 24:00:00 | 291.15 | 98892 | 1.5 | 180 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18 | 9/6 | 24:00:00 | 284.15 | 98833 | 10.3 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
[5 empty] | 2.8111 | [7 empty] | 20.8889 |  |  |  |  | 9.3111 | [7 empty] | 13.3333
Winter | 1/28 | [12 empty] | 1/7
| !Date | Time | Ta [K] | Pb [Pa] | Ws [m/s] | Wd [deg] | Hr [g/kg] | Ith [kJ/m^2] | Idn [kJ/m^2] | Ts [K] | Rn [-] | Sn [-] | T [C] | !Date | Time | Ta [K] | Pb [Pa] | Ws [m/s] | Wd [deg] | Hr [g/kg] | Ith [kJ/m^2] | Idn [kJ/m^2] | Ts [K] | Rn [-] | Sn [-] | T [C]
| 1/28 | 01:00:00 | 275.15 | 98752 | 5.1 | 360 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2 | 1/7 | 01:00:00 | 282.15 | 98815 | 6.7 | 280 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
| 1/28 | 02:00:00 | 274.15 | 98743 | 4.6 | 340 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1 | 1/7 | 02:00:00 | 281.15 | 98806 | 7.7 | 280 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
| 1/28 | 03:00:00 | 275.15 | 98752 | 3.6 | 320 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2 | 1/7 | 03:00:00 | 280.15 | 98798 | 11.8 | 270 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
| 1/28 | 04:00:00 | 275.15 | 98752 | 3.6 | 340 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2 | 1/7 | 04:00:00 | 280.15 | 98798 | 13.4 | 280 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
| 1/28 | 05:00:00 | 274.15 | 98743 | 2.6 | 340 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1 | 1/7 | 05:00:00 | 279.15 | 98789 | 10.3 | 290 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
| 1/28 | 06:00:00 | 273.15 | 98734 | 3.1 | 300 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0 | 1/7 | 06:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
| 1/28 | 07:00:00 | 274.15 | 98743 | 3.6 | 320 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1 | 1/7 | 07:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
8 | 1/28 | 08:00:00 | 274.15 | 98743 | 3.6 | 340 | 3.5803 | 0 | 0 | 258.398 | 0 | 1 | 1 | 1/7 | 08:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6 | 8
9 | 1/28 | 09:00:00 | 275.15 | 98752 | 3.6 | 350 | 3.5799 | 72 | 25.2 | 259.34 | 0 | 1 | 2 | 1/7 | 09:00:00 | 278.15 | 98780 | 9.3 | 280 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5 | 9
10 | 1/28 | 10:00:00 | 275.15 | 98752 | 3.6 | 330 | 3.5799 | 345.6 | 910.8 | 259.34 | 0 | 1 | 2 | 1/7 | 10:00:00 | 279.15 | 98789 | 10.3 | 280 | 4.8307 | 93.6 | 0 | 264.767 | 0 | 1 | 6 | 10
11 | 1/28 | 11:00:00 | 276.15 | 98762 | 2.6 | 310 | 4.1841 | 640.8 | 1386 | 260.746 | 0 | 1 | 3 | 1/7 | 11:00:00 | 279.15 | 98789 | 9.3 | 290 | 4.8307 | 223.2 | 0 | 264.767 | 0 | 1 | 6 | 11
12 | 1/28 | 12:00:00 | 276.15 | 98762 | 3.1 | 290 | 4.1841 | 835.2 | 1447.2 | 260.746 | 0 | 1 | 3 | 1/7 | 12:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.187 | 306 | 25.2 | 264.996 | 0 | 1 | 6 | 12
13 | 1/28 | 13:00:00 | 277.15 | 98771 | 1.5 | 164 | 4.1838 | 885.6 | 1929.6 | 261.69 | 0 | 1 | 4 | 1/7 | 13:00:00 | 279.15 | 98789 | 7.7 | 290 | 5.187 | 579.6 | 1252.8 | 264.528 | 0 | 1 | 6 | 13
14 | 1/28 | 14:00:00 | 278.15 | 98780 | 1.5 | 139 | 4.1834 | 784.8 | 1810.8 | 262.634 | 0 | 1 | 5 | 1/7 | 14:00:00 | 280.15 | 98798 | 13.4 | 280 | 4.8303 | 478.8 | 1105.2 | 265.246 | 0 | 1 | 7 | 14
15 | 1/28 | 15:00:00 | 277.15 | 98771 | 1.5 | 182 | 4.1838 | 547.2 | 1227.6 | 261.69 | 0 | 1 | 4 | 1/7 | 15:00:00 | 279.15 | 98789 | 13.4 | 270 | 4.8307 | 273.6 | 626.4 | 264.299 | 0 | 1 | 6 | 15
16 | 1/28 | 16:00:00 | 278.15 | 98780 | 1 | 268 | 4.1834 | 230.4 | 529.2 | 262.634 | 0 | 1 | 5 | 1/7 | 16:00:00 | 279.15 | 98789 | 11.3 | 260 | 4.8307 | 72 | 18 | 264.041 | 0 | 1 | 6 | 16
| 1/28 | 17:00:00 | 277.15 | 98771 | 2.1 | 310 | 3.8896 | 3.6 | 0 | 261.458 | 0 | 1 | 4 | 1/7 | 17:00:00 | 279.15 | 98789 | 11.3 | 270 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
| 1/28 | 18:00:00 | 275.15 | 98752 | 3.6 | 310 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2 | 1/7 | 18:00:00 | 279.15 | 98789 | 10.8 | 270 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
| 1/28 | 19:00:00 | 274.15 | 98743 | 1.5 | 300 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1 | 1/7 | 19:00:00 | 279.15 | 98789 | 10.3 | 270 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
| 1/28 | 20:00:00 | 273.15 | 98734 | 2.1 | 300 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0 | 1/7 | 20:00:00 | 279.15 | 98789 | 9.8 | 270 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
| 1/28 | 21:00:00 | 273.15 | 98734 | 2.6 | 290 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0 | 1/7 | 21:00:00 | 279.15 | 98789 | 12.9 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
| 1/28 | 22:00:00 | 272.15 | 98724 | 2.6 | 290 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1 | 1/7 | 22:00:00 | 279.15 | 98789 | 7.2 | 260 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
| 1/28 | 23:00:00 | 273.15 | 98734 | 2.1 | 290 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0 | 1/7 | 23:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
| 1/28 | 24:00:00 | 272.15 | 98724 | 1.5 | 270 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1 | 1/7 | 24:00:00 | 279.15 | 98789 | 11.3 | 280 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
[5 empty] | 2.4444 | 293.875 | [6 empty] | 3.2222 |  |  |  |  | 10.0222 | 277.0833 | [6 empty] | 6
[5 empty] | Light breeze |  | Fresh Breeze
|  |  |  | Summer | 29 Septmeber |  | 06 Septmeber
|  |  |  | Winter | 28 Janurary |  | 07 Janurary

## Weather Data (All)
ID | !Date | Time | Ta [K] | Pb [Pa] | Ws [m/s] | Wd [deg] | Hr [g/kg] | Ith [kJ/m^2] | Idn [kJ/m^2] | Ts [K] | Rn [-] | Sn [-] | T [C]
1 | 1/1 | 00:00:00 | 277.15 | 98771 | 9.8 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4 |  | Beaufort wind scale |  | Descriptive terms |  | Wind speed (m/s) | Occurrence (hours) | Occurrence (%)
2 | 1/1 | 01:00:00 | 283.15 | 98824 | 4.6 | 230 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10 |  | 0 |  | Calm |  | <1 | 241 | 2.751%
3 | 1/1 | 02:00:00 | 283.15 | 98824 | 6.2 | 230 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10 |  | 1 |  | Light air |  | 1-2 | 664 | 7.578%
4 | 1/1 | 03:00:00 | 282.15 | 98815 | 7.7 | 240 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9 |  | 2 |  | Light breeze |  | 2-3 | 1168 | 13.33%
5 | 1/1 | 04:00:00 | 282.15 | 98815 | 7.7 | 230 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9 |  | 3 |  | Gentle breeze |  | 3-5 | 2782 | 31.75%
6 | 1/1 | 05:00:00 | 282.15 | 98815 | 5.7 | 230 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9 |  | 4 |  | Moderate breeze |  | 5-8 | 2786 | 31.8%
7 | 1/1 | 06:00:00 | 281.15 | 98806 | 6.2 | 230 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8 |  | 5 |  | Fresh breeze |  | 8-11 | 882 | 10.07%
8 | 1/1 | 07:00:00 | 281.15 | 98806 | 7.7 | 230 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8 |  | 6 |  | Strong breeze |  | 11-14 | 189 | 2.157%
9 | 1/1 | 08:00:00 | 281.15 | 98806 | 6.2 | 220 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8 |  | 7 |  | Near gale |  | 14-17 | 41 | 0.4679%
10 | 1/1 | 09:00:00 | 281.15 | 98806 | 7.2 | 230 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8 |  | 8 |  | Gale |  | 17-21 | 9 | 0.1027%
11 | 1/1 | 10:00:00 | 281.15 | 98806 | 7.2 | 230 | 5.9698 | 154.8 | 219.6 | 266.881 | 0 | 1 | 8 |  | 9 |  | Strong gale |  | 21-24 | 0 | 0%
12 | 1/1 | 11:00:00 | 280.15 | 98798 | 6.2 | 240 | 5.9703 | 374.4 | 889.2 | 265.931 | 0 | 1 | 7 |  | 10 |  | Storm |  | 24-28 | 0 | 0%
13 | 1/1 | 12:00:00 | 281.15 | 98806 | 7.7 | 220 | 6.4 | 514.8 | 903.6 | 267.107 | 0 | 1 | 8 |  | 11 |  | Violent storm |  | 28-32 | 0 | 0%
14 | 1/1 | 13:00:00 | 281.15 | 98806 | 6.2 | 230 | 6.4 | 298.8 | 25.2 | 267.58 | 0 | 1 | 8 |  | 12 |  | Hurricane |  | >32 | 0 | 0%
15 | 1/1 | 14:00:00 | 279.15 | 98789 | 8.2 | 250 | 5.5666 | 435.6 | 792 | 264.756 | 0 | 1 | 6
16 | 1/1 | 15:00:00 | 279.15 | 98789 | 6.7 | 250 | 5.5666 | 234 | 273.6 | 264.756 | 0 | 1 | 6
17 | 1/1 | 16:00:00 | 279.15 | 98789 | 5.7 | 230 | 5.187 | 50.4 | 0 | 264.269 | 0 | 1 | 6
18 | 1/1 | 17:00:00 | 279.15 | 98789 | 4.1 | 240 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
19 | 1/1 | 18:00:00 | 279.15 | 98789 | 4.6 | 240 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
20 | 1/1 | 19:00:00 | 278.15 | 98780 | 4.6 | 240 | 5.1875 | 0 | 0 | 263.323 | 0 | 1 | 5 |  |  | Light breeze |  | Fresh Breeze
21 | 1/1 | 20:00:00 | 278.15 | 98780 | 6.2 | 240 | 5.1875 | 0 | 0 | 263.323 | 0 | 1 | 5 |  | Summer | 2029-09-01 |  | 2006-09-01
22 | 1/1 | 21:00:00 | 278.15 | 98780 | 6.7 | 250 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5 |  | Winter | 2028-01-01 |  | 2007-01-01
23 | 1/1 | 22:00:00 | 277.15 | 98771 | 6.7 | 240 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
24 | 1/1 | 23:00:00 | 277.15 | 98771 | 5.7 | 240 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
25 | 1/1 | 24:00:00 | 276.15 | 98762 | 5.1 | 260 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
26 | 1/2 | 01:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
27 | 1/2 | 02:00:00 | 276.15 | 98762 | 3.6 | 230 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
28 | 1/2 | 03:00:00 | 275.15 | 98752 | 4.1 | 210 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
29 | 1/2 | 04:00:00 | 275.15 | 98752 | 3.6 | 220 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
30 | 1/2 | 05:00:00 | 275.15 | 98752 | 4.6 | 230 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
31 | 1/2 | 06:00:00 | 275.15 | 98752 | 5.7 | 220 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
32 | 1/2 | 07:00:00 | 276.15 | 98762 | 8.2 | 230 | 3.8899 | 0 | 0 | 260.515 | 0 | 1 | 3
33 | 1/2 | 08:00:00 | 275.15 | 98752 | 5.7 | 230 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
34 | 1/2 | 09:00:00 | 274.15 | 98743 | 5.7 | 230 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
35 | 1/2 | 10:00:00 | 275.15 | 98752 | 4.1 | 230 | 4.1846 | 158.4 | 180 | 260.056 | 0 | 1 | 2
36 | 1/2 | 11:00:00 | 276.15 | 98762 | 6.2 | 240 | 4.1841 | 381.6 | 810 | 261.001 | 0 | 1 | 3
37 | 1/2 | 12:00:00 | 277.15 | 98771 | 7.2 | 230 | 3.8896 | 529.2 | 1216.8 | 261.714 | 0 | 1 | 4
38 | 1/2 | 13:00:00 | 277.15 | 98771 | 7.2 | 240 | 3.8896 | 550.8 | 961.2 | 261.714 | 0 | 1 | 4
39 | 1/2 | 14:00:00 | 277.15 | 98771 | 6.7 | 240 | 3.8896 | 446.4 | 1062 | 261.714 | 0 | 1 | 4
40 | 1/2 | 15:00:00 | 278.15 | 98780 | 7.2 | 240 | 3.5789 | 241.2 | 554.4 | 262.425 | 0 | 1 | 5
41 | 1/2 | 16:00:00 | 277.15 | 98771 | 9.8 | 240 | 3.5793 | 50.4 | 0 | 261.481 | 0 | 1 | 4
42 | 1/2 | 17:00:00 | 276.15 | 98762 | 7.2 | 240 | 3.5796 | 0 | 0 | 260.538 | 0 | 1 | 3
43 | 1/2 | 18:00:00 | 276.15 | 98762 | 8.7 | 240 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
44 | 1/2 | 19:00:00 | 276.15 | 98762 | 5.7 | 230 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
45 | 1/2 | 20:00:00 | 276.15 | 98762 | 6.7 | 230 | 3.8899 | 0 | 0 | 260.515 | 0 | 1 | 3
46 | 1/2 | 21:00:00 | 276.15 | 98762 | 5.1 | 240 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
47 | 1/2 | 22:00:00 | 276.15 | 98762 | 6.7 | 220 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
48 | 1/2 | 23:00:00 | 276.15 | 98762 | 6.2 | 220 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
49 | 1/2 | 24:00:00 | 276.15 | 98762 | 5.1 | 210 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
50 | 1/3 | 01:00:00 | 276.15 | 98762 | 4.1 | 180 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
51 | 1/3 | 02:00:00 | 277.15 | 98771 | 5.7 | 190 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
52 | 1/3 | 03:00:00 | 276.15 | 98762 | 6.7 | 170 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
53 | 1/3 | 04:00:00 | 277.15 | 98771 | 7.7 | 170 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
54 | 1/3 | 05:00:00 | 280.15 | 98798 | 11.3 | 190 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
55 | 1/3 | 06:00:00 | 281.15 | 98806 | 12.3 | 210 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
56 | 1/3 | 07:00:00 | 283.15 | 98824 | 10.3 | 220 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
57 | 1/3 | 08:00:00 | 284.15 | 98833 | 14.9 | 230 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
58 | 1/3 | 09:00:00 | 281.15 | 98806 | 14.9 | 260 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
59 | 1/3 | 10:00:00 | 280.15 | 98798 | 13.4 | 250 | 5.1865 | 162 | 237.6 | 265.476 | 0 | 1 | 7
60 | 1/3 | 11:00:00 | 280.15 | 98798 | 14.4 | 250 | 4.8303 | 385.2 | 928.8 | 265.246 | 0 | 1 | 7
61 | 1/3 | 12:00:00 | 279.15 | 98789 | 13.9 | 260 | 4.4964 | 529.2 | 1202.4 | 264.069 | 0 | 1 | 6
62 | 1/3 | 13:00:00 | 279.15 | 98789 | 13.9 | 260 | 4.183 | 554.4 | 964.8 | 263.837 | 0 | 1 | 6
63 | 1/3 | 14:00:00 | 278.15 | 98780 | 13.9 | 260 | 4.4968 | 450 | 1051.2 | 263.123 | 0 | 1 | 5
64 | 1/3 | 15:00:00 | 278.15 | 98780 | 13.4 | 270 | 3.8892 | 248.4 | 568.8 | 262.659 | 0 | 1 | 5
65 | 1/3 | 16:00:00 | 277.15 | 98771 | 13.9 | 270 | 3.5793 | 54 | 0 | 261.481 | 0 | 1 | 4
66 | 1/3 | 17:00:00 | 276.15 | 98762 | 13.9 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
67 | 1/3 | 18:00:00 | 276.15 | 98762 | 10.3 | 260 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
68 | 1/3 | 19:00:00 | 277.15 | 98771 | 12.3 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
69 | 1/3 | 20:00:00 | 278.15 | 98780 | 11.3 | 250 | 4.1834 | 0 | 0 | 262.891 | 0 | 1 | 5
70 | 1/3 | 21:00:00 | 278.15 | 98780 | 9.8 | 250 | 4.1834 | 0 | 0 | 262.891 | 0 | 1 | 5
71 | 1/3 | 22:00:00 | 276.15 | 98762 | 10.3 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
72 | 1/3 | 23:00:00 | 277.15 | 98771 | 11.3 | 280 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
73 | 1/3 | 24:00:00 | 276.15 | 98762 | 10.8 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
74 | 1/4 | 01:00:00 | 276.15 | 98762 | 13.4 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
75 | 1/4 | 02:00:00 | 276.15 | 98762 | 12.3 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
76 | 1/4 | 03:00:00 | 276.15 | 98762 | 10.3 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
77 | 1/4 | 04:00:00 | 277.15 | 98771 | 9.3 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
78 | 1/4 | 05:00:00 | 277.15 | 98771 | 9.8 | 280 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
79 | 1/4 | 06:00:00 | 277.15 | 98771 | 8.7 | 270 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
80 | 1/4 | 07:00:00 | 277.15 | 98771 | 7.7 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
81 | 1/4 | 08:00:00 | 278.15 | 98780 | 8.2 | 260 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
82 | 1/4 | 09:00:00 | 278.15 | 98780 | 5.7 | 250 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
83 | 1/4 | 10:00:00 | 278.15 | 98780 | 6.2 | 250 | 4.8311 | 90 | 0 | 263.818 | 0 | 1 | 5
84 | 1/4 | 11:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.8311 | 216 | 0 | 263.818 | 0 | 1 | 5
85 | 1/4 | 12:00:00 | 278.15 | 98780 | 8.7 | 250 | 4.8311 | 295.2 | 18 | 263.818 | 0 | 1 | 5
86 | 1/4 | 13:00:00 | 278.15 | 98780 | 9.8 | 250 | 5.1875 | 309.6 | 21.6 | 264.047 | 0 | 1 | 5
87 | 1/4 | 14:00:00 | 278.15 | 98780 | 9.8 | 250 | 5.1875 | 252 | 3.6 | 264.047 | 0 | 1 | 5
88 | 1/4 | 15:00:00 | 279.15 | 98789 | 11.3 | 250 | 5.187 | 140.4 | 0 | 264.996 | 0 | 1 | 6
89 | 1/4 | 16:00:00 | 278.15 | 98780 | 11.8 | 250 | 5.1875 | 32.4 | 0 | 264.047 | 0 | 1 | 5
90 | 1/4 | 17:00:00 | 279.15 | 98789 | 12.9 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
91 | 1/4 | 18:00:00 | 279.15 | 98789 | 15.9 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
92 | 1/4 | 19:00:00 | 279.15 | 98789 | 14.9 | 250 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
93 | 1/4 | 20:00:00 | 279.15 | 98789 | 14.9 | 250 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
94 | 1/4 | 21:00:00 | 280.15 | 98798 | 14.4 | 260 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
95 | 1/4 | 22:00:00 | 280.15 | 98798 | 17.5 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
96 | 1/4 | 23:00:00 | 280.15 | 98798 | 16.5 | 260 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
97 | 1/4 | 24:00:00 | 281.15 | 98806 | 17.5 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
98 | 1/5 | 01:00:00 | 282.15 | 98815 | 19 | 270 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
99 | 1/5 | 02:00:00 | 279.15 | 98789 | 17 | 290 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
100 | 1/5 | 03:00:00 | 278.15 | 98780 | 13.9 | 280 | 5.5671 | 0 | 0 | 263.807 | 0 | 1 | 5
101 | 1/5 | 04:00:00 | 280.15 | 98798 | 14.4 | 280 | 4.8303 | 0 | 0 | 265.246 | 0 | 1 | 7
102 | 1/5 | 05:00:00 | 280.15 | 98798 | 13.9 | 270 | 4.8303 | 0 | 0 | 265.715 | 0 | 1 | 7
103 | 1/5 | 06:00:00 | 278.15 | 98780 | 15.4 | 290 | 5.5671 | 0 | 0 | 263.807 | 0 | 1 | 5
104 | 1/5 | 07:00:00 | 278.15 | 98780 | 14.4 | 290 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
105 | 1/5 | 08:00:00 | 278.15 | 98780 | 15.9 | 280 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
106 | 1/5 | 09:00:00 | 278.15 | 98780 | 14.9 | 280 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
107 | 1/5 | 10:00:00 | 276.15 | 98762 | 13.9 | 280 | 4.832 | 165.6 | 252 | 261.459 | 0 | 1 | 3
108 | 1/5 | 11:00:00 | 276.15 | 98762 | 14.4 | 280 | 4.832 | 392.4 | 914.4 | 261.459 | 0 | 1 | 3
109 | 1/5 | 12:00:00 | 278.15 | 98780 | 14.9 | 280 | 4.8311 | 572.4 | 1479.6 | 263.095 | 0 | 1 | 5
110 | 1/5 | 13:00:00 | 279.15 | 98789 | 15.9 | 310 | 3.8889 | 604.8 | 1180.8 | 263.345 | 0 | 1 | 6
111 | 1/5 | 14:00:00 | 279.15 | 98789 | 11.8 | 320 | 3.8889 | 493.2 | 1159.2 | 263.345 | 0 | 1 | 6
112 | 1/5 | 15:00:00 | 279.15 | 98789 | 7.2 | 310 | 4.183 | 277.2 | 741.6 | 263.578 | 0 | 1 | 6
113 | 1/5 | 16:00:00 | 278.15 | 98780 | 8.7 | 310 | 3.5789 | 64.8 | 0 | 262.168 | 0 | 1 | 5
114 | 1/5 | 17:00:00 | 277.15 | 98771 | 7.7 | 290 | 3.2918 | 0 | 0 | 261.246 | 0 | 1 | 4
115 | 1/5 | 18:00:00 | 276.15 | 98762 | 7.2 | 280 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
116 | 1/5 | 19:00:00 | 276.15 | 98762 | 9.3 | 280 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
117 | 1/5 | 20:00:00 | 276.15 | 98762 | 7.2 | 290 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
118 | 1/5 | 21:00:00 | 276.15 | 98762 | 7.2 | 280 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
119 | 1/5 | 22:00:00 | 276.15 | 98762 | 8.7 | 290 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
120 | 1/5 | 23:00:00 | 277.15 | 98771 | 10.3 | 290 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
121 | 1/5 | 24:00:00 | 277.15 | 98771 | 9.3 | 300 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
122 | 1/6 | 01:00:00 | 276.15 | 98762 | 8.2 | 300 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
123 | 1/6 | 02:00:00 | 276.15 | 98762 | 8.7 | 290 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
124 | 1/6 | 03:00:00 | 275.15 | 98752 | 6.2 | 280 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
125 | 1/6 | 04:00:00 | 275.15 | 98752 | 7.2 | 300 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
126 | 1/6 | 05:00:00 | 275.15 | 98752 | 4.1 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
127 | 1/6 | 06:00:00 | 275.15 | 98752 | 5.1 | 290 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
128 | 1/6 | 07:00:00 | 275.15 | 98752 | 7.2 | 290 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
129 | 1/6 | 08:00:00 | 275.15 | 98752 | 7.7 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
130 | 1/6 | 09:00:00 | 274.15 | 98743 | 6.2 | 290 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
131 | 1/6 | 10:00:00 | 274.15 | 98743 | 4.6 | 290 | 3.8907 | 75.6 | 0 | 259.445 | 0 | 1 | 1
132 | 1/6 | 11:00:00 | 276.15 | 98762 | 4.6 | 270 | 4.1841 | 421.2 | 1044 | 260.746 | 0 | 1 | 3
133 | 1/6 | 12:00:00 | 278.15 | 98780 | 5.7 | 260 | 4.8311 | 579.6 | 1465.2 | 263.095 | 0 | 1 | 5
134 | 1/6 | 13:00:00 | 278.15 | 98780 | 4.1 | 250 | 4.8311 | 572.4 | 1000.8 | 263.352 | 0 | 1 | 5
135 | 1/6 | 14:00:00 | 279.15 | 98789 | 6.2 | 250 | 5.187 | 259.2 | 7.2 | 264.996 | 0 | 1 | 6
136 | 1/6 | 15:00:00 | 280.15 | 98798 | 7.7 | 260 | 5.5661 | 266.4 | 522 | 265.704 | 0 | 1 | 7
137 | 1/6 | 16:00:00 | 279.15 | 98789 | 9.3 | 260 | 5.187 | 36 | 0 | 264.996 | 0 | 1 | 6
138 | 1/6 | 17:00:00 | 279.15 | 98789 | 6.2 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
139 | 1/6 | 18:00:00 | 279.15 | 98789 | 5.1 | 240 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
140 | 1/6 | 19:00:00 | 280.15 | 98798 | 8.7 | 250 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
141 | 1/6 | 20:00:00 | 280.15 | 98798 | 8.2 | 250 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
142 | 1/6 | 21:00:00 | 281.15 | 98806 | 5.7 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
143 | 1/6 | 22:00:00 | 282.15 | 98815 | 7.2 | 250 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
144 | 1/6 | 23:00:00 | 282.15 | 98815 | 8.2 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
145 | 1/6 | 24:00:00 | 282.15 | 98815 | 8.7 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
146 | 1/7 | 01:00:00 | 282.15 | 98815 | 6.7 | 280 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
147 | 1/7 | 02:00:00 | 281.15 | 98806 | 7.7 | 280 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
148 | 1/7 | 03:00:00 | 280.15 | 98798 | 11.8 | 270 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
149 | 1/7 | 04:00:00 | 280.15 | 98798 | 13.4 | 280 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
150 | 1/7 | 05:00:00 | 279.15 | 98789 | 10.3 | 290 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
151 | 1/7 | 06:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
152 | 1/7 | 07:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6 |  | 10.0222
153 | 1/7 | 08:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
154 | 1/7 | 09:00:00 | 278.15 | 98780 | 9.3 | 280 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
155 | 1/7 | 10:00:00 | 279.15 | 98789 | 10.3 | 280 | 4.8307 | 93.6 | 0 | 264.767 | 0 | 1 | 6
156 | 1/7 | 11:00:00 | 279.15 | 98789 | 9.3 | 290 | 4.8307 | 223.2 | 0 | 264.767 | 0 | 1 | 6
157 | 1/7 | 12:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.187 | 306 | 25.2 | 264.996 | 0 | 1 | 6
158 | 1/7 | 13:00:00 | 279.15 | 98789 | 7.7 | 290 | 5.187 | 579.6 | 1252.8 | 264.528 | 0 | 1 | 6
159 | 1/7 | 14:00:00 | 280.15 | 98798 | 13.4 | 280 | 4.8303 | 478.8 | 1105.2 | 265.246 | 0 | 1 | 7
160 | 1/7 | 15:00:00 | 279.15 | 98789 | 13.4 | 270 | 4.8307 | 273.6 | 626.4 | 264.299 | 0 | 1 | 6
161 | 1/7 | 16:00:00 | 279.15 | 98789 | 11.3 | 260 | 4.8307 | 72 | 18 | 264.041 | 0 | 1 | 6
162 | 1/7 | 17:00:00 | 279.15 | 98789 | 11.3 | 270 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
163 | 1/7 | 18:00:00 | 279.15 | 98789 | 10.8 | 270 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
164 | 1/7 | 19:00:00 | 279.15 | 98789 | 10.3 | 270 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
165 | 1/7 | 20:00:00 | 279.15 | 98789 | 9.8 | 270 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
166 | 1/7 | 21:00:00 | 279.15 | 98789 | 12.9 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
167 | 1/7 | 22:00:00 | 279.15 | 98789 | 7.2 | 260 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
168 | 1/7 | 23:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
169 | 1/7 | 24:00:00 | 279.15 | 98789 | 11.3 | 280 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
170 | 1/8 | 01:00:00 | 279.15 | 98789 | 9.3 | 280 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
171 | 1/8 | 02:00:00 | 279.15 | 98789 | 9.3 | 290 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
172 | 1/8 | 03:00:00 | 279.15 | 98789 | 10.8 | 290 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
173 | 1/8 | 04:00:00 | 279.15 | 98789 | 11.3 | 290 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
174 | 1/8 | 05:00:00 | 279.15 | 98789 | 3.6 | 290 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
175 | 1/8 | 06:00:00 | 279.15 | 98789 | 4.6 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
176 | 1/8 | 07:00:00 | 279.15 | 98789 | 5.7 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
177 | 1/8 | 08:00:00 | 279.15 | 98789 | 6.7 | 290 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
178 | 1/8 | 09:00:00 | 279.15 | 98789 | 5.1 | 290 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
179 | 1/8 | 10:00:00 | 279.15 | 98789 | 5.7 | 290 | 5.5666 | 97.2 | 0 | 265.224 | 0 | 1 | 6
180 | 1/8 | 11:00:00 | 280.15 | 98798 | 3.6 | 270 | 5.5661 | 226.8 | 0 | 266.174 | 0 | 1 | 7
181 | 1/8 | 12:00:00 | 280.15 | 98798 | 6.2 | 270 | 5.9703 | 309.6 | 21.6 | 266.402 | 0 | 1 | 7
182 | 1/8 | 13:00:00 | 280.15 | 98798 | 4.6 | 250 | 5.9703 | 324 | 28.8 | 266.402 | 0 | 1 | 7
183 | 1/8 | 14:00:00 | 281.15 | 98806 | 8.2 | 270 | 6.4 | 270 | 3.6 | 267.58 | 0 | 1 | 8
184 | 1/8 | 15:00:00 | 281.15 | 98806 | 7.2 | 270 | 6.8577 | 154.8 | 0 | 267.805 | 0 | 1 | 8
185 | 1/8 | 16:00:00 | 281.15 | 98806 | 8.7 | 270 | 6.8577 | 39.6 | 0 | 267.805 | 0 | 1 | 8
186 | 1/8 | 17:00:00 | 281.15 | 98806 | 8.7 | 270 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
187 | 1/8 | 18:00:00 | 281.15 | 98806 | 8.2 | 270 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
188 | 1/8 | 19:00:00 | 281.15 | 98806 | 6.2 | 260 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
189 | 1/8 | 20:00:00 | 281.15 | 98806 | 6.7 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
190 | 1/8 | 21:00:00 | 281.15 | 98806 | 4.1 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
191 | 1/8 | 22:00:00 | 281.15 | 98806 | 8.2 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
192 | 1/8 | 23:00:00 | 281.15 | 98806 | 10.8 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
193 | 1/8 | 24:00:00 | 281.15 | 98806 | 12.9 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
194 | 1/9 | 01:00:00 | 280.15 | 98798 | 12.3 | 260 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
195 | 1/9 | 02:00:00 | 280.15 | 98798 | 9.3 | 270 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
196 | 1/9 | 03:00:00 | 280.15 | 98798 | 13.9 | 270 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
197 | 1/9 | 04:00:00 | 280.15 | 98798 | 11.3 | 270 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
198 | 1/9 | 05:00:00 | 280.15 | 98798 | 12.9 | 270 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
199 | 1/9 | 06:00:00 | 280.15 | 98798 | 12.9 | 270 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
200 | 1/9 | 07:00:00 | 280.15 | 98798 | 10.3 | 270 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
201 | 1/9 | 08:00:00 | 281.15 | 98806 | 9.3 | 260 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
202 | 1/9 | 09:00:00 | 281.15 | 98806 | 7.7 | 250 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
203 | 1/9 | 10:00:00 | 281.15 | 98806 | 6.7 | 250 | 6.4 | 97.2 | 0 | 267.58 | 0 | 1 | 8
204 | 1/9 | 11:00:00 | 281.15 | 98806 | 5.7 | 260 | 6.4 | 226.8 | 0 | 267.58 | 0 | 1 | 8
205 | 1/9 | 12:00:00 | 281.15 | 98806 | 6.7 | 280 | 6.8577 | 313.2 | 25.2 | 267.805 | 0 | 1 | 8
206 | 1/9 | 13:00:00 | 282.15 | 98815 | 6.7 | 280 | 6.3994 | 594 | 1260 | 268.057 | 0 | 1 | 9
207 | 1/9 | 14:00:00 | 281.15 | 98806 | 6.7 | 280 | 5.9698 | 493.2 | 882 | 266.881 | 0 | 1 | 8
208 | 1/9 | 15:00:00 | 281.15 | 98806 | 6.7 | 280 | 5.5656 | 158.4 | 0 | 267.125 | 0 | 1 | 8
209 | 1/9 | 16:00:00 | 281.15 | 98806 | 4.6 | 270 | 5.5656 | 79.2 | 151.2 | 266.392 | 0 | 1 | 8
210 | 1/9 | 17:00:00 | 279.15 | 98789 | 7.7 | 270 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
211 | 1/9 | 18:00:00 | 278.15 | 98780 | 6.7 | 270 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
212 | 1/9 | 19:00:00 | 277.15 | 98771 | 2.6 | 270 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
213 | 1/9 | 20:00:00 | 276.15 | 98762 | 2.6 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
214 | 1/9 | 21:00:00 | 276.15 | 98762 | 2.6 | 270 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
215 | 1/9 | 22:00:00 | 277.15 | 98771 | 2.1 | 260 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
216 | 1/9 | 23:00:00 | 276.15 | 98762 | 2.1 | 260 | 4.832 | 0 | 0 | 261.203 | 0 | 1 | 3
217 | 1/9 | 24:00:00 | 276.15 | 98762 | 2.6 | 240 | 4.832 | 0 | 0 | 261.203 | 0 | 1 | 3
218 | 1/10 | 01:00:00 | 277.15 | 98771 | 6.7 | 260 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
219 | 1/10 | 02:00:00 | 277.15 | 98771 | 5.7 | 260 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
220 | 1/10 | 03:00:00 | 278.15 | 98780 | 5.1 | 260 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
221 | 1/10 | 04:00:00 | 279.15 | 98789 | 6.7 | 250 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
222 | 1/10 | 05:00:00 | 279.15 | 98789 | 5.7 | 260 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
223 | 1/10 | 06:00:00 | 279.15 | 98789 | 4.6 | 250 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
224 | 1/10 | 07:00:00 | 279.15 | 98789 | 4.6 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
225 | 1/10 | 08:00:00 | 279.15 | 98789 | 8.7 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
226 | 1/10 | 09:00:00 | 279.15 | 98789 | 7.2 | 260 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
227 | 1/10 | 10:00:00 | 279.15 | 98789 | 7.2 | 260 | 4.8307 | 183.6 | 298.8 | 264.299 | 0 | 1 | 6
228 | 1/10 | 11:00:00 | 280.15 | 98798 | 8.7 | 260 | 4.8303 | 421.2 | 1004.4 | 265.246 | 0 | 1 | 7
229 | 1/10 | 12:00:00 | 280.15 | 98798 | 6.7 | 260 | 4.8303 | 576 | 1004.4 | 265.246 | 0 | 1 | 7
230 | 1/10 | 13:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.5661 | 334.8 | 36 | 266.174 | 0 | 1 | 7
231 | 1/10 | 14:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.9703 | 277.2 | 7.2 | 266.402 | 0 | 1 | 7
232 | 1/10 | 15:00:00 | 281.15 | 98806 | 6.2 | 240 | 6.4 | 165.6 | 0 | 267.58 | 0 | 1 | 8
233 | 1/10 | 16:00:00 | 281.15 | 98806 | 6.7 | 250 | 6.4 | 43.2 | 0 | 267.58 | 0 | 1 | 8
234 | 1/10 | 17:00:00 | 281.15 | 98806 | 6.7 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
235 | 1/10 | 18:00:00 | 281.15 | 98806 | 7.2 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
236 | 1/10 | 19:00:00 | 281.15 | 98806 | 7.7 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
237 | 1/10 | 20:00:00 | 282.15 | 98815 | 8.7 | 250 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
238 | 1/10 | 21:00:00 | 282.15 | 98815 | 8.7 | 250 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
239 | 1/10 | 22:00:00 | 282.15 | 98815 | 9.3 | 250 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
240 | 1/10 | 23:00:00 | 281.15 | 98806 | 7.2 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
241 | 1/10 | 24:00:00 | 281.15 | 98806 | 3.6 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
242 | 1/11 | 01:00:00 | 281.15 | 98806 | 3.6 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
243 | 1/11 | 02:00:00 | 281.15 | 98806 | 4.1 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
244 | 1/11 | 03:00:00 | 282.15 | 98815 | 6.7 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
245 | 1/11 | 04:00:00 | 282.15 | 98815 | 7.2 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
246 | 1/11 | 05:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
247 | 1/11 | 06:00:00 | 281.15 | 98806 | 10.3 | 270 | 6.8577 | 0 | 0 | 267.071 | 0 | 1 | 8
248 | 1/11 | 07:00:00 | 281.15 | 98806 | 6.7 | 280 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
249 | 1/11 | 08:00:00 | 281.15 | 98806 | 5.7 | 280 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
250 | 1/11 | 09:00:00 | 282.15 | 98815 | 8.2 | 260 | 6.8571 | 3.6 | 0 | 268.758 | 0 | 1 | 9
251 | 1/11 | 10:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 104.4 | 0 | 268.758 | 0 | 1 | 9
252 | 1/11 | 11:00:00 | 282.15 | 98815 | 6.7 | 260 | 7.3438 | 234 | 0 | 268.983 | 0 | 1 | 9
253 | 1/11 | 12:00:00 | 282.15 | 98815 | 7.7 | 260 | 7.3438 | 320.4 | 25.2 | 268.983 | 0 | 1 | 9
254 | 1/11 | 13:00:00 | 282.15 | 98815 | 6.2 | 260 | 7.3438 | 338.4 | 28.8 | 268.983 | 0 | 1 | 9
255 | 1/11 | 14:00:00 | 282.15 | 98815 | 4.1 | 250 | 7.3438 | 284.4 | 7.2 | 268.983 | 0 | 1 | 9
256 | 1/11 | 15:00:00 | 282.15 | 98815 | 9.3 | 260 | 6.8571 | 169.2 | 0 | 268.758 | 0 | 1 | 9
257 | 1/11 | 16:00:00 | 282.15 | 98815 | 5.1 | 250 | 6.8571 | 46.8 | 0 | 268.758 | 0 | 1 | 9
258 | 1/11 | 17:00:00 | 282.15 | 98815 | 6.7 | 250 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
259 | 1/11 | 18:00:00 | 282.15 | 98815 | 7.7 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
260 | 1/11 | 19:00:00 | 282.15 | 98815 | 7.2 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
261 | 1/11 | 20:00:00 | 282.15 | 98815 | 8.2 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
262 | 1/11 | 21:00:00 | 282.15 | 98815 | 8.7 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
263 | 1/11 | 22:00:00 | 282.15 | 98815 | 7.2 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
264 | 1/11 | 23:00:00 | 281.15 | 98806 | 9.3 | 250 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
265 | 1/11 | 24:00:00 | 281.15 | 98806 | 8.7 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
266 | 1/12 | 01:00:00 | 281.15 | 98806 | 6.7 | 240 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
267 | 1/12 | 02:00:00 | 281.15 | 98806 | 5.1 | 230 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
268 | 1/12 | 03:00:00 | 281.15 | 98806 | 5.7 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
269 | 1/12 | 04:00:00 | 282.15 | 98815 | 12.9 | 250 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
270 | 1/12 | 05:00:00 | 282.15 | 98815 | 14.4 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
271 | 1/12 | 06:00:00 | 282.15 | 98815 | 15.9 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
272 | 1/12 | 07:00:00 | 282.15 | 98815 | 18.5 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
273 | 1/12 | 08:00:00 | 282.15 | 98815 | 15.9 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
274 | 1/12 | 09:00:00 | 281.15 | 98806 | 14.9 | 290 | 5.5656 | 7.2 | 0 | 266.653 | 0 | 1 | 8
275 | 1/12 | 10:00:00 | 281.15 | 98806 | 8.7 | 290 | 5.1861 | 194.4 | 324 | 266.423 | 0 | 1 | 8
276 | 1/12 | 11:00:00 | 280.15 | 98798 | 8.7 | 280 | 5.1865 | 460.8 | 1245.6 | 265.216 | 0 | 1 | 7
277 | 1/12 | 12:00:00 | 281.15 | 98806 | 10.8 | 300 | 5.1861 | 626.4 | 1555.2 | 266.163 | 0 | 1 | 8
278 | 1/12 | 13:00:00 | 281.15 | 98806 | 9.3 | 310 | 5.1861 | 662.4 | 1386 | 266.163 | 0 | 1 | 8
279 | 1/12 | 14:00:00 | 280.15 | 98798 | 7.2 | 300 | 4.8303 | 558 | 1432.8 | 264.986 | 0 | 1 | 7
280 | 1/12 | 15:00:00 | 280.15 | 98798 | 7.7 | 290 | 4.496 | 338.4 | 903.6 | 264.755 | 0 | 1 | 7
281 | 1/12 | 16:00:00 | 279.15 | 98789 | 6.7 | 290 | 4.183 | 86.4 | 57.6 | 263.959 | 0 | 1 | 6
282 | 1/12 | 17:00:00 | 278.15 | 98780 | 7.2 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
283 | 1/12 | 18:00:00 | 277.15 | 98771 | 6.2 | 290 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
284 | 1/12 | 19:00:00 | 277.15 | 98771 | 8.2 | 290 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
285 | 1/12 | 20:00:00 | 276.15 | 98762 | 5.7 | 280 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
286 | 1/12 | 21:00:00 | 276.15 | 98762 | 5.7 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
287 | 1/12 | 22:00:00 | 275.15 | 98752 | 5.7 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
288 | 1/12 | 23:00:00 | 276.15 | 98762 | 8.2 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
289 | 1/12 | 24:00:00 | 275.15 | 98752 | 5.7 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
290 | 1/13 | 01:00:00 | 276.15 | 98762 | 5.7 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
291 | 1/13 | 02:00:00 | 275.15 | 98752 | 4.1 | 290 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
292 | 1/13 | 03:00:00 | 275.15 | 98752 | 3.6 | 310 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
293 | 1/13 | 04:00:00 | 275.15 | 98752 | 3.6 | 290 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
294 | 1/13 | 05:00:00 | 275.15 | 98752 | 4.6 | 300 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
295 | 1/13 | 06:00:00 | 275.15 | 98752 | 5.7 | 320 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
296 | 1/13 | 07:00:00 | 274.15 | 98743 | 3.6 | 310 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
297 | 1/13 | 08:00:00 | 274.15 | 98743 | 3.6 | 300 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
298 | 1/13 | 09:00:00 | 273.15 | 98734 | 3.6 | 310 | 3.5806 | 3.6 | 0 | 258.163 | 0 | 1 | 0
299 | 1/13 | 10:00:00 | 273.15 | 98734 | 3.1 | 300 | 3.5806 | 97.2 | 0 | 258.163 | 0 | 1 | 0
300 | 1/13 | 11:00:00 | 274.15 | 98743 | 3.6 | 310 | 3.5803 | 298.8 | 118.8 | 259 | 0 | 1 | 1
301 | 1/13 | 12:00:00 | 275.15 | 98752 | 3.6 | 310 | 3.8903 | 388.8 | 147.6 | 260.286 | 0 | 1 | 2
302 | 1/13 | 13:00:00 | 276.15 | 98762 | 2.1 | 310 | 3.8899 | 504 | 403.2 | 261.122 | 0 | 1 | 3
303 | 1/13 | 14:00:00 | 277.15 | 98771 | 2.6 | 360 | 3.5793 | 525.6 | 936 | 261.603 | 0 | 1 | 4
304 | 1/13 | 15:00:00 | 277.15 | 98771 | 1.5 | 159 | 3.5793 | 320.4 | 705.6 | 261.603 | 0 | 1 | 4
305 | 1/13 | 16:00:00 | 276.15 | 98762 | 1 | 271 | 3.5796 | 86.4 | 32.4 | 260.659 | 0 | 1 | 3
306 | 1/13 | 17:00:00 | 275.15 | 98752 | 0.5 | 360 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
307 | 1/13 | 18:00:00 | 275.15 | 98752 | 0 | 142 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
308 | 1/13 | 19:00:00 | 274.15 | 98743 | 0 | 126 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
309 | 1/13 | 20:00:00 | 274.15 | 98743 | 0.5 | 206 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
310 | 1/13 | 21:00:00 | 273.15 | 98734 | 0.5 | 200 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
311 | 1/13 | 22:00:00 | 274.15 | 98743 | 1 | 180 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
312 | 1/13 | 23:00:00 | 272.15 | 98724 | 1 | 220 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
313 | 1/13 | 24:00:00 | 272.15 | 98724 | 1.5 | 210 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
314 | 1/14 | 01:00:00 | 271.15 | 98715 | 2.1 | 240 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
315 | 1/14 | 02:00:00 | 272.15 | 98724 | 2.1 | 250 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
316 | 1/14 | 03:00:00 | 271.15 | 98715 | 2.1 | 250 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
317 | 1/14 | 04:00:00 | 272.15 | 98724 | 2.6 | 270 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
318 | 1/14 | 05:00:00 | 273.15 | 98734 | 1.5 | 260 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
319 | 1/14 | 06:00:00 | 272.15 | 98724 | 1.5 | 220 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
320 | 1/14 | 07:00:00 | 272.15 | 98724 | 0.5 | 131 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
321 | 1/14 | 08:00:00 | 271.15 | 98715 | 1 | 250 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
322 | 1/14 | 09:00:00 | 272.15 | 98724 | 1 | 260 | 3.0271 | 10.8 | 0 | 256.647 | 0 | 1 | -1
323 | 1/14 | 10:00:00 | 272.15 | 98724 | 0.5 | 230 | 3.0271 | 144 | 3.6 | 256.647 | 0 | 1 | -1
324 | 1/14 | 11:00:00 | 275.15 | 98752 | 0.5 | 193 | 3.5799 | 367.2 | 324 | 259.832 | 0 | 1 | 2
325 | 1/14 | 12:00:00 | 276.15 | 98762 | 0.5 | 49 | 3.5796 | 561.6 | 896.4 | 260.659 | 0 | 1 | 3
326 | 1/14 | 13:00:00 | 276.15 | 98762 | 1 | 108 | 3.5796 | 594 | 813.6 | 260.659 | 0 | 1 | 3
327 | 1/14 | 14:00:00 | 276.15 | 98762 | 1.5 | 43 | 3.5796 | 504 | 936 | 260.659 | 0 | 1 | 3
328 | 1/14 | 15:00:00 | 276.15 | 98762 | 2.1 | 160 | 3.5796 | 309.6 | 306 | 260.659 | 0 | 1 | 3
329 | 1/14 | 16:00:00 | 275.15 | 98752 | 2.1 | 130 | 3.5799 | 82.8 | 0 | 259.832 | 0 | 1 | 2
330 | 1/14 | 17:00:00 | 273.15 | 98734 | 2.6 | 130 | 3.293 | 0 | 0 | 257.823 | 0 | 1 | 0
331 | 1/14 | 18:00:00 | 273.15 | 98734 | 3.1 | 130 | 3.293 | 0 | 0 | 256.813 | 0 | 1 | 0
332 | 1/14 | 19:00:00 | 272.15 | 98724 | 2.6 | 140 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
333 | 1/14 | 20:00:00 | 272.15 | 98724 | 3.6 | 160 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
334 | 1/14 | 21:00:00 | 272.15 | 98724 | 2.6 | 160 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
335 | 1/14 | 22:00:00 | 270.15 | 98705 | 2.6 | 140 | 3.0276 | 0 | 0 | 254.971 | 0 | 1 | -3
336 | 1/14 | 23:00:00 | 271.15 | 98715 | 2.6 | 140 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
337 | 1/14 | 24:00:00 | 271.15 | 98715 | 2.6 | 150 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
338 | 1/15 | 01:00:00 | 270.15 | 98705 | 2.1 | 140 | 3.0276 | 0 | 0 | 253.763 | 0 | 1 | -3
339 | 1/15 | 02:00:00 | 270.15 | 98705 | 1.5 | 150 | 2.7812 | 0 | 0 | 253.532 | 0 | 1 | -3
340 | 1/15 | 03:00:00 | 270.15 | 98705 | 0.5 | 27 | 2.8531 | 0 | 0 | 253.601 | 0 | 1 | -3
341 | 1/15 | 04:00:00 | 269.15 | 98696 | 0 | 60 | 2.7814 | 0 | 0 | 252.593 | 0 | 1 | -4
342 | 1/15 | 05:00:00 | 270.15 | 98705 | 1 | 100 | 3.0276 | 0 | 0 | 253.763 | 0 | 1 | -3
343 | 1/15 | 06:00:00 | 269.15 | 98696 | 0.5 | 81 | 2.7814 | 0 | 0 | 252.593 | 0 | 1 | -4
344 | 1/15 | 07:00:00 | 269.15 | 98696 | 1 | 207 | 2.7814 | 0 | 0 | 252.593 | 0 | 1 | -4
345 | 1/15 | 08:00:00 | 269.15 | 98696 | 2.1 | 120 | 2.7814 | 0 | 0 | 253.245 | 0 | 1 | -4
346 | 1/15 | 09:00:00 | 270.15 | 98705 | 1 | 130 | 2.8289 | 7.2 | 0 | 254.682 | 0 | 1 | -3
347 | 1/15 | 10:00:00 | 271.15 | 98715 | 1 | 100 | 2.8772 | 118.8 | 0 | 255.672 | 0 | 1 | -2
348 | 1/15 | 11:00:00 | 271.15 | 98715 | 1.5 | 120 | 3.2936 | 460.8 | 1000.8 | 255.591 | 0 | 1 | -2
349 | 1/15 | 12:00:00 | 272.15 | 98724 | 1 | 100 | 3.5512 | 345.6 | 32.4 | 257.195 | 0 | 1 | -1
350 | 1/15 | 13:00:00 | 272.15 | 98724 | 1.5 | 120 | 3.581 | 367.2 | 54 | 257.218 | 0 | 1 | -1
351 | 1/15 | 14:00:00 | 273.15 | 98734 | 3.1 | 140 | 3.6713 | 313.2 | 32.4 | 258.233 | 0 | 1 | 0
352 | 1/15 | 15:00:00 | 274.15 | 98743 | 2.6 | 120 | 3.8907 | 194.4 | 0 | 259.34 | 0 | 1 | 1
353 | 1/15 | 16:00:00 | 273.15 | 98734 | 1.5 | 58 | 3.891 | 111.6 | 190.8 | 257.685 | 0 | 1 | 0
354 | 1/15 | 17:00:00 | 272.15 | 98724 | 3.1 | 90 | 3.581 | 0 | 0 | 256.103 | 0 | 1 | -1
355 | 1/15 | 18:00:00 | 272.15 | 98724 | 2.6 | 100 | 3.2934 | 0 | 0 | 255.873 | 0 | 1 | -1
356 | 1/15 | 19:00:00 | 271.15 | 98715 | 3.1 | 90 | 3.2936 | 0 | 0 | 254.933 | 0 | 1 | -2
357 | 1/15 | 20:00:00 | 271.15 | 98715 | 2.6 | 100 | 3.2936 | 0 | 0 | 254.933 | 0 | 1 | -2
358 | 1/15 | 21:00:00 | 272.15 | 98724 | 2.6 | 100 | 3.2934 | 0 | 0 | 255.873 | 0 | 1 | -1
359 | 1/15 | 22:00:00 | 272.15 | 98724 | 3.1 | 120 | 3.581 | 0 | 0 | 256.764 | 0 | 1 | -1
360 | 1/15 | 23:00:00 | 272.15 | 98724 | 2.1 | 110 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
361 | 1/15 | 24:00:00 | 273.15 | 98734 | 2.1 | 120 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
362 | 1/16 | 01:00:00 | 272.15 | 98724 | 2.1 | 110 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
363 | 1/16 | 02:00:00 | 270.15 | 98705 | 3.1 | 140 | 2.7812 | 0 | 0 | 254.636 | 0 | 1 | -3
364 | 1/16 | 03:00:00 | 270.15 | 98705 | 0.5 | 142 | 3.0276 | 0 | 0 | 253.763 | 0 | 1 | -3
365 | 1/16 | 04:00:00 | 272.15 | 98724 | 2.1 | 140 | 3.2934 | 0 | 0 | 255.873 | 0 | 1 | -1
366 | 1/16 | 05:00:00 | 271.15 | 98715 | 0.5 | 90 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
367 | 1/16 | 06:00:00 | 271.15 | 98715 | 1 | 58 | 3.2936 | 0 | 0 | 256.043 | 0 | 1 | -2
368 | 1/16 | 07:00:00 | 272.15 | 98724 | 1.5 | 100 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
369 | 1/16 | 08:00:00 | 271.15 | 98715 | 2.1 | 100 | 3.2936 | 0 | 0 | 256.043 | 0 | 1 | -2
370 | 1/16 | 09:00:00 | 271.15 | 98715 | 2.1 | 110 | 3.2936 | 18 | 0 | 255.591 | 0 | 1 | -2
371 | 1/16 | 10:00:00 | 272.15 | 98724 | 2.6 | 140 | 3.2934 | 230.4 | 561.6 | 256.282 | 0 | 1 | -1
372 | 1/16 | 11:00:00 | 273.15 | 98734 | 0 | 249 | 3.5806 | 500.4 | 1177.2 | 257.455 | 0 | 1 | 0
373 | 1/16 | 12:00:00 | 274.15 | 98743 | 2.1 | 150 | 3.8907 | 673.2 | 1670.4 | 258.628 | 0 | 1 | 1
374 | 1/16 | 13:00:00 | 275.15 | 98752 | 2.1 | 150 | 3.8903 | 723.6 | 1767.6 | 259.157 | 0 | 1 | 2
375 | 1/16 | 14:00:00 | 276.15 | 98762 | 3.6 | 160 | 3.8899 | 615.6 | 1616.4 | 260.099 | 0 | 1 | 3
376 | 1/16 | 15:00:00 | 276.15 | 98762 | 0.5 | 32 | 4.1841 | 385.2 | 1062 | 260.329 | 0 | 1 | 3
377 | 1/16 | 16:00:00 | 275.15 | 98752 | 1 | 109 | 3.8903 | 118.8 | 255.6 | 259.157 | 0 | 1 | 2
378 | 1/16 | 17:00:00 | 273.15 | 98734 | 3.1 | 150 | 3.5806 | 0 | 0 | 257.044 | 0 | 1 | 0
379 | 1/16 | 18:00:00 | 273.15 | 98734 | 0 | 299 | 3.492 | 0 | 0 | 256.975 | 0 | 1 | 0
380 | 1/16 | 19:00:00 | 271.15 | 98715 | 0 | 144 | 3.2936 | 0 | 0 | 254.933 | 0 | 1 | -2
381 | 1/16 | 20:00:00 | 272.15 | 98724 | 1 | 84 | 3.4344 | 0 | 0 | 255.988 | 0 | 1 | -1
382 | 1/16 | 21:00:00 | 271.15 | 98715 | 2.1 | 170 | 3.2936 | 0 | 0 | 254.933 | 0 | 1 | -2
383 | 1/16 | 22:00:00 | 271.15 | 98715 | 1 | 250 | 3.2936 | 0 | 0 | 254.933 | 0 | 1 | -2
384 | 1/16 | 23:00:00 | 272.15 | 98724 | 1.5 | 9 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
385 | 1/16 | 24:00:00 | 272.15 | 98724 | 3.1 | 210 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
386 | 1/17 | 01:00:00 | 271.15 | 98715 | 2.1 | 220 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
387 | 1/17 | 02:00:00 | 273.15 | 98734 | 3.6 | 210 | 3.4629 | 0 | 0 | 258.071 | 0 | 1 | 0
388 | 1/17 | 03:00:00 | 274.15 | 98743 | 5.7 | 230 | 4.0651 | 0 | 0 | 259.583 | 0 | 1 | 1
389 | 1/17 | 04:00:00 | 274.15 | 98743 | 3.6 | 220 | 4.185 | 0 | 0 | 259.674 | 0 | 1 | 1
390 | 1/17 | 05:00:00 | 273.15 | 98734 | 2.6 | 240 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
391 | 1/17 | 06:00:00 | 272.15 | 98724 | 0.5 | 190 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
392 | 1/17 | 07:00:00 | 272.15 | 98724 | 2.1 | 260 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
393 | 1/17 | 08:00:00 | 272.15 | 98724 | 0.5 | 116 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
394 | 1/17 | 09:00:00 | 271.15 | 98715 | 1 | 174 | 3.2936 | 7.2 | 0 | 256.147 | 0 | 1 | -2
395 | 1/17 | 10:00:00 | 272.15 | 98724 | 1 | 238 | 3.581 | 75.6 | 0 | 257.322 | 0 | 1 | -1
396 | 1/17 | 11:00:00 | 273.15 | 98734 | 1 | 161 | 3.891 | 162 | 0 | 258.498 | 0 | 1 | 0
397 | 1/17 | 12:00:00 | 273.15 | 98734 | 1.5 | 30 | 3.891 | 219.6 | 0 | 258.498 | 0 | 1 | 0
398 | 1/17 | 13:00:00 | 275.15 | 98752 | 1 | 200 | 4.4981 | 230.4 | 0 | 260.851 | 0 | 1 | 2
399 | 1/17 | 14:00:00 | 275.15 | 98752 | 2.6 | 160 | 4.4981 | 198 | 0 | 260.851 | 0 | 1 | 2
400 | 1/17 | 15:00:00 | 275.15 | 98752 | 2.1 | 220 | 4.4981 | 126 | 0 | 260.851 | 0 | 1 | 2
401 | 1/17 | 16:00:00 | 276.15 | 98762 | 1.5 | 176 | 4.4977 | 104.4 | 104.4 | 261.352 | 0 | 1 | 3
402 | 1/17 | 17:00:00 | 275.15 | 98752 | 3.6 | 260 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
403 | 1/17 | 18:00:00 | 273.15 | 98734 | 0.5 | 240 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
404 | 1/17 | 19:00:00 | 273.15 | 98734 | 1.5 | 121 | 3.492 | 0 | 0 | 258.094 | 0 | 1 | 0
405 | 1/17 | 20:00:00 | 273.15 | 98734 | 2.1 | 260 | 3.377 | 0 | 0 | 258.001 | 0 | 1 | 0
406 | 1/17 | 21:00:00 | 274.15 | 98743 | 3.6 | 250 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
407 | 1/17 | 22:00:00 | 273.15 | 98734 | 3.1 | 240 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
408 | 1/17 | 23:00:00 | 275.15 | 98752 | 3.1 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
409 | 1/17 | 24:00:00 | 274.15 | 98743 | 2.1 | 210 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
410 | 1/18 | 01:00:00 | 276.15 | 98762 | 4.1 | 210 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
411 | 1/18 | 02:00:00 | 277.15 | 98771 | 4.1 | 220 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
412 | 1/18 | 03:00:00 | 279.15 | 98789 | 4.6 | 230 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
413 | 1/18 | 04:00:00 | 279.15 | 98789 | 3.6 | 200 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
414 | 1/18 | 05:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
415 | 1/18 | 06:00:00 | 279.15 | 98789 | 6.2 | 240 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
416 | 1/18 | 07:00:00 | 279.15 | 98789 | 5.1 | 240 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
417 | 1/18 | 08:00:00 | 280.15 | 98798 | 7.2 | 250 | 6.4005 | 0 | 0 | 266.157 | 0 | 1 | 7
418 | 1/18 | 09:00:00 | 280.15 | 98798 | 5.7 | 240 | 6.4005 | 25.2 | 0 | 266.157 | 0 | 1 | 7
419 | 1/18 | 10:00:00 | 281.15 | 98806 | 4.6 | 240 | 6.4 | 126 | 0 | 267.58 | 0 | 1 | 8
420 | 1/18 | 11:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.8577 | 266.4 | 3.6 | 267.805 | 0 | 1 | 8
421 | 1/18 | 12:00:00 | 281.15 | 98806 | 2.1 | 210 | 6.8577 | 360 | 57.6 | 267.805 | 0 | 1 | 8
422 | 1/18 | 13:00:00 | 281.15 | 98806 | 6.2 | 270 | 6.8577 | 687.6 | 1119.6 | 267.332 | 0 | 1 | 8
423 | 1/18 | 14:00:00 | 281.15 | 98806 | 5.1 | 270 | 5.9698 | 630 | 1544.4 | 266.62 | 0 | 1 | 8
424 | 1/18 | 15:00:00 | 280.15 | 98798 | 5.1 | 260 | 5.5661 | 403.2 | 1112.4 | 265.444 | 0 | 1 | 7
425 | 1/18 | 16:00:00 | 280.15 | 98798 | 4.6 | 250 | 5.1865 | 129.6 | 212.4 | 265.216 | 0 | 1 | 7
426 | 1/18 | 17:00:00 | 279.15 | 98789 | 5.7 | 260 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
427 | 1/18 | 18:00:00 | 279.15 | 98789 | 7.7 | 270 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
428 | 1/18 | 19:00:00 | 278.15 | 98780 | 6.7 | 250 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
429 | 1/18 | 20:00:00 | 278.15 | 98780 | 5.1 | 250 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
430 | 1/18 | 21:00:00 | 278.15 | 98780 | 5.1 | 240 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
431 | 1/18 | 22:00:00 | 278.15 | 98780 | 2.1 | 230 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
432 | 1/18 | 23:00:00 | 278.15 | 98780 | 1.5 | 62 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
433 | 1/18 | 24:00:00 | 278.15 | 98780 | 4.1 | 240 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
434 | 1/19 | 01:00:00 | 279.15 | 98789 | 4.6 | 240 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
435 | 1/19 | 02:00:00 | 279.15 | 98789 | 5.7 | 260 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
436 | 1/19 | 03:00:00 | 278.15 | 98780 | 7.2 | 250 | 5.5671 | 0 | 0 | 263.807 | 0 | 1 | 5
437 | 1/19 | 04:00:00 | 279.15 | 98789 | 6.2 | 260 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
438 | 1/19 | 05:00:00 | 278.15 | 98780 | 5.1 | 260 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
439 | 1/19 | 06:00:00 | 278.15 | 98780 | 6.2 | 260 | 5.1875 | 0 | 0 | 263.323 | 0 | 1 | 5
440 | 1/19 | 07:00:00 | 278.15 | 98780 | 6.7 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
441 | 1/19 | 08:00:00 | 279.15 | 98789 | 9.8 | 270 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
442 | 1/19 | 09:00:00 | 279.15 | 98789 | 9.8 | 260 | 5.187 | 28.8 | 0 | 264.528 | 0 | 1 | 6
443 | 1/19 | 10:00:00 | 278.15 | 98780 | 8.2 | 280 | 4.8311 | 237.6 | 561.6 | 263.352 | 0 | 1 | 5
444 | 1/19 | 11:00:00 | 278.15 | 98780 | 7.7 | 270 | 4.8311 | 525.6 | 1382.4 | 263.095 | 0 | 1 | 5
445 | 1/19 | 12:00:00 | 278.15 | 98780 | 8.2 | 280 | 4.8311 | 705.6 | 1684.8 | 263.095 | 0 | 1 | 5
446 | 1/19 | 13:00:00 | 279.15 | 98789 | 8.7 | 270 | 4.4964 | 748.8 | 1760.4 | 263.81 | 0 | 1 | 6
447 | 1/19 | 14:00:00 | 279.15 | 98789 | 8.7 | 270 | 4.4964 | 608.4 | 1353.6 | 264.069 | 0 | 1 | 6
448 | 1/19 | 15:00:00 | 279.15 | 98789 | 6.7 | 250 | 4.8307 | 392.4 | 946.8 | 264.299 | 0 | 1 | 6
449 | 1/19 | 16:00:00 | 278.15 | 98780 | 8.7 | 260 | 4.8311 | 126 | 147.6 | 263.352 | 0 | 1 | 5
450 | 1/19 | 17:00:00 | 277.15 | 98771 | 10.8 | 260 | 4.8316 | 0 | 0 | 262.405 | 0 | 1 | 4
451 | 1/19 | 18:00:00 | 277.15 | 98771 | 9.8 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
452 | 1/19 | 19:00:00 | 274.15 | 98743 | 14.4 | 300 | 4.185 | 0 | 0 | 258.857 | 0 | 1 | 1
453 | 1/19 | 20:00:00 | 275.15 | 98752 | 7.7 | 280 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
454 | 1/19 | 21:00:00 | 276.15 | 98762 | 9.3 | 280 | 3.8899 | 0 | 0 | 260.515 | 0 | 1 | 3
455 | 1/19 | 22:00:00 | 275.15 | 98752 | 7.2 | 290 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
456 | 1/19 | 23:00:00 | 275.15 | 98752 | 7.2 | 290 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
457 | 1/19 | 24:00:00 | 275.15 | 98752 | 8.7 | 280 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
458 | 1/20 | 01:00:00 | 275.15 | 98752 | 8.2 | 270 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
459 | 1/20 | 02:00:00 | 276.15 | 98762 | 7.7 | 270 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
460 | 1/20 | 03:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
461 | 1/20 | 04:00:00 | 276.15 | 98762 | 10.3 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
462 | 1/20 | 05:00:00 | 275.15 | 98752 | 8.7 | 290 | 4.4981 | 0 | 0 | 260.745 | 0 | 1 | 2
463 | 1/20 | 06:00:00 | 275.15 | 98752 | 5.1 | 280 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
464 | 1/20 | 07:00:00 | 275.15 | 98752 | 3.6 | 290 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
465 | 1/20 | 08:00:00 | 276.15 | 98762 | 4.6 | 290 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
466 | 1/20 | 09:00:00 | 276.15 | 98762 | 4.6 | 310 | 4.4977 | 18 | 0 | 261.693 | 0 | 1 | 3
467 | 1/20 | 10:00:00 | 276.15 | 98762 | 4.1 | 290 | 4.832 | 136.8 | 0 | 261.921 | 0 | 1 | 3
468 | 1/20 | 11:00:00 | 276.15 | 98762 | 4.1 | 290 | 4.832 | 507.6 | 907.2 | 261.459 | 0 | 1 | 3
469 | 1/20 | 12:00:00 | 277.15 | 98771 | 3.1 | 280 | 5.1879 | 374.4 | 64.8 | 263.098 | 0 | 1 | 4
470 | 1/20 | 13:00:00 | 277.15 | 98771 | 3.6 | 290 | 5.1879 | 716.4 | 1166.4 | 262.633 | 0 | 1 | 4
471 | 1/20 | 14:00:00 | 278.15 | 98780 | 3.6 | 260 | 5.5671 | 342 | 50.4 | 264.274 | 0 | 1 | 5
472 | 1/20 | 15:00:00 | 278.15 | 98780 | 2.6 | 270 | 5.5671 | 223.2 | 0 | 264.274 | 0 | 1 | 5
473 | 1/20 | 16:00:00 | 279.15 | 98789 | 6.7 | 280 | 5.9708 | 72 | 0 | 265.451 | 0 | 1 | 6
474 | 1/20 | 17:00:00 | 279.15 | 98789 | 6.2 | 270 | 5.9708 | 0 | 0 | 264.982 | 0 | 1 | 6
475 | 1/20 | 18:00:00 | 280.15 | 98798 | 8.2 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
476 | 1/20 | 19:00:00 | 279.15 | 98789 | 8.2 | 270 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
477 | 1/20 | 20:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
478 | 1/20 | 21:00:00 | 280.15 | 98798 | 9.3 | 260 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
479 | 1/20 | 22:00:00 | 281.15 | 98806 | 9.3 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
480 | 1/20 | 23:00:00 | 281.15 | 98806 | 5.1 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
481 | 1/20 | 24:00:00 | 281.15 | 98806 | 4.6 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
482 | 1/21 | 01:00:00 | 282.15 | 98815 | 9.8 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
483 | 1/21 | 02:00:00 | 282.15 | 98815 | 10.8 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
484 | 1/21 | 03:00:00 | 282.15 | 98815 | 10.3 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
485 | 1/21 | 04:00:00 | 282.15 | 98815 | 8.7 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
486 | 1/21 | 05:00:00 | 282.15 | 98815 | 10.3 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
487 | 1/21 | 06:00:00 | 282.15 | 98815 | 9.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
488 | 1/21 | 07:00:00 | 281.15 | 98806 | 11.3 | 280 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
489 | 1/21 | 08:00:00 | 280.15 | 98798 | 9.3 | 280 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
490 | 1/21 | 09:00:00 | 280.15 | 98798 | 13.4 | 280 | 4.496 | 39.6 | 0 | 264.755 | 0 | 1 | 7
491 | 1/21 | 10:00:00 | 280.15 | 98798 | 12.3 | 280 | 4.496 | 270 | 720 | 264.755 | 0 | 1 | 7
492 | 1/21 | 11:00:00 | 280.15 | 98798 | 12.3 | 280 | 4.496 | 550.8 | 1116 | 264.755 | 0 | 1 | 7
493 | 1/21 | 12:00:00 | 280.15 | 98798 | 11.8 | 270 | 4.496 | 381.6 | 72 | 265.483 | 0 | 1 | 7
494 | 1/21 | 13:00:00 | 279.15 | 98789 | 12.3 | 270 | 4.4964 | 406.8 | 54 | 264.536 | 0 | 1 | 6
495 | 1/21 | 14:00:00 | 279.15 | 98789 | 13.4 | 270 | 4.4964 | 352.8 | 43.2 | 264.536 | 0 | 1 | 6
496 | 1/21 | 15:00:00 | 279.15 | 98789 | 18.5 | 280 | 4.4964 | 417.6 | 777.6 | 264.069 | 0 | 1 | 6
497 | 1/21 | 16:00:00 | 278.15 | 98780 | 15.4 | 280 | 4.4968 | 79.2 | 0 | 263.588 | 0 | 1 | 5
498 | 1/21 | 17:00:00 | 277.15 | 98771 | 12.9 | 290 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
499 | 1/21 | 18:00:00 | 278.15 | 98780 | 14.4 | 280 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
500 | 1/21 | 19:00:00 | 278.15 | 98780 | 11.8 | 280 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
501 | 1/21 | 20:00:00 | 278.15 | 98780 | 12.9 | 280 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
502 | 1/21 | 21:00:00 | 278.15 | 98780 | 9.8 | 270 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
503 | 1/21 | 22:00:00 | 278.15 | 98780 | 9.8 | 290 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
504 | 1/21 | 23:00:00 | 278.15 | 98780 | 7.2 | 270 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
505 | 1/21 | 24:00:00 | 278.15 | 98780 | 6.2 | 280 | 4.1834 | 0 | 0 | 262.891 | 0 | 1 | 5
506 | 1/22 | 01:00:00 | 278.15 | 98780 | 10.3 | 270 | 4.1834 | 0 | 0 | 262.891 | 0 | 1 | 5
507 | 1/22 | 02:00:00 | 278.15 | 98780 | 10.8 | 270 | 4.1834 | 0 | 0 | 262.634 | 0 | 1 | 5
508 | 1/22 | 03:00:00 | 278.15 | 98780 | 9.8 | 270 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
509 | 1/22 | 04:00:00 | 278.15 | 98780 | 8.2 | 260 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
510 | 1/22 | 05:00:00 | 279.15 | 98789 | 9.8 | 260 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
511 | 1/22 | 06:00:00 | 279.15 | 98789 | 13.9 | 260 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
512 | 1/22 | 07:00:00 | 280.15 | 98798 | 12.3 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
513 | 1/22 | 08:00:00 | 280.15 | 98798 | 14.4 | 280 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
514 | 1/22 | 09:00:00 | 280.15 | 98798 | 16.5 | 270 | 5.1865 | 21.6 | 0 | 265.946 | 0 | 1 | 7
515 | 1/22 | 10:00:00 | 280.15 | 98798 | 14.9 | 270 | 5.1865 | 262.8 | 590.4 | 265.476 | 0 | 1 | 7
516 | 1/22 | 11:00:00 | 280.15 | 98798 | 15.4 | 270 | 5.1865 | 525.6 | 1198.8 | 265.476 | 0 | 1 | 7
517 | 1/22 | 12:00:00 | 280.15 | 98798 | 13.4 | 280 | 5.1865 | 702 | 1245.6 | 265.476 | 0 | 1 | 7
518 | 1/22 | 13:00:00 | 280.15 | 98798 | 11.3 | 280 | 5.5661 | 741.6 | 1285.2 | 265.704 | 0 | 1 | 7
519 | 1/22 | 14:00:00 | 280.15 | 98798 | 9.8 | 280 | 5.1865 | 644.4 | 1177.2 | 265.476 | 0 | 1 | 7
520 | 1/22 | 15:00:00 | 280.15 | 98798 | 8.2 | 280 | 4.496 | 457.2 | 1191.6 | 264.755 | 0 | 1 | 7
521 | 1/22 | 16:00:00 | 279.15 | 98789 | 6.7 | 290 | 4.4964 | 151.2 | 216 | 264.069 | 0 | 1 | 6
522 | 1/22 | 17:00:00 | 278.15 | 98780 | 8.7 | 270 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
523 | 1/22 | 18:00:00 | 278.15 | 98780 | 10.3 | 280 | 4.4968 | 0 | 0 | 262.865 | 0 | 1 | 5
524 | 1/22 | 19:00:00 | 278.15 | 98780 | 8.7 | 280 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
525 | 1/22 | 20:00:00 | 278.15 | 98780 | 8.7 | 290 | 4.4968 | 0 | 0 | 262.865 | 0 | 1 | 5
526 | 1/22 | 21:00:00 | 277.15 | 98771 | 7.7 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
527 | 1/22 | 22:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
528 | 1/22 | 23:00:00 | 277.15 | 98771 | 7.7 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
529 | 1/22 | 24:00:00 | 277.15 | 98771 | 6.7 | 260 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
530 | 1/23 | 01:00:00 | 277.15 | 98771 | 5.7 | 300 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
531 | 1/23 | 02:00:00 | 277.15 | 98771 | 5.1 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
532 | 1/23 | 03:00:00 | 277.15 | 98771 | 4.1 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
533 | 1/23 | 04:00:00 | 277.15 | 98771 | 6.2 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
534 | 1/23 | 05:00:00 | 277.15 | 98771 | 5.1 | 290 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
535 | 1/23 | 06:00:00 | 276.15 | 98762 | 6.2 | 270 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
536 | 1/23 | 07:00:00 | 276.15 | 98762 | 5.1 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
537 | 1/23 | 08:00:00 | 276.15 | 98762 | 5.1 | 270 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
538 | 1/23 | 09:00:00 | 277.15 | 98771 | 5.7 | 280 | 4.4973 | 46.8 | 0 | 261.92 | 0 | 1 | 4
539 | 1/23 | 10:00:00 | 277.15 | 98771 | 5.7 | 260 | 4.4973 | 273.6 | 619.2 | 262.177 | 0 | 1 | 4
540 | 1/23 | 11:00:00 | 277.15 | 98771 | 5.7 | 270 | 4.8316 | 540 | 1224 | 262.405 | 0 | 1 | 4
541 | 1/23 | 12:00:00 | 278.15 | 98780 | 5.7 | 270 | 4.4968 | 716.4 | 1274.4 | 263.123 | 0 | 1 | 5
542 | 1/23 | 13:00:00 | 278.15 | 98780 | 5.7 | 280 | 4.4968 | 759.6 | 1540.8 | 263.123 | 0 | 1 | 5
543 | 1/23 | 14:00:00 | 277.15 | 98771 | 6.7 | 280 | 4.8316 | 702 | 1670.4 | 262.149 | 0 | 1 | 4
544 | 1/23 | 15:00:00 | 277.15 | 98771 | 9.3 | 280 | 4.4973 | 471.6 | 1263.6 | 261.92 | 0 | 1 | 4
545 | 1/23 | 16:00:00 | 277.15 | 98771 | 7.2 | 290 | 4.1838 | 172.8 | 241.2 | 261.69 | 0 | 1 | 4
546 | 1/23 | 17:00:00 | 276.15 | 98762 | 7.2 | 280 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
547 | 1/23 | 18:00:00 | 276.15 | 98762 | 7.7 | 280 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
548 | 1/23 | 19:00:00 | 276.15 | 98762 | 8.2 | 290 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
549 | 1/23 | 20:00:00 | 275.15 | 98752 | 6.7 | 290 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
550 | 1/23 | 21:00:00 | 274.15 | 98743 | 4.6 | 290 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
551 | 1/23 | 22:00:00 | 275.15 | 98752 | 3.1 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
552 | 1/23 | 23:00:00 | 275.15 | 98752 | 6.2 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
553 | 1/23 | 24:00:00 | 275.15 | 98752 | 4.6 | 280 | 4.4981 | 0 | 0 | 260.851 | 0 | 1 | 2
554 | 1/24 | 01:00:00 | 276.15 | 98762 | 5.1 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
555 | 1/24 | 02:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
556 | 1/24 | 03:00:00 | 276.15 | 98762 | 3.6 | 250 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
557 | 1/24 | 04:00:00 | 276.15 | 98762 | 3.1 | 220 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
558 | 1/24 | 05:00:00 | 276.15 | 98762 | 4.1 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
559 | 1/24 | 06:00:00 | 276.15 | 98762 | 4.1 | 230 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
560 | 1/24 | 07:00:00 | 275.15 | 98752 | 2.1 | 210 | 4.4981 | 0 | 0 | 260.745 | 0 | 1 | 2
561 | 1/24 | 08:00:00 | 275.15 | 98752 | 3.1 | 160 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
562 | 1/24 | 09:00:00 | 275.15 | 98752 | 3.6 | 130 | 4.4981 | 28.8 | 0 | 260.745 | 0 | 1 | 2
563 | 1/24 | 10:00:00 | 275.15 | 98752 | 4.6 | 130 | 4.4981 | 154.8 | 0 | 260.745 | 0 | 1 | 2
564 | 1/24 | 11:00:00 | 275.15 | 98752 | 5.7 | 120 | 4.4981 | 306 | 25.2 | 260.745 | 0 | 1 | 2
565 | 1/24 | 12:00:00 | 275.15 | 98752 | 4.1 | 120 | 4.4981 | 244.8 | 0 | 260.851 | 0 | 1 | 2
566 | 1/24 | 13:00:00 | 275.15 | 98752 | 3.6 | 110 | 4.4981 | 428.4 | 64.8 | 260.745 | 0 | 1 | 2
567 | 1/24 | 14:00:00 | 275.15 | 98752 | 3.1 | 130 | 4.4981 | 226.8 | 0 | 260.851 | 0 | 1 | 2
568 | 1/24 | 15:00:00 | 276.15 | 98762 | 1 | 120 | 4.832 | 154.8 | 0 | 262.027 | 0 | 1 | 3
569 | 1/24 | 16:00:00 | 276.15 | 98762 | 1 | 109 | 4.832 | 93.6 | 0 | 261.921 | 0 | 1 | 3
570 | 1/24 | 17:00:00 | 276.15 | 98762 | 0.5 | 256 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
571 | 1/24 | 18:00:00 | 276.15 | 98762 | 1 | 334 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
572 | 1/24 | 19:00:00 | 276.15 | 98762 | 0.5 | 242 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
573 | 1/24 | 20:00:00 | 276.15 | 98762 | 1.5 | 247 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
574 | 1/24 | 21:00:00 | 276.15 | 98762 | 1 | 205 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
575 | 1/24 | 22:00:00 | 277.15 | 98771 | 1 | 123 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
576 | 1/24 | 23:00:00 | 277.15 | 98771 | 1.5 | 335 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
577 | 1/24 | 24:00:00 | 277.15 | 98771 | 1.5 | 150 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
578 | 1/25 | 01:00:00 | 278.15 | 98780 | 2.1 | 160 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
579 | 1/25 | 02:00:00 | 279.15 | 98789 | 2.6 | 200 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
580 | 1/25 | 03:00:00 | 279.15 | 98789 | 2.6 | 180 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
581 | 1/25 | 04:00:00 | 280.15 | 98798 | 2.1 | 210 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
582 | 1/25 | 05:00:00 | 281.15 | 98806 | 3.6 | 220 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
583 | 1/25 | 06:00:00 | 281.15 | 98806 | 3.1 | 220 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
584 | 1/25 | 07:00:00 | 280.15 | 98798 | 3.6 | 220 | 6.4005 | 0 | 0 | 266.157 | 0 | 1 | 7
585 | 1/25 | 08:00:00 | 281.15 | 98806 | 4.1 | 230 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
586 | 1/25 | 09:00:00 | 280.15 | 98798 | 3.6 | 220 | 5.9703 | 28.8 | 0 | 266.402 | 0 | 1 | 7
587 | 1/25 | 10:00:00 | 280.15 | 98798 | 5.7 | 210 | 5.9703 | 288 | 644.4 | 265.931 | 0 | 1 | 7
588 | 1/25 | 11:00:00 | 281.15 | 98806 | 3.6 | 170 | 5.9698 | 561.6 | 961.2 | 266.881 | 0 | 1 | 8
589 | 1/25 | 12:00:00 | 281.15 | 98806 | 4.6 | 190 | 5.9698 | 410.4 | 57.6 | 267.353 | 0 | 1 | 8
590 | 1/25 | 13:00:00 | 281.15 | 98806 | 6.7 | 200 | 5.5656 | 435.6 | 57.6 | 267.125 | 0 | 1 | 8
591 | 1/25 | 14:00:00 | 282.15 | 98815 | 6.2 | 210 | 5.5651 | 381.6 | 43.2 | 268.075 | 0 | 1 | 9
592 | 1/25 | 15:00:00 | 282.15 | 98815 | 6.2 | 200 | 5.9692 | 259.2 | 3.6 | 268.304 | 0 | 1 | 9
593 | 1/25 | 16:00:00 | 282.15 | 98815 | 6.7 | 190 | 5.9692 | 100.8 | 0 | 268.304 | 0 | 1 | 9
594 | 1/25 | 17:00:00 | 282.15 | 98815 | 5.1 | 200 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
595 | 1/25 | 18:00:00 | 282.15 | 98815 | 6.7 | 190 | 5.5651 | 0 | 0 | 268.075 | 0 | 1 | 9
596 | 1/25 | 19:00:00 | 282.15 | 98815 | 5.7 | 190 | 5.5651 | 0 | 0 | 268.075 | 0 | 1 | 9
597 | 1/25 | 20:00:00 | 282.15 | 98815 | 5.1 | 190 | 5.5651 | 0 | 0 | 268.075 | 0 | 1 | 9
598 | 1/25 | 21:00:00 | 282.15 | 98815 | 4.6 | 180 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
599 | 1/25 | 22:00:00 | 282.15 | 98815 | 5.7 | 180 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
600 | 1/25 | 23:00:00 | 281.15 | 98806 | 6.7 | 170 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
601 | 1/25 | 24:00:00 | 281.15 | 98806 | 5.7 | 170 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
602 | 1/26 | 01:00:00 | 280.15 | 98798 | 5.7 | 170 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
603 | 1/26 | 02:00:00 | 279.15 | 98789 | 3.6 | 250 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
604 | 1/26 | 03:00:00 | 277.15 | 98771 | 4.6 | 260 | 4.8316 | 0 | 0 | 262.405 | 0 | 1 | 4
605 | 1/26 | 04:00:00 | 277.15 | 98771 | 2.6 | 270 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
606 | 1/26 | 05:00:00 | 276.15 | 98762 | 2.1 | 210 | 4.832 | 0 | 0 | 261.459 | 0 | 1 | 3
607 | 1/26 | 06:00:00 | 276.15 | 98762 | 2.6 | 210 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
608 | 1/26 | 07:00:00 | 276.15 | 98762 | 3.1 | 230 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
609 | 1/26 | 08:00:00 | 275.15 | 98752 | 2.6 | 230 | 4.4981 | 0 | 0 | 260.03 | 0 | 1 | 2
610 | 1/26 | 09:00:00 | 275.15 | 98752 | 2.6 | 170 | 4.1846 | 61.2 | 0 | 259.802 | 0 | 1 | 2
611 | 1/26 | 10:00:00 | 274.15 | 98743 | 2.6 | 160 | 4.185 | 320.4 | 849.6 | 258.857 | 0 | 1 | 1
612 | 1/26 | 11:00:00 | 277.15 | 98771 | 3.6 | 150 | 4.4973 | 612 | 1540.8 | 261.92 | 0 | 1 | 4
613 | 1/26 | 12:00:00 | 277.15 | 98771 | 3.6 | 170 | 4.4973 | 759.6 | 1209.6 | 262.177 | 0 | 1 | 4
614 | 1/26 | 13:00:00 | 278.15 | 98780 | 5.7 | 210 | 4.4968 | 446.4 | 93.6 | 263.588 | 0 | 1 | 5
615 | 1/26 | 14:00:00 | 278.15 | 98780 | 5.7 | 220 | 4.4968 | 705.6 | 1155.6 | 263.123 | 0 | 1 | 5
616 | 1/26 | 15:00:00 | 278.15 | 98780 | 7.2 | 230 | 4.1834 | 486 | 982.8 | 262.891 | 0 | 1 | 5
617 | 1/26 | 16:00:00 | 277.15 | 98771 | 6.7 | 240 | 3.5793 | 194.4 | 244.8 | 261.481 | 0 | 1 | 4
618 | 1/26 | 17:00:00 | 277.15 | 98771 | 7.2 | 240 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
619 | 1/26 | 18:00:00 | 277.15 | 98771 | 6.7 | 240 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
620 | 1/26 | 19:00:00 | 275.15 | 98752 | 7.7 | 250 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
621 | 1/26 | 20:00:00 | 275.15 | 98752 | 4.6 | 230 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
622 | 1/26 | 21:00:00 | 275.15 | 98752 | 5.7 | 240 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
623 | 1/26 | 22:00:00 | 275.15 | 98752 | 5.1 | 240 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
624 | 1/26 | 23:00:00 | 275.15 | 98752 | 4.6 | 240 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
625 | 1/26 | 24:00:00 | 274.15 | 98743 | 1.5 | 247 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
626 | 1/27 | 01:00:00 | 275.15 | 98752 | 4.1 | 210 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
627 | 1/27 | 02:00:00 | 275.15 | 98752 | 3.6 | 220 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
628 | 1/27 | 03:00:00 | 275.15 | 98752 | 4.1 | 240 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
629 | 1/27 | 04:00:00 | 275.15 | 98752 | 5.1 | 250 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
630 | 1/27 | 05:00:00 | 275.15 | 98752 | 4.6 | 240 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
631 | 1/27 | 06:00:00 | 276.15 | 98762 | 5.1 | 260 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
632 | 1/27 | 07:00:00 | 276.15 | 98762 | 4.1 | 260 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
633 | 1/27 | 08:00:00 | 275.15 | 98752 | 5.7 | 270 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
634 | 1/27 | 09:00:00 | 275.15 | 98752 | 3.1 | 250 | 4.1846 | 64.8 | 0 | 260.056 | 0 | 1 | 2
635 | 1/27 | 10:00:00 | 276.15 | 98762 | 4.1 | 250 | 4.4977 | 313.2 | 705.6 | 261.231 | 0 | 1 | 3
636 | 1/27 | 11:00:00 | 277.15 | 98771 | 4.6 | 250 | 4.8316 | 590.4 | 1296 | 262.405 | 0 | 1 | 4
637 | 1/27 | 12:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.4968 | 770.4 | 1216.8 | 263.123 | 0 | 1 | 5
638 | 1/27 | 13:00:00 | 277.15 | 98771 | 5.7 | 250 | 4.4973 | 453.6 | 93.6 | 262.64 | 0 | 1 | 4
639 | 1/27 | 14:00:00 | 277.15 | 98771 | 5.7 | 250 | 4.1838 | 723.6 | 1353.6 | 261.946 | 0 | 1 | 4
640 | 1/27 | 15:00:00 | 274.15 | 98743 | 4.6 | 280 | 4.185 | 277.2 | 10.8 | 259.569 | 0 | 1 | 1
641 | 1/27 | 16:00:00 | 274.15 | 98743 | 2.6 | 250 | 4.185 | 205.2 | 331.2 | 259.111 | 0 | 1 | 1
642 | 1/27 | 17:00:00 | 275.15 | 98752 | 2.1 | 180 | 4.4981 | 0 | 0 | 260.745 | 0 | 1 | 2
643 | 1/27 | 18:00:00 | 274.15 | 98743 | 2.6 | 220 | 4.185 | 0 | 0 | 259.111 | 0 | 1 | 1
644 | 1/27 | 19:00:00 | 274.15 | 98743 | 1 | 260 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
645 | 1/27 | 20:00:00 | 274.15 | 98743 | 1.5 | 180 | 4.185 | 0 | 0 | 258.857 | 0 | 1 | 1
646 | 1/27 | 21:00:00 | 274.15 | 98743 | 4.1 | 360 | 4.185 | 0 | 0 | 258.857 | 0 | 1 | 1
647 | 1/27 | 22:00:00 | 275.15 | 98752 | 4.1 | 360 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
648 | 1/27 | 23:00:00 | 275.15 | 98752 | 5.1 | 350 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
649 | 1/27 | 24:00:00 | 275.15 | 98752 | 3.6 | 10 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
650 | 1/28 | 01:00:00 | 275.15 | 98752 | 5.1 | 360 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
651 | 1/28 | 02:00:00 | 274.15 | 98743 | 4.6 | 340 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
652 | 1/28 | 03:00:00 | 275.15 | 98752 | 3.6 | 320 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
653 | 1/28 | 04:00:00 | 275.15 | 98752 | 3.6 | 340 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
654 | 1/28 | 05:00:00 | 274.15 | 98743 | 2.6 | 340 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
655 | 1/28 | 06:00:00 | 273.15 | 98734 | 3.1 | 300 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0
656 | 1/28 | 07:00:00 | 274.15 | 98743 | 3.6 | 320 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
657 | 1/28 | 08:00:00 | 274.15 | 98743 | 3.6 | 340 | 3.5803 | 0 | 0 | 258.398 | 0 | 1 | 1
658 | 1/28 | 09:00:00 | 275.15 | 98752 | 3.6 | 350 | 3.5799 | 72 | 25.2 | 259.34 | 0 | 1 | 2
659 | 1/28 | 10:00:00 | 275.15 | 98752 | 3.6 | 330 | 3.5799 | 345.6 | 910.8 | 259.34 | 0 | 1 | 2
660 | 1/28 | 11:00:00 | 276.15 | 98762 | 2.6 | 310 | 4.1841 | 640.8 | 1386 | 260.746 | 0 | 1 | 3
661 | 1/28 | 12:00:00 | 276.15 | 98762 | 3.1 | 290 | 4.1841 | 835.2 | 1447.2 | 260.746 | 0 | 1 | 3
662 | 1/28 | 13:00:00 | 277.15 | 98771 | 1.5 | 164 | 4.1838 | 885.6 | 1929.6 | 261.69 | 0 | 1 | 4
663 | 1/28 | 14:00:00 | 278.15 | 98780 | 1.5 | 139 | 4.1834 | 784.8 | 1810.8 | 262.634 | 0 | 1 | 5
664 | 1/28 | 15:00:00 | 277.15 | 98771 | 1.5 | 182 | 4.1838 | 547.2 | 1227.6 | 261.69 | 0 | 1 | 4
665 | 1/28 | 16:00:00 | 278.15 | 98780 | 1 | 268 | 4.1834 | 230.4 | 529.2 | 262.634 | 0 | 1 | 5
666 | 1/28 | 17:00:00 | 277.15 | 98771 | 2.1 | 310 | 3.8896 | 3.6 | 0 | 261.458 | 0 | 1 | 4
667 | 1/28 | 18:00:00 | 275.15 | 98752 | 3.6 | 310 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
668 | 1/28 | 19:00:00 | 274.15 | 98743 | 1.5 | 300 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
669 | 1/28 | 20:00:00 | 273.15 | 98734 | 2.1 | 300 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
670 | 1/28 | 21:00:00 | 273.15 | 98734 | 2.6 | 290 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
671 | 1/28 | 22:00:00 | 272.15 | 98724 | 2.6 | 290 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
672 | 1/28 | 23:00:00 | 273.15 | 98734 | 2.1 | 290 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
673 | 1/28 | 24:00:00 | 272.15 | 98724 | 1.5 | 270 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
674 | 1/29 | 01:00:00 | 271.15 | 98715 | 2.1 | 270 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
675 | 1/29 | 02:00:00 | 272.15 | 98724 | 2.1 | 300 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
676 | 1/29 | 03:00:00 | 273.15 | 98734 | 1 | 320 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
677 | 1/29 | 04:00:00 | 273.15 | 98734 | 0.5 | 250 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
678 | 1/29 | 05:00:00 | 273.15 | 98734 | 0 | 138 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
679 | 1/29 | 06:00:00 | 272.15 | 98724 | 1 | 210 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
680 | 1/29 | 07:00:00 | 272.15 | 98724 | 1 | 190 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
681 | 1/29 | 08:00:00 | 273.15 | 98734 | 0.5 | 150 | 3.6408 | 0 | 0 | 258.314 | 0 | 1 | 0
682 | 1/29 | 09:00:00 | 273.15 | 98734 | 0.5 | 130 | 3.7329 | 25.2 | 0 | 258.383 | 0 | 1 | 0
683 | 1/29 | 10:00:00 | 274.15 | 98743 | 0.5 | 157 | 3.8267 | 176.4 | 0 | 259.293 | 0 | 1 | 1
684 | 1/29 | 11:00:00 | 274.15 | 98743 | 0 | 226 | 3.8907 | 655.2 | 1450.8 | 258.628 | 0 | 1 | 1
685 | 1/29 | 12:00:00 | 274.15 | 98743 | 0.5 | 100 | 3.8907 | 853.2 | 1886.4 | 258.628 | 0 | 1 | 1
686 | 1/29 | 13:00:00 | 275.15 | 98752 | 0.5 | 40 | 4.1846 | 903.6 | 1987.2 | 259.802 | 0 | 1 | 2
687 | 1/29 | 14:00:00 | 275.15 | 98752 | 1.5 | 40 | 4.1846 | 752.4 | 1342.8 | 260.056 | 0 | 1 | 2
688 | 1/29 | 15:00:00 | 275.15 | 98752 | 2.1 | 70 | 4.1846 | 529.2 | 1040.4 | 260.056 | 0 | 1 | 2
689 | 1/29 | 16:00:00 | 274.15 | 98743 | 2.6 | 80 | 4.185 | 230.4 | 295.2 | 259.111 | 0 | 1 | 1
690 | 1/29 | 17:00:00 | 274.15 | 98743 | 1.5 | 70 | 4.185 | 3.6 | 0 | 259.674 | 0 | 1 | 1
691 | 1/29 | 18:00:00 | 274.15 | 98743 | 2.1 | 80 | 4.185 | 0 | 0 | 259.674 | 0 | 1 | 1
692 | 1/29 | 19:00:00 | 274.15 | 98743 | 2.6 | 90 | 4.185 | 0 | 0 | 259.674 | 0 | 1 | 1
693 | 1/29 | 20:00:00 | 275.15 | 98752 | 4.1 | 120 | 4.4981 | 0 | 0 | 260.745 | 0 | 1 | 2
694 | 1/29 | 21:00:00 | 274.15 | 98743 | 4.1 | 130 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
695 | 1/29 | 22:00:00 | 274.15 | 98743 | 4.6 | 130 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
696 | 1/29 | 23:00:00 | 274.15 | 98743 | 3.1 | 150 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
697 | 1/29 | 24:00:00 | 273.15 | 98734 | 2.6 | 90 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0
698 | 1/30 | 01:00:00 | 272.15 | 98724 | 2.6 | 120 | 3.581 | 0 | 0 | 256.513 | 0 | 1 | -1
699 | 1/30 | 02:00:00 | 273.15 | 98734 | 1.5 | 100 | 3.891 | 0 | 0 | 257.685 | 0 | 1 | 0
700 | 1/30 | 03:00:00 | 273.15 | 98734 | 1.5 | 70 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0
701 | 1/30 | 04:00:00 | 273.15 | 98734 | 1.5 | 70 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
702 | 1/30 | 05:00:00 | 272.15 | 98724 | 1.5 | 196 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
703 | 1/30 | 06:00:00 | 273.15 | 98734 | 2.1 | 60 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
704 | 1/30 | 07:00:00 | 272.15 | 98724 | 2.1 | 60 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
705 | 1/30 | 08:00:00 | 272.15 | 98724 | 1.5 | 204 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
706 | 1/30 | 09:00:00 | 273.15 | 98734 | 2.6 | 60 | 3.891 | 43.2 | 0 | 258.394 | 0 | 1 | 0
707 | 1/30 | 10:00:00 | 273.15 | 98734 | 1.5 | 60 | 3.891 | 194.4 | 0 | 258.394 | 0 | 1 | 0
708 | 1/30 | 11:00:00 | 273.15 | 98734 | 2.6 | 60 | 3.891 | 352.8 | 21.6 | 258.394 | 0 | 1 | 0
709 | 1/30 | 12:00:00 | 274.15 | 98743 | 2.1 | 60 | 3.5803 | 457.2 | 75.6 | 259.108 | 0 | 1 | 1
710 | 1/30 | 13:00:00 | 274.15 | 98743 | 2.6 | 60 | 3.5803 | 482.4 | 86.4 | 259.108 | 0 | 1 | 1
711 | 1/30 | 14:00:00 | 274.15 | 98743 | 2.1 | 60 | 3.5803 | 428.4 | 46.8 | 259.108 | 0 | 1 | 1
712 | 1/30 | 15:00:00 | 275.15 | 98752 | 3.1 | 60 | 3.5799 | 579.6 | 1328.4 | 259.34 | 0 | 1 | 2
713 | 1/30 | 16:00:00 | 275.15 | 98752 | 2.6 | 60 | 3.5799 | 255.6 | 601.2 | 259.34 | 0 | 1 | 2
714 | 1/30 | 17:00:00 | 275.15 | 98752 | 2.6 | 50 | 3.5799 | 18 | 0 | 259.34 | 0 | 1 | 2
715 | 1/30 | 18:00:00 | 274.15 | 98743 | 3.1 | 30 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
716 | 1/30 | 19:00:00 | 274.15 | 98743 | 3.1 | 40 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
717 | 1/30 | 20:00:00 | 274.15 | 98743 | 2.1 | 50 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
718 | 1/30 | 21:00:00 | 273.15 | 98734 | 1.5 | 8 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0
719 | 1/30 | 22:00:00 | 273.15 | 98734 | 1 | 40 | 3.5806 | 0 | 0 | 257.707 | 0 | 1 | 0
720 | 1/30 | 23:00:00 | 273.15 | 98734 | 1.5 | 105 | 3.5806 | 0 | 0 | 257.707 | 0 | 1 | 0
721 | 1/30 | 24:00:00 | 273.15 | 98734 | 2.1 | 70 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
722 | 1/31 | 01:00:00 | 273.15 | 98734 | 3.1 | 70 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
723 | 1/31 | 02:00:00 | 273.15 | 98734 | 3.1 | 80 | 3.293 | 0 | 0 | 257.931 | 0 | 1 | 0
724 | 1/31 | 03:00:00 | 273.15 | 98734 | 3.6 | 70 | 3.293 | 0 | 0 | 257.931 | 0 | 1 | 0
725 | 1/31 | 04:00:00 | 273.15 | 98734 | 3.1 | 80 | 3.293 | 0 | 0 | 257.931 | 0 | 1 | 0
726 | 1/31 | 05:00:00 | 272.15 | 98724 | 2.6 | 80 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
727 | 1/31 | 06:00:00 | 272.15 | 98724 | 2.6 | 70 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
728 | 1/31 | 07:00:00 | 272.15 | 98724 | 3.1 | 70 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
729 | 1/31 | 08:00:00 | 272.15 | 98724 | 3.1 | 70 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
730 | 1/31 | 09:00:00 | 272.15 | 98724 | 2.6 | 70 | 3.581 | 82.8 | 54 | 256.764 | 0 | 1 | -1
731 | 1/31 | 10:00:00 | 273.15 | 98734 | 3.1 | 70 | 3.891 | 360 | 810 | 257.937 | 0 | 1 | 0
732 | 1/31 | 11:00:00 | 273.15 | 98734 | 4.6 | 80 | 3.5806 | 648 | 1252.8 | 257.707 | 0 | 1 | 0
733 | 1/31 | 12:00:00 | 273.15 | 98734 | 4.6 | 80 | 3.5806 | 464.4 | 54 | 258.163 | 0 | 1 | 0
734 | 1/31 | 13:00:00 | 274.15 | 98743 | 5.7 | 80 | 3.2927 | 889.2 | 1076.4 | 258.419 | 0 | 1 | 1
735 | 1/31 | 14:00:00 | 274.15 | 98743 | 7.2 | 90 | 3.2927 | 439.2 | 46.8 | 258.876 | 0 | 1 | 1
736 | 1/31 | 15:00:00 | 273.15 | 98734 | 5.1 | 90 | 3.0267 | 313.2 | 14.4 | 257.698 | 0 | 1 | 0
737 | 1/31 | 16:00:00 | 273.15 | 98734 | 5.1 | 80 | 3.5806 | 140.4 | 0 | 258.163 | 0 | 1 | 0
738 | 1/31 | 17:00:00 | 273.15 | 98734 | 5.7 | 80 | 3.5806 | 10.8 | 0 | 258.163 | 0 | 1 | 0
739 | 1/31 | 18:00:00 | 273.15 | 98734 | 5.1 | 70 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
740 | 1/31 | 19:00:00 | 272.95 | 98732 | 4.1 | 65 | 3.8271 | 0 | 0 | 257.703 | 0 | 1 | -0.2
741 | 1/31 | 20:00:00 | 272.95 | 98732 | 4 | 67 | 3.8271 | 0 | 0 | 258.158 | 0 | 1 | -0.2
742 | 1/31 | 21:00:00 | 272.95 | 98732 | 4.1 | 70 | 3.8271 | 0 | 0 | 258.158 | 0 | 1 | -0.2
743 | 1/31 | 22:00:00 | 273.15 | 98734 | 6 | 127 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
744 | 1/31 | 23:00:00 | 273.35 | 98736 | 7.8 | 185 | 3.9486 | 0 | 0 | 258.172 | 0 | 1 | 0.2
745 | 1/31 | 24:00:00 | 273.95 | 98741 | 9.8 | 242 | 4.1247 | 0 | 0 | 259.334 | 0 | 1 | 0.8
746 | 2/1 | 01:00:00 | 274.15 | 98743 | 11.4 | 302 | 4.185 | 0 | 0 | 258.857 | 0 | 1 | 1
747 | 2/1 | 02:00:00 | 274.15 | 98743 | 11.1 | 302 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
748 | 2/1 | 03:00:00 | 274.15 | 98743 | 10.7 | 305 | 3.6405 | 0 | 0 | 258.697 | 0 | 1 | 1
749 | 2/1 | 04:00:00 | 274.15 | 98743 | 9.9 | 307 | 3.4337 | 0 | 0 | 258.992 | 0 | 1 | 1
750 | 2/1 | 05:00:00 | 274.15 | 98743 | 8.9 | 307 | 3.2927 | 0 | 0 | 258.876 | 0 | 1 | 1
751 | 2/1 | 06:00:00 | 274.15 | 98743 | 8.6 | 315 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
752 | 2/1 | 07:00:00 | 274.15 | 98743 | 7.7 | 310 | 3.2927 | 0 | 0 | 258.876 | 0 | 1 | 1
753 | 2/1 | 08:00:00 | 274.15 | 98743 | 7.2 | 310 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
754 | 2/1 | 09:00:00 | 274.15 | 98743 | 9.3 | 330 | 4.185 | 50.4 | 0 | 259.569 | 0 | 1 | 1
755 | 2/1 | 10:00:00 | 274.15 | 98743 | 9.3 | 330 | 3.2927 | 374.4 | 774 | 258.419 | 0 | 1 | 1
756 | 2/1 | 11:00:00 | 275.15 | 98752 | 6.7 | 310 | 4.1846 | 662.4 | 1396.8 | 260.056 | 0 | 1 | 2
757 | 2/1 | 12:00:00 | 274.15 | 98743 | 8.2 | 320 | 3.2927 | 856.8 | 1281.6 | 258.419 | 0 | 1 | 1
758 | 2/1 | 13:00:00 | 275.15 | 98752 | 9.3 | 320 | 3.0262 | 907.2 | 1335.6 | 259.127 | 0 | 1 | 2
759 | 2/1 | 14:00:00 | 275.15 | 98752 | 7.2 | 330 | 3.5799 | 806.4 | 1231.2 | 259.594 | 0 | 1 | 2
760 | 2/1 | 15:00:00 | 275.15 | 98752 | 7.7 | 330 | 4.4981 | 608.4 | 1515.6 | 260.03 | 0 | 1 | 2
761 | 2/1 | 16:00:00 | 274.15 | 98743 | 7.7 | 320 | 4.185 | 284.4 | 730.8 | 258.857 | 0 | 1 | 1
762 | 2/1 | 17:00:00 | 273.15 | 98734 | 7.2 | 320 | 3.891 | 32.4 | 0 | 257.685 | 0 | 1 | 0
763 | 2/1 | 18:00:00 | 272.15 | 98724 | 4.6 | 300 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
764 | 2/1 | 19:00:00 | 272.15 | 98724 | 5.7 | 290 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
765 | 2/1 | 20:00:00 | 272.15 | 98724 | 6.7 | 300 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
766 | 2/1 | 21:00:00 | 271.15 | 98715 | 6.7 | 310 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
767 | 2/1 | 22:00:00 | 271.15 | 98715 | 5.7 | 300 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
768 | 2/1 | 23:00:00 | 271.15 | 98715 | 6.7 | 310 | 3.2936 | 0 | 0 | 255.341 | 0 | 1 | -2
769 | 2/1 | 24:00:00 | 271.15 | 98715 | 6.7 | 300 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
770 | 2/2 | 01:00:00 | 270.15 | 98705 | 6.2 | 310 | 3.0276 | 0 | 0 | 254.971 | 0 | 1 | -3
771 | 2/2 | 02:00:00 | 271.15 | 98715 | 6.7 | 310 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
772 | 2/2 | 03:00:00 | 270.15 | 98705 | 4.1 | 260 | 2.7812 | 0 | 0 | 254.636 | 0 | 1 | -3
773 | 2/2 | 04:00:00 | 270.15 | 98705 | 5.1 | 300 | 3.0276 | 0 | 0 | 254.971 | 0 | 1 | -3
774 | 2/2 | 05:00:00 | 271.15 | 98715 | 6.2 | 300 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
775 | 2/2 | 06:00:00 | 271.15 | 98715 | 5.7 | 310 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
776 | 2/2 | 07:00:00 | 270.15 | 98705 | 4.6 | 300 | 3.0276 | 0 | 0 | 254.971 | 0 | 1 | -3
777 | 2/2 | 08:00:00 | 271.15 | 98715 | 5.1 | 300 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
778 | 2/2 | 09:00:00 | 271.15 | 98715 | 5.7 | 310 | 3.2936 | 32.4 | 0 | 256.147 | 0 | 1 | -2
779 | 2/2 | 10:00:00 | 272.15 | 98724 | 4.6 | 300 | 3.581 | 129.6 | 0 | 257.322 | 0 | 1 | -1
780 | 2/2 | 11:00:00 | 272.15 | 98724 | 5.7 | 310 | 3.0271 | 475.2 | 280.8 | 256.647 | 0 | 1 | -1
781 | 2/2 | 12:00:00 | 273.15 | 98734 | 4.1 | 310 | 3.891 | 925.2 | 1692 | 257.685 | 0 | 1 | 0
782 | 2/2 | 13:00:00 | 274.15 | 98743 | 5.1 | 330 | 4.185 | 975.6 | 2034 | 258.857 | 0 | 1 | 1
783 | 2/2 | 14:00:00 | 274.15 | 98743 | 4.1 | 330 | 4.185 | 871.2 | 1378.8 | 258.857 | 0 | 1 | 1
784 | 2/2 | 15:00:00 | 274.15 | 98743 | 5.1 | 310 | 4.185 | 201.6 | 0 | 259.674 | 0 | 1 | 1
785 | 2/2 | 16:00:00 | 274.15 | 98743 | 5.1 | 310 | 4.185 | 298.8 | 172.8 | 258.857 | 0 | 1 | 1
786 | 2/2 | 17:00:00 | 273.15 | 98734 | 5.1 | 320 | 3.891 | 36 | 0 | 257.685 | 0 | 1 | 0
787 | 2/2 | 18:00:00 | 273.15 | 98734 | 6.2 | 320 | 3.891 | 0 | 0 | 257.685 | 0 | 1 | 0
788 | 2/2 | 19:00:00 | 273.15 | 98734 | 5.1 | 310 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
789 | 2/2 | 20:00:00 | 273.15 | 98734 | 4.6 | 310 | 3.891 | 0 | 0 | 257.685 | 0 | 1 | 0
790 | 2/2 | 21:00:00 | 273.15 | 98734 | 4.6 | 320 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
791 | 2/2 | 22:00:00 | 272.15 | 98724 | 3.6 | 320 | 3.581 | 0 | 0 | 256.513 | 0 | 1 | -1
792 | 2/2 | 23:00:00 | 272.15 | 98724 | 4.1 | 320 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
793 | 2/2 | 24:00:00 | 273.15 | 98734 | 5.7 | 350 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
794 | 2/3 | 01:00:00 | 273.15 | 98734 | 5.7 | 340 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
795 | 2/3 | 02:00:00 | 272.15 | 98724 | 4.6 | 320 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
796 | 2/3 | 03:00:00 | 272.15 | 98724 | 4.6 | 310 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
797 | 2/3 | 04:00:00 | 272.15 | 98724 | 4.6 | 320 | 3.581 | 0 | 0 | 256.513 | 0 | 1 | -1
798 | 2/3 | 05:00:00 | 272.15 | 98724 | 4.1 | 330 | 3.581 | 0 | 0 | 256.513 | 0 | 1 | -1
799 | 2/3 | 06:00:00 | 272.15 | 98724 | 4.1 | 350 | 3.581 | 0 | 0 | 256.513 | 0 | 1 | -1
800 | 2/3 | 07:00:00 | 273.15 | 98734 | 4.6 | 360 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0
801 | 2/3 | 08:00:00 | 273.15 | 98734 | 4.6 | 350 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0
802 | 2/3 | 09:00:00 | 273.15 | 98734 | 4.1 | 340 | 3.891 | 100.8 | 79.2 | 257.937 | 0 | 1 | 0
803 | 2/3 | 10:00:00 | 274.15 | 98743 | 4.6 | 350 | 4.185 | 396 | 806.4 | 259.111 | 0 | 1 | 1
804 | 2/3 | 11:00:00 | 274.15 | 98743 | 4.1 | 350 | 4.185 | 694.8 | 1260 | 259.111 | 0 | 1 | 1
805 | 2/3 | 12:00:00 | 275.15 | 98752 | 4.1 | 350 | 4.4981 | 939.6 | 1954.8 | 260.03 | 0 | 1 | 2
806 | 2/3 | 13:00:00 | 276.15 | 98762 | 3.6 | 360 | 3.2921 | 925.2 | 1465.2 | 260.304 | 0 | 1 | 3
807 | 2/3 | 14:00:00 | 277.15 | 98771 | 3.1 | 360 | 3.0256 | 882 | 1886.4 | 260.885 | 0 | 1 | 4
808 | 2/3 | 15:00:00 | 276.15 | 98762 | 4.1 | 340 | 2.7796 | 651.6 | 1404 | 259.577 | 0 | 1 | 3
809 | 2/3 | 16:00:00 | 275.15 | 98752 | 5.1 | 340 | 3.2924 | 313.2 | 813.6 | 259.107 | 0 | 1 | 2
810 | 2/3 | 17:00:00 | 275.15 | 98752 | 4.6 | 350 | 3.2924 | 21.6 | 0 | 259.82 | 0 | 1 | 2
811 | 2/3 | 18:00:00 | 275.15 | 98752 | 3.1 | 350 | 3.2924 | 0 | 0 | 259.82 | 0 | 1 | 2
812 | 2/3 | 19:00:00 | 274.15 | 98743 | 3.6 | 330 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
813 | 2/3 | 20:00:00 | 274.15 | 98743 | 4.6 | 340 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
814 | 2/3 | 21:00:00 | 274.15 | 98743 | 5.7 | 360 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
815 | 2/3 | 22:00:00 | 274.15 | 98743 | 5.7 | 350 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
816 | 2/3 | 23:00:00 | 274.15 | 98743 | 3.6 | 360 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
817 | 2/3 | 24:00:00 | 274.15 | 98743 | 4.6 | 350 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
818 | 2/4 | 01:00:00 | 274.15 | 98743 | 5.1 | 350 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
819 | 2/4 | 02:00:00 | 273.15 | 98734 | 6.2 | 350 | 3.5806 | 0 | 0 | 257.707 | 0 | 1 | 0
820 | 2/4 | 03:00:00 | 273.15 | 98734 | 5.1 | 360 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0
821 | 2/4 | 04:00:00 | 274.15 | 98743 | 6.2 | 350 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
822 | 2/4 | 05:00:00 | 273.15 | 98734 | 6.2 | 360 | 3.0267 | 0 | 0 | 256.991 | 0 | 1 | 0
823 | 2/4 | 06:00:00 | 273.15 | 98734 | 5.1 | 330 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
824 | 2/4 | 07:00:00 | 273.15 | 98734 | 6.7 | 340 | 3.293 | 0 | 0 | 257.224 | 0 | 1 | 0
825 | 2/4 | 08:00:00 | 273.15 | 98734 | 7.2 | 340 | 3.5806 | 0 | 0 | 257.455 | 0 | 1 | 0
826 | 2/4 | 09:00:00 | 273.15 | 98734 | 5.7 | 330 | 3.891 | 108 | 86.4 | 257.937 | 0 | 1 | 0
827 | 2/4 | 10:00:00 | 274.15 | 98743 | 7.2 | 350 | 3.2927 | 439.2 | 1022.4 | 258.166 | 0 | 1 | 1
828 | 2/4 | 11:00:00 | 275.15 | 98752 | 7.7 | 350 | 3.5799 | 756 | 1760.4 | 259.34 | 0 | 1 | 2
829 | 2/4 | 12:00:00 | 276.15 | 98762 | 5.1 | 340 | 3.0259 | 910.8 | 1332 | 260.068 | 0 | 1 | 3
830 | 2/4 | 13:00:00 | 275.15 | 98752 | 4.6 | 340 | 3.0262 | 961.2 | 1375.2 | 259.127 | 0 | 1 | 2
831 | 2/4 | 14:00:00 | 276.15 | 98762 | 4.1 | 350 | 3.5796 | 860.4 | 1666.8 | 260.538 | 0 | 1 | 3
832 | 2/4 | 15:00:00 | 276.15 | 98762 | 4.1 | 330 | 3.5796 | 626.4 | 1180.8 | 260.538 | 0 | 1 | 3
833 | 2/4 | 16:00:00 | 276.15 | 98762 | 3.6 | 350 | 3.5796 | 309.6 | 694.8 | 260.538 | 0 | 1 | 3
834 | 2/4 | 17:00:00 | 275.15 | 98752 | 4.1 | 340 | 3.5799 | 50.4 | 0 | 259.34 | 0 | 1 | 2
835 | 2/4 | 18:00:00 | 275.15 | 98752 | 3.6 | 340 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
836 | 2/4 | 19:00:00 | 275.15 | 98752 | 5.1 | 360 | 3.5799 | 0 | 0 | 259.34 | 0 | 1 | 2
837 | 2/4 | 20:00:00 | 275.15 | 98752 | 4.1 | 360 | 3.5799 | 0 | 0 | 259.34 | 0 | 1 | 2
838 | 2/4 | 21:00:00 | 275.15 | 98752 | 4.6 | 350 | 3.2924 | 0 | 0 | 259.107 | 0 | 1 | 2
839 | 2/4 | 22:00:00 | 275.15 | 98752 | 5.1 | 350 | 3.2924 | 0 | 0 | 259.107 | 0 | 1 | 2
840 | 2/4 | 23:00:00 | 274.15 | 98743 | 4.1 | 300 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
841 | 2/4 | 24:00:00 | 274.15 | 98743 | 4.6 | 300 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
842 | 2/5 | 01:00:00 | 274.15 | 98743 | 5.1 | 310 | 3.0265 | 0 | 0 | 258.305 | 0 | 1 | 1
843 | 2/5 | 02:00:00 | 274.15 | 98743 | 6.2 | 320 | 3.0265 | 0 | 0 | 258.305 | 0 | 1 | 1
844 | 2/5 | 03:00:00 | 274.15 | 98743 | 5.7 | 310 | 3.0265 | 0 | 0 | 258.305 | 0 | 1 | 1
845 | 2/5 | 04:00:00 | 274.15 | 98743 | 4.1 | 320 | 3.0265 | 0 | 0 | 258.305 | 0 | 1 | 1
846 | 2/5 | 05:00:00 | 274.15 | 98743 | 4.6 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
847 | 2/5 | 06:00:00 | 275.15 | 98752 | 4.6 | 310 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
848 | 2/5 | 07:00:00 | 275.15 | 98752 | 5.1 | 310 | 3.2924 | 0 | 0 | 259.361 | 0 | 1 | 2
849 | 2/5 | 08:00:00 | 275.15 | 98752 | 5.7 | 340 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
850 | 2/5 | 09:00:00 | 276.15 | 98762 | 6.2 | 360 | 3.8899 | 111.6 | 86.4 | 260.77 | 0 | 1 | 3
851 | 2/5 | 10:00:00 | 276.15 | 98762 | 4.1 | 360 | 4.1841 | 424.8 | 853.2 | 261.001 | 0 | 1 | 3
852 | 2/5 | 11:00:00 | 277.15 | 98771 | 4.1 | 10 | 4.1838 | 727.2 | 1476 | 261.946 | 0 | 1 | 4
853 | 2/5 | 12:00:00 | 277.15 | 98771 | 5.1 | 10 | 4.4973 | 921.6 | 1335.6 | 262.177 | 0 | 1 | 4
854 | 2/5 | 13:00:00 | 278.15 | 98780 | 5.7 | 10 | 4.4968 | 540 | 90 | 263.588 | 0 | 1 | 5
855 | 2/5 | 14:00:00 | 278.15 | 98780 | 6.2 | 10 | 4.8311 | 482.4 | 68.4 | 263.818 | 0 | 1 | 5
856 | 2/5 | 15:00:00 | 278.15 | 98780 | 4.6 | 30 | 4.8311 | 356.4 | 21.6 | 263.818 | 0 | 1 | 5
857 | 2/5 | 16:00:00 | 276.15 | 98762 | 2.6 | 80 | 4.832 | 176.4 | 0 | 261.921 | 0 | 1 | 3
858 | 2/5 | 17:00:00 | 275.15 | 98752 | 2.6 | 90 | 4.4981 | 28.8 | 0 | 260.745 | 0 | 1 | 2
859 | 2/5 | 18:00:00 | 275.15 | 98752 | 2.6 | 90 | 4.4981 | 0 | 0 | 260.745 | 0 | 1 | 2
860 | 2/5 | 19:00:00 | 274.15 | 98743 | 1.5 | 155 | 4.185 | 0 | 0 | 259.111 | 0 | 1 | 1
861 | 2/5 | 20:00:00 | 274.15 | 98743 | 2.1 | 40 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
862 | 2/5 | 21:00:00 | 274.15 | 98743 | 2.1 | 70 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
863 | 2/5 | 22:00:00 | 274.15 | 98743 | 1.5 | 216 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
864 | 2/5 | 23:00:00 | 274.15 | 98743 | 1 | 124 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
865 | 2/5 | 24:00:00 | 274.15 | 98743 | 1.5 | 40 | 4.185 | 0 | 0 | 259.111 | 0 | 1 | 1
866 | 2/6 | 01:00:00 | 273.15 | 98734 | 2.1 | 30 | 3.891 | 0 | 0 | 257.685 | 0 | 1 | 0
867 | 2/6 | 02:00:00 | 273.15 | 98734 | 1 | 20 | 3.891 | 0 | 0 | 257.685 | 0 | 1 | 0
868 | 2/6 | 03:00:00 | 273.15 | 98734 | 1.5 | 59 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
869 | 2/6 | 04:00:00 | 272.15 | 98724 | 1 | 30 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
870 | 2/6 | 05:00:00 | 272.15 | 98724 | 1.5 | 10 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
871 | 2/6 | 06:00:00 | 272.15 | 98724 | 2.1 | 350 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
872 | 2/6 | 07:00:00 | 273.15 | 98734 | 2.6 | 360 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
873 | 2/6 | 08:00:00 | 272.15 | 98724 | 2.1 | 360 | 3.581 | 0 | 0 | 256.764 | 0 | 1 | -1
874 | 2/6 | 09:00:00 | 273.15 | 98734 | 2.1 | 20 | 3.891 | 118.8 | 115.2 | 257.937 | 0 | 1 | 0
875 | 2/6 | 10:00:00 | 273.15 | 98734 | 2.1 | 10 | 3.891 | 468 | 1065.6 | 257.685 | 0 | 1 | 0
876 | 2/6 | 11:00:00 | 274.15 | 98743 | 1.5 | 156 | 4.185 | 788.4 | 1616.4 | 258.857 | 0 | 1 | 1
877 | 2/6 | 12:00:00 | 276.15 | 98762 | 1.5 | 26 | 4.1841 | 604.8 | 252 | 261.463 | 0 | 1 | 3
878 | 2/6 | 13:00:00 | 276.15 | 98762 | 2.6 | 40 | 4.1841 | 993.6 | 1461.6 | 261.001 | 0 | 1 | 3
879 | 2/6 | 14:00:00 | 277.15 | 98771 | 1.5 | 299 | 4.1838 | 892.8 | 1684.8 | 261.946 | 0 | 1 | 4
880 | 2/6 | 15:00:00 | 276.15 | 98762 | 2.6 | 40 | 4.1841 | 658.8 | 1209.6 | 261.001 | 0 | 1 | 3
881 | 2/6 | 16:00:00 | 277.15 | 98771 | 2.6 | 70 | 4.1838 | 334.8 | 745.2 | 261.946 | 0 | 1 | 4
882 | 2/6 | 17:00:00 | 276.15 | 98762 | 1 | 32 | 4.1841 | 64.8 | 0 | 260.746 | 0 | 1 | 3
883 | 2/6 | 18:00:00 | 275.15 | 98752 | 1.5 | 360 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
884 | 2/6 | 19:00:00 | 275.15 | 98752 | 2.1 | 360 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
885 | 2/6 | 20:00:00 | 275.15 | 98752 | 2.1 | 360 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
886 | 2/6 | 21:00:00 | 276.15 | 98762 | 1.5 | 360 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
887 | 2/6 | 22:00:00 | 276.15 | 98762 | 2.6 | 360 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
888 | 2/6 | 23:00:00 | 276.15 | 98762 | 2.6 | 360 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
889 | 2/6 | 24:00:00 | 276.15 | 98762 | 2.1 | 350 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
890 | 2/7 | 01:00:00 | 276.15 | 98762 | 2.1 | 360 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
891 | 2/7 | 02:00:00 | 276.15 | 98762 | 2.1 | 360 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
892 | 2/7 | 03:00:00 | 276.15 | 98762 | 1.5 | 350 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
893 | 2/7 | 04:00:00 | 276.15 | 98762 | 2.1 | 340 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
894 | 2/7 | 05:00:00 | 275.15 | 98752 | 3.1 | 350 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
895 | 2/7 | 06:00:00 | 274.15 | 98743 | 3.6 | 320 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
896 | 2/7 | 07:00:00 | 275.15 | 98752 | 1 | 340 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
897 | 2/7 | 08:00:00 | 274.15 | 98743 | 2.6 | 300 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
898 | 2/7 | 09:00:00 | 275.15 | 98752 | 2.1 | 290 | 4.1846 | 68.4 | 0 | 260.516 | 0 | 1 | 2
899 | 2/7 | 10:00:00 | 275.15 | 98752 | 2.6 | 310 | 4.1846 | 252 | 0 | 260.516 | 0 | 1 | 2
900 | 2/7 | 11:00:00 | 276.15 | 98762 | 2.6 | 330 | 4.4977 | 421.2 | 36 | 261.693 | 0 | 1 | 3
901 | 2/7 | 12:00:00 | 276.15 | 98762 | 3.1 | 350 | 4.4977 | 532.8 | 79.2 | 261.693 | 0 | 1 | 3
902 | 2/7 | 13:00:00 | 277.15 | 98771 | 2.1 | 350 | 4.4973 | 561.6 | 118.8 | 262.64 | 0 | 1 | 4
903 | 2/7 | 14:00:00 | 278.15 | 98780 | 1.5 | 54 | 4.8311 | 504 | 108 | 263.818 | 0 | 1 | 5
904 | 2/7 | 15:00:00 | 279.15 | 98789 | 2.6 | 270 | 4.8307 | 716.4 | 1191.6 | 264.041 | 0 | 1 | 6
905 | 2/7 | 16:00:00 | 278.15 | 98780 | 4.1 | 280 | 4.8311 | 226.8 | 86.4 | 263.818 | 0 | 1 | 5
906 | 2/7 | 17:00:00 | 277.15 | 98771 | 4.1 | 280 | 4.8316 | 32.4 | 0 | 262.976 | 0 | 1 | 4
907 | 2/7 | 18:00:00 | 276.15 | 98762 | 3.6 | 290 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
908 | 2/7 | 19:00:00 | 277.15 | 98771 | 5.1 | 310 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
909 | 2/7 | 20:00:00 | 278.15 | 98780 | 3.6 | 10 | 4.1834 | 0 | 0 | 263.132 | 0 | 1 | 5
910 | 2/7 | 21:00:00 | 277.15 | 98771 | 3.6 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
911 | 2/7 | 22:00:00 | 277.15 | 98771 | 4.6 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
912 | 2/7 | 23:00:00 | 277.15 | 98771 | 6.2 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
913 | 2/7 | 24:00:00 | 277.15 | 98771 | 6.2 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
914 | 2/8 | 01:00:00 | 277.15 | 98771 | 5.1 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
915 | 2/8 | 02:00:00 | 277.15 | 98771 | 4.6 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
916 | 2/8 | 03:00:00 | 275.15 | 98752 | 3.6 | 310 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
917 | 2/8 | 04:00:00 | 276.15 | 98762 | 4.6 | 330 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
918 | 2/8 | 05:00:00 | 276.15 | 98762 | 3.1 | 330 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
919 | 2/8 | 06:00:00 | 273.15 | 98734 | 3.1 | 270 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
920 | 2/8 | 07:00:00 | 273.15 | 98734 | 4.1 | 280 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
921 | 2/8 | 08:00:00 | 272.15 | 98724 | 3.1 | 270 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
922 | 2/8 | 09:00:00 | 272.15 | 98724 | 3.6 | 290 | 3.2934 | 64.8 | 0 | 256.987 | 0 | 1 | -1
923 | 2/8 | 10:00:00 | 274.15 | 98743 | 2.6 | 270 | 3.8907 | 212.4 | 0 | 259.445 | 0 | 1 | 1
924 | 2/8 | 11:00:00 | 275.15 | 98752 | 4.6 | 260 | 3.8903 | 504 | 208.8 | 260.286 | 0 | 1 | 2
925 | 2/8 | 12:00:00 | 278.15 | 98780 | 5.7 | 270 | 4.1834 | 878.4 | 1022.4 | 263.132 | 0 | 1 | 5
926 | 2/8 | 13:00:00 | 278.15 | 98780 | 7.2 | 280 | 4.1834 | 1094.4 | 2077.2 | 262.634 | 0 | 1 | 5
927 | 2/8 | 14:00:00 | 277.15 | 98771 | 7.7 | 270 | 4.1838 | 990 | 2066.4 | 261.69 | 0 | 1 | 4
928 | 2/8 | 15:00:00 | 277.15 | 98771 | 6.7 | 260 | 4.4973 | 734.4 | 1324.8 | 261.92 | 0 | 1 | 4
929 | 2/8 | 16:00:00 | 276.15 | 98762 | 7.2 | 260 | 4.4977 | 201.6 | 0 | 261.693 | 0 | 1 | 3
930 | 2/8 | 17:00:00 | 275.15 | 98752 | 11.3 | 280 | 4.4981 | 75.6 | 86.4 | 260.285 | 0 | 1 | 2
931 | 2/8 | 18:00:00 | 275.15 | 98752 | 10.3 | 270 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
932 | 2/8 | 19:00:00 | 275.15 | 98752 | 6.2 | 280 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
933 | 2/8 | 20:00:00 | 276.15 | 98762 | 8.8 | 280 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
934 | 2/8 | 21:00:00 | 277.15 | 98771 | 8.2 | 270 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
935 | 2/8 | 22:00:00 | 277.15 | 98771 | 8.8 | 280 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
936 | 2/8 | 23:00:00 | 277.15 | 98771 | 8.2 | 280 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
937 | 2/8 | 24:00:00 | 277.15 | 98771 | 6.7 | 270 | 4.8316 | 0 | 0 | 262.405 | 0 | 1 | 4
938 | 2/9 | 01:00:00 | 276.15 | 98762 | 7.2 | 270 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
939 | 2/9 | 02:00:00 | 276.15 | 98762 | 7.2 | 280 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
940 | 2/9 | 03:00:00 | 276.15 | 98762 | 7.2 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
941 | 2/9 | 04:00:00 | 276.15 | 98762 | 7.7 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
942 | 2/9 | 05:00:00 | 276.15 | 98762 | 11.3 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
943 | 2/9 | 06:00:00 | 276.15 | 98762 | 9.3 | 280 | 4.832 | 0 | 0 | 261.203 | 0 | 1 | 3
944 | 2/9 | 07:00:00 | 276.15 | 98762 | 10.3 | 280 | 4.832 | 0 | 0 | 261.459 | 0 | 1 | 3
945 | 2/9 | 08:00:00 | 276.15 | 98762 | 11.3 | 280 | 4.832 | 0 | 0 | 261.203 | 0 | 1 | 3
946 | 2/9 | 09:00:00 | 277.15 | 98771 | 5.1 | 280 | 4.8316 | 154.8 | 241.2 | 262.149 | 0 | 1 | 4
947 | 2/9 | 10:00:00 | 277.15 | 98771 | 7.2 | 270 | 4.8316 | 514.8 | 1263.6 | 262.149 | 0 | 1 | 4
948 | 2/9 | 11:00:00 | 278.15 | 98780 | 5.1 | 280 | 5.1875 | 842.4 | 1825.2 | 263.323 | 0 | 1 | 5
949 | 2/9 | 12:00:00 | 279.15 | 98789 | 5.1 | 280 | 5.187 | 1054.8 | 2080.8 | 264.269 | 0 | 1 | 6
950 | 2/9 | 13:00:00 | 280.15 | 98798 | 6.7 | 280 | 5.1865 | 1108.8 | 2145.6 | 265.216 | 0 | 1 | 7
951 | 2/9 | 14:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.5656 | 1004.4 | 2059.2 | 266.392 | 0 | 1 | 8
952 | 2/9 | 15:00:00 | 281.15 | 98806 | 7.7 | 270 | 5.5656 | 752.4 | 1713.6 | 266.392 | 0 | 1 | 8
953 | 2/9 | 16:00:00 | 280.15 | 98798 | 6.7 | 290 | 5.5661 | 403.2 | 1047.6 | 265.444 | 0 | 1 | 7
954 | 2/9 | 17:00:00 | 279.15 | 98789 | 6.2 | 270 | 5.187 | 86.4 | 147.6 | 264.269 | 0 | 1 | 6
955 | 2/9 | 18:00:00 | 277.15 | 98771 | 6.7 | 290 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
956 | 2/9 | 19:00:00 | 276.15 | 98762 | 5.7 | 280 | 4.832 | 0 | 0 | 261.203 | 0 | 1 | 3
957 | 2/9 | 20:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.832 | 0 | 0 | 261.203 | 0 | 1 | 3
958 | 2/9 | 21:00:00 | 276.15 | 98762 | 5.1 | 270 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
959 | 2/9 | 22:00:00 | 275.15 | 98752 | 5.7 | 280 | 4.4981 | 0 | 0 | 259.615 | 0 | 1 | 2
960 | 2/9 | 23:00:00 | 274.15 | 98743 | 5.1 | 280 | 4.185 | 0 | 0 | 259.674 | 0 | 1 | 1
961 | 2/9 | 24:00:00 | 275.15 | 98752 | 5.1 | 270 | 4.4981 | 0 | 0 | 260.745 | 0 | 1 | 2
962 | 2/10 | 01:00:00 | 275.15 | 98752 | 4.1 | 290 | 4.4981 | 0 | 0 | 260.745 | 0 | 1 | 2
963 | 2/10 | 02:00:00 | 276.15 | 98762 | 6.7 | 280 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
964 | 2/10 | 03:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
965 | 2/10 | 04:00:00 | 276.15 | 98762 | 6.2 | 270 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
966 | 2/10 | 05:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
967 | 2/10 | 06:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
968 | 2/10 | 07:00:00 | 275.15 | 98752 | 3.1 | 280 | 4.4981 | 0 | 0 | 260.03 | 0 | 1 | 2
969 | 2/10 | 08:00:00 | 275.15 | 98752 | 0.5 | 226 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
970 | 2/10 | 09:00:00 | 275.15 | 98752 | 1.5 | 352 | 4.4981 | 86.4 | 0 | 260.745 | 0 | 1 | 2
971 | 2/10 | 10:00:00 | 276.15 | 98762 | 3.1 | 280 | 4.832 | 277.2 | 7.2 | 261.921 | 0 | 1 | 3
972 | 2/10 | 11:00:00 | 276.15 | 98762 | 3.1 | 270 | 4.832 | 450 | 39.6 | 261.921 | 0 | 1 | 3
973 | 2/10 | 12:00:00 | 276.15 | 98762 | 3.1 | 260 | 4.832 | 561.6 | 115.2 | 261.921 | 0 | 1 | 3
974 | 2/10 | 13:00:00 | 277.15 | 98771 | 3.6 | 260 | 5.1879 | 590.4 | 118.8 | 263.098 | 0 | 1 | 4
975 | 2/10 | 14:00:00 | 278.15 | 98780 | 4.1 | 260 | 5.1875 | 964.8 | 1353.6 | 263.581 | 0 | 1 | 5
976 | 2/10 | 15:00:00 | 278.15 | 98780 | 4.6 | 270 | 5.1875 | 727.2 | 1458 | 263.581 | 0 | 1 | 5
977 | 2/10 | 16:00:00 | 277.15 | 98771 | 4.1 | 250 | 4.8316 | 396 | 896.4 | 262.405 | 0 | 1 | 4
978 | 2/10 | 17:00:00 | 277.15 | 98771 | 4.1 | 270 | 4.8316 | 86.4 | 72 | 262.405 | 0 | 1 | 4
979 | 2/10 | 18:00:00 | 276.15 | 98762 | 3.6 | 270 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
980 | 2/10 | 19:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
981 | 2/10 | 20:00:00 | 275.15 | 98752 | 5.1 | 280 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
982 | 2/10 | 21:00:00 | 274.15 | 98743 | 2.1 | 260 | 4.185 | 0 | 0 | 259.111 | 0 | 1 | 1
983 | 2/10 | 22:00:00 | 274.15 | 98743 | 2.6 | 270 | 4.185 | 0 | 0 | 259.111 | 0 | 1 | 1
984 | 2/10 | 23:00:00 | 274.15 | 98743 | 2.1 | 240 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
985 | 2/10 | 24:00:00 | 274.15 | 98743 | 2.6 | 240 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
986 | 2/11 | 01:00:00 | 273.15 | 98734 | 2.1 | 240 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
987 | 2/11 | 02:00:00 | 273.15 | 98734 | 2.1 | 230 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
988 | 2/11 | 03:00:00 | 273.15 | 98734 | 2.6 | 240 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
989 | 2/11 | 04:00:00 | 274.15 | 98743 | 2.6 | 230 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
990 | 2/11 | 05:00:00 | 274.15 | 98743 | 2.6 | 210 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
991 | 2/11 | 06:00:00 | 274.15 | 98743 | 3.6 | 220 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
992 | 2/11 | 07:00:00 | 274.15 | 98743 | 2.1 | 210 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
993 | 2/11 | 08:00:00 | 274.15 | 98743 | 4.1 | 220 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
994 | 2/11 | 09:00:00 | 274.15 | 98743 | 4.6 | 230 | 3.8907 | 93.6 | 0 | 259.34 | 0 | 1 | 1
995 | 2/11 | 10:00:00 | 275.15 | 98752 | 3.6 | 230 | 3.8903 | 288 | 3.6 | 260.286 | 0 | 1 | 2
996 | 2/11 | 11:00:00 | 275.15 | 98752 | 3.6 | 250 | 3.8903 | 464.4 | 39.6 | 260.286 | 0 | 1 | 2
997 | 2/11 | 12:00:00 | 275.15 | 98752 | 4.6 | 240 | 3.8903 | 576 | 54 | 260.286 | 0 | 1 | 2
998 | 2/11 | 13:00:00 | 275.15 | 98752 | 3.6 | 250 | 3.8903 | 604.8 | 129.6 | 260.286 | 0 | 1 | 2
999 | 2/11 | 14:00:00 | 275.15 | 98752 | 4.1 | 250 | 3.8903 | 993.6 | 1238.4 | 259.826 | 0 | 1 | 2
1000 | 2/11 | 15:00:00 | 275.15 | 98752 | 4.6 | 240 | 3.8903 | 417.6 | 43.2 | 260.286 | 0 | 1 | 2
1001 | 2/11 | 16:00:00 | 275.15 | 98752 | 3.6 | 240 | 3.8903 | 230.4 | 0 | 260.286 | 0 | 1 | 2
1002 | 2/11 | 17:00:00 | 275.15 | 98752 | 2.6 | 250 | 3.8903 | 54 | 0 | 260.286 | 0 | 1 | 2
1003 | 2/11 | 18:00:00 | 275.15 | 98752 | 3.6 | 240 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
1004 | 2/11 | 19:00:00 | 275.15 | 98752 | 1.5 | 91 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1005 | 2/11 | 20:00:00 | 275.15 | 98752 | 2.6 | 200 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
1006 | 2/11 | 21:00:00 | 275.15 | 98752 | 1 | 251 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1007 | 2/11 | 22:00:00 | 275.15 | 98752 | 0 | 98 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1008 | 2/11 | 23:00:00 | 275.15 | 98752 | 1.5 | 101 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1009 | 2/11 | 24:00:00 | 275.15 | 98752 | 1 | 144 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1010 | 2/12 | 01:00:00 | 275.15 | 98752 | 1.5 | 99 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1011 | 2/12 | 02:00:00 | 275.15 | 98752 | 0.5 | 217 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1012 | 2/12 | 03:00:00 | 275.15 | 98752 | 1.5 | 210 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1013 | 2/12 | 04:00:00 | 275.15 | 98752 | 1.5 | 250 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1014 | 2/12 | 05:00:00 | 275.15 | 98752 | 1.5 | 112 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1015 | 2/12 | 06:00:00 | 275.15 | 98752 | 1.5 | 74 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1016 | 2/12 | 07:00:00 | 274.15 | 98743 | 0.5 | 200 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
1017 | 2/12 | 08:00:00 | 275.15 | 98752 | 0.5 | 270 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
1018 | 2/12 | 09:00:00 | 275.15 | 98752 | 1.5 | 270 | 4.1846 | 100.8 | 0 | 260.516 | 0 | 1 | 2
1019 | 2/12 | 10:00:00 | 276.15 | 98762 | 1.5 | 82 | 4.1841 | 298.8 | 3.6 | 261.463 | 0 | 1 | 3
1020 | 2/12 | 11:00:00 | 276.15 | 98762 | 1.5 | 0 | 4.1841 | 475.2 | 39.6 | 261.463 | 0 | 1 | 3
1021 | 2/12 | 12:00:00 | 277.15 | 98771 | 1.5 | 41 | 4.1838 | 586.8 | 54 | 262.41 | 0 | 1 | 4
1022 | 2/12 | 13:00:00 | 277.15 | 98771 | 2.6 | 170 | 3.8896 | 615.6 | 57.6 | 262.177 | 0 | 1 | 4
1023 | 2/12 | 14:00:00 | 277.15 | 98771 | 2.1 | 170 | 3.8896 | 561.6 | 50.4 | 262.177 | 0 | 1 | 4
1024 | 2/12 | 15:00:00 | 277.15 | 98771 | 2.1 | 170 | 3.8896 | 428.4 | 32.4 | 262.177 | 0 | 1 | 4
1025 | 2/12 | 16:00:00 | 277.15 | 98771 | 2.1 | 140 | 3.8896 | 237.6 | 0 | 262.177 | 0 | 1 | 4
1026 | 2/12 | 17:00:00 | 276.15 | 98762 | 2.6 | 140 | 3.8899 | 57.6 | 0 | 261.231 | 0 | 1 | 3
1027 | 2/12 | 18:00:00 | 276.15 | 98762 | 3.1 | 140 | 3.8899 | 0 | 0 | 261.231 | 0 | 1 | 3
1028 | 2/12 | 19:00:00 | 276.15 | 98762 | 1.5 | 160 | 3.8899 | 0 | 0 | 261.231 | 0 | 1 | 3
1029 | 2/12 | 20:00:00 | 276.15 | 98762 | 2.1 | 180 | 3.5796 | 0 | 0 | 260.999 | 0 | 1 | 3
1030 | 2/12 | 21:00:00 | 276.15 | 98762 | 2.6 | 160 | 3.8899 | 0 | 0 | 261.231 | 0 | 1 | 3
1031 | 2/12 | 22:00:00 | 275.15 | 98752 | 3.6 | 180 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
1032 | 2/12 | 23:00:00 | 275.15 | 98752 | 3.1 | 160 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
1033 | 2/12 | 24:00:00 | 274.15 | 98743 | 3.6 | 160 | 3.8907 | 0 | 0 | 258.215 | 0 | 1 | 1
1034 | 2/13 | 01:00:00 | 273.15 | 98734 | 5.1 | 160 | 3.5806 | 0 | 0 | 257.707 | 0 | 1 | 0
1035 | 2/13 | 02:00:00 | 274.15 | 98743 | 4.1 | 150 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
1036 | 2/13 | 03:00:00 | 274.15 | 98743 | 3.6 | 150 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
1037 | 2/13 | 04:00:00 | 274.15 | 98743 | 5.1 | 140 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
1038 | 2/13 | 05:00:00 | 274.15 | 98743 | 6.2 | 140 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
1039 | 2/13 | 06:00:00 | 274.15 | 98743 | 5.7 | 140 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
1040 | 2/13 | 07:00:00 | 274.15 | 98743 | 6.2 | 130 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
1041 | 2/13 | 08:00:00 | 274.15 | 98743 | 5.7 | 130 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
1042 | 2/13 | 09:00:00 | 274.15 | 98743 | 4.6 | 120 | 4.185 | 108 | 0 | 259.569 | 0 | 1 | 1
1043 | 2/13 | 10:00:00 | 275.15 | 98752 | 6.2 | 140 | 4.4981 | 306 | 18 | 260.745 | 0 | 1 | 2
1044 | 2/13 | 11:00:00 | 276.15 | 98762 | 5.7 | 130 | 4.832 | 482.4 | 64.8 | 261.921 | 0 | 1 | 3
1045 | 2/13 | 12:00:00 | 277.15 | 98771 | 5.7 | 130 | 5.1879 | 594 | 122.4 | 263.098 | 0 | 1 | 4
1046 | 2/13 | 13:00:00 | 277.15 | 98771 | 6.7 | 130 | 5.1879 | 626.4 | 129.6 | 263.098 | 0 | 1 | 4
1047 | 2/13 | 14:00:00 | 278.15 | 98780 | 5.7 | 130 | 5.5671 | 568.8 | 115.2 | 264.274 | 0 | 1 | 5
1048 | 2/13 | 15:00:00 | 278.15 | 98780 | 6.2 | 120 | 5.5671 | 435.6 | 36 | 264.274 | 0 | 1 | 5
1049 | 2/13 | 16:00:00 | 279.15 | 98789 | 5.1 | 120 | 5.5666 | 244.8 | 0 | 265.224 | 0 | 1 | 6
1050 | 2/13 | 17:00:00 | 279.15 | 98789 | 6.7 | 120 | 5.5666 | 61.2 | 0 | 265.224 | 0 | 1 | 6
1051 | 2/13 | 18:00:00 | 278.15 | 98780 | 7.7 | 120 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1052 | 2/13 | 19:00:00 | 278.15 | 98780 | 6.2 | 110 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1053 | 2/13 | 20:00:00 | 278.15 | 98780 | 5.7 | 110 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1054 | 2/13 | 21:00:00 | 278.15 | 98780 | 4.6 | 130 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1055 | 2/13 | 22:00:00 | 278.15 | 98780 | 4.1 | 110 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1056 | 2/13 | 23:00:00 | 278.15 | 98780 | 4.1 | 90 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1057 | 2/13 | 24:00:00 | 278.15 | 98780 | 4.6 | 90 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1058 | 2/14 | 01:00:00 | 278.15 | 98780 | 3.6 | 80 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
1059 | 2/14 | 02:00:00 | 277.15 | 98771 | 3.6 | 80 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1060 | 2/14 | 03:00:00 | 277.15 | 98771 | 3.1 | 60 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1061 | 2/14 | 04:00:00 | 277.15 | 98771 | 3.1 | 50 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1062 | 2/14 | 05:00:00 | 277.15 | 98771 | 4.1 | 40 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1063 | 2/14 | 06:00:00 | 277.15 | 98771 | 3.6 | 40 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1064 | 2/14 | 07:00:00 | 277.15 | 98771 | 4.1 | 40 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1065 | 2/14 | 08:00:00 | 277.15 | 98771 | 4.1 | 50 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1066 | 2/14 | 09:00:00 | 277.15 | 98771 | 3.6 | 50 | 5.1879 | 68.4 | 0 | 263.204 | 0 | 1 | 4
1067 | 2/14 | 10:00:00 | 278.15 | 98780 | 3.1 | 60 | 5.5671 | 190.8 | 0 | 264.381 | 0 | 1 | 5
1068 | 2/14 | 11:00:00 | 278.15 | 98780 | 3.1 | 40 | 5.5671 | 493.2 | 75.6 | 264.274 | 0 | 1 | 5
1069 | 2/14 | 12:00:00 | 278.15 | 98780 | 4.6 | 40 | 5.5671 | 604.8 | 122.4 | 264.274 | 0 | 1 | 5
1070 | 2/14 | 13:00:00 | 278.15 | 98780 | 3.6 | 50 | 5.5671 | 388.8 | 0 | 264.381 | 0 | 1 | 5
1071 | 2/14 | 14:00:00 | 278.15 | 98780 | 2.6 | 60 | 5.5671 | 579.6 | 241.2 | 264.274 | 0 | 1 | 5
1072 | 2/14 | 15:00:00 | 279.15 | 98789 | 3.6 | 70 | 5.9708 | 799.2 | 1191.6 | 264.982 | 0 | 1 | 6
1073 | 2/14 | 16:00:00 | 280.15 | 98798 | 4.1 | 80 | 5.9703 | 255.6 | 0 | 266.402 | 0 | 1 | 7
1074 | 2/14 | 17:00:00 | 279.15 | 98789 | 3.6 | 80 | 5.9708 | 64.8 | 0 | 265.451 | 0 | 1 | 6
1075 | 2/14 | 18:00:00 | 279.15 | 98789 | 4.1 | 60 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
1076 | 2/14 | 19:00:00 | 279.15 | 98789 | 4.1 | 70 | 5.9708 | 0 | 0 | 264.982 | 0 | 1 | 6
1077 | 2/14 | 20:00:00 | 278.15 | 98780 | 4.6 | 80 | 5.5671 | 0 | 0 | 263.807 | 0 | 1 | 5
1078 | 2/14 | 21:00:00 | 278.15 | 98780 | 3.6 | 80 | 5.5671 | 0 | 0 | 263.807 | 0 | 1 | 5
1079 | 2/14 | 22:00:00 | 278.15 | 98780 | 3.1 | 80 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1080 | 2/14 | 23:00:00 | 278.15 | 98780 | 3.6 | 90 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1081 | 2/14 | 24:00:00 | 278.15 | 98780 | 2.6 | 90 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
1082 | 2/15 | 01:00:00 | 278.15 | 98780 | 2.6 | 70 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
1083 | 2/15 | 02:00:00 | 278.15 | 98780 | 3.1 | 80 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
1084 | 2/15 | 03:00:00 | 278.15 | 98780 | 3.1 | 80 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
1085 | 2/15 | 04:00:00 | 277.15 | 98771 | 2.6 | 90 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1086 | 2/15 | 05:00:00 | 277.15 | 98771 | 2.6 | 90 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1087 | 2/15 | 06:00:00 | 277.15 | 98771 | 1.5 | 90 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1088 | 2/15 | 07:00:00 | 277.15 | 98771 | 1.5 | 149 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1089 | 2/15 | 08:00:00 | 277.15 | 98771 | 2.6 | 70 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
1090 | 2/15 | 09:00:00 | 277.15 | 98771 | 1.5 | 152 | 5.1879 | 75.6 | 0 | 263.204 | 0 | 1 | 4
1091 | 2/15 | 10:00:00 | 277.15 | 98771 | 2.6 | 80 | 5.1879 | 198 | 0 | 263.204 | 0 | 1 | 4
1092 | 2/15 | 11:00:00 | 277.15 | 98771 | 2.6 | 80 | 5.1879 | 504 | 75.6 | 263.098 | 0 | 1 | 4
1093 | 2/15 | 12:00:00 | 278.15 | 98780 | 4.6 | 90 | 5.5671 | 615.6 | 126 | 264.274 | 0 | 1 | 5
1094 | 2/15 | 13:00:00 | 278.15 | 98780 | 2.6 | 90 | 5.5671 | 648 | 133.2 | 264.274 | 0 | 1 | 5
1095 | 2/15 | 14:00:00 | 279.15 | 98789 | 4.6 | 120 | 5.5666 | 590.4 | 118.8 | 265.224 | 0 | 1 | 6
1096 | 2/15 | 15:00:00 | 279.15 | 98789 | 4.1 | 110 | 5.5666 | 453.6 | 39.6 | 265.224 | 0 | 1 | 6
1097 | 2/15 | 16:00:00 | 279.15 | 98789 | 3.1 | 140 | 5.5666 | 262.8 | 0 | 265.224 | 0 | 1 | 6
1098 | 2/15 | 17:00:00 | 279.15 | 98789 | 3.6 | 110 | 5.5666 | 68.4 | 0 | 265.224 | 0 | 1 | 6
1099 | 2/15 | 18:00:00 | 278.15 | 98780 | 4.1 | 110 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
1100 | 2/15 | 19:00:00 | 277.15 | 98771 | 3.6 | 120 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1101 | 2/15 | 20:00:00 | 277.15 | 98771 | 3.6 | 120 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
1102 | 2/15 | 21:00:00 | 277.15 | 98771 | 2.6 | 140 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1103 | 2/15 | 22:00:00 | 277.15 | 98771 | 4.1 | 150 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1104 | 2/15 | 23:00:00 | 277.15 | 98771 | 3.1 | 150 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1105 | 2/15 | 24:00:00 | 277.15 | 98771 | 2.1 | 160 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1106 | 2/16 | 01:00:00 | 277.15 | 98771 | 3.1 | 160 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1107 | 2/16 | 02:00:00 | 278.15 | 98780 | 2.6 | 180 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
1108 | 2/16 | 03:00:00 | 277.15 | 98771 | 3.6 | 190 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
1109 | 2/16 | 04:00:00 | 277.15 | 98771 | 3.6 | 170 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
1110 | 2/16 | 05:00:00 | 277.15 | 98771 | 4.1 | 160 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
1111 | 2/16 | 06:00:00 | 277.15 | 98771 | 3.1 | 170 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
1112 | 2/16 | 07:00:00 | 277.15 | 98771 | 3.1 | 150 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1113 | 2/16 | 08:00:00 | 277.15 | 98771 | 3.6 | 140 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1114 | 2/16 | 09:00:00 | 277.15 | 98771 | 3.6 | 160 | 5.1879 | 129.6 | 0 | 263.098 | 0 | 1 | 4
1115 | 2/16 | 10:00:00 | 277.15 | 98771 | 2.6 | 190 | 5.1879 | 334.8 | 18 | 263.098 | 0 | 1 | 4
1116 | 2/16 | 11:00:00 | 278.15 | 98780 | 3.1 | 230 | 5.5671 | 514.8 | 72 | 264.274 | 0 | 1 | 5
1117 | 2/16 | 12:00:00 | 279.15 | 98789 | 4.6 | 280 | 5.5666 | 630 | 262.8 | 265.224 | 0 | 1 | 6
1118 | 2/16 | 13:00:00 | 279.15 | 98789 | 4.6 | 260 | 5.5666 | 1188 | 1562.4 | 264.756 | 0 | 1 | 6
1119 | 2/16 | 14:00:00 | 279.15 | 98789 | 5.1 | 270 | 5.187 | 1087.2 | 1605.6 | 264.528 | 0 | 1 | 6
1120 | 2/16 | 15:00:00 | 279.15 | 98789 | 5.1 | 270 | 4.8307 | 842.4 | 1350 | 264.299 | 0 | 1 | 6
1121 | 2/16 | 16:00:00 | 278.15 | 98780 | 5.7 | 270 | 5.1875 | 522 | 1252.8 | 263.323 | 0 | 1 | 5
1122 | 2/16 | 17:00:00 | 278.15 | 98780 | 6.7 | 280 | 4.8311 | 140.4 | 190.8 | 263.095 | 0 | 1 | 5
1123 | 2/16 | 18:00:00 | 278.15 | 98780 | 4.1 | 280 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
1124 | 2/16 | 19:00:00 | 276.15 | 98762 | 6.2 | 280 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
1125 | 2/16 | 20:00:00 | 276.15 | 98762 | 6.7 | 280 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
1126 | 2/16 | 21:00:00 | 276.15 | 98762 | 7.2 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
1127 | 2/16 | 22:00:00 | 275.15 | 98752 | 4.1 | 290 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
1128 | 2/16 | 23:00:00 | 275.15 | 98752 | 4.1 | 280 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
1129 | 2/16 | 24:00:00 | 275.15 | 98752 | 4.6 | 290 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
1130 | 2/17 | 01:00:00 | 274.15 | 98743 | 6.2 | 280 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1131 | 2/17 | 02:00:00 | 273.15 | 98734 | 3.1 | 250 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
1132 | 2/17 | 03:00:00 | 273.15 | 98734 | 3.6 | 280 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
1133 | 2/17 | 04:00:00 | 274.15 | 98743 | 3.6 | 300 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
1134 | 2/17 | 05:00:00 | 274.15 | 98743 | 3.1 | 280 | 3.5803 | 0 | 0 | 258.398 | 0 | 1 | 1
1135 | 2/17 | 06:00:00 | 274.15 | 98743 | 6.7 | 280 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1136 | 2/17 | 07:00:00 | 274.15 | 98743 | 8.8 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1137 | 2/17 | 08:00:00 | 274.15 | 98743 | 7.2 | 260 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1138 | 2/17 | 09:00:00 | 275.15 | 98752 | 8.2 | 260 | 4.1846 | 262.8 | 576 | 259.802 | 0 | 1 | 2
1139 | 2/17 | 10:00:00 | 276.15 | 98762 | 6.7 | 260 | 4.4977 | 666 | 1562.4 | 260.975 | 0 | 1 | 3
1140 | 2/17 | 11:00:00 | 278.15 | 98780 | 5.7 | 260 | 4.4968 | 954 | 1458 | 263.123 | 0 | 1 | 5
1141 | 2/17 | 12:00:00 | 278.15 | 98780 | 6.7 | 260 | 4.4968 | 1159.2 | 1670.4 | 263.123 | 0 | 1 | 5
1142 | 2/17 | 13:00:00 | 279.15 | 98789 | 6.7 | 250 | 4.4964 | 1213.2 | 1710 | 264.069 | 0 | 1 | 6
1143 | 2/17 | 14:00:00 | 279.15 | 98789 | 7.2 | 270 | 4.4964 | 1112.4 | 1634.4 | 264.069 | 0 | 1 | 6
1144 | 2/17 | 15:00:00 | 279.15 | 98789 | 7.7 | 270 | 4.4964 | 864 | 1598.4 | 264.069 | 0 | 1 | 6
1145 | 2/17 | 16:00:00 | 279.15 | 98789 | 6.7 | 260 | 4.4964 | 511.2 | 1112.4 | 264.069 | 0 | 1 | 6
1146 | 2/17 | 17:00:00 | 278.15 | 98780 | 7.2 | 260 | 4.4968 | 151.2 | 226.8 | 262.865 | 0 | 1 | 5
1147 | 2/17 | 18:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.4968 | 0 | 0 | 262.865 | 0 | 1 | 5
1148 | 2/17 | 19:00:00 | 278.15 | 98780 | 8.2 | 250 | 4.4968 | 0 | 0 | 262.865 | 0 | 1 | 5
1149 | 2/17 | 20:00:00 | 278.15 | 98780 | 4.6 | 240 | 4.1834 | 0 | 0 | 262.634 | 0 | 1 | 5
1150 | 2/17 | 21:00:00 | 278.15 | 98780 | 5.7 | 240 | 4.1834 | 0 | 0 | 262.634 | 0 | 1 | 5
1151 | 2/17 | 22:00:00 | 278.15 | 98780 | 3.6 | 230 | 4.1834 | 0 | 0 | 262.634 | 0 | 1 | 5
1152 | 2/17 | 23:00:00 | 277.15 | 98771 | 5.7 | 240 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
1153 | 2/17 | 24:00:00 | 277.15 | 98771 | 6.2 | 230 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
1154 | 2/18 | 01:00:00 | 277.15 | 98771 | 5.7 | 240 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
1155 | 2/18 | 02:00:00 | 277.15 | 98771 | 5.1 | 220 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
1156 | 2/18 | 03:00:00 | 276.15 | 98762 | 5.7 | 230 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1157 | 2/18 | 04:00:00 | 276.15 | 98762 | 4.1 | 230 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1158 | 2/18 | 05:00:00 | 276.15 | 98762 | 3.6 | 220 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1159 | 2/18 | 06:00:00 | 277.15 | 98771 | 6.2 | 230 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
1160 | 2/18 | 07:00:00 | 277.15 | 98771 | 4.1 | 240 | 4.8316 | 0 | 0 | 262.405 | 0 | 1 | 4
1161 | 2/18 | 08:00:00 | 277.15 | 98771 | 6.7 | 230 | 4.8316 | 7.2 | 0 | 262.405 | 0 | 1 | 4
1162 | 2/18 | 09:00:00 | 278.15 | 98780 | 7.2 | 230 | 5.1875 | 262.8 | 687.6 | 263.581 | 0 | 1 | 5
1163 | 2/18 | 10:00:00 | 279.15 | 98789 | 5.1 | 240 | 5.187 | 356.4 | 46.8 | 264.996 | 0 | 1 | 6
1164 | 2/18 | 11:00:00 | 281.15 | 98806 | 5.1 | 230 | 5.5656 | 968.4 | 1389.6 | 266.653 | 0 | 1 | 8
1165 | 2/18 | 12:00:00 | 281.15 | 98806 | 5.1 | 240 | 5.5656 | 1173.6 | 1656 | 266.653 | 0 | 1 | 8
1166 | 2/18 | 13:00:00 | 281.15 | 98806 | 6.7 | 240 | 5.5656 | 1227.6 | 1692 | 266.653 | 0 | 1 | 8
1167 | 2/18 | 14:00:00 | 282.15 | 98815 | 5.1 | 240 | 5.9692 | 1123.2 | 1609.2 | 267.83 | 0 | 1 | 9
1168 | 2/18 | 15:00:00 | 282.15 | 98815 | 6.7 | 220 | 5.9692 | 874.8 | 1580.4 | 267.83 | 0 | 1 | 9
1169 | 2/18 | 16:00:00 | 282.15 | 98815 | 8.2 | 220 | 5.9692 | 525.6 | 860.4 | 267.83 | 0 | 1 | 9
1170 | 2/18 | 17:00:00 | 281.15 | 98806 | 7.2 | 220 | 5.9698 | 86.4 | 0 | 267.353 | 0 | 1 | 8
1171 | 2/18 | 18:00:00 | 281.15 | 98806 | 7.7 | 230 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
1172 | 2/18 | 19:00:00 | 281.15 | 98806 | 6.7 | 220 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
1173 | 2/18 | 20:00:00 | 280.15 | 98798 | 7.7 | 240 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
1174 | 2/18 | 21:00:00 | 280.15 | 98798 | 8.2 | 230 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
1175 | 2/18 | 22:00:00 | 279.15 | 98789 | 6.7 | 230 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
1176 | 2/18 | 23:00:00 | 279.15 | 98789 | 4.1 | 260 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
1177 | 2/18 | 24:00:00 | 279.15 | 98789 | 4.6 | 220 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
1178 | 2/19 | 01:00:00 | 278.15 | 98780 | 6.2 | 210 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
1179 | 2/19 | 02:00:00 | 279.15 | 98789 | 7.2 | 210 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
1180 | 2/19 | 03:00:00 | 279.15 | 98789 | 11.3 | 220 | 4.4964 | 0 | 0 | 264.31 | 0 | 1 | 6
1181 | 2/19 | 04:00:00 | 279.15 | 98789 | 11.8 | 220 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
1182 | 2/19 | 05:00:00 | 279.15 | 98789 | 9.3 | 220 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
1183 | 2/19 | 06:00:00 | 279.15 | 98789 | 7.7 | 220 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
1184 | 2/19 | 07:00:00 | 279.15 | 98789 | 7.7 | 210 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
1185 | 2/19 | 08:00:00 | 279.15 | 98789 | 5.7 | 200 | 5.5666 | 7.2 | 0 | 265.224 | 0 | 1 | 6
1186 | 2/19 | 09:00:00 | 279.15 | 98789 | 5.1 | 200 | 5.5666 | 154.8 | 0 | 265.224 | 0 | 1 | 6
1187 | 2/19 | 10:00:00 | 279.15 | 98789 | 6.2 | 220 | 5.5666 | 367.2 | 21.6 | 265.224 | 0 | 1 | 6
1188 | 2/19 | 11:00:00 | 279.15 | 98789 | 5.1 | 220 | 5.9708 | 547.2 | 219.6 | 265.451 | 0 | 1 | 6
1189 | 2/19 | 12:00:00 | 278.15 | 98780 | 4.6 | 250 | 5.5671 | 1195.2 | 1551.6 | 263.807 | 0 | 1 | 5
1190 | 2/19 | 13:00:00 | 278.15 | 98780 | 6.7 | 250 | 5.5671 | 1249.2 | 1958.4 | 263.807 | 0 | 1 | 5
1191 | 2/19 | 14:00:00 | 278.15 | 98780 | 4.6 | 230 | 5.1875 | 1216.8 | 2163.6 | 263.323 | 0 | 1 | 5
1192 | 2/19 | 15:00:00 | 279.15 | 98789 | 6.2 | 230 | 5.5666 | 896.4 | 1267.2 | 264.756 | 0 | 1 | 6
1193 | 2/19 | 16:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.5666 | 298.8 | 18 | 265.224 | 0 | 1 | 6
1194 | 2/19 | 17:00:00 | 278.15 | 98780 | 3.6 | 240 | 5.1875 | 165.6 | 349.2 | 263.581 | 0 | 1 | 5
1195 | 2/19 | 18:00:00 | 277.15 | 98771 | 4.1 | 220 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
1196 | 2/19 | 19:00:00 | 278.15 | 98780 | 6.2 | 230 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
1197 | 2/19 | 20:00:00 | 277.15 | 98771 | 4.6 | 250 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
1198 | 2/19 | 21:00:00 | 277.15 | 98771 | 2.6 | 250 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
1199 | 2/19 | 22:00:00 | 276.15 | 98762 | 3.1 | 220 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
1200 | 2/19 | 23:00:00 | 276.15 | 98762 | 1.5 | 250 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1201 | 2/19 | 24:00:00 | 276.15 | 98762 | 3.1 | 250 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1202 | 2/20 | 01:00:00 | 275.15 | 98752 | 2.1 | 250 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
1203 | 2/20 | 02:00:00 | 275.15 | 98752 | 2.6 | 250 | 4.4981 | 0 | 0 | 260.03 | 0 | 1 | 2
1204 | 2/20 | 03:00:00 | 275.15 | 98752 | 4.1 | 260 | 4.4981 | 0 | 0 | 260.03 | 0 | 1 | 2
1205 | 2/20 | 04:00:00 | 275.15 | 98752 | 3.1 | 250 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
1206 | 2/20 | 05:00:00 | 275.15 | 98752 | 3.1 | 230 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
1207 | 2/20 | 06:00:00 | 275.15 | 98752 | 3.1 | 230 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
1208 | 2/20 | 07:00:00 | 275.15 | 98752 | 5.1 | 250 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
1209 | 2/20 | 08:00:00 | 275.15 | 98752 | 4.6 | 260 | 4.1846 | 21.6 | 0 | 260.056 | 0 | 1 | 2
1210 | 2/20 | 09:00:00 | 275.15 | 98752 | 6.7 | 260 | 4.1846 | 295.2 | 547.2 | 260.056 | 0 | 1 | 2
1211 | 2/20 | 10:00:00 | 276.15 | 98762 | 7.7 | 250 | 4.4977 | 723.6 | 1641.6 | 260.975 | 0 | 1 | 3
1212 | 2/20 | 11:00:00 | 276.15 | 98762 | 5.7 | 250 | 4.4977 | 1015.2 | 1537.2 | 261.231 | 0 | 1 | 3
1213 | 2/20 | 12:00:00 | 277.15 | 98771 | 7.2 | 260 | 4.4973 | 1220.4 | 1699.2 | 262.177 | 0 | 1 | 4
1214 | 2/20 | 13:00:00 | 277.15 | 98771 | 8.2 | 260 | 4.4973 | 1278 | 1735.2 | 262.177 | 0 | 1 | 4
1215 | 2/20 | 14:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.1834 | 1173.6 | 1461.6 | 262.891 | 0 | 1 | 5
1216 | 2/20 | 15:00:00 | 278.15 | 98780 | 6.7 | 250 | 4.4968 | 921.6 | 1411.2 | 263.123 | 0 | 1 | 5
1217 | 2/20 | 16:00:00 | 277.15 | 98771 | 7.2 | 260 | 4.1838 | 597.6 | 1242 | 261.69 | 0 | 1 | 4
1218 | 2/20 | 17:00:00 | 277.15 | 98771 | 6.2 | 260 | 4.1838 | 190.8 | 241.2 | 261.69 | 0 | 1 | 4
1219 | 2/20 | 18:00:00 | 276.15 | 98762 | 6.7 | 260 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
1220 | 2/20 | 19:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
1221 | 2/20 | 20:00:00 | 276.15 | 98762 | 4.1 | 250 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1222 | 2/20 | 21:00:00 | 275.15 | 98752 | 2.1 | 230 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
1223 | 2/20 | 22:00:00 | 275.15 | 98752 | 3.6 | 250 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
1224 | 2/20 | 23:00:00 | 275.15 | 98752 | 2.6 | 240 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
1225 | 2/20 | 24:00:00 | 275.15 | 98752 | 3.1 | 260 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
1226 | 2/21 | 01:00:00 | 275.15 | 98752 | 1.5 | 285 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
1227 | 2/21 | 02:00:00 | 275.15 | 98752 | 4.6 | 270 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
1228 | 2/21 | 03:00:00 | 275.15 | 98752 | 4.1 | 270 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
1229 | 2/21 | 04:00:00 | 274.15 | 98743 | 4.1 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1230 | 2/21 | 05:00:00 | 274.15 | 98743 | 6.2 | 270 | 4.185 | 0 | 0 | 259.111 | 0 | 1 | 1
1231 | 2/21 | 06:00:00 | 274.15 | 98743 | 4.1 | 280 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1232 | 2/21 | 07:00:00 | 274.15 | 98743 | 5.1 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1233 | 2/21 | 08:00:00 | 273.15 | 98734 | 5.7 | 270 | 3.891 | 32.4 | 0 | 257.685 | 0 | 1 | 0
1234 | 2/21 | 09:00:00 | 274.15 | 98743 | 4.6 | 270 | 3.8907 | 327.6 | 712.8 | 258.628 | 0 | 1 | 1
1235 | 2/21 | 10:00:00 | 275.15 | 98752 | 7.2 | 280 | 3.8903 | 745.2 | 1461.6 | 259.572 | 0 | 1 | 2
1236 | 2/21 | 11:00:00 | 276.15 | 98762 | 6.7 | 280 | 4.1841 | 1098 | 2134.8 | 260.746 | 0 | 1 | 3
1237 | 2/21 | 12:00:00 | 277.15 | 98771 | 9.3 | 280 | 4.1838 | 1245.6 | 1501.2 | 261.946 | 0 | 1 | 4
1238 | 2/21 | 13:00:00 | 277.15 | 98771 | 7.7 | 280 | 3.8896 | 1303.2 | 1544.4 | 261.714 | 0 | 1 | 4
1239 | 2/21 | 14:00:00 | 278.15 | 98780 | 6.2 | 300 | 3.5789 | 1198.8 | 1486.8 | 262.425 | 0 | 1 | 5
1240 | 2/21 | 15:00:00 | 278.15 | 98780 | 5.7 | 290 | 3.8892 | 943.2 | 1692 | 262.659 | 0 | 1 | 5
1241 | 2/21 | 16:00:00 | 278.15 | 98780 | 8.8 | 290 | 3.5789 | 579.6 | 993.6 | 262.425 | 0 | 1 | 5
1242 | 2/21 | 17:00:00 | 276.15 | 98762 | 6.2 | 280 | 3.8899 | 190.8 | 205.2 | 260.77 | 0 | 1 | 3
1243 | 2/21 | 18:00:00 | 275.15 | 98752 | 6.7 | 280 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
1244 | 2/21 | 19:00:00 | 275.15 | 98752 | 6.7 | 280 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
1245 | 2/21 | 20:00:00 | 275.15 | 98752 | 6.2 | 280 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
1246 | 2/21 | 21:00:00 | 274.15 | 98743 | 5.1 | 260 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1247 | 2/21 | 22:00:00 | 274.15 | 98743 | 6.2 | 270 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1248 | 2/21 | 23:00:00 | 274.15 | 98743 | 6.2 | 270 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1249 | 2/21 | 24:00:00 | 274.15 | 98743 | 5.1 | 270 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1250 | 2/22 | 01:00:00 | 274.15 | 98743 | 6.2 | 270 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
1251 | 2/22 | 02:00:00 | 275.15 | 98752 | 5.7 | 260 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
1252 | 2/22 | 03:00:00 | 275.15 | 98752 | 4.6 | 250 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
1253 | 2/22 | 04:00:00 | 275.15 | 98752 | 4.1 | 250 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
1254 | 2/22 | 05:00:00 | 275.15 | 98752 | 3.1 | 262 | 4.3388 | 0 | 0 | 260.736 | 0 | 1 | 2
1255 | 2/22 | 06:00:00 | 275.15 | 98752 | 2.1 | 190 | 4.4981 | 0 | 0 | 260.745 | 0 | 1 | 2
1256 | 2/22 | 07:00:00 | 274.15 | 98743 | 5.7 | 240 | 4.185 | 0 | 0 | 259.111 | 0 | 1 | 1
1257 | 2/22 | 08:00:00 | 274.15 | 98743 | 5.1 | 220 | 4.185 | 36 | 0 | 259.111 | 0 | 1 | 1
1258 | 2/22 | 09:00:00 | 275.15 | 98752 | 4.1 | 210 | 3.8903 | 345.6 | 745.2 | 259.572 | 0 | 1 | 2
1259 | 2/22 | 10:00:00 | 275.15 | 98752 | 3.6 | 210 | 3.8903 | 766.8 | 1486.8 | 259.572 | 0 | 1 | 2
1260 | 2/22 | 11:00:00 | 276.15 | 98762 | 5.1 | 200 | 4.1841 | 1123.2 | 2152.8 | 260.746 | 0 | 1 | 3
1261 | 2/22 | 12:00:00 | 276.15 | 98762 | 6.2 | 190 | 3.8899 | 1270.8 | 1573.2 | 260.77 | 0 | 1 | 3
1262 | 2/22 | 13:00:00 | 276.15 | 98762 | 7.7 | 200 | 4.1841 | 734.4 | 90 | 261.463 | 0 | 1 | 3
1263 | 2/22 | 14:00:00 | 275.15 | 98752 | 7.7 | 180 | 4.4981 | 673.2 | 136.8 | 260.745 | 0 | 1 | 2
1264 | 2/22 | 15:00:00 | 274.15 | 98743 | 6.7 | 170 | 4.185 | 532.8 | 144 | 259.569 | 0 | 1 | 1
1265 | 2/22 | 16:00:00 | 275.15 | 98752 | 7.7 | 180 | 4.4981 | 331.2 | 21.6 | 260.745 | 0 | 1 | 2
1266 | 2/22 | 17:00:00 | 277.15 | 98771 | 7.2 | 200 | 4.8316 | 111.6 | 0 | 262.87 | 0 | 1 | 4
1267 | 2/22 | 18:00:00 | 277.15 | 98771 | 6.7 | 210 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
1268 | 2/22 | 19:00:00 | 278.15 | 98780 | 5.1 | 220 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1269 | 2/22 | 20:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.9708 | 0 | 0 | 264.982 | 0 | 1 | 6
1270 | 2/22 | 21:00:00 | 280.15 | 98798 | 6.7 | 240 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
1271 | 2/22 | 22:00:00 | 279.15 | 98789 | 9.8 | 260 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
1272 | 2/22 | 23:00:00 | 278.15 | 98780 | 11.8 | 260 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
1273 | 2/22 | 24:00:00 | 276.15 | 98762 | 12.4 | 260 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1274 | 2/23 | 01:00:00 | 276.15 | 98762 | 13.4 | 260 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
1275 | 2/23 | 02:00:00 | 276.15 | 98762 | 9.3 | 260 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
1276 | 2/23 | 03:00:00 | 275.15 | 98752 | 6.7 | 250 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
1277 | 2/23 | 04:00:00 | 275.15 | 98752 | 3.6 | 351 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
1278 | 2/23 | 05:00:00 | 275.15 | 98752 | 3.6 | 230 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
1279 | 2/23 | 06:00:00 | 275.15 | 98752 | 5.1 | 210 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
1280 | 2/23 | 07:00:00 | 275.15 | 98752 | 6.2 | 230 | 3.5799 | 0 | 0 | 260.054 | 0 | 1 | 2
1281 | 2/23 | 08:00:00 | 275.15 | 98752 | 6.2 | 230 | 3.5799 | 43.2 | 0 | 259.594 | 0 | 1 | 2
1282 | 2/23 | 09:00:00 | 275.15 | 98752 | 6.2 | 220 | 3.5799 | 342 | 637.2 | 259.594 | 0 | 1 | 2
1283 | 2/23 | 10:00:00 | 276.15 | 98762 | 6.7 | 230 | 3.5796 | 745.2 | 1267.2 | 260.538 | 0 | 1 | 3
1284 | 2/23 | 11:00:00 | 277.15 | 98771 | 9.3 | 230 | 3.5793 | 1083.6 | 1400.4 | 261.481 | 0 | 1 | 4
1285 | 2/23 | 12:00:00 | 278.15 | 98780 | 7.7 | 230 | 3.2915 | 1296 | 1544.4 | 262.189 | 0 | 1 | 5
1286 | 2/23 | 13:00:00 | 278.15 | 98780 | 10.3 | 240 | 3.2915 | 1350 | 1587.6 | 262.189 | 0 | 1 | 5
1287 | 2/23 | 14:00:00 | 278.15 | 98780 | 11.3 | 240 | 3.2915 | 1242 | 1508.4 | 262.189 | 0 | 1 | 5
1288 | 2/23 | 15:00:00 | 279.15 | 98789 | 10.3 | 230 | 3.2912 | 1044 | 2084.4 | 262.874 | 0 | 1 | 6
1289 | 2/23 | 16:00:00 | 278.15 | 98780 | 9.3 | 230 | 3.2915 | 655.2 | 1242 | 261.933 | 0 | 1 | 5
1290 | 2/23 | 17:00:00 | 278.15 | 98780 | 9.8 | 220 | 3.0253 | 230.4 | 475.2 | 261.696 | 0 | 1 | 5
1291 | 2/23 | 18:00:00 | 277.15 | 98771 | 9.8 | 220 | 3.2918 | 0 | 0 | 260.991 | 0 | 1 | 4
1292 | 2/23 | 19:00:00 | 276.15 | 98762 | 11.8 | 220 | 3.5796 | 0 | 0 | 260.283 | 0 | 1 | 3
1293 | 2/23 | 20:00:00 | 276.15 | 98762 | 10.3 | 210 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1294 | 2/23 | 21:00:00 | 275.15 | 98752 | 8.2 | 220 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
1295 | 2/23 | 22:00:00 | 276.15 | 98762 | 8.2 | 220 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1296 | 2/23 | 23:00:00 | 276.15 | 98762 | 7.7 | 230 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1297 | 2/23 | 24:00:00 | 276.15 | 98762 | 7.7 | 230 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1298 | 2/24 | 01:00:00 | 276.15 | 98762 | 7.2 | 240 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1299 | 2/24 | 02:00:00 | 275.15 | 98752 | 7.7 | 250 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
1300 | 2/24 | 03:00:00 | 276.15 | 98762 | 9.8 | 260 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1301 | 2/24 | 04:00:00 | 276.15 | 98762 | 11.3 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1302 | 2/24 | 05:00:00 | 276.15 | 98762 | 11.8 | 270 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1303 | 2/24 | 06:00:00 | 276.15 | 98762 | 13.9 | 270 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1304 | 2/24 | 07:00:00 | 276.15 | 98762 | 9.8 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1305 | 2/24 | 08:00:00 | 276.15 | 98762 | 7.2 | 270 | 4.1841 | 50.4 | 0 | 261.001 | 0 | 1 | 3
1306 | 2/24 | 09:00:00 | 277.15 | 98771 | 8.8 | 270 | 4.4973 | 356.4 | 766.8 | 262.177 | 0 | 1 | 4
1307 | 2/24 | 10:00:00 | 277.15 | 98771 | 10.8 | 270 | 4.8316 | 759.6 | 1447.2 | 262.405 | 0 | 1 | 4
1308 | 2/24 | 11:00:00 | 278.15 | 98780 | 11.8 | 280 | 4.4968 | 1098 | 1828.8 | 263.123 | 0 | 1 | 5
1309 | 2/24 | 12:00:00 | 277.15 | 98771 | 8.2 | 260 | 4.8316 | 1306.8 | 1728 | 262.405 | 0 | 1 | 4
1310 | 2/24 | 13:00:00 | 278.15 | 98780 | 11.3 | 270 | 4.1834 | 1364.4 | 1569.6 | 262.891 | 0 | 1 | 5
1311 | 2/24 | 14:00:00 | 277.15 | 98771 | 11.8 | 260 | 4.4973 | 1256.4 | 1702.8 | 262.177 | 0 | 1 | 4
1312 | 2/24 | 15:00:00 | 278.15 | 98780 | 9.8 | 260 | 4.1834 | 1000.8 | 1321.2 | 262.891 | 0 | 1 | 5
1313 | 2/24 | 16:00:00 | 277.15 | 98771 | 9.8 | 260 | 4.1838 | 630 | 1108.8 | 261.946 | 0 | 1 | 4
1314 | 2/24 | 17:00:00 | 277.15 | 98771 | 10.3 | 260 | 4.1838 | 230.4 | 255.6 | 261.946 | 0 | 1 | 4
1315 | 2/24 | 18:00:00 | 277.15 | 98771 | 9.8 | 260 | 4.1838 | 0 | 0 | 261.946 | 0 | 1 | 4
1316 | 2/24 | 19:00:00 | 276.15 | 98762 | 8.8 | 260 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
1317 | 2/24 | 20:00:00 | 276.15 | 98762 | 7.7 | 260 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1318 | 2/24 | 21:00:00 | 276.15 | 98762 | 6.2 | 250 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1319 | 2/24 | 22:00:00 | 276.15 | 98762 | 3.1 | 230 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
1320 | 2/24 | 23:00:00 | 277.15 | 98771 | 4.1 | 230 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
1321 | 2/24 | 24:00:00 | 277.15 | 98771 | 4.6 | 220 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
1322 | 2/25 | 01:00:00 | 276.15 | 98762 | 3.6 | 210 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1323 | 2/25 | 02:00:00 | 276.15 | 98762 | 3.1 | 220 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
1324 | 2/25 | 03:00:00 | 276.15 | 98762 | 4.1 | 210 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
1325 | 2/25 | 04:00:00 | 277.15 | 98771 | 2.6 | 220 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
1326 | 2/25 | 05:00:00 | 278.15 | 98780 | 3.1 | 250 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
1327 | 2/25 | 06:00:00 | 278.15 | 98780 | 3.6 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
1328 | 2/25 | 07:00:00 | 278.15 | 98780 | 6.7 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
1329 | 2/25 | 08:00:00 | 277.15 | 98771 | 4.1 | 280 | 5.1879 | 57.6 | 0 | 262.633 | 0 | 1 | 4
1330 | 2/25 | 09:00:00 | 278.15 | 98780 | 5.1 | 260 | 5.1875 | 396 | 957.6 | 263.323 | 0 | 1 | 5
1331 | 2/25 | 10:00:00 | 279.15 | 98789 | 3.6 | 260 | 5.5666 | 777.6 | 1436.4 | 264.756 | 0 | 1 | 6
1332 | 2/25 | 11:00:00 | 280.15 | 98798 | 4.6 | 280 | 5.5661 | 1116 | 1821.6 | 265.704 | 0 | 1 | 7
1333 | 2/25 | 12:00:00 | 281.15 | 98806 | 4.6 | 270 | 5.5656 | 1324.8 | 1728 | 266.653 | 0 | 1 | 8
1334 | 2/25 | 13:00:00 | 281.15 | 98806 | 3.6 | 280 | 5.5656 | 1378.8 | 1771.2 | 266.653 | 0 | 1 | 8
1335 | 2/25 | 14:00:00 | 281.15 | 98806 | 3.6 | 250 | 5.1861 | 1274.4 | 1702.8 | 266.423 | 0 | 1 | 8
1336 | 2/25 | 15:00:00 | 281.15 | 98806 | 4.1 | 260 | 5.5656 | 1015.2 | 1724.4 | 266.653 | 0 | 1 | 8
1337 | 2/25 | 16:00:00 | 281.15 | 98806 | 4.6 | 250 | 5.5656 | 644.4 | 1278 | 266.653 | 0 | 1 | 8
1338 | 2/25 | 17:00:00 | 281.15 | 98806 | 2.6 | 250 | 5.5656 | 241.2 | 360 | 266.653 | 0 | 1 | 8
1339 | 2/25 | 18:00:00 | 280.15 | 98798 | 2.1 | 200 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
1340 | 2/25 | 19:00:00 | 280.15 | 98798 | 2.6 | 170 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
1341 | 2/25 | 20:00:00 | 280.15 | 98798 | 2.6 | 160 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
1342 | 2/25 | 21:00:00 | 280.15 | 98798 | 4.1 | 170 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
1343 | 2/25 | 22:00:00 | 280.15 | 98798 | 3.6 | 180 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
1344 | 2/25 | 23:00:00 | 281.15 | 98806 | 4.1 | 190 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
1345 | 2/25 | 24:00:00 | 281.15 | 98806 | 4.6 | 220 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
1346 | 2/26 | 01:00:00 | 282.15 | 98815 | 4.1 | 210 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
1347 | 2/26 | 02:00:00 | 282.15 | 98815 | 4.6 | 210 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
1348 | 2/26 | 03:00:00 | 282.15 | 98815 | 5.1 | 210 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
1349 | 2/26 | 04:00:00 | 282.15 | 98815 | 5.7 | 210 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
1350 | 2/26 | 05:00:00 | 282.15 | 98815 | 7.2 | 220 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
1351 | 2/26 | 06:00:00 | 282.15 | 98815 | 6.2 | 210 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
1352 | 2/26 | 07:00:00 | 283.15 | 98824 | 6.2 | 230 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
1353 | 2/26 | 08:00:00 | 283.15 | 98824 | 7.7 | 230 | 7.3431 | 36 | 0 | 269.936 | 0 | 1 | 10
1354 | 2/26 | 09:00:00 | 282.15 | 98815 | 5.7 | 230 | 7.3438 | 216 | 0 | 268.983 | 0 | 1 | 9
1355 | 2/26 | 10:00:00 | 282.15 | 98815 | 8.8 | 270 | 6.8571 | 442.8 | 72 | 268.758 | 0 | 1 | 9
1356 | 2/26 | 11:00:00 | 279.15 | 98789 | 10.3 | 280 | 5.5666 | 1137.6 | 1486.8 | 264.756 | 0 | 1 | 6
1357 | 2/26 | 12:00:00 | 279.15 | 98789 | 9.8 | 280 | 5.187 | 1350 | 1749.6 | 264.528 | 0 | 1 | 6
1358 | 2/26 | 13:00:00 | 280.15 | 98798 | 9.8 | 290 | 4.8303 | 1407.6 | 1807.2 | 265.246 | 0 | 1 | 7
1359 | 2/26 | 14:00:00 | 279.15 | 98789 | 8.2 | 280 | 4.8307 | 1296 | 1717.2 | 264.299 | 0 | 1 | 6
1360 | 2/26 | 15:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.183 | 1040.4 | 1350 | 263.837 | 0 | 1 | 6
1361 | 2/26 | 16:00:00 | 279.15 | 98789 | 10.8 | 280 | 3.8889 | 669.6 | 1159.2 | 263.603 | 0 | 1 | 6
1362 | 2/26 | 17:00:00 | 277.15 | 98771 | 8.2 | 270 | 3.8896 | 259.2 | 295.2 | 261.714 | 0 | 1 | 4
1363 | 2/26 | 18:00:00 | 277.15 | 98771 | 7.7 | 270 | 3.5793 | 0 | 0 | 261.481 | 0 | 1 | 4
1364 | 2/26 | 19:00:00 | 276.15 | 98762 | 6.2 | 270 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
1365 | 2/26 | 20:00:00 | 275.15 | 98752 | 3.6 | 250 | 3.5799 | 0 | 0 | 260.054 | 0 | 1 | 2
1366 | 2/26 | 21:00:00 | 274.15 | 98743 | 4.1 | 270 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
1367 | 2/26 | 22:00:00 | 275.15 | 98752 | 5.1 | 260 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
1368 | 2/26 | 23:00:00 | 275.15 | 98752 | 5.7 | 260 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
1369 | 2/26 | 24:00:00 | 275.15 | 98752 | 6.7 | 260 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
1370 | 2/27 | 01:00:00 | 274.15 | 98743 | 5.1 | 260 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1371 | 2/27 | 02:00:00 | 274.15 | 98743 | 5.1 | 260 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1372 | 2/27 | 03:00:00 | 274.15 | 98743 | 5.7 | 270 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1373 | 2/27 | 04:00:00 | 274.15 | 98743 | 5.1 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1374 | 2/27 | 05:00:00 | 274.15 | 98743 | 7.2 | 260 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1375 | 2/27 | 06:00:00 | 274.15 | 98743 | 7.7 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1376 | 2/27 | 07:00:00 | 275.15 | 98752 | 7.7 | 270 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
1377 | 2/27 | 08:00:00 | 275.15 | 98752 | 8.8 | 270 | 3.8903 | 79.2 | 43.2 | 259.572 | 0 | 1 | 2
1378 | 2/27 | 09:00:00 | 275.15 | 98752 | 7.7 | 260 | 4.1846 | 410.4 | 759.6 | 260.056 | 0 | 1 | 2
1379 | 2/27 | 10:00:00 | 277.15 | 98771 | 9.3 | 260 | 4.4973 | 824.4 | 1526.4 | 262.177 | 0 | 1 | 4
1380 | 2/27 | 11:00:00 | 277.15 | 98771 | 8.2 | 260 | 4.1838 | 1166.4 | 1432.8 | 261.946 | 0 | 1 | 4
1381 | 2/27 | 12:00:00 | 277.15 | 98771 | 7.2 | 260 | 4.1838 | 1378.8 | 1569.6 | 261.946 | 0 | 1 | 4
1382 | 2/27 | 13:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.1834 | 1432.8 | 1609.2 | 262.891 | 0 | 1 | 5
1383 | 2/27 | 14:00:00 | 278.15 | 98780 | 6.7 | 250 | 4.4968 | 1321.2 | 1738.8 | 263.123 | 0 | 1 | 5
1384 | 2/27 | 15:00:00 | 279.15 | 98789 | 6.2 | 240 | 3.8889 | 1062 | 1368 | 263.603 | 0 | 1 | 6
1385 | 2/27 | 16:00:00 | 279.15 | 98789 | 7.7 | 250 | 3.8889 | 727.2 | 1411.2 | 263.345 | 0 | 1 | 6
1386 | 2/27 | 17:00:00 | 278.15 | 98780 | 4.6 | 240 | 3.8892 | 288 | 597.6 | 262.402 | 0 | 1 | 5
1387 | 2/27 | 18:00:00 | 278.15 | 98780 | 3.1 | 220 | 4.1834 | 7.2 | 0 | 262.891 | 0 | 1 | 5
1388 | 2/27 | 19:00:00 | 277.15 | 98771 | 3.6 | 200 | 3.8896 | 0 | 0 | 261.458 | 0 | 1 | 4
1389 | 2/27 | 20:00:00 | 277.15 | 98771 | 3.6 | 200 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
1390 | 2/27 | 21:00:00 | 277.15 | 98771 | 4.6 | 180 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
1391 | 2/27 | 22:00:00 | 277.15 | 98771 | 5.7 | 210 | 4.1838 | 0 | 0 | 262.41 | 0 | 1 | 4
1392 | 2/27 | 23:00:00 | 278.15 | 98780 | 5.7 | 210 | 4.1834 | 0 | 0 | 263.356 | 0 | 1 | 5
1393 | 2/27 | 24:00:00 | 277.15 | 98771 | 6.2 | 200 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
1394 | 2/28 | 01:00:00 | 278.15 | 98780 | 5.7 | 220 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
1395 | 2/28 | 02:00:00 | 278.15 | 98780 | 4.6 | 210 | 4.4968 | 0 | 0 | 262.445 | 0 | 1 | 5
1396 | 2/28 | 03:00:00 | 278.15 | 98780 | 3.6 | 210 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
1397 | 2/28 | 04:00:00 | 278.15 | 98780 | 4.6 | 220 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
1398 | 2/28 | 05:00:00 | 278.15 | 98780 | 3.6 | 200 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
1399 | 2/28 | 06:00:00 | 278.15 | 98780 | 3.6 | 200 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
1400 | 2/28 | 07:00:00 | 279.15 | 98789 | 4.1 | 210 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
1401 | 2/28 | 08:00:00 | 278.15 | 98780 | 2.1 | 170 | 5.1875 | 79.2 | 18 | 263.581 | 0 | 1 | 5
1402 | 2/28 | 09:00:00 | 280.15 | 98798 | 3.6 | 210 | 5.9703 | 428.4 | 878.4 | 265.931 | 0 | 1 | 7
1403 | 2/28 | 10:00:00 | 280.15 | 98798 | 4.6 | 220 | 5.9703 | 838.8 | 1512 | 265.931 | 0 | 1 | 7
1404 | 2/28 | 11:00:00 | 281.15 | 98806 | 5.7 | 220 | 5.9698 | 1180.8 | 1850.4 | 266.881 | 0 | 1 | 8
1405 | 2/28 | 12:00:00 | 281.15 | 98806 | 4.6 | 220 | 5.9698 | 1389.6 | 1756.8 | 266.881 | 0 | 1 | 8
1406 | 2/28 | 13:00:00 | 282.15 | 98815 | 6.2 | 230 | 5.5651 | 1443.6 | 1810.8 | 267.601 | 0 | 1 | 9
1407 | 2/28 | 14:00:00 | 282.15 | 98815 | 4.6 | 230 | 5.9692 | 1332 | 1710 | 267.83 | 0 | 1 | 9
1408 | 2/28 | 15:00:00 | 282.15 | 98815 | 3.6 | 210 | 5.9692 | 1072.8 | 1756.8 | 267.83 | 0 | 1 | 9
1409 | 2/28 | 16:00:00 | 281.15 | 98806 | 4.6 | 200 | 5.9698 | 698.4 | 1332 | 266.881 | 0 | 1 | 8
1410 | 2/28 | 17:00:00 | 281.15 | 98806 | 7.2 | 200 | 5.5656 | 284.4 | 424.8 | 266.653 | 0 | 1 | 8
1411 | 2/28 | 18:00:00 | 281.15 | 98806 | 7.2 | 200 | 5.5656 | 7.2 | 0 | 267.125 | 0 | 1 | 8
1412 | 2/28 | 19:00:00 | 280.65 | 98802 | 7.1 | 202 | 5.8872 | 0 | 0 | 266.832 | 0 | 1 | 7.5
1413 | 2/28 | 20:00:00 | 281.15 | 98806 | 8.3 | 217 | 6.0537 | 0 | 0 | 267.398 | 0 | 1 | 8
1414 | 2/28 | 21:00:00 | 281.35 | 98808 | 9.4 | 230 | 6.0536 | 0 | 0 | 267.589 | 0 | 1 | 8.2
1415 | 2/28 | 22:00:00 | 279.65 | 98793 | 8.2 | 245 | 5.3736 | 0 | 0 | 265.116 | 0 | 1 | 6.5
1416 | 2/28 | 23:00:00 | 277.95 | 98777 | 7.2 | 260 | 4.6615 | 0 | 0 | 263.048 | 0 | 1 | 4.8
1417 | 2/28 | 24:00:00 | 275.95 | 98759 | 5.2 | 272 | 4.035 | 0 | 0 | 260.697 | 0 | 1 | 2.8
1418 | 3/1 | 01:00:00 | 274.15 | 98743 | 3.5 | 282 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
1419 | 3/1 | 02:00:00 | 274.15 | 98743 | 3.7 | 290 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
1420 | 3/1 | 03:00:00 | 274.15 | 98743 | 3.7 | 285 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
1421 | 3/1 | 04:00:00 | 274.15 | 98743 | 3.5 | 277 | 3.6405 | 0 | 0 | 259.155 | 0 | 1 | 1
1422 | 3/1 | 05:00:00 | 274.15 | 98743 | 3.1 | 275 | 3.7325 | 0 | 0 | 259.224 | 0 | 1 | 1
1423 | 3/1 | 06:00:00 | 274.15 | 98743 | 2.7 | 270 | 3.8267 | 0 | 0 | 259.293 | 0 | 1 | 1
1424 | 3/1 | 07:00:00 | 274.15 | 98743 | 2.6 | 270 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
1425 | 3/1 | 08:00:00 | 274.15 | 98743 | 2.6 | 280 | 3.8907 | 90 | 25.2 | 258.882 | 0 | 1 | 1
1426 | 3/1 | 09:00:00 | 274.15 | 98743 | 2.6 | 270 | 3.8907 | 450 | 763.2 | 258.882 | 0 | 1 | 1
1427 | 3/1 | 10:00:00 | 275.15 | 98752 | 4.1 | 270 | 3.8903 | 921.6 | 1641.6 | 259.572 | 0 | 1 | 2
1428 | 3/1 | 11:00:00 | 277.15 | 98771 | 4.1 | 290 | 3.8896 | 1288.8 | 2314.8 | 261.458 | 0 | 1 | 4
1429 | 3/1 | 12:00:00 | 278.15 | 98780 | 4.1 | 270 | 3.8892 | 1425.6 | 1605.6 | 262.659 | 0 | 1 | 5
1430 | 3/1 | 13:00:00 | 278.15 | 98780 | 4.6 | 260 | 3.5789 | 1479.6 | 1648.8 | 262.425 | 0 | 1 | 5
1431 | 3/1 | 14:00:00 | 277.15 | 98771 | 4.1 | 300 | 3.5793 | 1368 | 1569.6 | 261.481 | 0 | 1 | 4
1432 | 3/1 | 15:00:00 | 277.15 | 98771 | 4.1 | 290 | 3.5793 | 1105.2 | 1393.2 | 261.481 | 0 | 1 | 4
1433 | 3/1 | 16:00:00 | 277.15 | 98771 | 2.6 | 310 | 3.8896 | 723.6 | 1209.6 | 261.714 | 0 | 1 | 4
1434 | 3/1 | 17:00:00 | 278.15 | 98780 | 4.1 | 260 | 4.4968 | 298.8 | 453.6 | 263.123 | 0 | 1 | 5
1435 | 3/1 | 18:00:00 | 277.15 | 98771 | 3.6 | 260 | 3.8896 | 21.6 | 0 | 261.458 | 0 | 1 | 4
1436 | 3/1 | 19:00:00 | 275.15 | 98752 | 2.1 | 270 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
1437 | 3/1 | 20:00:00 | 275.15 | 98752 | 3.6 | 280 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
1438 | 3/1 | 21:00:00 | 273.15 | 98734 | 3.6 | 290 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
1439 | 3/1 | 22:00:00 | 274.15 | 98743 | 4.1 | 290 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
1440 | 3/1 | 23:00:00 | 273.15 | 98734 | 3.6 | 300 | 3.6713 | 0 | 0 | 258.337 | 0 | 1 | 0
1441 | 3/1 | 24:00:00 | 273.35 | 98735 | 3.2 | 37 | 3.764 | 0 | 0 | 258.596 | 0 | 1 | 0.2
1442 | 3/2 | 01:00:00 | 273.45 | 98737 | 2.9 | 104 | 3.8588 | 0 | 0 | 258.759 | 0 | 1 | 0.3
1443 | 3/2 | 02:00:00 | 273.65 | 98739 | 2.5 | 316 | 3.9198 | 0 | 0 | 258.994 | 0 | 1 | 0.5
1444 | 3/2 | 03:00:00 | 273.85 | 98740 | 2.2 | 274 | 4.0065 | 0 | 0 | 259.253 | 0 | 1 | 0.7
1445 | 3/2 | 04:00:00 | 273.95 | 98742 | 1.9 | 108 | 4.0948 | 0 | 0 | 259.416 | 0 | 1 | 0.8
1446 | 3/2 | 05:00:00 | 274.15 | 98743 | 1.5 | 350 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
1447 | 3/2 | 06:00:00 | 273.15 | 98734 | 2.1 | 30 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
1448 | 3/2 | 07:00:00 | 273.15 | 98734 | 2.1 | 10 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
1449 | 3/2 | 08:00:00 | 273.15 | 98734 | 1.5 | 102 | 3.891 | 97.2 | 39.6 | 257.937 | 0 | 1 | 0
1450 | 3/2 | 09:00:00 | 273.15 | 98734 | 1.5 | 310 | 3.891 | 496.8 | 1022.4 | 257.685 | 0 | 1 | 0
1451 | 3/2 | 10:00:00 | 274.15 | 98743 | 1 | 131 | 3.5803 | 946.8 | 1670.4 | 258.398 | 0 | 1 | 1
1452 | 3/2 | 11:00:00 | 275.15 | 98752 | 1.5 | 176 | 3.5799 | 1314 | 2343.6 | 259.34 | 0 | 1 | 2
1453 | 3/2 | 12:00:00 | 277.15 | 98771 | 2.1 | 30 | 4.8316 | 1530 | 2545.2 | 262.149 | 0 | 1 | 4
1454 | 3/2 | 13:00:00 | 277.15 | 98771 | 1.5 | 47 | 3.0256 | 1598.4 | 2660.4 | 260.755 | 0 | 1 | 4
1455 | 3/2 | 14:00:00 | 278.15 | 98780 | 1 | 251 | 2.7791 | 1483.2 | 2566.8 | 261.457 | 0 | 1 | 5
1456 | 3/2 | 15:00:00 | 278.15 | 98780 | 0.5 | 237 | 2.7791 | 1209.6 | 2289.6 | 261.323 | 0 | 1 | 5
1457 | 3/2 | 16:00:00 | 278.15 | 98780 | 1.5 | 25 | 2.7791 | 795.6 | 1530 | 261.323 | 0 | 1 | 5
1458 | 3/2 | 17:00:00 | 277.15 | 98771 | 1.5 | 238 | 2.7793 | 334.8 | 698.4 | 260.517 | 0 | 1 | 4
1459 | 3/2 | 18:00:00 | 276.15 | 98762 | 1.5 | 90 | 3.0259 | 25.2 | 0 | 260.068 | 0 | 1 | 3
1460 | 3/2 | 19:00:00 | 275.15 | 98752 | 1 | 80 | 3.0262 | 0 | 0 | 259.127 | 0 | 1 | 2
1461 | 3/2 | 20:00:00 | 275.15 | 98752 | 1 | 130 | 2.7799 | 0 | 0 | 258.766 | 0 | 1 | 2
1462 | 3/2 | 21:00:00 | 275.15 | 98752 | 1 | 80 | 3.0262 | 0 | 0 | 259.127 | 0 | 1 | 2
1463 | 3/2 | 22:00:00 | 275.15 | 98752 | 0.5 | 110 | 2.7799 | 0 | 0 | 258.766 | 0 | 1 | 2
1464 | 3/2 | 23:00:00 | 273.15 | 98734 | 1 | 114 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
1465 | 3/2 | 24:00:00 | 272.95 | 98732 | 1.1 | 32 | 2.8282 | 0 | 0 | 256.987 | 0 | 1 | -0.2
1466 | 3/3 | 01:00:00 | 272.85 | 98731 | 1.2 | 240 | 2.8524 | 0 | 0 | 257.032 | 0 | 1 | -0.3
1467 | 3/3 | 02:00:00 | 272.65 | 98729 | 1.2 | 203 | 2.9013 | 0 | 0 | 256.89 | 0 | 1 | -0.5
1468 | 3/3 | 03:00:00 | 272.45 | 98728 | 1.3 | 284 | 2.951 | 0 | 0 | 256.748 | 0 | 1 | -0.7
1469 | 3/3 | 04:00:00 | 272.35 | 98726 | 1.4 | 348 | 2.9762 | 0 | 0 | 256.789 | 0 | 1 | -0.8
1470 | 3/3 | 05:00:00 | 272.15 | 98724 | 1.5 | 120 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1471 | 3/3 | 06:00:00 | 272.15 | 98724 | 0 | 192 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1472 | 3/3 | 07:00:00 | 272.15 | 98724 | 0 | 285 | 2.7806 | 0 | 0 | 255.817 | 0 | 1 | -1
1473 | 3/3 | 08:00:00 | 272.15 | 98724 | 0 | 188 | 3.0271 | 108 | 75.6 | 256.051 | 0 | 1 | -1
1474 | 3/3 | 09:00:00 | 272.15 | 98724 | 0 | 142 | 3.0271 | 342 | 136.8 | 256.647 | 0 | 1 | -1
1475 | 3/3 | 10:00:00 | 273.15 | 98734 | 0 | 303 | 3.0267 | 777.6 | 612 | 257.478 | 0 | 1 | 0
1476 | 3/3 | 11:00:00 | 275.15 | 98752 | 1.5 | 264 | 3.2924 | 1170 | 1245.6 | 259.482 | 0 | 1 | 2
1477 | 3/3 | 12:00:00 | 276.15 | 98762 | 2.6 | 130 | 3.5796 | 1342.8 | 1267.2 | 260.659 | 0 | 1 | 3
1478 | 3/3 | 13:00:00 | 276.15 | 98762 | 2.6 | 150 | 3.5796 | 1620 | 2336.4 | 260.283 | 0 | 1 | 3
1479 | 3/3 | 14:00:00 | 276.15 | 98762 | 3.6 | 120 | 3.5796 | 1497.6 | 2548.8 | 260.283 | 0 | 1 | 3
1480 | 3/3 | 15:00:00 | 276.15 | 98762 | 2.1 | 110 | 3.5796 | 1216.8 | 2224.8 | 260.283 | 0 | 1 | 3
1481 | 3/3 | 16:00:00 | 276.15 | 98762 | 2.6 | 120 | 3.8899 | 806.4 | 1490.4 | 260.515 | 0 | 1 | 3
1482 | 3/3 | 17:00:00 | 276.15 | 98762 | 3.1 | 90 | 3.8899 | 349.2 | 712.8 | 260.515 | 0 | 1 | 3
1483 | 3/3 | 18:00:00 | 275.15 | 98752 | 2.1 | 90 | 3.8903 | 32.4 | 0 | 259.572 | 0 | 1 | 2
1484 | 3/3 | 19:00:00 | 275.15 | 98752 | 2.6 | 80 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
1485 | 3/3 | 20:00:00 | 274.15 | 98743 | 3.1 | 90 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1486 | 3/3 | 21:00:00 | 274.15 | 98743 | 3.6 | 90 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
1487 | 3/3 | 22:00:00 | 273.15 | 98734 | 0 | 272 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
1488 | 3/3 | 23:00:00 | 273.15 | 98734 | 2.1 | 60 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
1489 | 3/3 | 24:00:00 | 273.15 | 98734 | 1.8 | 233 | 3.827 | 0 | 0 | 258.452 | 0 | 1 | 0
1490 | 3/4 | 01:00:00 | 273.15 | 98734 | 1.4 | 276 | 3.7954 | 0 | 0 | 258.429 | 0 | 1 | 0
1491 | 3/4 | 02:00:00 | 273.15 | 98734 | 1 | 105 | 3.7329 | 0 | 0 | 258.383 | 0 | 1 | 0
1492 | 3/4 | 03:00:00 | 273.15 | 98734 | 0.7 | 270 | 3.6713 | 0 | 0 | 258.337 | 0 | 1 | 0
1493 | 3/4 | 04:00:00 | 273.15 | 98734 | 0.3 | 211 | 3.6408 | 0 | 0 | 258.314 | 0 | 1 | 0
1494 | 3/4 | 05:00:00 | 273.15 | 98734 | 0 | 106 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
1495 | 3/4 | 06:00:00 | 273.15 | 98734 | 0 | 340 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
1496 | 3/4 | 07:00:00 | 273.15 | 98734 | 2.1 | 40 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
1497 | 3/4 | 08:00:00 | 273.15 | 98734 | 1.5 | 146 | 3.5806 | 61.2 | 0 | 258.163 | 0 | 1 | 0
1498 | 3/4 | 09:00:00 | 273.15 | 98734 | 1.5 | 20 | 3.5806 | 536.4 | 1090.8 | 257.455 | 0 | 1 | 0
1499 | 3/4 | 10:00:00 | 275.15 | 98752 | 1 | 190 | 3.5799 | 993.6 | 1710 | 259.34 | 0 | 1 | 2
1500 | 3/4 | 11:00:00 | 276.15 | 98762 | 2.1 | 90 | 3.5796 | 1360.8 | 2383.2 | 260.283 | 0 | 1 | 3
1501 | 3/4 | 12:00:00 | 277.15 | 98771 | 1.5 | 16 | 3.5793 | 1587.6 | 2624.4 | 261.225 | 0 | 1 | 4
1502 | 3/4 | 13:00:00 | 277.15 | 98771 | 0 | 36 | 3.5793 | 1641.6 | 2667.6 | 261.225 | 0 | 1 | 4
1503 | 3/4 | 14:00:00 | 277.15 | 98771 | 0 | 81 | 3.2918 | 1522.8 | 2574 | 260.991 | 0 | 1 | 4
1504 | 3/4 | 15:00:00 | 278.15 | 98780 | 1 | 2 | 3.5789 | 1238.4 | 2246.4 | 262.168 | 0 | 1 | 5
1505 | 3/4 | 16:00:00 | 278.15 | 98780 | 1 | 287 | 3.2915 | 828 | 1522.8 | 261.933 | 0 | 1 | 5
1506 | 3/4 | 17:00:00 | 278.15 | 98780 | 1 | 311 | 3.2915 | 363.6 | 748.8 | 261.933 | 0 | 1 | 5
1507 | 3/4 | 18:00:00 | 277.15 | 98771 | 0.5 | 80 | 3.5793 | 36 | 0 | 261.603 | 0 | 1 | 4
1508 | 3/4 | 19:00:00 | 276.15 | 98762 | 0.5 | 70 | 3.2921 | 0 | 0 | 260.304 | 0 | 1 | 3
1509 | 3/4 | 20:00:00 | 276.15 | 98762 | 0.5 | 339 | 3.0259 | 0 | 0 | 260.068 | 0 | 1 | 3
1510 | 3/4 | 21:00:00 | 275.15 | 98752 | 2.1 | 260 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
1511 | 3/4 | 22:00:00 | 273.15 | 98734 | 2.6 | 280 | 3.293 | 0 | 0 | 257.823 | 0 | 1 | 0
1512 | 3/4 | 23:00:00 | 272.15 | 98724 | 3.1 | 280 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1513 | 3/4 | 24:00:00 | 272.15 | 98724 | 3.3 | 188 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1514 | 3/5 | 01:00:00 | 272.15 | 98724 | 3.4 | 282 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1515 | 3/5 | 02:00:00 | 272.15 | 98724 | 3.6 | 333 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1516 | 3/5 | 03:00:00 | 272.15 | 98724 | 3.8 | 136 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1517 | 3/5 | 04:00:00 | 272.15 | 98724 | 3.9 | 321 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1518 | 3/5 | 05:00:00 | 272.15 | 98724 | 4.1 | 290 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1519 | 3/5 | 06:00:00 | 272.15 | 98724 | 4.1 | 290 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1520 | 3/5 | 07:00:00 | 272.15 | 98724 | 4.1 | 290 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1521 | 3/5 | 08:00:00 | 272.15 | 98724 | 4.6 | 290 | 3.0271 | 86.4 | 0 | 256.647 | 0 | 1 | -1
1522 | 3/5 | 09:00:00 | 273.15 | 98734 | 4.6 | 270 | 3.293 | 367.2 | 151.2 | 257.823 | 0 | 1 | 0
1523 | 3/5 | 10:00:00 | 274.15 | 98743 | 4.1 | 260 | 3.5803 | 644.4 | 273.6 | 259 | 0 | 1 | 1
1524 | 3/5 | 11:00:00 | 276.15 | 98762 | 5.7 | 270 | 3.5796 | 1191.6 | 1195.2 | 260.659 | 0 | 1 | 3
1525 | 3/5 | 12:00:00 | 278.15 | 98780 | 5.7 | 280 | 3.5789 | 1540.8 | 2041.2 | 262.425 | 0 | 1 | 5
1526 | 3/5 | 13:00:00 | 279.15 | 98789 | 8.2 | 290 | 3.8889 | 1580.4 | 2239.2 | 263.603 | 0 | 1 | 6
1527 | 3/5 | 14:00:00 | 279.15 | 98789 | 9.3 | 290 | 4.183 | 1396.8 | 1479.6 | 263.959 | 0 | 1 | 6
1528 | 3/5 | 15:00:00 | 279.15 | 98789 | 8.7 | 300 | 4.183 | 1252.8 | 2095.2 | 263.578 | 0 | 1 | 6
1529 | 3/5 | 16:00:00 | 279.15 | 98789 | 8.2 | 300 | 4.4964 | 842.4 | 1738.8 | 263.81 | 0 | 1 | 6
1530 | 3/5 | 17:00:00 | 279.15 | 98789 | 7.7 | 280 | 4.4964 | 378 | 860.4 | 263.81 | 0 | 1 | 6
1531 | 3/5 | 18:00:00 | 278.15 | 98780 | 6.2 | 270 | 4.8311 | 28.8 | 0 | 263.818 | 0 | 1 | 5
1532 | 3/5 | 19:00:00 | 277.15 | 98771 | 5.1 | 280 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
1533 | 3/5 | 20:00:00 | 277.15 | 98771 | 6.7 | 300 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
1534 | 3/5 | 21:00:00 | 278.15 | 98780 | 7.7 | 300 | 4.1834 | 0 | 0 | 262.634 | 0 | 1 | 5
1535 | 3/5 | 22:00:00 | 277.15 | 98771 | 8.2 | 310 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
1536 | 3/5 | 23:00:00 | 278.15 | 98780 | 8.2 | 320 | 4.1834 | 0 | 0 | 262.634 | 0 | 1 | 5
1537 | 3/5 | 24:00:00 | 277.95 | 98778 | 7.7 | 90 | 4.1835 | 0 | 0 | 262.943 | 0 | 1 | 4.8
1538 | 3/6 | 01:00:00 | 277.85 | 98777 | 7.2 | 227 | 4.1835 | 0 | 0 | 262.848 | 0 | 1 | 4.7
1539 | 3/6 | 02:00:00 | 277.65 | 98775 | 6.7 | 359 | 4.1836 | 0 | 0 | 262.659 | 0 | 1 | 4.5
1540 | 3/6 | 03:00:00 | 277.45 | 98774 | 6.1 | 62 | 4.1836 | 0 | 0 | 262.47 | 0 | 1 | 4.3
1541 | 3/6 | 04:00:00 | 277.35 | 98772 | 5.6 | 105 | 4.1837 | 0 | 0 | 262.375 | 0 | 1 | 4.2
1542 | 3/6 | 05:00:00 | 277.15 | 98771 | 5.1 | 320 | 4.1838 | 0 | 0 | 261.946 | 0 | 1 | 4
1543 | 3/6 | 06:00:00 | 277.15 | 98771 | 5.1 | 330 | 4.1838 | 0 | 0 | 262.41 | 0 | 1 | 4
1544 | 3/6 | 07:00:00 | 277.15 | 98771 | 3.6 | 320 | 4.1838 | 0 | 0 | 262.41 | 0 | 1 | 4
1545 | 3/6 | 08:00:00 | 277.15 | 98771 | 2.6 | 310 | 4.4973 | 75.6 | 0 | 262.64 | 0 | 1 | 4
1546 | 3/6 | 09:00:00 | 277.15 | 98771 | 2.1 | 350 | 4.4973 | 302.4 | 7.2 | 262.64 | 0 | 1 | 4
1547 | 3/6 | 10:00:00 | 276.15 | 98762 | 2.1 | 60 | 4.832 | 540 | 50.4 | 261.921 | 0 | 1 | 3
1548 | 3/6 | 11:00:00 | 276.15 | 98762 | 2.1 | 120 | 4.832 | 734.4 | 140.4 | 261.921 | 0 | 1 | 3
1549 | 3/6 | 12:00:00 | 275.15 | 98752 | 2.6 | 130 | 4.4981 | 849.6 | 158.4 | 260.745 | 0 | 1 | 2
1550 | 3/6 | 13:00:00 | 275.15 | 98752 | 2.1 | 110 | 4.4981 | 878.4 | 162 | 260.745 | 0 | 1 | 2
1551 | 3/6 | 14:00:00 | 276.15 | 98762 | 2.1 | 130 | 4.4977 | 813.6 | 154.8 | 261.693 | 0 | 1 | 3
1552 | 3/6 | 15:00:00 | 276.15 | 98762 | 2.1 | 130 | 4.4977 | 666 | 129.6 | 261.693 | 0 | 1 | 3
1553 | 3/6 | 16:00:00 | 276.15 | 98762 | 1 | 139 | 4.4977 | 450 | 32.4 | 261.693 | 0 | 1 | 3
1554 | 3/6 | 17:00:00 | 276.15 | 98762 | 4.1 | 100 | 3.8899 | 205.2 | 0 | 261.231 | 0 | 1 | 3
1555 | 3/6 | 18:00:00 | 276.15 | 98762 | 3.1 | 110 | 3.5796 | 28.8 | 0 | 260.999 | 0 | 1 | 3
1556 | 3/6 | 19:00:00 | 275.15 | 98752 | 2.1 | 110 | 3.2924 | 0 | 0 | 259.107 | 0 | 1 | 2
1557 | 3/6 | 20:00:00 | 274.15 | 98743 | 3.1 | 110 | 3.2927 | 0 | 0 | 258.166 | 0 | 1 | 1
1558 | 3/6 | 21:00:00 | 273.15 | 98734 | 3.1 | 130 | 3.0267 | 0 | 0 | 256.991 | 0 | 1 | 0
1559 | 3/6 | 22:00:00 | 272.15 | 98724 | 2.6 | 130 | 3.0271 | 0 | 0 | 256.051 | 0 | 1 | -1
1560 | 3/6 | 23:00:00 | 270.15 | 98705 | 0 | 214 | 2.7812 | 0 | 0 | 253.937 | 0 | 1 | -3
1561 | 3/6 | 24:00:00 | 269.95 | 98704 | 0 | 329 | 2.7342 | 0 | 0 | 254.401 | 0 | 1 | -3.2
1562 | 3/7 | 01:00:00 | 269.85 | 98702 | 0 | 358 | 2.711 | 0 | 0 | 254.283 | 0 | 1 | -3.3
1563 | 3/7 | 02:00:00 | 269.65 | 98701 | 0 | 70 | 2.6651 | 0 | 0 | 254.048 | 0 | 1 | -3.5
1564 | 3/7 | 03:00:00 | 269.45 | 98699 | 0 | 299 | 2.6199 | 0 | 0 | 253.813 | 0 | 1 | -3.7
1565 | 3/7 | 04:00:00 | 269.35 | 98697 | 0 | 337 | 2.5976 | 0 | 0 | 253.695 | 0 | 1 | -3.8
1566 | 3/7 | 05:00:00 | 269.15 | 98696 | 0 | 277 | 2.5535 | 0 | 0 | 253.46 | 0 | 1 | -4
1567 | 3/7 | 06:00:00 | 269.15 | 98696 | 0 | 270 | 2.3427 | 0 | 0 | 253.12 | 0 | 1 | -4
1568 | 3/7 | 07:00:00 | 269.15 | 98696 | 0 | 46 | 2.5535 | 0 | 0 | 253.46 | 0 | 1 | -4
1569 | 3/7 | 08:00:00 | 268.15 | 98686 | 0 | 65 | 2.343 | 72 | 0 | 252.285 | 0 | 1 | -5
1570 | 3/7 | 09:00:00 | 270.15 | 98705 | 0 | 239 | 2.5532 | 410.4 | 234 | 254.295 | 0 | 1 | -3
1571 | 3/7 | 10:00:00 | 272.15 | 98724 | 0 | 273 | 2.5527 | 957.6 | 1195.2 | 255.952 | 0 | 1 | -1
1572 | 3/7 | 11:00:00 | 273.15 | 98734 | 1 | 5 | 2.7804 | 1274.4 | 1263.6 | 257.128 | 0 | 1 | 0
1573 | 3/7 | 12:00:00 | 274.15 | 98743 | 0.5 | 39 | 3.0265 | 1472.4 | 1342.8 | 258.305 | 0 | 1 | 1
1574 | 3/7 | 13:00:00 | 275.15 | 98752 | 0.5 | 210 | 3.0262 | 1605.6 | 1785.6 | 259.127 | 0 | 1 | 2
1575 | 3/7 | 14:00:00 | 276.15 | 98762 | 1 | 40 | 3.8899 | 1180.8 | 824.4 | 261.122 | 0 | 1 | 3
1576 | 3/7 | 15:00:00 | 276.15 | 98762 | 0 | 126 | 2.7796 | 1292.4 | 1886.4 | 259.706 | 0 | 1 | 3
1577 | 3/7 | 16:00:00 | 277.15 | 98771 | 0 | 358 | 2.7793 | 889.2 | 1594.8 | 260.517 | 0 | 1 | 4
1578 | 3/7 | 17:00:00 | 277.15 | 98771 | 0 | 11 | 2.7793 | 414 | 795.6 | 260.517 | 0 | 1 | 4
1579 | 3/7 | 18:00:00 | 276.15 | 98762 | 0 | 48 | 2.7796 | 57.6 | 0 | 259.706 | 0 | 1 | 3
1580 | 3/7 | 19:00:00 | 274.15 | 98743 | 0.5 | 220 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
1581 | 3/7 | 20:00:00 | 273.15 | 98734 | 0 | 144 | 2.5525 | 0 | 0 | 256.773 | 0 | 1 | 0
1582 | 3/7 | 21:00:00 | 272.15 | 98724 | 0 | 217 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
1583 | 3/7 | 22:00:00 | 272.15 | 98724 | 0 | 313 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
1584 | 3/7 | 23:00:00 | 272.15 | 98724 | 0 | 255 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
1585 | 3/7 | 24:00:00 | 271.65 | 98720 | 0.2 | 165 | 2.9512 | 0 | 0 | 256.106 | 0 | 1 | -1.5
1586 | 3/8 | 01:00:00 | 271.15 | 98715 | 0.3 | 243 | 2.8528 | 0 | 0 | 255.648 | 0 | 1 | -2
1587 | 3/8 | 02:00:00 | 270.65 | 98710 | 0.5 | 322 | 2.781 | 0 | 0 | 255.107 | 0 | 1 | -2.5
1588 | 3/8 | 03:00:00 | 270.15 | 98705 | 0.7 | 295 | 2.7109 | 0 | 0 | 254.566 | 0 | 1 | -3
1589 | 3/8 | 04:00:00 | 269.65 | 98701 | 0.8 | 345 | 2.6199 | 0 | 0 | 254.001 | 0 | 1 | -3.5
1590 | 3/8 | 05:00:00 | 269.15 | 98696 | 1 | 320 | 2.5535 | 0 | 0 | 253.46 | 0 | 1 | -4
1591 | 3/8 | 06:00:00 | 269.15 | 98696 | 1 | 300 | 2.7814 | 0 | 0 | 253.796 | 0 | 1 | -4
1592 | 3/8 | 07:00:00 | 268.15 | 98686 | 1 | 310 | 2.5537 | 0 | 0 | 252.621 | 0 | 1 | -5
1593 | 3/8 | 08:00:00 | 270.15 | 98705 | 1 | 355 | 2.7812 | 79.2 | 0 | 254.636 | 0 | 1 | -3
1594 | 3/8 | 09:00:00 | 272.15 | 98724 | 0.5 | 310 | 3.581 | 198 | 0 | 257.322 | 0 | 1 | -1
1595 | 3/8 | 10:00:00 | 274.15 | 98743 | 0.5 | 289 | 4.185 | 345.6 | 0 | 259.674 | 0 | 1 | 1
1596 | 3/8 | 11:00:00 | 275.15 | 98752 | 1.5 | 166 | 4.4981 | 464.4 | 0 | 260.851 | 0 | 1 | 2
1597 | 3/8 | 12:00:00 | 276.15 | 98762 | 2.1 | 20 | 2.7796 | 1674 | 2048.4 | 259.706 | 0 | 1 | 3
1598 | 3/8 | 13:00:00 | 277.15 | 98771 | 2.1 | 70 | 2.7793 | 1746 | 2761.2 | 260.517 | 0 | 1 | 4
1599 | 3/8 | 14:00:00 | 278.15 | 98780 | 2.1 | 40 | 2.7791 | 1634.4 | 2714.4 | 261.323 | 0 | 1 | 5
1600 | 3/8 | 15:00:00 | 278.15 | 98780 | 2.6 | 60 | 2.3407 | 1350 | 2466 | 260.703 | 0 | 1 | 5
1601 | 3/8 | 16:00:00 | 279.15 | 98789 | 3.1 | 50 | 2.551 | 921.6 | 1684.8 | 261.882 | 0 | 1 | 6
1602 | 3/8 | 17:00:00 | 279.15 | 98789 | 2.6 | 40 | 2.551 | 435.6 | 867.6 | 261.882 | 0 | 1 | 6
1603 | 3/8 | 18:00:00 | 279.15 | 98789 | 2.1 | 70 | 2.7788 | 68.4 | 0 | 262.262 | 0 | 1 | 6
1604 | 3/8 | 19:00:00 | 277.15 | 98771 | 2.1 | 50 | 3.0256 | 0 | 0 | 261.472 | 0 | 1 | 4
1605 | 3/8 | 20:00:00 | 276.15 | 98762 | 2.1 | 40 | 3.0259 | 0 | 0 | 260.068 | 0 | 1 | 3
1606 | 3/8 | 21:00:00 | 275.15 | 98752 | 2.6 | 10 | 2.7799 | 0 | 0 | 258.766 | 0 | 1 | 2
1607 | 3/8 | 22:00:00 | 275.15 | 98752 | 2.6 | 10 | 2.7799 | 0 | 0 | 258.766 | 0 | 1 | 2
1608 | 3/8 | 23:00:00 | 275.15 | 98752 | 2.6 | 360 | 3.0262 | 0 | 0 | 259.69 | 0 | 1 | 2
1609 | 3/8 | 24:00:00 | 275.15 | 98752 | 2.6 | 101 | 3.2375 | 0 | 0 | 259.435 | 0 | 1 | 2
1610 | 3/9 | 01:00:00 | 275.15 | 98752 | 2.6 | 263 | 3.4914 | 0 | 0 | 259.762 | 0 | 1 | 2
1611 | 3/9 | 02:00:00 | 275.15 | 98752 | 2.6 | 48 | 3.7322 | 0 | 0 | 260.061 | 0 | 1 | 2
1612 | 3/9 | 03:00:00 | 275.15 | 98752 | 2.6 | 86 | 3.9769 | 0 | 0 | 260.355 | 0 | 1 | 2
1613 | 3/9 | 04:00:00 | 275.15 | 98752 | 2.6 | 175 | 4.2457 | 0 | 0 | 260.668 | 0 | 1 | 2
1614 | 3/9 | 05:00:00 | 275.15 | 98752 | 2.6 | 10 | 4.4981 | 0 | 0 | 260.285 | 0 | 1 | 2
1615 | 3/9 | 06:00:00 | 275.15 | 98752 | 3.1 | 360 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
1616 | 3/9 | 07:00:00 | 275.15 | 98752 | 2.6 | 10 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
1617 | 3/9 | 08:00:00 | 274.15 | 98743 | 2.1 | 10 | 4.185 | 187.2 | 205.2 | 258.857 | 0 | 1 | 1
1618 | 3/9 | 09:00:00 | 276.15 | 98762 | 3.1 | 20 | 4.1841 | 644.4 | 1148.4 | 260.746 | 0 | 1 | 3
1619 | 3/9 | 10:00:00 | 277.15 | 98771 | 2.6 | 20 | 4.1838 | 1108.8 | 1944 | 261.69 | 0 | 1 | 4
1620 | 3/9 | 11:00:00 | 278.15 | 98780 | 2.1 | 20 | 3.8892 | 1483.2 | 2466 | 262.402 | 0 | 1 | 5
1621 | 3/9 | 12:00:00 | 279.15 | 98789 | 3.1 | 10 | 3.5786 | 1710 | 2109.6 | 263.11 | 0 | 1 | 6
1622 | 3/9 | 13:00:00 | 279.15 | 98789 | 4.1 | 30 | 4.183 | 918 | 583.2 | 264.303 | 0 | 1 | 6
1623 | 3/9 | 14:00:00 | 280.15 | 98798 | 3.6 | 20 | 4.8303 | 1627.2 | 1825.2 | 264.986 | 0 | 1 | 7
1624 | 3/9 | 15:00:00 | 279.15 | 98789 | 4.1 | 20 | 4.8307 | 698.4 | 273.6 | 264.767 | 0 | 1 | 6
1625 | 3/9 | 16:00:00 | 279.15 | 98789 | 4.1 | 20 | 4.8307 | 478.8 | 61.2 | 264.767 | 0 | 1 | 6
1626 | 3/9 | 17:00:00 | 279.15 | 98789 | 3.6 | 20 | 4.8307 | 417.6 | 644.4 | 264.299 | 0 | 1 | 6
1627 | 3/9 | 18:00:00 | 278.15 | 98780 | 2.6 | 20 | 4.8311 | 68.4 | 0 | 263.352 | 0 | 1 | 5
1628 | 3/9 | 19:00:00 | 278.15 | 98780 | 4.1 | 20 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
1629 | 3/9 | 20:00:00 | 276.15 | 98762 | 2.6 | 10 | 4.832 | 0 | 0 | 261.203 | 0 | 1 | 3
1630 | 3/9 | 21:00:00 | 276.15 | 98762 | 3.1 | 10 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
1631 | 3/9 | 22:00:00 | 276.15 | 98762 | 2.6 | 20 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
1632 | 3/9 | 23:00:00 | 276.15 | 98762 | 2.1 | 20 | 4.832 | 0 | 0 | 261.921 | 0 | 1 | 3
1633 | 3/9 | 24:00:00 | 275.95 | 98760 | 2.4 | 289 | 4.7296 | 0 | 0 | 261.769 | 0 | 1 | 2.8
1634 | 3/10 | 01:00:00 | 275.85 | 98758 | 2.6 | 56 | 4.5959 | 0 | 0 | 261.583 | 0 | 1 | 2.7
1635 | 3/10 | 02:00:00 | 275.65 | 98757 | 2.8 | 59 | 4.4979 | 0 | 0 | 261.325 | 0 | 1 | 2.5
1636 | 3/10 | 03:00:00 | 275.45 | 98755 | 3.1 | 264 | 4.4018 | 0 | 0 | 261.067 | 0 | 1 | 2.3
1637 | 3/10 | 04:00:00 | 275.35 | 98754 | 3.3 | 189 | 4.2764 | 0 | 0 | 260.88 | 0 | 1 | 2.2
1638 | 3/10 | 05:00:00 | 275.15 | 98752 | 3.6 | 10 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
1639 | 3/10 | 06:00:00 | 275.15 | 98752 | 3.6 | 10 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
1640 | 3/10 | 07:00:00 | 274.15 | 98743 | 2.1 | 20 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
1641 | 3/10 | 08:00:00 | 275.15 | 98752 | 1 | 55 | 3.8903 | 194.4 | 176.4 | 259.826 | 0 | 1 | 2
1642 | 3/10 | 09:00:00 | 275.15 | 98752 | 1 | 10 | 3.8903 | 626.4 | 1080 | 259.826 | 0 | 1 | 2
1643 | 3/10 | 10:00:00 | 277.15 | 98771 | 0.5 | 109 | 3.8896 | 594 | 68.4 | 262.177 | 0 | 1 | 4
1644 | 3/10 | 11:00:00 | 277.15 | 98771 | 1 | 38 | 4.1838 | 1418.4 | 1616.4 | 261.946 | 0 | 1 | 4
1645 | 3/10 | 12:00:00 | 279.15 | 98789 | 2.6 | 60 | 4.4964 | 1724.4 | 2610 | 263.81 | 0 | 1 | 6
1646 | 3/10 | 13:00:00 | 279.15 | 98789 | 3.6 | 70 | 4.4964 | 1778.4 | 2635.2 | 263.81 | 0 | 1 | 6
1647 | 3/10 | 14:00:00 | 280.15 | 98798 | 2.6 | 40 | 4.1826 | 1558.8 | 1652.4 | 264.782 | 0 | 1 | 7
1648 | 3/10 | 15:00:00 | 279.15 | 98789 | 3.1 | 20 | 3.8889 | 1285.2 | 1468.8 | 263.603 | 0 | 1 | 6
1649 | 3/10 | 16:00:00 | 279.15 | 98789 | 2.6 | 60 | 3.8889 | 889.2 | 1353.6 | 263.603 | 0 | 1 | 6
1650 | 3/10 | 17:00:00 | 279.15 | 98789 | 1 | 227 | 4.183 | 432 | 752.4 | 263.837 | 0 | 1 | 6
1651 | 3/10 | 18:00:00 | 279.15 | 98789 | 0.5 | 290 | 4.183 | 75.6 | 0 | 263.837 | 0 | 1 | 6
1652 | 3/10 | 19:00:00 | 277.15 | 98771 | 0 | 155 | 4.1838 | 0 | 0 | 261.946 | 0 | 1 | 4
1653 | 3/10 | 20:00:00 | 276.15 | 98762 | 0 | 141 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
1654 | 3/10 | 21:00:00 | 276.15 | 98762 | 0 | 348 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
1655 | 3/10 | 22:00:00 | 275.15 | 98752 | 0 | 134 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
1656 | 3/10 | 23:00:00 | 274.15 | 98743 | 0 | 210 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
1657 | 3/10 | 24:00:00 | 273.95 | 98742 | 0.3 | 177 | 3.4917 | 0 | 0 | 258.741 | 0 | 1 | 0.8
1658 | 3/11 | 01:00:00 | 273.85 | 98740 | 0.7 | 6 | 3.3768 | 0 | 0 | 258.554 | 0 | 1 | 0.7
1659 | 3/11 | 02:00:00 | 273.65 | 98739 | 1 | 129 | 3.2929 | 0 | 0 | 258.295 | 0 | 1 | 0.5
1660 | 3/11 | 03:00:00 | 273.45 | 98737 | 1.4 | 149 | 3.2109 | 0 | 0 | 257.925 | 0 | 1 | 0.3
1661 | 3/11 | 04:00:00 | 273.35 | 98735 | 1.8 | 263 | 3.1044 | 0 | 0 | 257.737 | 0 | 1 | 0.2
1662 | 3/11 | 05:00:00 | 273.15 | 98734 | 2.1 | 330 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
1663 | 3/11 | 06:00:00 | 272.15 | 98724 | 2.1 | 320 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
1664 | 3/11 | 07:00:00 | 272.15 | 98724 | 1.5 | 320 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
1665 | 3/11 | 08:00:00 | 272.15 | 98724 | 2.6 | 310 | 3.0271 | 147.6 | 0 | 256.647 | 0 | 1 | -1
1666 | 3/11 | 09:00:00 | 274.15 | 98743 | 1.5 | 176 | 3.2927 | 540 | 478.8 | 258.655 | 0 | 1 | 1
1667 | 3/11 | 10:00:00 | 276.15 | 98762 | 2.6 | 360 | 3.2921 | 1076.4 | 1364.4 | 260.304 | 0 | 1 | 3
1668 | 3/11 | 11:00:00 | 277.15 | 98771 | 1 | 188 | 3.5793 | 1407.6 | 1519.2 | 261.603 | 0 | 1 | 4
1669 | 3/11 | 12:00:00 | 278.15 | 98780 | 1.5 | 128 | 3.5789 | 1756.8 | 2372.4 | 262.168 | 0 | 1 | 5
1670 | 3/11 | 13:00:00 | 279.15 | 98789 | 2.1 | 10 | 3.5786 | 1810.8 | 2764.8 | 263.11 | 0 | 1 | 6
1671 | 3/11 | 14:00:00 | 280.15 | 98798 | 2.6 | 10 | 3.5783 | 1681.2 | 2084.4 | 264.053 | 0 | 1 | 7
1672 | 3/11 | 15:00:00 | 280.15 | 98798 | 1.5 | 5 | 3.5783 | 727.2 | 82.8 | 264.779 | 0 | 1 | 7
1673 | 3/11 | 16:00:00 | 280.15 | 98798 | 3.6 | 320 | 3.5783 | 504 | 50.4 | 264.779 | 0 | 1 | 7
1674 | 3/11 | 17:00:00 | 278.15 | 98780 | 6.2 | 320 | 3.0253 | 478.8 | 990 | 261.696 | 0 | 1 | 5
1675 | 3/11 | 18:00:00 | 278.15 | 98780 | 5.1 | 300 | 3.2915 | 86.4 | 32.4 | 261.933 | 0 | 1 | 5
1676 | 3/11 | 19:00:00 | 277.15 | 98771 | 4.1 | 280 | 3.2918 | 0 | 0 | 260.991 | 0 | 1 | 4
1677 | 3/11 | 20:00:00 | 276.15 | 98762 | 4.1 | 290 | 3.5796 | 0 | 0 | 260.283 | 0 | 1 | 3
1678 | 3/11 | 21:00:00 | 277.15 | 98771 | 6.2 | 280 | 3.5793 | 0 | 0 | 261.481 | 0 | 1 | 4
1679 | 3/11 | 22:00:00 | 277.15 | 98771 | 6.7 | 280 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
1680 | 3/11 | 23:00:00 | 277.15 | 98771 | 7.2 | 270 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
1681 | 3/11 | 24:00:00 | 277.15 | 98771 | 7 | 184 | 4.0345 | 0 | 0 | 262.07 | 0 | 1 | 4
1682 | 3/12 | 01:00:00 | 277.15 | 98771 | 6.9 | 148 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
1683 | 3/12 | 02:00:00 | 277.15 | 98771 | 6.7 | 140 | 4.338 | 0 | 0 | 262.415 | 0 | 1 | 4
1684 | 3/12 | 03:00:00 | 277.15 | 98771 | 6.5 | 33 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
1685 | 3/12 | 04:00:00 | 277.15 | 98771 | 6.4 | 269 | 4.6617 | 0 | 0 | 262.755 | 0 | 1 | 4
1686 | 3/12 | 05:00:00 | 277.15 | 98771 | 6.2 | 300 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
1687 | 3/12 | 06:00:00 | 277.15 | 98771 | 5.7 | 300 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
1688 | 3/12 | 07:00:00 | 277.15 | 98771 | 5.1 | 310 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
1689 | 3/12 | 08:00:00 | 277.15 | 98771 | 4.6 | 320 | 4.4973 | 122.4 | 0 | 262.64 | 0 | 1 | 4
1690 | 3/12 | 09:00:00 | 277.15 | 98771 | 4.1 | 320 | 4.8316 | 370.8 | 25.2 | 262.87 | 0 | 1 | 4
1691 | 3/12 | 10:00:00 | 277.15 | 98771 | 6.7 | 360 | 4.8316 | 615.6 | 57.6 | 262.87 | 0 | 1 | 4
1692 | 3/12 | 11:00:00 | 278.15 | 98780 | 7.2 | 360 | 5.1875 | 810 | 147.6 | 264.047 | 0 | 1 | 5
1693 | 3/12 | 12:00:00 | 279.15 | 98789 | 8.2 | 10 | 5.187 | 925.2 | 162 | 264.996 | 0 | 1 | 6
1694 | 3/12 | 13:00:00 | 279.15 | 98789 | 7.2 | 360 | 4.8307 | 954 | 342 | 264.767 | 0 | 1 | 6
1695 | 3/12 | 14:00:00 | 279.15 | 98789 | 8.2 | 10 | 4.8307 | 1594.8 | 1764 | 264.299 | 0 | 1 | 6
1696 | 3/12 | 15:00:00 | 279.15 | 98789 | 6.2 | 360 | 4.8307 | 1321.2 | 1558.8 | 264.299 | 0 | 1 | 6
1697 | 3/12 | 16:00:00 | 278.15 | 98780 | 5.1 | 10 | 5.1875 | 511.2 | 90 | 264.047 | 0 | 1 | 5
1698 | 3/12 | 17:00:00 | 278.15 | 98780 | 5.1 | 10 | 4.8311 | 460.8 | 698.4 | 263.352 | 0 | 1 | 5
1699 | 3/12 | 18:00:00 | 277.15 | 98771 | 5.7 | 360 | 4.4973 | 86.4 | 0 | 262.177 | 0 | 1 | 4
1700 | 3/12 | 19:00:00 | 277.15 | 98771 | 2.6 | 360 | 4.1838 | 0 | 0 | 261.946 | 0 | 1 | 4
1701 | 3/12 | 20:00:00 | 277.15 | 98771 | 2.1 | 340 | 4.1838 | 0 | 0 | 262.41 | 0 | 1 | 4
1702 | 3/12 | 21:00:00 | 277.15 | 98771 | 2.1 | 350 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
1703 | 3/12 | 22:00:00 | 276.15 | 98762 | 4.6 | 350 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
1704 | 3/12 | 23:00:00 | 276.15 | 98762 | 3.6 | 330 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
1705 | 3/12 | 24:00:00 | 276.15 | 98762 | 3.1 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
1706 | 3/13 | 01:00:00 | 276.15 | 98762 | 2.6 | 330 | 3.8899 | 0 | 0 | 261.231 | 0 | 1 | 3
1707 | 3/13 | 02:00:00 | 275.15 | 98752 | 2.1 | 290 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
1708 | 3/13 | 03:00:00 | 274.15 | 98743 | 1.5 | 280 | 3.5803 | 0 | 0 | 258.398 | 0 | 1 | 1
1709 | 3/13 | 04:00:00 | 273.15 | 98734 | 3.1 | 260 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
1710 | 3/13 | 05:00:00 | 272.15 | 98724 | 2.6 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
1711 | 3/13 | 06:00:00 | 272.15 | 98724 | 2.6 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
1712 | 3/13 | 07:00:00 | 272.15 | 98724 | 3.6 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
1713 | 3/13 | 08:00:00 | 274.15 | 98743 | 3.6 | 260 | 3.5803 | 162 | 0 | 259 | 0 | 1 | 1
1714 | 3/13 | 09:00:00 | 276.15 | 98762 | 5.1 | 260 | 4.1841 | 730.8 | 1378.8 | 260.746 | 0 | 1 | 3
1715 | 3/13 | 10:00:00 | 277.15 | 98771 | 5.7 | 270 | 4.4973 | 1202.4 | 2005.2 | 261.92 | 0 | 1 | 4
1716 | 3/13 | 11:00:00 | 277.15 | 98771 | 7.2 | 270 | 4.8316 | 1573.2 | 2491.2 | 262.149 | 0 | 1 | 4
1717 | 3/13 | 12:00:00 | 278.15 | 98780 | 7.2 | 280 | 4.8311 | 1692 | 2145.6 | 263.352 | 0 | 1 | 5
1718 | 3/13 | 13:00:00 | 280.15 | 98798 | 6.7 | 270 | 4.8303 | 1843.2 | 2653.2 | 264.986 | 0 | 1 | 7
1719 | 3/13 | 14:00:00 | 281.15 | 98806 | 6.7 | 270 | 4.8299 | 1717.2 | 2649.6 | 265.932 | 0 | 1 | 8
1720 | 3/13 | 15:00:00 | 281.15 | 98806 | 7.2 | 280 | 4.8299 | 1422 | 2196 | 265.932 | 0 | 1 | 8
1721 | 3/13 | 16:00:00 | 281.15 | 98806 | 6.7 | 280 | 4.8299 | 939.6 | 1281.6 | 266.193 | 0 | 1 | 8
1722 | 3/13 | 17:00:00 | 280.15 | 98798 | 6.2 | 270 | 5.1865 | 262.8 | 0 | 265.946 | 0 | 1 | 7
1723 | 3/13 | 18:00:00 | 279.15 | 98789 | 6.2 | 280 | 5.187 | 90 | 7.2 | 264.528 | 0 | 1 | 6
1724 | 3/13 | 19:00:00 | 278.15 | 98780 | 6.2 | 260 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
1725 | 3/13 | 20:00:00 | 277.15 | 98771 | 7.2 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
1726 | 3/13 | 21:00:00 | 277.15 | 98771 | 6.7 | 290 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
1727 | 3/13 | 22:00:00 | 277.15 | 98771 | 3.1 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
1728 | 3/13 | 23:00:00 | 277.15 | 98771 | 6.2 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
1729 | 3/13 | 24:00:00 | 277.15 | 98771 | 5.7 | 290 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
1730 | 3/14 | 01:00:00 | 276.15 | 98762 | 6.7 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
1731 | 3/14 | 02:00:00 | 276.15 | 98762 | 8.2 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
1732 | 3/14 | 03:00:00 | 277.15 | 98771 | 8.7 | 280 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
1733 | 3/14 | 04:00:00 | 276.15 | 98762 | 7.7 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
1734 | 3/14 | 05:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
1735 | 3/14 | 06:00:00 | 276.15 | 98762 | 6.2 | 280 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
1736 | 3/14 | 07:00:00 | 276.15 | 98762 | 6.7 | 280 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
1737 | 3/14 | 08:00:00 | 276.15 | 98762 | 6.2 | 280 | 4.4977 | 273.6 | 432 | 260.975 | 0 | 1 | 3
1738 | 3/14 | 09:00:00 | 277.15 | 98771 | 8.2 | 270 | 4.8316 | 752.4 | 1501.2 | 262.149 | 0 | 1 | 4
1739 | 3/14 | 10:00:00 | 279.15 | 98789 | 7.7 | 280 | 5.187 | 1224 | 2030.4 | 264.269 | 0 | 1 | 6
1740 | 3/14 | 11:00:00 | 280.15 | 98798 | 8.7 | 300 | 4.8303 | 1598.4 | 2505.6 | 264.986 | 0 | 1 | 7
1741 | 3/14 | 12:00:00 | 281.15 | 98806 | 8.7 | 290 | 4.8299 | 1821.6 | 2635.2 | 265.932 | 0 | 1 | 8
1742 | 3/14 | 13:00:00 | 283.15 | 98824 | 8.2 | 290 | 5.1851 | 1756.8 | 2260.8 | 268.319 | 0 | 1 | 10
1743 | 3/14 | 14:00:00 | 283.15 | 98824 | 9.8 | 300 | 4.4948 | 1641.6 | 1918.8 | 267.852 | 0 | 1 | 10
1744 | 3/14 | 15:00:00 | 283.15 | 98824 | 8.7 | 300 | 4.829 | 1360.8 | 1951.2 | 268.086 | 0 | 1 | 10
1745 | 3/14 | 16:00:00 | 283.15 | 98824 | 8.2 | 270 | 5.1851 | 957.6 | 1522.8 | 268.319 | 0 | 1 | 10
1746 | 3/14 | 17:00:00 | 282.15 | 98815 | 7.7 | 310 | 5.1856 | 493.2 | 943.2 | 267.371 | 0 | 1 | 9
1747 | 3/14 | 18:00:00 | 280.15 | 98798 | 3.6 | 280 | 5.1865 | 104.4 | 54 | 265.216 | 0 | 1 | 7
1748 | 3/14 | 19:00:00 | 280.15 | 98798 | 5.1 | 280 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
1749 | 3/14 | 20:00:00 | 279.15 | 98789 | 7.2 | 280 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
1750 | 3/14 | 21:00:00 | 279.15 | 98789 | 6.7 | 280 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
1751 | 3/14 | 22:00:00 | 278.15 | 98780 | 6.2 | 280 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
1752 | 3/14 | 23:00:00 | 279.15 | 98789 | 6.7 | 280 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
1753 | 3/14 | 24:00:00 | 278.95 | 98787 | 7 | 168 | 5.114 | 0 | 0 | 264.761 | 0 | 1 | 5.8
1754 | 3/15 | 01:00:00 | 278.85 | 98786 | 7.2 | 257 | 5.0779 | 0 | 0 | 264.643 | 0 | 1 | 5.7
1755 | 3/15 | 02:00:00 | 278.65 | 98784 | 7.4 | 166 | 5.0063 | 0 | 0 | 264.407 | 0 | 1 | 5.5
1756 | 3/15 | 03:00:00 | 278.45 | 98783 | 7.7 | 62 | 4.9355 | 0 | 0 | 264.172 | 0 | 1 | 5.3
1757 | 3/15 | 04:00:00 | 278.35 | 98781 | 7.9 | 61 | 4.9005 | 0 | 0 | 264.054 | 0 | 1 | 5.2
1758 | 3/15 | 05:00:00 | 278.15 | 98780 | 8.2 | 270 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
1759 | 3/15 | 06:00:00 | 278.15 | 98780 | 6.7 | 270 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
1760 | 3/15 | 07:00:00 | 277.15 | 98771 | 6.7 | 260 | 4.8316 | 3.6 | 0 | 262.149 | 0 | 1 | 4
1761 | 3/15 | 08:00:00 | 278.15 | 98780 | 9.3 | 270 | 4.8311 | 273.6 | 601.2 | 263.352 | 0 | 1 | 5
1762 | 3/15 | 09:00:00 | 278.15 | 98780 | 7.7 | 270 | 5.1875 | 403.2 | 39.6 | 264.047 | 0 | 1 | 5
1763 | 3/15 | 10:00:00 | 279.15 | 98789 | 10.8 | 270 | 5.187 | 651.6 | 61.2 | 264.996 | 0 | 1 | 6
1764 | 3/15 | 11:00:00 | 279.15 | 98789 | 8.2 | 260 | 5.187 | 846 | 151.2 | 264.996 | 0 | 1 | 6
1765 | 3/15 | 12:00:00 | 280.15 | 98798 | 6.2 | 270 | 5.1865 | 961.2 | 338.4 | 265.946 | 0 | 1 | 7
1766 | 3/15 | 13:00:00 | 280.15 | 98798 | 9.3 | 280 | 5.1865 | 1778.4 | 1836 | 265.476 | 0 | 1 | 7
1767 | 3/15 | 14:00:00 | 280.15 | 98798 | 10.8 | 280 | 4.8303 | 1760.4 | 2599.2 | 264.986 | 0 | 1 | 7
1768 | 3/15 | 15:00:00 | 280.15 | 98798 | 9.3 | 270 | 4.8303 | 1465.2 | 2394 | 264.986 | 0 | 1 | 7
1769 | 3/15 | 16:00:00 | 280.15 | 98798 | 10.3 | 280 | 4.496 | 1036.8 | 1857.6 | 264.755 | 0 | 1 | 7
1770 | 3/15 | 17:00:00 | 280.15 | 98798 | 11.8 | 270 | 4.8303 | 540 | 1180.8 | 264.986 | 0 | 1 | 7
1771 | 3/15 | 18:00:00 | 279.15 | 98789 | 9.3 | 270 | 4.8307 | 108 | 93.6 | 264.041 | 0 | 1 | 6
1772 | 3/15 | 19:00:00 | 279.15 | 98789 | 9.3 | 280 | 4.4964 | 0 | 0 | 263.81 | 0 | 1 | 6
1773 | 3/15 | 20:00:00 | 278.15 | 98780 | 6.7 | 290 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
1774 | 3/15 | 21:00:00 | 278.15 | 98780 | 9.3 | 280 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
1775 | 3/15 | 22:00:00 | 278.15 | 98780 | 7.2 | 280 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
1776 | 3/15 | 23:00:00 | 278.15 | 98780 | 6.2 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
1777 | 3/15 | 24:00:00 | 277.95 | 98778 | 5.8 | 154 | 4.9007 | 0 | 0 | 263.674 | 0 | 1 | 4.8
1778 | 3/16 | 01:00:00 | 277.85 | 98777 | 5.3 | 280 | 4.9358 | 0 | 0 | 263.602 | 0 | 1 | 4.7
1779 | 3/16 | 02:00:00 | 277.65 | 98775 | 4.9 | 100 | 5.0067 | 0 | 0 | 263.565 | 0 | 1 | 4.5
1780 | 3/16 | 03:00:00 | 277.45 | 98774 | 4.5 | 37 | 5.0785 | 0 | 0 | 263.421 | 0 | 1 | 4.3
1781 | 3/16 | 04:00:00 | 277.35 | 98772 | 4 | 288 | 5.1148 | 0 | 0 | 263.349 | 0 | 1 | 4.2
1782 | 3/16 | 05:00:00 | 277.15 | 98771 | 3.6 | 260 | 5.1879 | 0 | 0 | 262.633 | 0 | 1 | 4
1783 | 3/16 | 06:00:00 | 277.15 | 98771 | 3.6 | 260 | 5.1879 | 0 | 0 | 262.633 | 0 | 1 | 4
1784 | 3/16 | 07:00:00 | 276.15 | 98762 | 3.1 | 290 | 4.832 | 10.8 | 0 | 261.203 | 0 | 1 | 3
1785 | 3/16 | 08:00:00 | 277.15 | 98771 | 3.1 | 270 | 5.1879 | 162 | 0 | 263.098 | 0 | 1 | 4
1786 | 3/16 | 09:00:00 | 278.15 | 98780 | 6.2 | 260 | 5.1875 | 795.6 | 1242 | 263.323 | 0 | 1 | 5
1787 | 3/16 | 10:00:00 | 279.15 | 98789 | 5.7 | 270 | 5.187 | 1274.4 | 2181.6 | 264.269 | 0 | 1 | 6
1788 | 3/16 | 11:00:00 | 280.15 | 98798 | 3.6 | 270 | 5.1865 | 1645.2 | 2520 | 265.216 | 0 | 1 | 7
1789 | 3/16 | 12:00:00 | 282.15 | 98815 | 2.6 | 260 | 4.8294 | 1760.4 | 1836 | 267.139 | 0 | 1 | 9
1790 | 3/16 | 13:00:00 | 282.15 | 98815 | 2.6 | 96 | 4.4952 | 1004.4 | 349.2 | 267.379 | 0 | 1 | 9
1791 | 3/16 | 14:00:00 | 282.15 | 98815 | 3.1 | 230 | 4.1819 | 936 | 165.6 | 267.144 | 0 | 1 | 9
1792 | 3/16 | 15:00:00 | 282.15 | 98815 | 3.6 | 240 | 3.8878 | 1407.6 | 1587.6 | 266.436 | 0 | 1 | 9
1793 | 3/16 | 16:00:00 | 282.15 | 98815 | 2.1 | 160 | 4.1819 | 1058.4 | 1591.2 | 266.411 | 0 | 1 | 9
1794 | 3/16 | 17:00:00 | 282.15 | 98815 | 3.6 | 180 | 3.8878 | 558 | 997.2 | 266.175 | 0 | 1 | 9
1795 | 3/16 | 18:00:00 | 281.15 | 98806 | 3.6 | 200 | 3.8882 | 115.2 | 64.8 | 265.232 | 0 | 1 | 8
1796 | 3/16 | 19:00:00 | 280.15 | 98798 | 2.1 | 200 | 3.5783 | 0 | 0 | 264.053 | 0 | 1 | 7
1797 | 3/16 | 20:00:00 | 279.15 | 98789 | 3.1 | 180 | 3.8889 | 0 | 0 | 263.603 | 0 | 1 | 6
1798 | 3/16 | 21:00:00 | 279.15 | 98789 | 3.1 | 190 | 3.8889 | 0 | 0 | 263.603 | 0 | 1 | 6
1799 | 3/16 | 22:00:00 | 278.15 | 98780 | 3.6 | 180 | 3.8892 | 0 | 0 | 262.781 | 0 | 1 | 5
1800 | 3/16 | 23:00:00 | 278.15 | 98780 | 3.1 | 200 | 3.8892 | 0 | 0 | 262.781 | 0 | 1 | 5
1801 | 3/16 | 24:00:00 | 278.35 | 98781 | 3.1 | 201 | 3.9468 | 0 | 0 | 263.017 | 0 | 1 | 5.2
1802 | 3/17 | 01:00:00 | 278.45 | 98783 | 3.1 | 231 | 3.9756 | 0 | 0 | 263.134 | 0 | 1 | 5.3
1803 | 3/17 | 02:00:00 | 278.65 | 98784 | 3.1 | 143 | 4.0339 | 0 | 0 | 263.37 | 0 | 1 | 5.5
1804 | 3/17 | 03:00:00 | 278.85 | 98786 | 3.1 | 87 | 4.093 | 0 | 0 | 263.606 | 0 | 1 | 5.7
1805 | 3/17 | 04:00:00 | 278.95 | 98787 | 3.1 | 35 | 4.1228 | 0 | 0 | 263.724 | 0 | 1 | 5.8
1806 | 3/17 | 05:00:00 | 279.15 | 98789 | 3.1 | 210 | 4.183 | 0 | 0 | 264.303 | 0 | 1 | 6
1807 | 3/17 | 06:00:00 | 279.15 | 98789 | 3.1 | 240 | 4.4964 | 0 | 0 | 264.069 | 0 | 1 | 6
1808 | 3/17 | 07:00:00 | 279.15 | 98789 | 5.7 | 220 | 4.4964 | 10.8 | 0 | 264.536 | 0 | 1 | 6
1809 | 3/17 | 08:00:00 | 280.15 | 98798 | 4.1 | 220 | 4.8303 | 306 | 417.6 | 265.246 | 0 | 1 | 7
1810 | 3/17 | 09:00:00 | 280.15 | 98798 | 4.1 | 230 | 5.1865 | 774 | 1357.2 | 265.476 | 0 | 1 | 7
1811 | 3/17 | 10:00:00 | 282.15 | 98815 | 4.1 | 230 | 5.5651 | 1220.4 | 1468.8 | 267.601 | 0 | 1 | 9
1812 | 3/17 | 11:00:00 | 282.15 | 98815 | 7.7 | 240 | 5.9692 | 871.2 | 147.6 | 268.304 | 0 | 1 | 9
1813 | 3/17 | 12:00:00 | 283.15 | 98824 | 7.2 | 250 | 5.9687 | 986.4 | 165.6 | 269.255 | 0 | 1 | 10
1814 | 3/17 | 13:00:00 | 284.15 | 98833 | 5.1 | 240 | 5.9681 | 1008 | 165.6 | 270.206 | 0 | 1 | 11
1815 | 3/17 | 14:00:00 | 285.15 | 98841 | 6.2 | 250 | 5.9676 | 939.6 | 327.6 | 271.157 | 0 | 1 | 12
1816 | 3/17 | 15:00:00 | 286.15 | 98850 | 6.2 | 250 | 5.5631 | 1501.2 | 1915.2 | 271.13 | 0 | 1 | 13
1817 | 3/17 | 16:00:00 | 285.15 | 98841 | 7.7 | 250 | 5.1842 | 1072.8 | 1872 | 269.95 | 0 | 1 | 12
1818 | 3/17 | 17:00:00 | 285.15 | 98841 | 6.7 | 240 | 5.1842 | 572.4 | 1188 | 269.95 | 0 | 1 | 12
1819 | 3/17 | 18:00:00 | 285.15 | 98841 | 4.6 | 240 | 4.8281 | 126 | 154.8 | 269.716 | 0 | 1 | 12
1820 | 3/17 | 19:00:00 | 283.15 | 98824 | 0 | 20 | 5.5646 | 0 | 0 | 268.675 | 0 | 1 | 10
1821 | 3/17 | 20:00:00 | 283.15 | 98824 | 2.6 | 220 | 5.5646 | 0 | 0 | 268.675 | 0 | 1 | 10
1822 | 3/17 | 21:00:00 | 282.15 | 98815 | 1 | 223 | 5.5651 | 0 | 0 | 267.846 | 0 | 1 | 9
1823 | 3/17 | 22:00:00 | 282.15 | 98815 | 5.7 | 220 | 5.5651 | 0 | 0 | 267.846 | 0 | 1 | 9
1824 | 3/17 | 23:00:00 | 282.15 | 98815 | 3.1 | 230 | 5.5651 | 0 | 0 | 267.846 | 0 | 1 | 9
1825 | 3/17 | 24:00:00 | 282.15 | 98815 | 4.6 | 220 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
1826 | 3/18 | 01:00:00 | 282.15 | 98815 | 4 | 115 | 5.6439 | 0 | 0 | 267.892 | 0 | 1 | 9
1827 | 3/18 | 02:00:00 | 282.15 | 98815 | 3.4 | 4 | 5.7237 | 0 | 0 | 267.938 | 0 | 1 | 9
1828 | 3/18 | 03:00:00 | 282.15 | 98815 | 2.7 | 221 | 5.8045 | 0 | 0 | 267.984 | 0 | 1 | 9
1829 | 3/18 | 04:00:00 | 282.15 | 98815 | 2.1 | 161 | 5.8864 | 0 | 0 | 268.029 | 0 | 1 | 9
1830 | 3/18 | 05:00:00 | 282.15 | 98815 | 1.5 | 355 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
1831 | 3/18 | 06:00:00 | 281.15 | 98806 | 2.1 | 160 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
1832 | 3/18 | 07:00:00 | 280.15 | 98798 | 3.1 | 140 | 5.5661 | 28.8 | 0 | 265.444 | 0 | 1 | 7
1833 | 3/18 | 08:00:00 | 280.15 | 98798 | 4.1 | 130 | 5.9703 | 349.2 | 763.2 | 265.247 | 0 | 1 | 7
1834 | 3/18 | 09:00:00 | 281.15 | 98806 | 4.1 | 140 | 5.9698 | 838.8 | 1641.6 | 266.62 | 0 | 1 | 8
1835 | 3/18 | 10:00:00 | 283.15 | 98824 | 3.6 | 150 | 5.9687 | 1335.6 | 2304 | 268.088 | 0 | 1 | 10
1836 | 3/18 | 11:00:00 | 286.15 | 98850 | 4.1 | 210 | 5.1837 | 1692 | 2545.2 | 270.896 | 0 | 1 | 13
1837 | 3/18 | 12:00:00 | 288.15 | 98867 | 4.6 | 200 | 5.1829 | 1933.2 | 2822.4 | 272.649 | 0 | 1 | 15
1838 | 3/18 | 13:00:00 | 287.15 | 98858 | 8.7 | 220 | 5.1833 | 1969.2 | 2822.4 | 271.843 | 0 | 1 | 14
1839 | 3/18 | 14:00:00 | 286.15 | 98850 | 7.2 | 220 | 5.1837 | 1825.2 | 2692.8 | 270.896 | 0 | 1 | 13
1840 | 3/18 | 15:00:00 | 285.15 | 98841 | 8.2 | 200 | 5.5636 | 1522.8 | 2257.2 | 270.182 | 0 | 1 | 12
1841 | 3/18 | 16:00:00 | 285.15 | 98841 | 6.2 | 200 | 5.9676 | 1026 | 1558.8 | 270.678 | 0 | 1 | 12
1842 | 3/18 | 17:00:00 | 284.15 | 98833 | 5.7 | 190 | 5.9681 | 586.8 | 1198.8 | 269.465 | 0 | 1 | 11
1843 | 3/18 | 18:00:00 | 284.15 | 98833 | 7.7 | 190 | 5.9681 | 129.6 | 111.6 | 269.728 | 0 | 1 | 11
1844 | 3/18 | 19:00:00 | 284.15 | 98833 | 6.2 | 200 | 5.9681 | 0 | 0 | 270.206 | 0 | 1 | 11
1845 | 3/18 | 20:00:00 | 284.15 | 98833 | 5.1 | 200 | 5.5641 | 0 | 0 | 269.975 | 0 | 1 | 11
1846 | 3/18 | 21:00:00 | 283.15 | 98824 | 5.1 | 220 | 6.3988 | 0 | 0 | 269.483 | 0 | 1 | 10
1847 | 3/18 | 22:00:00 | 282.15 | 98815 | 8.7 | 210 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
1848 | 3/18 | 23:00:00 | 282.15 | 98815 | 9.3 | 220 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
1849 | 3/18 | 24:00:00 | 281.95 | 98814 | 8.4 | 223 | 6.181 | 0 | 0 | 268.115 | 0 | 1 | 8.8
1850 | 3/19 | 01:00:00 | 281.85 | 98812 | 7.6 | 141 | 5.9694 | 0 | 0 | 267.906 | 0 | 1 | 8.7
1851 | 3/19 | 02:00:00 | 281.65 | 98811 | 6.7 | 70 | 5.7642 | 0 | 0 | 267.602 | 0 | 1 | 8.5
1852 | 3/19 | 03:00:00 | 281.45 | 98809 | 5.8 | 262 | 5.5654 | 0 | 0 | 267.181 | 0 | 1 | 8.3
1853 | 3/19 | 04:00:00 | 281.35 | 98808 | 5 | 64 | 5.3727 | 0 | 0 | 266.972 | 0 | 1 | 8.2
1854 | 3/19 | 05:00:00 | 281.15 | 98806 | 4.1 | 220 | 5.1861 | 0 | 0 | 266.895 | 0 | 1 | 8
1855 | 3/19 | 06:00:00 | 281.15 | 98806 | 4.6 | 230 | 4.8299 | 0 | 0 | 266.664 | 0 | 1 | 8
1856 | 3/19 | 07:00:00 | 280.15 | 98798 | 3.6 | 240 | 4.8303 | 36 | 0 | 264.986 | 0 | 1 | 7
1857 | 3/19 | 08:00:00 | 280.15 | 98798 | 5.7 | 230 | 4.8303 | 363.6 | 759.6 | 264.986 | 0 | 1 | 7
1858 | 3/19 | 09:00:00 | 281.15 | 98806 | 4.1 | 230 | 4.8299 | 867.6 | 1692 | 265.932 | 0 | 1 | 8
1859 | 3/19 | 10:00:00 | 283.15 | 98824 | 9.3 | 250 | 4.829 | 1346.4 | 2257.2 | 267.824 | 0 | 1 | 10
1860 | 3/19 | 11:00:00 | 283.15 | 98824 | 9.8 | 260 | 4.4948 | 1623.6 | 2084.4 | 267.852 | 0 | 1 | 10
1861 | 3/19 | 12:00:00 | 284.15 | 98833 | 7.2 | 250 | 4.4944 | 1944 | 2671.2 | 268.535 | 0 | 1 | 11
1862 | 3/19 | 13:00:00 | 284.15 | 98833 | 8.2 | 250 | 4.1811 | 1990.8 | 2826 | 268.3 | 0 | 1 | 11
1863 | 3/19 | 14:00:00 | 285.15 | 98841 | 7.7 | 250 | 4.1808 | 1854 | 2739.6 | 269.244 | 0 | 1 | 12
1864 | 3/19 | 15:00:00 | 284.15 | 98833 | 5.7 | 250 | 4.4944 | 1551.6 | 2451.6 | 268.535 | 0 | 1 | 11
1865 | 3/19 | 16:00:00 | 283.15 | 98824 | 5.7 | 260 | 4.829 | 1112.4 | 1911.6 | 267.824 | 0 | 1 | 10
1866 | 3/19 | 17:00:00 | 282.15 | 98815 | 3.1 | 260 | 5.1856 | 604.8 | 1234.8 | 267.11 | 0 | 1 | 9
1867 | 3/19 | 18:00:00 | 282.15 | 98815 | 1 | 225 | 5.1856 | 147.6 | 241.2 | 267.11 | 0 | 1 | 9
1868 | 3/19 | 19:00:00 | 281.15 | 98806 | 0 | 66 | 5.1861 | 0 | 0 | 266.163 | 0 | 1 | 8
1869 | 3/19 | 20:00:00 | 281.15 | 98806 | 0 | 342 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
1870 | 3/19 | 21:00:00 | 280.15 | 98798 | 0 | 239 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
1871 | 3/19 | 22:00:00 | 280.15 | 98798 | 2.1 | 80 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
1872 | 3/19 | 23:00:00 | 279.15 | 98789 | 1.5 | 40 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
1873 | 3/19 | 24:00:00 | 278.95 | 98787 | 1.6 | 250 | 5.8881 | 0 | 0 | 265.323 | 0 | 1 | 5.8
1874 | 3/20 | 01:00:00 | 278.85 | 98786 | 1.7 | 117 | 5.8471 | 0 | 0 | 265.205 | 0 | 1 | 5.7
1875 | 3/20 | 02:00:00 | 278.65 | 98784 | 1.8 | 226 | 5.7658 | 0 | 0 | 264.97 | 0 | 1 | 5.5
1876 | 3/20 | 03:00:00 | 278.45 | 98783 | 1.9 | 262 | 5.6856 | 0 | 0 | 264.735 | 0 | 1 | 5.3
1877 | 3/20 | 04:00:00 | 278.35 | 98781 | 2 | 357 | 5.6459 | 0 | 0 | 264.617 | 0 | 1 | 5.2
1878 | 3/20 | 05:00:00 | 278.15 | 98780 | 2.1 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1879 | 3/20 | 06:00:00 | 278.15 | 98780 | 2.1 | 50 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1880 | 3/20 | 07:00:00 | 278.15 | 98780 | 1.5 | 210 | 5.5671 | 21.6 | 0 | 264.274 | 0 | 1 | 5
1881 | 3/20 | 08:00:00 | 278.15 | 98780 | 1.5 | 60 | 5.5671 | 198 | 0 | 264.274 | 0 | 1 | 5
1882 | 3/20 | 09:00:00 | 278.15 | 98780 | 1.5 | 297 | 5.5671 | 464.4 | 32.4 | 264.274 | 0 | 1 | 5
1883 | 3/20 | 10:00:00 | 278.15 | 98780 | 2.1 | 30 | 5.5671 | 716.4 | 64.8 | 264.274 | 0 | 1 | 5
1884 | 3/20 | 11:00:00 | 279.15 | 98789 | 2.1 | 20 | 5.9708 | 907.2 | 154.8 | 265.451 | 0 | 1 | 6
1885 | 3/20 | 12:00:00 | 279.15 | 98789 | 2.1 | 30 | 5.9708 | 1022.4 | 165.6 | 265.451 | 0 | 1 | 6
1886 | 3/20 | 13:00:00 | 279.15 | 98789 | 4.6 | 10 | 5.9708 | 1044 | 230.4 | 265.451 | 0 | 1 | 6
1887 | 3/20 | 14:00:00 | 279.15 | 98789 | 5.1 | 10 | 5.9708 | 972 | 162 | 265.451 | 0 | 1 | 6
1888 | 3/20 | 15:00:00 | 279.15 | 98789 | 6.2 | 10 | 5.9708 | 817.2 | 144 | 265.451 | 0 | 1 | 6
1889 | 3/20 | 16:00:00 | 279.15 | 98789 | 5.7 | 20 | 5.9708 | 590.4 | 50.4 | 265.451 | 0 | 1 | 6
1890 | 3/20 | 17:00:00 | 278.15 | 98780 | 4.1 | 20 | 5.5671 | 324 | 10.8 | 264.274 | 0 | 1 | 5
1891 | 3/20 | 18:00:00 | 278.15 | 98780 | 4.6 | 350 | 5.5671 | 82.8 | 0 | 264.274 | 0 | 1 | 5
1892 | 3/20 | 19:00:00 | 278.15 | 98780 | 3.6 | 360 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
1893 | 3/20 | 20:00:00 | 278.15 | 98780 | 3.6 | 360 | 5.5671 | 0 | 0 | 263.807 | 0 | 1 | 5
1894 | 3/20 | 21:00:00 | 278.15 | 98780 | 1.5 | 350 | 5.1875 | 0 | 0 | 263.323 | 0 | 1 | 5
1895 | 3/20 | 22:00:00 | 277.15 | 98771 | 3.6 | 330 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
1896 | 3/20 | 23:00:00 | 276.15 | 98762 | 2.1 | 320 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
1897 | 3/20 | 24:00:00 | 275.85 | 98758 | 2.3 | 235 | 4.4335 | 0 | 0 | 261.469 | 0 | 1 | 2.7
1898 | 3/21 | 01:00:00 | 275.45 | 98755 | 2.4 | 322 | 4.4018 | 0 | 0 | 261.067 | 0 | 1 | 2.3
1899 | 3/21 | 02:00:00 | 275.15 | 98752 | 2.6 | 63 | 4.3388 | 0 | 0 | 260.736 | 0 | 1 | 2
1900 | 3/21 | 03:00:00 | 274.85 | 98749 | 2.8 | 264 | 4.2767 | 0 | 0 | 260.406 | 0 | 1 | 1.7
1901 | 3/21 | 04:00:00 | 274.45 | 98746 | 2.9 | 333 | 4.2459 | 0 | 0 | 260.004 | 0 | 1 | 1.3
1902 | 3/21 | 05:00:00 | 274.15 | 98743 | 3.1 | 270 | 4.185 | 0 | 0 | 259.674 | 0 | 1 | 1
1903 | 3/21 | 06:00:00 | 274.15 | 98743 | 3.1 | 270 | 4.185 | 0 | 0 | 259.674 | 0 | 1 | 1
1904 | 3/21 | 07:00:00 | 275.15 | 98752 | 3.1 | 260 | 4.1846 | 21.6 | 0 | 260.622 | 0 | 1 | 2
1905 | 3/21 | 08:00:00 | 275.15 | 98752 | 2.6 | 250 | 4.1846 | 403.2 | 777.6 | 259.802 | 0 | 1 | 2
1906 | 3/21 | 09:00:00 | 276.15 | 98762 | 2.1 | 250 | 4.4977 | 478.8 | 57.6 | 261.693 | 0 | 1 | 3
1907 | 3/21 | 10:00:00 | 277.15 | 98771 | 4.1 | 240 | 5.1879 | 727.2 | 270 | 263.098 | 0 | 1 | 4
1908 | 3/21 | 11:00:00 | 280.15 | 98798 | 4.1 | 250 | 5.5661 | 1760.4 | 2077.2 | 265.444 | 0 | 1 | 7
1909 | 3/21 | 12:00:00 | 282.15 | 98815 | 4.6 | 250 | 5.5651 | 1864.8 | 2206.8 | 267.601 | 0 | 1 | 9
1910 | 3/21 | 13:00:00 | 282.15 | 98815 | 5.1 | 250 | 5.1856 | 1908 | 2264.4 | 267.371 | 0 | 1 | 9
1911 | 3/21 | 14:00:00 | 283.15 | 98824 | 5.7 | 250 | 4.829 | 1890 | 2430 | 267.824 | 0 | 1 | 10
1912 | 3/21 | 15:00:00 | 283.15 | 98824 | 5.1 | 260 | 5.1851 | 1494 | 1645.2 | 268.319 | 0 | 1 | 10
1913 | 3/21 | 16:00:00 | 283.15 | 98824 | 2.6 | 210 | 5.1851 | 601.2 | 216 | 268.793 | 0 | 1 | 10
1914 | 3/21 | 17:00:00 | 283.15 | 98824 | 4.1 | 220 | 5.1851 | 601.2 | 842.4 | 268.319 | 0 | 1 | 10
1915 | 3/21 | 18:00:00 | 283.15 | 98824 | 2.6 | 190 | 5.5646 | 158.4 | 133.2 | 268.55 | 0 | 1 | 10
1916 | 3/21 | 19:00:00 | 283.15 | 98824 | 2.1 | 190 | 5.5646 | 0 | 0 | 267.859 | 0 | 1 | 10
1917 | 3/21 | 20:00:00 | 282.15 | 98815 | 1.5 | 170 | 5.5651 | 0 | 0 | 268.075 | 0 | 1 | 9
1918 | 3/21 | 21:00:00 | 282.15 | 98815 | 2.1 | 200 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
1919 | 3/21 | 22:00:00 | 282.15 | 98815 | 4.1 | 210 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
1920 | 3/21 | 23:00:00 | 281.15 | 98806 | 3.6 | 220 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
1921 | 3/21 | 24:00:00 | 281.35 | 98808 | 3.6 | 188 | 6.3998 | 0 | 0 | 267.77 | 0 | 1 | 8.2
1922 | 3/22 | 01:00:00 | 281.45 | 98809 | 3.6 | 33 | 6.3998 | 0 | 0 | 267.865 | 0 | 1 | 8.3
1923 | 3/22 | 02:00:00 | 281.65 | 98811 | 3.6 | 350 | 6.3997 | 0 | 0 | 268.056 | 0 | 1 | 8.5
1924 | 3/22 | 03:00:00 | 281.85 | 98812 | 3.6 | 120 | 6.3996 | 0 | 0 | 268.246 | 0 | 1 | 8.7
1925 | 3/22 | 04:00:00 | 281.95 | 98814 | 3.6 | 13 | 6.3995 | 0 | 0 | 268.341 | 0 | 1 | 8.8
1926 | 3/22 | 05:00:00 | 282.15 | 98815 | 3.6 | 170 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
1927 | 3/22 | 06:00:00 | 281.15 | 98806 | 3.6 | 170 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
1928 | 3/22 | 07:00:00 | 281.15 | 98806 | 3.6 | 170 | 5.9698 | 28.8 | 0 | 267.353 | 0 | 1 | 8
1929 | 3/22 | 08:00:00 | 281.15 | 98806 | 4.1 | 190 | 5.9698 | 219.6 | 0 | 267.353 | 0 | 1 | 8
1930 | 3/22 | 09:00:00 | 281.15 | 98806 | 5.7 | 200 | 5.5656 | 878.4 | 1123.2 | 266.653 | 0 | 1 | 8
1931 | 3/22 | 10:00:00 | 281.15 | 98806 | 5.7 | 190 | 5.5656 | 1414.8 | 2149.2 | 266.392 | 0 | 1 | 8
1932 | 3/22 | 11:00:00 | 282.15 | 98815 | 6.2 | 200 | 5.1856 | 1789.2 | 2574 | 267.11 | 0 | 1 | 9
1933 | 3/22 | 12:00:00 | 282.15 | 98815 | 6.2 | 200 | 5.1856 | 1890 | 1854 | 267.371 | 0 | 1 | 9
1934 | 3/22 | 13:00:00 | 281.15 | 98806 | 5.1 | 190 | 5.1861 | 1069.2 | 201.6 | 266.895 | 0 | 1 | 8
1935 | 3/22 | 14:00:00 | 281.15 | 98806 | 6.7 | 200 | 5.9698 | 993.6 | 162 | 267.353 | 0 | 1 | 8
1936 | 3/22 | 15:00:00 | 281.15 | 98806 | 5.7 | 210 | 5.9698 | 835.2 | 144 | 267.353 | 0 | 1 | 8
1937 | 3/22 | 16:00:00 | 282.15 | 98815 | 8.2 | 210 | 6.3994 | 1094.4 | 1537.2 | 268.057 | 0 | 1 | 9
1938 | 3/22 | 17:00:00 | 282.15 | 98815 | 8.2 | 260 | 5.9692 | 651.6 | 1281.6 | 267.568 | 0 | 1 | 9
1939 | 3/22 | 18:00:00 | 281.15 | 98806 | 5.7 | 250 | 5.1861 | 180 | 216 | 266.163 | 0 | 1 | 8
1940 | 3/22 | 19:00:00 | 279.15 | 98789 | 8.7 | 270 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
1941 | 3/22 | 20:00:00 | 277.15 | 98771 | 3.1 | 250 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
1942 | 3/22 | 21:00:00 | 277.15 | 98771 | 3.1 | 250 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
1943 | 3/22 | 22:00:00 | 278.15 | 98780 | 6.2 | 260 | 4.4968 | 0 | 0 | 262.865 | 0 | 1 | 5
1944 | 3/22 | 23:00:00 | 278.15 | 98780 | 6.2 | 260 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
1945 | 3/22 | 24:00:00 | 278.75 | 98785 | 5.9 | 318 | 4.8655 | 0 | 0 | 264.299 | 0 | 1 | 5.6
1946 | 3/23 | 01:00:00 | 278.15 | 98779 | 5 | 248 | 4.7626 | 0 | 0 | 263.662 | 0 | 1 | 5
1947 | 3/23 | 02:00:00 | 277.55 | 98774 | 4.1 | 279 | 4.6283 | 0 | 0 | 263.112 | 0 | 1 | 4.4
1948 | 3/23 | 03:00:00 | 276.95 | 98769 | 3.2 | 250 | 4.5298 | 0 | 0 | 262.474 | 0 | 1 | 3.8
1949 | 3/23 | 04:00:00 | 276.35 | 98763 | 2.3 | 76 | 4.4014 | 0 | 0 | 261.813 | 0 | 1 | 3.2
1950 | 3/23 | 05:00:00 | 275.75 | 98758 | 1.4 | 307 | 4.3073 | 0 | 0 | 261.176 | 0 | 1 | 2.6
1951 | 3/23 | 06:00:00 | 275.15 | 98752 | 0.5 | 205 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
1952 | 3/23 | 07:00:00 | 274.15 | 98743 | 2.1 | 170 | 4.185 | 64.8 | 0 | 258.857 | 0 | 1 | 1
1953 | 3/23 | 08:00:00 | 275.15 | 98752 | 1.5 | 234 | 4.1846 | 187.2 | 0 | 260.622 | 0 | 1 | 2
1954 | 3/23 | 09:00:00 | 277.15 | 98771 | 2.1 | 220 | 4.4973 | 583.2 | 255.6 | 262.64 | 0 | 1 | 4
1955 | 3/23 | 10:00:00 | 279.15 | 98789 | 2.1 | 180 | 5.187 | 1440 | 1836 | 264.269 | 0 | 1 | 6
1956 | 3/23 | 11:00:00 | 280.15 | 98798 | 3.6 | 160 | 5.1865 | 1810.8 | 2584.8 | 265.216 | 0 | 1 | 7
1957 | 3/23 | 12:00:00 | 282.15 | 98815 | 6.2 | 180 | 4.4952 | 2034 | 2818.8 | 266.645 | 0 | 1 | 9
1958 | 3/23 | 13:00:00 | 283.15 | 98824 | 5.1 | 160 | 4.4948 | 2077.2 | 2844 | 267.59 | 0 | 1 | 10
1959 | 3/23 | 14:00:00 | 283.15 | 98824 | 5.1 | 170 | 3.8875 | 1944 | 2786.4 | 267.119 | 0 | 1 | 10
1960 | 3/23 | 15:00:00 | 283.15 | 98824 | 5.7 | 150 | 4.829 | 1627.2 | 2476.8 | 267.824 | 0 | 1 | 10
1961 | 3/23 | 16:00:00 | 283.15 | 98824 | 7.2 | 150 | 4.4948 | 1188 | 1666.8 | 267.59 | 0 | 1 | 10
1962 | 3/23 | 17:00:00 | 282.15 | 98815 | 5.7 | 160 | 4.8294 | 352.8 | 25.2 | 267.612 | 0 | 1 | 9
1963 | 3/23 | 18:00:00 | 281.15 | 98806 | 3.6 | 150 | 5.9698 | 100.8 | 0 | 267.353 | 0 | 1 | 8
1964 | 3/23 | 19:00:00 | 281.15 | 98806 | 3.1 | 150 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
1965 | 3/23 | 20:00:00 | 281.15 | 98806 | 4.6 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
1966 | 3/23 | 21:00:00 | 281.15 | 98806 | 5.7 | 150 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
1967 | 3/23 | 22:00:00 | 281.15 | 98806 | 4.6 | 160 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
1968 | 3/23 | 23:00:00 | 282.15 | 98815 | 5.1 | 190 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
1969 | 3/23 | 24:00:00 | 282.15 | 98815 | 5.1 | 210 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
1970 | 3/24 | 01:00:00 | 281.15 | 98806 | 3.6 | 220 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
1971 | 3/24 | 02:00:00 | 281.15 | 98806 | 4.6 | 220 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
1972 | 3/24 | 03:00:00 | 281.15 | 98806 | 4.1 | 200 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
1973 | 3/24 | 04:00:00 | 280.15 | 98798 | 3.1 | 180 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
1974 | 3/24 | 05:00:00 | 280.15 | 98798 | 4.1 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
1975 | 3/24 | 06:00:00 | 280.15 | 98798 | 4.6 | 120 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
1976 | 3/24 | 07:00:00 | 280.15 | 98798 | 4.6 | 130 | 6.4005 | 39.6 | 0 | 266.628 | 0 | 1 | 7
1977 | 3/24 | 08:00:00 | 280.15 | 98798 | 4.6 | 150 | 6.4005 | 241.2 | 0 | 266.628 | 0 | 1 | 7
1978 | 3/24 | 09:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 507.6 | 39.6 | 267.805 | 0 | 1 | 8
1979 | 3/24 | 10:00:00 | 281.15 | 98806 | 5.1 | 130 | 6.8577 | 759.6 | 68.4 | 267.805 | 0 | 1 | 8
1980 | 3/24 | 11:00:00 | 282.15 | 98815 | 5.7 | 140 | 7.3438 | 954 | 154.8 | 268.983 | 0 | 1 | 9
1981 | 3/24 | 12:00:00 | 282.15 | 98815 | 4.6 | 150 | 7.3438 | 1065.6 | 223.2 | 268.983 | 0 | 1 | 9
1982 | 3/24 | 13:00:00 | 283.15 | 98824 | 4.6 | 160 | 7.3431 | 1083.6 | 226.8 | 269.936 | 0 | 1 | 10
1983 | 3/24 | 14:00:00 | 284.15 | 98833 | 5.1 | 210 | 6.8558 | 1015.2 | 162 | 270.663 | 0 | 1 | 11
1984 | 3/24 | 15:00:00 | 284.15 | 98833 | 5.1 | 210 | 6.8558 | 856.8 | 144 | 270.663 | 0 | 1 | 11
1985 | 3/24 | 16:00:00 | 284.15 | 98833 | 4.1 | 210 | 6.8558 | 626.4 | 54 | 270.663 | 0 | 1 | 11
1986 | 3/24 | 17:00:00 | 284.15 | 98833 | 3.1 | 200 | 6.8558 | 356.4 | 14.4 | 270.663 | 0 | 1 | 11
1987 | 3/24 | 18:00:00 | 284.15 | 98833 | 3.6 | 190 | 6.8558 | 108 | 0 | 270.663 | 0 | 1 | 11
1988 | 3/24 | 19:00:00 | 284.15 | 98833 | 2.6 | 220 | 6.8558 | 0 | 0 | 270.663 | 0 | 1 | 11
1989 | 3/24 | 20:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
1990 | 3/24 | 21:00:00 | 282.15 | 98815 | 0 | 311 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
1991 | 3/24 | 22:00:00 | 282.15 | 98815 | 0 | 258 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
1992 | 3/24 | 23:00:00 | 282.15 | 98815 | 0 | 257 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
1993 | 3/24 | 24:00:00 | 281.95 | 98814 | 0.1 | 56 | 6.8571 | 0 | 0 | 268.676 | 0 | 1 | 8.8
1994 | 3/25 | 01:00:00 | 281.85 | 98812 | 0.2 | 240 | 6.8573 | 0 | 0 | 268.581 | 0 | 1 | 8.7
1995 | 3/25 | 02:00:00 | 281.65 | 98811 | 0.2 | 15 | 6.8574 | 0 | 0 | 268.39 | 0 | 1 | 8.5
1996 | 3/25 | 03:00:00 | 281.45 | 98809 | 0.3 | 18 | 6.8575 | 0 | 0 | 268.2 | 0 | 1 | 8.3
1997 | 3/25 | 04:00:00 | 281.35 | 98808 | 0.4 | 37 | 6.8576 | 0 | 0 | 268.105 | 0 | 1 | 8.2
1998 | 3/25 | 05:00:00 | 281.15 | 98806 | 0.5 | 215 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
1999 | 3/25 | 06:00:00 | 281.15 | 98806 | 0.5 | 65 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
2000 | 3/25 | 07:00:00 | 281.15 | 98806 | 2.6 | 70 | 6.8577 | 43.2 | 0 | 267.805 | 0 | 1 | 8
2001 | 3/25 | 08:00:00 | 281.15 | 98806 | 2.6 | 70 | 6.8577 | 151.2 | 0 | 267.914 | 0 | 1 | 8
2002 | 3/25 | 09:00:00 | 282.15 | 98815 | 3.6 | 110 | 7 | 356.4 | 0 | 268.935 | 0 | 1 | 9
2003 | 3/25 | 10:00:00 | 282.15 | 98815 | 4.6 | 140 | 6.9044 | 579.6 | 14.4 | 268.889 | 0 | 1 | 9
2004 | 3/25 | 11:00:00 | 283.15 | 98824 | 3.6 | 150 | 7.2931 | 964.8 | 43.2 | 269.914 | 0 | 1 | 10
2005 | 3/25 | 12:00:00 | 283.15 | 98824 | 2.6 | 170 | 6.9514 | 1076.4 | 194.4 | 269.756 | 0 | 1 | 10
2006 | 3/25 | 13:00:00 | 285.15 | 98841 | 5.1 | 180 | 6.8552 | 1980 | 1886.4 | 271.136 | 0 | 1 | 12
2007 | 3/25 | 14:00:00 | 285.15 | 98841 | 6.2 | 170 | 6.487 | 1850.4 | 2322 | 270.953 | 0 | 1 | 12
2008 | 3/25 | 15:00:00 | 286.15 | 98850 | 4.6 | 200 | 6.3971 | 1562.4 | 1771.2 | 271.858 | 0 | 1 | 13
2009 | 3/25 | 16:00:00 | 286.15 | 98850 | 4.1 | 180 | 6.5314 | 1216.8 | 2030.4 | 271.66 | 0 | 1 | 13
2010 | 3/25 | 17:00:00 | 285.15 | 98841 | 3.1 | 170 | 6.6688 | 698.4 | 1332 | 270.78 | 0 | 1 | 12
2011 | 3/25 | 18:00:00 | 284.15 | 98833 | 3.1 | 160 | 6.354 | 205.2 | 345.6 | 269.935 | 0 | 1 | 11
2012 | 3/25 | 19:00:00 | 284.15 | 98833 | 2.6 | 110 | 6.052 | 0 | 0 | 269.774 | 0 | 1 | 11
2013 | 3/25 | 20:00:00 | 283.15 | 98824 | 0.5 | 55 | 6.1804 | 0 | 0 | 269.369 | 0 | 1 | 10
2014 | 3/25 | 21:00:00 | 283.15 | 98824 | 5.1 | 120 | 6.3988 | 0 | 0 | 269.483 | 0 | 1 | 10
2015 | 3/25 | 22:00:00 | 283.15 | 98824 | 6.7 | 130 | 6.1804 | 0 | 0 | 269.369 | 0 | 1 | 10
2016 | 3/25 | 23:00:00 | 281.15 | 98806 | 5.1 | 160 | 6.1815 | 0 | 0 | 267.467 | 0 | 1 | 8
2017 | 3/25 | 24:00:00 | 281.15 | 98806 | 8.7 | 180 | 6.1815 | 0 | 0 | 267.467 | 0 | 1 | 8
2018 | 3/26 | 01:00:00 | 280.15 | 98798 | 7.7 | 190 | 6.182 | 0 | 0 | 266.515 | 0 | 1 | 7
2019 | 3/26 | 02:00:00 | 280.15 | 98798 | 5.7 | 190 | 6.182 | 0 | 0 | 266.515 | 0 | 1 | 7
2020 | 3/26 | 03:00:00 | 279.15 | 98789 | 5.7 | 210 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
2021 | 3/26 | 04:00:00 | 279.15 | 98789 | 7.7 | 210 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
2022 | 3/26 | 05:00:00 | 278.15 | 98780 | 6.7 | 220 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
2023 | 3/26 | 06:00:00 | 279.15 | 98789 | 6.7 | 210 | 5.9708 | 0 | 0 | 264.982 | 0 | 1 | 6
2024 | 3/26 | 07:00:00 | 279.15 | 98789 | 7.2 | 220 | 5.9708 | 82.8 | 0 | 264.982 | 0 | 1 | 6
2025 | 3/26 | 08:00:00 | 280.15 | 98798 | 7.2 | 210 | 6.182 | 471.6 | 806.4 | 266.045 | 0 | 1 | 7
2026 | 3/26 | 09:00:00 | 281.15 | 98806 | 7.2 | 210 | 5.1861 | 968.4 | 1472.4 | 266.423 | 0 | 1 | 8
2027 | 3/26 | 10:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.1856 | 1425.6 | 1936.8 | 267.371 | 0 | 1 | 9
2028 | 3/26 | 11:00:00 | 283.15 | 98824 | 6.7 | 220 | 5.5646 | 1771.2 | 1911.6 | 268.55 | 0 | 1 | 10
2029 | 3/26 | 12:00:00 | 282.15 | 98815 | 7.2 | 210 | 5.1856 | 1976.4 | 2361.6 | 267.371 | 0 | 1 | 9
2030 | 3/26 | 13:00:00 | 283.15 | 98824 | 7.2 | 210 | 5.1851 | 2012.4 | 2379.6 | 268.319 | 0 | 1 | 10
2031 | 3/26 | 14:00:00 | 283.15 | 98824 | 6.7 | 210 | 5.1851 | 1879.2 | 2314.8 | 268.319 | 0 | 1 | 10
2032 | 3/26 | 15:00:00 | 283.15 | 98824 | 7.2 | 210 | 5.1851 | 1587.6 | 1692 | 268.319 | 0 | 1 | 10
2033 | 3/26 | 16:00:00 | 283.15 | 98824 | 5.1 | 210 | 5.5646 | 648 | 230.4 | 269.025 | 0 | 1 | 10
2034 | 3/26 | 17:00:00 | 282.15 | 98815 | 5.7 | 200 | 5.9692 | 676.8 | 903.6 | 267.83 | 0 | 1 | 9
2035 | 3/26 | 18:00:00 | 282.15 | 98815 | 4.6 | 200 | 5.5651 | 118.8 | 0 | 268.075 | 0 | 1 | 9
2036 | 3/26 | 19:00:00 | 281.15 | 98806 | 2.1 | 250 | 5.1861 | 0 | 0 | 266.423 | 0 | 1 | 8
2037 | 3/26 | 20:00:00 | 280.15 | 98798 | 0 | 328 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
2038 | 3/26 | 21:00:00 | 280.15 | 98798 | 1.5 | 127 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
2039 | 3/26 | 22:00:00 | 280.15 | 98798 | 2.6 | 230 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
2040 | 3/26 | 23:00:00 | 279.15 | 98789 | 3.1 | 220 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2041 | 3/26 | 24:00:00 | 279.15 | 98789 | 2.6 | 240 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2042 | 3/27 | 01:00:00 | 279.15 | 98789 | 1.5 | 250 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2043 | 3/27 | 02:00:00 | 279.15 | 98789 | 1.5 | 230 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2044 | 3/27 | 03:00:00 | 279.15 | 98789 | 3.1 | 230 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2045 | 3/27 | 04:00:00 | 279.15 | 98789 | 2.6 | 240 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
2046 | 3/27 | 05:00:00 | 279.15 | 98789 | 3.1 | 260 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
2047 | 3/27 | 06:00:00 | 279.15 | 98789 | 5.1 | 260 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
2048 | 3/27 | 07:00:00 | 279.15 | 98789 | 4.1 | 260 | 5.9708 | 90 | 0 | 264.982 | 0 | 1 | 6
2049 | 3/27 | 08:00:00 | 279.15 | 98789 | 4.6 | 270 | 5.5666 | 489.6 | 676.8 | 264.756 | 0 | 1 | 6
2050 | 3/27 | 09:00:00 | 279.15 | 98789 | 4.6 | 290 | 5.187 | 550.8 | 183.6 | 264.996 | 0 | 1 | 6
2051 | 3/27 | 10:00:00 | 280.15 | 98798 | 5.1 | 280 | 5.1865 | 1447.2 | 1584 | 265.476 | 0 | 1 | 7
2052 | 3/27 | 11:00:00 | 281.15 | 98806 | 7.2 | 300 | 4.4957 | 1803.6 | 1947.6 | 265.96 | 0 | 1 | 8
2053 | 3/27 | 12:00:00 | 281.15 | 98806 | 9.3 | 290 | 4.4957 | 2005.2 | 1868.4 | 265.96 | 0 | 1 | 8
2054 | 3/27 | 13:00:00 | 281.15 | 98806 | 8.2 | 270 | 4.8299 | 1130.4 | 280.8 | 266.664 | 0 | 1 | 8
2055 | 3/27 | 14:00:00 | 281.15 | 98806 | 9.8 | 270 | 4.4957 | 1904.4 | 1504.8 | 265.96 | 0 | 1 | 8
2056 | 3/27 | 15:00:00 | 281.15 | 98806 | 9.8 | 270 | 4.4957 | 896.4 | 316.8 | 266.431 | 0 | 1 | 8
2057 | 3/27 | 16:00:00 | 281.15 | 98806 | 8.7 | 270 | 4.4957 | 662.4 | 61.2 | 266.431 | 0 | 1 | 8
2058 | 3/27 | 17:00:00 | 281.15 | 98806 | 9.8 | 270 | 4.4957 | 385.2 | 28.8 | 266.431 | 0 | 1 | 8
2059 | 3/27 | 18:00:00 | 280.15 | 98798 | 8.2 | 260 | 4.1826 | 230.4 | 248.4 | 264.782 | 0 | 1 | 7
2060 | 3/27 | 19:00:00 | 279.15 | 98789 | 6.7 | 250 | 4.183 | 0 | 0 | 263.837 | 0 | 1 | 6
2061 | 3/27 | 20:00:00 | 279.15 | 98789 | 5.1 | 250 | 4.183 | 0 | 0 | 263.578 | 0 | 1 | 6
2062 | 3/27 | 21:00:00 | 279.15 | 98789 | 6.2 | 260 | 4.4964 | 0 | 0 | 264.069 | 0 | 1 | 6
2063 | 3/27 | 22:00:00 | 279.15 | 98789 | 5.7 | 250 | 4.4964 | 0 | 0 | 263.81 | 0 | 1 | 6
2064 | 3/27 | 23:00:00 | 279.15 | 98789 | 7.2 | 250 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
2065 | 3/27 | 24:00:00 | 279.15 | 98789 | 6.2 | 250 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
2066 | 3/28 | 01:00:00 | 278.15 | 98780 | 1.5 | 106 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2067 | 3/28 | 02:00:00 | 278.15 | 98780 | 2.1 | 250 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2068 | 3/28 | 03:00:00 | 278.15 | 98780 | 5.1 | 260 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
2069 | 3/28 | 04:00:00 | 278.15 | 98780 | 4.6 | 270 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2070 | 3/28 | 05:00:00 | 278.15 | 98780 | 5.1 | 260 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
2071 | 3/28 | 06:00:00 | 278.15 | 98780 | 6.7 | 260 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
2072 | 3/28 | 07:00:00 | 277.15 | 98771 | 8.2 | 270 | 4.8316 | 104.4 | 25.2 | 262.149 | 0 | 1 | 4
2073 | 3/28 | 08:00:00 | 278.15 | 98780 | 9.8 | 260 | 4.8311 | 540 | 1069.2 | 263.095 | 0 | 1 | 5
2074 | 3/28 | 09:00:00 | 279.15 | 98789 | 10.3 | 260 | 4.8307 | 1072.8 | 1810.8 | 264.041 | 0 | 1 | 6
2075 | 3/28 | 10:00:00 | 280.15 | 98798 | 10.8 | 260 | 4.496 | 1562.4 | 2404.8 | 264.755 | 0 | 1 | 7
2076 | 3/28 | 11:00:00 | 281.15 | 98806 | 9.8 | 270 | 4.4957 | 1933.2 | 2617.2 | 265.7 | 0 | 1 | 8
2077 | 3/28 | 12:00:00 | 280.15 | 98798 | 9.8 | 270 | 4.1826 | 2026.8 | 2264.4 | 264.782 | 0 | 1 | 7
2078 | 3/28 | 13:00:00 | 282.15 | 98815 | 10.8 | 260 | 4.4952 | 2059.2 | 2412 | 266.906 | 0 | 1 | 9
2079 | 3/28 | 14:00:00 | 282.15 | 98815 | 10.8 | 260 | 4.1819 | 1926 | 2361.6 | 266.672 | 0 | 1 | 9
2080 | 3/28 | 15:00:00 | 282.15 | 98815 | 8.7 | 260 | 4.1819 | 1634.4 | 1623.6 | 266.672 | 0 | 1 | 9
2081 | 3/28 | 16:00:00 | 281.15 | 98806 | 10.3 | 260 | 3.8882 | 1213.2 | 1440 | 265.492 | 0 | 1 | 8
2082 | 3/28 | 17:00:00 | 281.15 | 98806 | 7.2 | 260 | 4.4957 | 712.8 | 1220.4 | 265.96 | 0 | 1 | 8
2083 | 3/28 | 18:00:00 | 280.15 | 98798 | 8.7 | 250 | 4.496 | 255.6 | 352.8 | 264.755 | 0 | 1 | 7
2084 | 3/28 | 19:00:00 | 279.15 | 98789 | 1.5 | 261 | 4.4964 | 0 | 0 | 264.069 | 0 | 1 | 6
2085 | 3/28 | 20:00:00 | 278.15 | 98780 | 6.7 | 270 | 4.4968 | 0 | 0 | 262.865 | 0 | 1 | 5
2086 | 3/28 | 21:00:00 | 277.15 | 98771 | 2.1 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2087 | 3/28 | 22:00:00 | 277.15 | 98771 | 4.6 | 260 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2088 | 3/28 | 23:00:00 | 277.15 | 98771 | 3.1 | 250 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2089 | 3/28 | 24:00:00 | 277.15 | 98771 | 5.1 | 260 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2090 | 3/29 | 01:00:00 | 277.15 | 98771 | 4.6 | 260 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2091 | 3/29 | 02:00:00 | 277.15 | 98771 | 3.1 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2092 | 3/29 | 03:00:00 | 276.15 | 98762 | 0 | 132 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2093 | 3/29 | 04:00:00 | 276.15 | 98762 | 0 | 26 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2094 | 3/29 | 05:00:00 | 276.15 | 98762 | 0 | 173 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2095 | 3/29 | 06:00:00 | 276.15 | 98762 | 0 | 58 | 4.832 | 0 | 0 | 260.786 | 0 | 1 | 3
2096 | 3/29 | 07:00:00 | 276.15 | 98762 | 0 | 216 | 4.4977 | 115.2 | 61.2 | 260.975 | 0 | 1 | 3
2097 | 3/29 | 08:00:00 | 277.15 | 98771 | 0 | 8 | 4.8316 | 561.6 | 1101.6 | 262.149 | 0 | 1 | 4
2098 | 3/29 | 09:00:00 | 277.15 | 98771 | 1 | 83 | 4.8316 | 1033.2 | 1288.8 | 262.405 | 0 | 1 | 4
2099 | 3/29 | 10:00:00 | 277.15 | 98771 | 3.1 | 120 | 4.8316 | 828 | 140.4 | 262.87 | 0 | 1 | 4
2100 | 3/29 | 11:00:00 | 277.15 | 98771 | 4.6 | 120 | 4.8316 | 1022.4 | 226.8 | 262.87 | 0 | 1 | 4
2101 | 3/29 | 12:00:00 | 277.15 | 98771 | 4.6 | 120 | 5.1879 | 1130.4 | 234 | 263.098 | 0 | 1 | 4
2102 | 3/29 | 13:00:00 | 277.15 | 98771 | 4.6 | 110 | 5.1879 | 1148.4 | 237.6 | 263.098 | 0 | 1 | 4
2103 | 3/29 | 14:00:00 | 277.15 | 98771 | 5.7 | 110 | 5.1879 | 1072.8 | 230.4 | 263.098 | 0 | 1 | 4
2104 | 3/29 | 15:00:00 | 277.15 | 98771 | 5.1 | 90 | 5.1879 | 910.8 | 151.2 | 263.098 | 0 | 1 | 4
2105 | 3/29 | 16:00:00 | 277.15 | 98771 | 4.6 | 90 | 5.1879 | 414 | 0 | 263.204 | 0 | 1 | 4
2106 | 3/29 | 17:00:00 | 278.15 | 98780 | 4.1 | 90 | 5.5671 | 244.8 | 0 | 264.381 | 0 | 1 | 5
2107 | 3/29 | 18:00:00 | 278.15 | 98780 | 3.6 | 70 | 5.5671 | 140.4 | 0 | 264.274 | 0 | 1 | 5
2108 | 3/29 | 19:00:00 | 278.15 | 98780 | 4.1 | 70 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
2109 | 3/29 | 20:00:00 | 278.15 | 98780 | 3.1 | 70 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
2110 | 3/29 | 21:00:00 | 278.15 | 98780 | 2.6 | 70 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
2111 | 3/29 | 22:00:00 | 279.15 | 98789 | 2.6 | 130 | 5.9708 | 0 | 0 | 265.559 | 0 | 1 | 6
2112 | 3/29 | 23:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
2113 | 3/29 | 24:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
2114 | 3/30 | 01:00:00 | 281.15 | 98806 | 2.6 | 150 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
2115 | 3/30 | 02:00:00 | 281.15 | 98806 | 2.1 | 160 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
2116 | 3/30 | 03:00:00 | 280.15 | 98798 | 1.5 | 170 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
2117 | 3/30 | 04:00:00 | 280.15 | 98798 | 1 | 170 | 6.4005 | 0 | 0 | 265.897 | 0 | 1 | 7
2118 | 3/30 | 05:00:00 | 280.15 | 98798 | 2.6 | 160 | 6.4005 | 0 | 0 | 265.897 | 0 | 1 | 7
2119 | 3/30 | 06:00:00 | 280.15 | 98798 | 3.1 | 160 | 6.4005 | 0 | 0 | 266.157 | 0 | 1 | 7
2120 | 3/30 | 07:00:00 | 280.15 | 98798 | 4.6 | 150 | 6.4005 | 118.8 | 25.2 | 266.157 | 0 | 1 | 7
2121 | 3/30 | 08:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 302.4 | 0 | 267.805 | 0 | 1 | 8
2122 | 3/30 | 09:00:00 | 281.15 | 98806 | 4.6 | 130 | 6.8577 | 579.6 | 46.8 | 267.805 | 0 | 1 | 8
2123 | 3/30 | 10:00:00 | 281.15 | 98806 | 4.1 | 140 | 6.8577 | 835.2 | 140.4 | 267.805 | 0 | 1 | 8
2124 | 3/30 | 11:00:00 | 282.15 | 98815 | 4.1 | 140 | 6.8571 | 1026 | 219.6 | 268.758 | 0 | 1 | 9
2125 | 3/30 | 12:00:00 | 280.15 | 98798 | 5.1 | 170 | 5.9703 | 1137.6 | 198 | 266.402 | 0 | 1 | 7
2126 | 3/30 | 13:00:00 | 280.15 | 98798 | 3.6 | 120 | 5.9703 | 2084.4 | 1364.4 | 265.931 | 0 | 1 | 7
2127 | 3/30 | 14:00:00 | 281.15 | 98806 | 5.1 | 120 | 6.4 | 1080 | 194.4 | 267.58 | 0 | 1 | 8
2128 | 3/30 | 15:00:00 | 281.15 | 98806 | 4.6 | 120 | 6.4 | 918 | 151.2 | 267.58 | 0 | 1 | 8
2129 | 3/30 | 16:00:00 | 282.15 | 98815 | 5.7 | 110 | 6.3994 | 684 | 57.6 | 268.532 | 0 | 1 | 9
2130 | 3/30 | 17:00:00 | 282.15 | 98815 | 5.7 | 140 | 5.9692 | 410.4 | 32.4 | 268.304 | 0 | 1 | 9
2131 | 3/30 | 18:00:00 | 280.15 | 98798 | 4.6 | 110 | 5.5661 | 262.8 | 493.2 | 265.704 | 0 | 1 | 7
2132 | 3/30 | 19:00:00 | 278.15 | 98780 | 2.1 | 120 | 5.5671 | 0 | 0 | 263.807 | 0 | 1 | 5
2133 | 3/30 | 20:00:00 | 278.15 | 98780 | 1.5 | 109 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
2134 | 3/30 | 21:00:00 | 279.15 | 98789 | 2.1 | 70 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
2135 | 3/30 | 22:00:00 | 277.15 | 98771 | 3.6 | 230 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
2136 | 3/30 | 23:00:00 | 274.15 | 98743 | 5.7 | 230 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
2137 | 3/30 | 24:00:00 | 273.15 | 98734 | 3.1 | 210 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
2138 | 3/31 | 01:00:00 | 274.15 | 98743 | 2.1 | 180 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
2139 | 3/31 | 02:00:00 | 274.15 | 98743 | 1 | 160 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
2140 | 3/31 | 03:00:00 | 274.15 | 98743 | 0.5 | 341 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
2141 | 3/31 | 04:00:00 | 274.15 | 98743 | 0 | 226 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
2142 | 3/31 | 05:00:00 | 274.15 | 98743 | 0 | 49 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
2143 | 3/31 | 06:00:00 | 274.15 | 98743 | 0 | 356 | 4.185 | 0 | 0 | 259.569 | 0 | 1 | 1
2144 | 3/31 | 07:00:00 | 274.15 | 98743 | 1 | 290 | 4.185 | 133.2 | 46.8 | 259.111 | 0 | 1 | 1
2145 | 3/31 | 08:00:00 | 275.15 | 98752 | 0 | 241 | 4.4981 | 316.8 | 3.6 | 260.745 | 0 | 1 | 2
2146 | 3/31 | 09:00:00 | 276.15 | 98762 | 3.6 | 310 | 4.4977 | 597.6 | 50.4 | 261.693 | 0 | 1 | 3
2147 | 3/31 | 10:00:00 | 276.15 | 98762 | 3.6 | 310 | 4.4977 | 853.2 | 302.4 | 261.693 | 0 | 1 | 3
2148 | 3/31 | 11:00:00 | 277.15 | 98771 | 5.7 | 280 | 4.8316 | 1886.4 | 2012.4 | 262.405 | 0 | 1 | 4
2149 | 3/31 | 12:00:00 | 276.15 | 98762 | 4.1 | 300 | 4.832 | 2084.4 | 1886.4 | 261.459 | 0 | 1 | 3
2150 | 3/31 | 13:00:00 | 277.15 | 98771 | 9.3 | 290 | 4.4973 | 1173.6 | 205.2 | 262.64 | 0 | 1 | 4
2151 | 3/31 | 14:00:00 | 277.15 | 98771 | 10.8 | 300 | 4.4973 | 1098 | 234 | 262.64 | 0 | 1 | 4
2152 | 3/31 | 15:00:00 | 276.15 | 98762 | 9.3 | 300 | 3.8899 | 936 | 158.4 | 261.231 | 0 | 1 | 3
2153 | 3/31 | 16:00:00 | 277.15 | 98771 | 9.3 | 290 | 3.8896 | 1263.6 | 1422 | 261.714 | 0 | 1 | 4
2154 | 3/31 | 17:00:00 | 276.15 | 98762 | 9.3 | 290 | 3.8899 | 759.6 | 1040.4 | 260.77 | 0 | 1 | 3
2155 | 3/31 | 18:00:00 | 276.15 | 98762 | 8.7 | 280 | 4.1841 | 277.2 | 244.8 | 261.001 | 0 | 1 | 3
2156 | 3/31 | 19:00:00 | 274.65 | 98748 | 6.3 | 275 | 3.8905 | 7.2 | 0 | 259.1 | 0 | 1 | 1.5
2157 | 3/31 | 20:00:00 | 274.35 | 98745 | 6.2 | 272 | 3.8906 | 0 | 0 | 258.817 | 0 | 1 | 1.2
2158 | 3/31 | 21:00:00 | 274.15 | 98743 | 5.4 | 272 | 3.8267 | 0 | 0 | 258.582 | 0 | 1 | 1
2159 | 3/31 | 22:00:00 | 276.15 | 98761 | 4.7 | 250 | 4.4334 | 0 | 0 | 260.929 | 0 | 1 | 3
2160 | 3/31 | 23:00:00 | 277.95 | 98777 | 3.5 | 237 | 5.0066 | 0 | 0 | 263.02 | 0 | 1 | 4.8
2161 | 3/31 | 24:00:00 | 279.35 | 98791 | 2.6 | 205 | 5.5665 | 0 | 0 | 265.414 | 0 | 1 | 6.2
2162 | 4/1 | 01:00:00 | 280.95 | 98804 | 2.4 | 170 | 6.3119 | 0 | 0 | 266.611 | 0 | 1 | 7.8
2163 | 4/1 | 02:00:00 | 280.15 | 98798 | 2.3 | 160 | 6.0542 | 0 | 0 | 266.555 | 0 | 1 | 7
2164 | 4/1 | 03:00:00 | 279.35 | 98791 | 2.6 | 135 | 5.8878 | 0 | 0 | 265.704 | 0 | 1 | 6.2
2165 | 4/1 | 04:00:00 | 279.15 | 98789 | 2.6 | 132 | 5.8879 | 0 | 0 | 265.513 | 0 | 1 | 6
2166 | 4/1 | 05:00:00 | 279.15 | 98789 | 2.2 | 184 | 5.9708 | 0 | 0 | 265.559 | 0 | 1 | 6
2167 | 4/1 | 06:00:00 | 279.65 | 98793 | 1.9 | 148 | 6.0545 | 0 | 0 | 266.08 | 0 | 1 | 6.5
2168 | 4/1 | 07:00:00 | 279.15 | 98789 | 3.1 | 130 | 5.9708 | 79.2 | 0 | 265.451 | 0 | 1 | 6
2169 | 4/1 | 08:00:00 | 280.15 | 98798 | 1 | 348 | 6.4005 | 583.2 | 770.4 | 266.157 | 0 | 1 | 7
2170 | 4/1 | 09:00:00 | 281.15 | 98806 | 1 | 6 | 6.4 | 1090.8 | 1299.6 | 267.107 | 0 | 1 | 8
2171 | 4/1 | 10:00:00 | 282.15 | 98815 | 3.1 | 110 | 6.3994 | 860.4 | 140.4 | 268.532 | 0 | 1 | 9
2172 | 4/1 | 11:00:00 | 281.15 | 98806 | 2.1 | 170 | 6.4 | 1051.2 | 190.8 | 267.58 | 0 | 1 | 8
2173 | 4/1 | 12:00:00 | 283.15 | 98824 | 2.1 | 239 | 6.8564 | 2088 | 1911.6 | 269.234 | 0 | 1 | 10
2174 | 4/1 | 13:00:00 | 283.15 | 98824 | 5.1 | 250 | 6.3988 | 2120.4 | 2358 | 269.007 | 0 | 1 | 10
2175 | 4/1 | 14:00:00 | 283.15 | 98824 | 5.1 | 290 | 6.8564 | 1980 | 2336.4 | 269.234 | 0 | 1 | 10
2176 | 4/1 | 15:00:00 | 283.15 | 98824 | 4.6 | 290 | 7.3431 | 1684.8 | 2077.2 | 269.46 | 0 | 1 | 10
2177 | 4/1 | 16:00:00 | 283.15 | 98824 | 6.2 | 290 | 6.8564 | 1263.6 | 1742.4 | 269.234 | 0 | 1 | 10
2178 | 4/1 | 17:00:00 | 284.15 | 98833 | 8.2 | 290 | 6.3982 | 813.6 | 1461.6 | 269.693 | 0 | 1 | 11
2179 | 4/1 | 18:00:00 | 283.15 | 98824 | 5.1 | 280 | 6.3988 | 284.4 | 331.2 | 269.007 | 0 | 1 | 10
2180 | 4/1 | 19:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.3988 | 14.4 | 0 | 268.744 | 0 | 1 | 10
2181 | 4/1 | 20:00:00 | 281.15 | 98806 | 5.7 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
2182 | 4/1 | 21:00:00 | 281.15 | 98806 | 5.7 | 280 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
2183 | 4/1 | 22:00:00 | 280.15 | 98798 | 4.6 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
2184 | 4/1 | 23:00:00 | 280.15 | 98798 | 6.7 | 280 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
2185 | 4/1 | 24:00:00 | 280.15 | 98798 | 5.7 | 290 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
2186 | 4/2 | 01:00:00 | 280.15 | 98798 | 3.6 | 290 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
2187 | 4/2 | 02:00:00 | 279.15 | 98789 | 3.6 | 300 | 5.9708 | 0 | 0 | 264.723 | 0 | 1 | 6
2188 | 4/2 | 03:00:00 | 279.15 | 98789 | 3.6 | 310 | 5.5666 | 0 | 0 | 264.497 | 0 | 1 | 6
2189 | 4/2 | 04:00:00 | 278.15 | 98780 | 4.1 | 270 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
2190 | 4/2 | 05:00:00 | 278.15 | 98780 | 4.1 | 270 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
2191 | 4/2 | 06:00:00 | 278.15 | 98780 | 4.1 | 270 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
2192 | 4/2 | 07:00:00 | 279.15 | 98789 | 3.6 | 290 | 5.5666 | 90 | 0 | 265.224 | 0 | 1 | 6
2193 | 4/2 | 08:00:00 | 279.15 | 98789 | 3.6 | 320 | 5.5666 | 205.2 | 0 | 265.332 | 0 | 1 | 6
2194 | 4/2 | 09:00:00 | 280.15 | 98798 | 3.1 | 310 | 5.5661 | 619.2 | 100.8 | 266.174 | 0 | 1 | 7
2195 | 4/2 | 10:00:00 | 280.15 | 98798 | 1.5 | 95 | 6.4005 | 871.2 | 144 | 266.628 | 0 | 1 | 7
2196 | 4/2 | 11:00:00 | 281.15 | 98806 | 2.1 | 20 | 6.4 | 1062 | 190.8 | 267.58 | 0 | 1 | 8
2197 | 4/2 | 12:00:00 | 283.15 | 98824 | 1 | 124 | 5.9687 | 2113.2 | 1926 | 268.779 | 0 | 1 | 10
2198 | 4/2 | 13:00:00 | 283.15 | 98824 | 1 | 120 | 5.9687 | 2145.6 | 2376 | 268.779 | 0 | 1 | 10
2199 | 4/2 | 14:00:00 | 285.15 | 98841 | 1.5 | 137 | 5.9676 | 2005.2 | 1882.8 | 270.678 | 0 | 1 | 12
2200 | 4/2 | 15:00:00 | 284.15 | 98833 | 1.5 | 6 | 5.5641 | 950.4 | 388.8 | 269.975 | 0 | 1 | 11
2201 | 4/2 | 16:00:00 | 284.15 | 98833 | 1.5 | 202 | 5.5641 | 1288.8 | 1443.6 | 269.498 | 0 | 1 | 11
2202 | 4/2 | 17:00:00 | 285.15 | 98841 | 2.1 | 230 | 5.5636 | 784.8 | 1281.6 | 270.447 | 0 | 1 | 12
2203 | 4/2 | 18:00:00 | 285.15 | 98841 | 3.6 | 290 | 5.9676 | 316.8 | 446.4 | 270.413 | 0 | 1 | 12
2204 | 4/2 | 19:00:00 | 283.15 | 98824 | 2.6 | 270 | 5.5646 | 18 | 0 | 268.55 | 0 | 1 | 10
2205 | 4/2 | 20:00:00 | 281.15 | 98806 | 3.1 | 290 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
2206 | 4/2 | 21:00:00 | 280.15 | 98798 | 2.6 | 270 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
2207 | 4/2 | 22:00:00 | 279.15 | 98789 | 0 | 306 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
2208 | 4/2 | 23:00:00 | 279.15 | 98789 | 1.5 | 220 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
2209 | 4/2 | 24:00:00 | 278.15 | 98780 | 1.5 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
2210 | 4/3 | 01:00:00 | 279.15 | 98789 | 0.5 | 166 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
2211 | 4/3 | 02:00:00 | 277.15 | 98771 | 1 | 55 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
2212 | 4/3 | 03:00:00 | 277.15 | 98771 | 1.5 | 189 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
2213 | 4/3 | 04:00:00 | 277.15 | 98771 | 3.1 | 160 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
2214 | 4/3 | 05:00:00 | 276.15 | 98762 | 2.1 | 140 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
2215 | 4/3 | 06:00:00 | 276.15 | 98762 | 1 | 9 | 4.4977 | 0 | 0 | 260.558 | 0 | 1 | 3
2216 | 4/3 | 07:00:00 | 276.15 | 98762 | 2.1 | 160 | 4.832 | 187.2 | 208.8 | 260.786 | 0 | 1 | 3
2217 | 4/3 | 08:00:00 | 279.15 | 98789 | 2.6 | 180 | 5.5666 | 669.6 | 1285.2 | 264.075 | 0 | 1 | 6
2218 | 4/3 | 09:00:00 | 281.15 | 98806 | 2.6 | 170 | 5.5656 | 1220.4 | 1980 | 265.967 | 0 | 1 | 8
2219 | 4/3 | 10:00:00 | 283.15 | 98824 | 4.1 | 170 | 5.5646 | 1692 | 2451.6 | 268.287 | 0 | 1 | 10
2220 | 4/3 | 11:00:00 | 286.15 | 98850 | 4.1 | 210 | 5.9671 | 2055.6 | 2732.4 | 271.361 | 0 | 1 | 13
2221 | 4/3 | 12:00:00 | 286.15 | 98850 | 5.7 | 210 | 4.8277 | 2275.2 | 2887.2 | 270.662 | 0 | 1 | 13
2222 | 4/3 | 13:00:00 | 287.15 | 98858 | 5.1 | 210 | 5.1833 | 2300.4 | 2887.2 | 271.843 | 0 | 1 | 14
2223 | 4/3 | 14:00:00 | 288.15 | 98867 | 6.7 | 200 | 4.4929 | 2160 | 2840.4 | 272.316 | 0 | 1 | 15
2224 | 4/3 | 15:00:00 | 288.15 | 98867 | 5.1 | 210 | 4.8269 | 1839.6 | 2541.6 | 272.553 | 0 | 1 | 15
2225 | 4/3 | 16:00:00 | 287.15 | 98858 | 5.7 | 200 | 4.8273 | 1386 | 2041.2 | 271.608 | 0 | 1 | 14
2226 | 4/3 | 17:00:00 | 286.15 | 98850 | 5.1 | 210 | 5.1837 | 849.6 | 1512 | 270.896 | 0 | 1 | 13
2227 | 4/3 | 18:00:00 | 286.15 | 98850 | 4.6 | 210 | 5.1837 | 327.6 | 468 | 270.896 | 0 | 1 | 13
2228 | 4/3 | 19:00:00 | 286.15 | 98850 | 5.7 | 220 | 5.5631 | 25.2 | 0 | 271.13 | 0 | 1 | 13
2229 | 4/3 | 20:00:00 | 284.15 | 98833 | 4.6 | 220 | 5.5641 | 0 | 0 | 269.234 | 0 | 1 | 11
2230 | 4/3 | 21:00:00 | 284.15 | 98833 | 3.1 | 210 | 5.5641 | 0 | 0 | 269.234 | 0 | 1 | 11
2231 | 4/3 | 22:00:00 | 283.15 | 98824 | 3.1 | 210 | 5.5646 | 0 | 0 | 268.55 | 0 | 1 | 10
2232 | 4/3 | 23:00:00 | 283.15 | 98824 | 5.1 | 230 | 5.5646 | 0 | 0 | 268.55 | 0 | 1 | 10
2233 | 4/3 | 24:00:00 | 283.15 | 98824 | 6.7 | 230 | 5.9687 | 0 | 0 | 268.779 | 0 | 1 | 10
2234 | 4/4 | 01:00:00 | 282.15 | 98815 | 4.6 | 230 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
2235 | 4/4 | 02:00:00 | 282.15 | 98815 | 3.6 | 240 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
2236 | 4/4 | 03:00:00 | 282.15 | 98815 | 4.1 | 240 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
2237 | 4/4 | 04:00:00 | 282.15 | 98815 | 1.5 | 290 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
2238 | 4/4 | 05:00:00 | 282.15 | 98815 | 2.6 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
2239 | 4/4 | 06:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
2240 | 4/4 | 07:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.8571 | 104.4 | 0 | 268.758 | 0 | 1 | 9
2241 | 4/4 | 08:00:00 | 282.15 | 98815 | 6.2 | 290 | 6.8571 | 356.4 | 10.8 | 268.758 | 0 | 1 | 9
2242 | 4/4 | 09:00:00 | 283.15 | 98824 | 3.6 | 310 | 7.3431 | 637.2 | 50.4 | 269.936 | 0 | 1 | 10
2243 | 4/4 | 10:00:00 | 283.15 | 98824 | 2.6 | 350 | 6.3988 | 892.8 | 144 | 269.483 | 0 | 1 | 10
2244 | 4/4 | 11:00:00 | 284.15 | 98833 | 4.1 | 310 | 6.3982 | 1083.6 | 223.2 | 270.435 | 0 | 1 | 11
2245 | 4/4 | 12:00:00 | 283.15 | 98824 | 5.1 | 300 | 6.3988 | 1191.6 | 198 | 269.483 | 0 | 1 | 10
2246 | 4/4 | 13:00:00 | 284.15 | 98833 | 4.1 | 320 | 5.9681 | 2181.6 | 1944 | 269.728 | 0 | 1 | 11
2247 | 4/4 | 14:00:00 | 285.15 | 98841 | 4.6 | 290 | 5.5636 | 2044.8 | 2250 | 270.447 | 0 | 1 | 12
2248 | 4/4 | 15:00:00 | 286.15 | 98850 | 5.1 | 310 | 4.8277 | 1857.6 | 2548.8 | 270.662 | 0 | 1 | 13
2249 | 4/4 | 16:00:00 | 286.15 | 98850 | 5.1 | 300 | 5.1837 | 1404 | 2052 | 270.896 | 0 | 1 | 13
2250 | 4/4 | 17:00:00 | 285.15 | 98841 | 5.7 | 280 | 5.1842 | 867.6 | 1530 | 269.95 | 0 | 1 | 12
2251 | 4/4 | 18:00:00 | 284.15 | 98833 | 5.7 | 280 | 5.5641 | 342 | 504 | 269.234 | 0 | 1 | 11
2252 | 4/4 | 19:00:00 | 282.15 | 98815 | 7.2 | 290 | 5.1856 | 28.8 | 0 | 267.11 | 0 | 1 | 9
2253 | 4/4 | 20:00:00 | 281.15 | 98806 | 7.2 | 300 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
2254 | 4/4 | 21:00:00 | 280.15 | 98798 | 5.7 | 290 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
2255 | 4/4 | 22:00:00 | 279.15 | 98789 | 5.7 | 290 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
2256 | 4/4 | 23:00:00 | 279.15 | 98789 | 3.6 | 290 | 4.4964 | 0 | 0 | 264.31 | 0 | 1 | 6
2257 | 4/4 | 24:00:00 | 278.15 | 98780 | 1.5 | 292 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
2258 | 4/5 | 01:00:00 | 278.15 | 98780 | 5.1 | 280 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
2259 | 4/5 | 02:00:00 | 278.15 | 98780 | 4.1 | 290 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
2260 | 4/5 | 03:00:00 | 278.15 | 98780 | 4.6 | 280 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
2261 | 4/5 | 04:00:00 | 279.15 | 98789 | 11.3 | 280 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
2262 | 4/5 | 05:00:00 | 279.15 | 98789 | 7.7 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
2263 | 4/5 | 06:00:00 | 279.15 | 98789 | 7.2 | 290 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
2264 | 4/5 | 07:00:00 | 279.15 | 98789 | 4.1 | 270 | 5.187 | 212.4 | 248.4 | 264.269 | 0 | 1 | 6
2265 | 4/5 | 08:00:00 | 280.15 | 98798 | 7.2 | 290 | 5.1865 | 705.6 | 1296 | 265.216 | 0 | 1 | 7
2266 | 4/5 | 09:00:00 | 281.15 | 98806 | 7.2 | 300 | 5.1861 | 1180.8 | 1681.2 | 266.423 | 0 | 1 | 8
2267 | 4/5 | 10:00:00 | 282.15 | 98815 | 5.1 | 310 | 5.1856 | 1641.6 | 2073.6 | 267.371 | 0 | 1 | 9
2268 | 4/5 | 11:00:00 | 283.15 | 98824 | 6.2 | 300 | 5.1851 | 1983.6 | 2322 | 268.319 | 0 | 1 | 10
2269 | 4/5 | 12:00:00 | 284.15 | 98833 | 6.7 | 290 | 5.5641 | 2174.4 | 2386.8 | 269.498 | 0 | 1 | 11
2270 | 4/5 | 13:00:00 | 285.15 | 98841 | 7.7 | 280 | 5.5636 | 2203.2 | 2397.6 | 270.447 | 0 | 1 | 12
2271 | 4/5 | 14:00:00 | 284.15 | 98833 | 6.7 | 270 | 5.5641 | 2062.8 | 2343.6 | 269.498 | 0 | 1 | 11
2272 | 4/5 | 15:00:00 | 284.15 | 98833 | 9.3 | 280 | 5.5641 | 1764 | 2149.2 | 269.498 | 0 | 1 | 11
2273 | 4/5 | 16:00:00 | 283.15 | 98824 | 8.2 | 280 | 5.9687 | 1335.6 | 1717.2 | 268.779 | 0 | 1 | 10
2274 | 4/5 | 17:00:00 | 283.15 | 98824 | 6.7 | 260 | 5.9687 | 828 | 1267.2 | 268.779 | 0 | 1 | 10
2275 | 4/5 | 18:00:00 | 282.15 | 98815 | 5.1 | 280 | 5.9692 | 334.8 | 414 | 267.83 | 0 | 1 | 9
2276 | 4/5 | 19:00:00 | 282.15 | 98815 | 6.2 | 280 | 5.5651 | 32.4 | 0 | 267.601 | 0 | 1 | 9
2277 | 4/5 | 20:00:00 | 281.15 | 98806 | 5.7 | 280 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
2278 | 4/5 | 21:00:00 | 280.15 | 98798 | 4.6 | 300 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
2279 | 4/5 | 22:00:00 | 279.15 | 98789 | 3.6 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
2280 | 4/5 | 23:00:00 | 278.15 | 98780 | 3.6 | 260 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
2281 | 4/5 | 24:00:00 | 278.15 | 98780 | 3.1 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
2282 | 4/6 | 01:00:00 | 277.15 | 98771 | 3.6 | 280 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
2283 | 4/6 | 02:00:00 | 277.15 | 98771 | 3.1 | 280 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
2284 | 4/6 | 03:00:00 | 277.15 | 98771 | 3.6 | 290 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
2285 | 4/6 | 04:00:00 | 276.15 | 98762 | 3.6 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2286 | 4/6 | 05:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
2287 | 4/6 | 06:00:00 | 276.15 | 98762 | 3.6 | 290 | 4.832 | 0 | 0 | 261.203 | 0 | 1 | 3
2288 | 4/6 | 07:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.832 | 230.4 | 277.2 | 261.203 | 0 | 1 | 3
2289 | 4/6 | 08:00:00 | 278.15 | 98780 | 4.6 | 260 | 5.1875 | 727.2 | 1321.2 | 263.323 | 0 | 1 | 5
2290 | 4/6 | 09:00:00 | 279.15 | 98789 | 5.7 | 270 | 5.5666 | 1198.8 | 1684.8 | 264.756 | 0 | 1 | 6
2291 | 4/6 | 10:00:00 | 281.15 | 98806 | 5.7 | 270 | 5.5656 | 1659.6 | 1681.2 | 266.653 | 0 | 1 | 8
2292 | 4/6 | 11:00:00 | 282.15 | 98815 | 7.7 | 270 | 5.5651 | 1112.4 | 194.4 | 268.075 | 0 | 1 | 9
2293 | 4/6 | 12:00:00 | 282.15 | 98815 | 7.2 | 280 | 5.5651 | 1216.8 | 237.6 | 268.075 | 0 | 1 | 9
2294 | 4/6 | 13:00:00 | 282.15 | 98815 | 7.2 | 290 | 5.5651 | 1231.2 | 205.2 | 268.075 | 0 | 1 | 9
2295 | 4/6 | 14:00:00 | 282.15 | 98815 | 7.2 | 280 | 5.5651 | 2080.8 | 1886.4 | 267.601 | 0 | 1 | 9
2296 | 4/6 | 15:00:00 | 282.15 | 98815 | 9.3 | 280 | 5.1856 | 1782 | 2163.6 | 267.371 | 0 | 1 | 9
2297 | 4/6 | 16:00:00 | 281.15 | 98806 | 9.8 | 280 | 5.1861 | 1353.6 | 1742.4 | 266.423 | 0 | 1 | 8
2298 | 4/6 | 17:00:00 | 282.15 | 98815 | 9.8 | 280 | 5.1856 | 846 | 1296 | 267.371 | 0 | 1 | 9
2299 | 4/6 | 18:00:00 | 281.15 | 98806 | 11.8 | 280 | 5.1861 | 349.2 | 435.6 | 266.423 | 0 | 1 | 8
2300 | 4/6 | 19:00:00 | 280.15 | 98798 | 10.8 | 280 | 5.1865 | 39.6 | 0 | 265.476 | 0 | 1 | 7
2301 | 4/6 | 20:00:00 | 280.15 | 98798 | 8.2 | 290 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
2302 | 4/6 | 21:00:00 | 280.15 | 98798 | 6.2 | 280 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
2303 | 4/6 | 22:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.5666 | 0 | 0 | 264.497 | 0 | 1 | 6
2304 | 4/6 | 23:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2305 | 4/6 | 24:00:00 | 279.15 | 98789 | 5.1 | 270 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2306 | 4/7 | 01:00:00 | 279.15 | 98789 | 4.1 | 280 | 5.5666 | 0 | 0 | 264.497 | 0 | 1 | 6
2307 | 4/7 | 02:00:00 | 279.15 | 98789 | 3.6 | 270 | 5.5666 | 0 | 0 | 264.497 | 0 | 1 | 6
2308 | 4/7 | 03:00:00 | 278.15 | 98780 | 4.1 | 270 | 5.5671 | 0 | 0 | 263.549 | 0 | 1 | 5
2309 | 4/7 | 04:00:00 | 279.15 | 98789 | 4.6 | 280 | 5.9708 | 0 | 0 | 265.559 | 0 | 1 | 6
2310 | 4/7 | 05:00:00 | 279.15 | 98789 | 5.1 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
2311 | 4/7 | 06:00:00 | 280.15 | 98798 | 3.6 | 290 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2312 | 4/7 | 07:00:00 | 280.15 | 98798 | 4.6 | 290 | 5.1865 | 129.6 | 0 | 265.946 | 0 | 1 | 7
2313 | 4/7 | 08:00:00 | 280.15 | 98798 | 4.6 | 290 | 5.1865 | 388.8 | 21.6 | 265.946 | 0 | 1 | 7
2314 | 4/7 | 09:00:00 | 280.15 | 98798 | 4.6 | 310 | 5.1865 | 676.8 | 57.6 | 265.946 | 0 | 1 | 7
2315 | 4/7 | 10:00:00 | 281.15 | 98806 | 5.1 | 310 | 4.8299 | 936 | 151.2 | 266.664 | 0 | 1 | 8
2316 | 4/7 | 11:00:00 | 281.15 | 98806 | 4.1 | 290 | 5.1861 | 1123.2 | 230.4 | 266.895 | 0 | 1 | 8
2317 | 4/7 | 12:00:00 | 281.15 | 98806 | 4.1 | 300 | 4.8299 | 1231.2 | 237.6 | 266.664 | 0 | 1 | 8
2318 | 4/7 | 13:00:00 | 282.15 | 98815 | 4.1 | 290 | 5.1856 | 1245.6 | 90 | 267.844 | 0 | 1 | 9
2319 | 4/7 | 14:00:00 | 282.15 | 98815 | 5.1 | 280 | 5.1856 | 709.2 | 7.2 | 267.953 | 0 | 1 | 9
2320 | 4/7 | 15:00:00 | 282.15 | 98815 | 4.1 | 290 | 5.1856 | 997.2 | 324 | 267.844 | 0 | 1 | 9
2321 | 4/7 | 16:00:00 | 284.15 | 98833 | 4.6 | 270 | 5.1847 | 1454.4 | 1789.2 | 269.003 | 0 | 1 | 11
2322 | 4/7 | 17:00:00 | 283.15 | 98824 | 5.1 | 280 | 5.1851 | 914.4 | 1576.8 | 268.056 | 0 | 1 | 10
2323 | 4/7 | 18:00:00 | 282.15 | 98815 | 4.6 | 280 | 5.1856 | 342 | 450 | 267.495 | 0 | 1 | 9
2324 | 4/7 | 19:00:00 | 281.15 | 98806 | 3.1 | 270 | 4.8299 | 39.6 | 0 | 266.316 | 0 | 1 | 8
2325 | 4/7 | 20:00:00 | 279.15 | 98789 | 2.6 | 260 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
2326 | 4/7 | 21:00:00 | 278.15 | 98780 | 2.1 | 260 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2327 | 4/7 | 22:00:00 | 278.15 | 98780 | 2.1 | 270 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2328 | 4/7 | 23:00:00 | 277.15 | 98771 | 2.6 | 270 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
2329 | 4/7 | 24:00:00 | 276.15 | 98762 | 1.5 | 290 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2330 | 4/8 | 01:00:00 | 275.15 | 98752 | 3.1 | 260 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
2331 | 4/8 | 02:00:00 | 276.15 | 98762 | 2.6 | 260 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2332 | 4/8 | 03:00:00 | 276.15 | 98762 | 1.5 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2333 | 4/8 | 04:00:00 | 276.15 | 98762 | 1.5 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2334 | 4/8 | 05:00:00 | 275.15 | 98752 | 1.5 | 280 | 4.1846 | 0 | 0 | 259.387 | 0 | 1 | 2
2335 | 4/8 | 06:00:00 | 276.15 | 98762 | 0 | 124 | 4.4977 | 0 | 0 | 260.558 | 0 | 1 | 3
2336 | 4/8 | 07:00:00 | 277.15 | 98771 | 0.5 | 140 | 4.8316 | 262.8 | 349.2 | 261.73 | 0 | 1 | 4
2337 | 4/8 | 08:00:00 | 279.15 | 98789 | 1 | 108 | 5.187 | 777.6 | 1429.2 | 263.847 | 0 | 1 | 6
2338 | 4/8 | 09:00:00 | 281.15 | 98806 | 1 | 107 | 5.5656 | 1335.6 | 1893.6 | 265.967 | 0 | 1 | 8
2339 | 4/8 | 10:00:00 | 283.15 | 98824 | 1.5 | 42 | 5.9687 | 1497.6 | 1220.4 | 269.025 | 0 | 1 | 10
2340 | 4/8 | 11:00:00 | 285.15 | 98841 | 2.1 | 180 | 6.3977 | 2188.8 | 2520 | 270.21 | 0 | 1 | 12
2341 | 4/8 | 12:00:00 | 287.15 | 98858 | 2.6 | 200 | 6.854 | 2386.8 | 2941.2 | 272.335 | 0 | 1 | 14
2342 | 4/8 | 13:00:00 | 289.15 | 98875 | 3.1 | 160 | 6.8529 | 2347.2 | 2710.8 | 274.807 | 0 | 1 | 16
2343 | 4/8 | 14:00:00 | 290.15 | 98883 | 2.6 | 150 | 6.8523 | 2228.4 | 2761.2 | 275.62 | 0 | 1 | 17
2344 | 4/8 | 15:00:00 | 291.15 | 98892 | 3.1 | 170 | 6.3944 | 1936.8 | 2682 | 276.195 | 0 | 1 | 18
2345 | 4/8 | 16:00:00 | 291.15 | 98892 | 3.1 | 180 | 6.3944 | 1479.6 | 2174.4 | 276.195 | 0 | 1 | 18
2346 | 4/8 | 17:00:00 | 291.15 | 98892 | 3.1 | 210 | 5.9645 | 939.6 | 1634.4 | 275.961 | 0 | 1 | 18
2347 | 4/8 | 18:00:00 | 291.15 | 98892 | 2.6 | 230 | 5.5607 | 399.6 | 759.6 | 275.578 | 0 | 1 | 18
2348 | 4/8 | 19:00:00 | 288.15 | 98867 | 1.5 | 283 | 5.1829 | 50.4 | 0 | 272.649 | 0 | 1 | 15
2349 | 4/8 | 20:00:00 | 287.15 | 98858 | 1.5 | 230 | 5.1833 | 0 | 0 | 271.843 | 0 | 1 | 14
2350 | 4/8 | 21:00:00 | 287.15 | 98858 | 1 | 129 | 5.1833 | 0 | 0 | 271.843 | 0 | 1 | 14
2351 | 4/8 | 22:00:00 | 283.15 | 98824 | 3.1 | 190 | 5.1851 | 0 | 0 | 268.319 | 0 | 1 | 10
2352 | 4/8 | 23:00:00 | 285.15 | 98841 | 1 | 166 | 5.1842 | 0 | 0 | 270.084 | 0 | 1 | 12
2353 | 4/8 | 24:00:00 | 285.15 | 98841 | 1.5 | 230 | 5.1842 | 0 | 0 | 270.084 | 0 | 1 | 12
2354 | 4/9 | 01:00:00 | 283.15 | 98824 | 2.1 | 180 | 5.1851 | 0 | 0 | 268.319 | 0 | 1 | 10
2355 | 4/9 | 02:00:00 | 282.15 | 98815 | 2.6 | 210 | 5.5651 | 0 | 0 | 267.846 | 0 | 1 | 9
2356 | 4/9 | 03:00:00 | 285.15 | 98841 | 5.1 | 230 | 6.3977 | 0 | 0 | 271.033 | 0 | 1 | 12
2357 | 4/9 | 04:00:00 | 284.15 | 98833 | 4.1 | 220 | 6.3982 | 0 | 0 | 270.204 | 0 | 1 | 11
2358 | 4/9 | 05:00:00 | 283.15 | 98824 | 2.6 | 210 | 5.9687 | 0 | 0 | 269.025 | 0 | 1 | 10
2359 | 4/9 | 06:00:00 | 282.15 | 98815 | 2.1 | 240 | 5.5651 | 3.6 | 0 | 267.846 | 0 | 1 | 9
2360 | 4/9 | 07:00:00 | 282.15 | 98815 | 2.1 | 240 | 5.5651 | 230.4 | 133.2 | 267.846 | 0 | 1 | 9
2361 | 4/9 | 08:00:00 | 284.15 | 98833 | 1 | 181 | 5.9681 | 702 | 957.6 | 269.854 | 0 | 1 | 11
2362 | 4/9 | 09:00:00 | 286.15 | 98850 | 1.5 | 24 | 6.3971 | 1245.6 | 1591.2 | 271.858 | 0 | 1 | 13
2363 | 4/9 | 10:00:00 | 288.15 | 98867 | 2.6 | 170 | 7.3399 | 1695.6 | 1911.6 | 274.218 | 0 | 1 | 15
2364 | 4/9 | 11:00:00 | 291.15 | 98892 | 3.1 | 180 | 7.855 | 2134.8 | 2440.8 | 277.17 | 0 | 1 | 18
2365 | 4/9 | 12:00:00 | 292.15 | 98900 | 5.1 | 220 | 7.3374 | 2383.2 | 2869.2 | 277.752 | 0 | 1 | 19
2366 | 4/9 | 13:00:00 | 292.15 | 98900 | 5.7 | 220 | 6.8511 | 2422.8 | 2923.2 | 277.377 | 0 | 1 | 19
2367 | 4/9 | 14:00:00 | 292.15 | 98900 | 6.2 | 240 | 7.3374 | 2246.4 | 2775.6 | 277.752 | 0 | 1 | 19
2368 | 4/9 | 15:00:00 | 290.15 | 98883 | 7.7 | 270 | 7.8557 | 1951.2 | 2660.4 | 275.639 | 0 | 1 | 17
2369 | 4/9 | 16:00:00 | 287.15 | 98858 | 9.3 | 280 | 7.8578 | 1472.4 | 2120.4 | 273.226 | 0 | 1 | 14
2370 | 4/9 | 17:00:00 | 285.15 | 98841 | 11.8 | 270 | 6.8552 | 885.6 | 1245.6 | 271.136 | 0 | 1 | 12
2371 | 4/9 | 18:00:00 | 284.15 | 98833 | 9.3 | 270 | 6.3982 | 406.8 | 759.6 | 269.693 | 0 | 1 | 11
2372 | 4/9 | 19:00:00 | 283.15 | 98824 | 9.3 | 270 | 6.3988 | 50.4 | 0 | 269.007 | 0 | 1 | 10
2373 | 4/9 | 20:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
2374 | 4/9 | 21:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
2375 | 4/9 | 22:00:00 | 282.15 | 98815 | 9.3 | 280 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
2376 | 4/9 | 23:00:00 | 281.15 | 98806 | 9.8 | 290 | 5.1861 | 0 | 0 | 266.423 | 0 | 1 | 8
2377 | 4/9 | 24:00:00 | 279.15 | 98789 | 9.3 | 290 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
2378 | 4/10 | 01:00:00 | 278.15 | 98780 | 10.3 | 290 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
2379 | 4/10 | 02:00:00 | 278.15 | 98780 | 7.7 | 300 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
2380 | 4/10 | 03:00:00 | 278.15 | 98780 | 4.1 | 300 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
2381 | 4/10 | 04:00:00 | 278.15 | 98780 | 5.1 | 290 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2382 | 4/10 | 05:00:00 | 278.15 | 98780 | 7.7 | 290 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
2383 | 4/10 | 06:00:00 | 278.15 | 98780 | 7.2 | 290 | 4.8311 | 10.8 | 0 | 263.352 | 0 | 1 | 5
2384 | 4/10 | 07:00:00 | 278.15 | 98780 | 7.2 | 290 | 4.8311 | 291.6 | 381.6 | 263.095 | 0 | 1 | 5
2385 | 4/10 | 08:00:00 | 280.15 | 98798 | 7.2 | 280 | 4.8303 | 810 | 1422 | 264.986 | 0 | 1 | 7
2386 | 4/10 | 09:00:00 | 281.15 | 98806 | 9.8 | 290 | 4.8299 | 1364.4 | 1976.4 | 265.932 | 0 | 1 | 8
2387 | 4/10 | 10:00:00 | 282.15 | 98815 | 8.8 | 300 | 4.4952 | 1854 | 2512.8 | 266.645 | 0 | 1 | 9
2388 | 4/10 | 11:00:00 | 284.15 | 98833 | 6.7 | 310 | 4.8285 | 2084.4 | 2228.4 | 269.033 | 0 | 1 | 11
2389 | 4/10 | 12:00:00 | 283.15 | 98824 | 5.7 | 300 | 4.829 | 2275.2 | 2422.8 | 268.086 | 0 | 1 | 10
2390 | 4/10 | 13:00:00 | 285.15 | 98841 | 6.2 | 290 | 5.1842 | 2296.8 | 2415.6 | 270.214 | 0 | 1 | 12
2391 | 4/10 | 14:00:00 | 283.15 | 98824 | 6.2 | 300 | 5.1851 | 2149.2 | 2246.4 | 268.319 | 0 | 1 | 10
2392 | 4/10 | 15:00:00 | 284.15 | 98833 | 7.2 | 270 | 5.1847 | 1962 | 2566.8 | 269.003 | 0 | 1 | 11
2393 | 4/10 | 16:00:00 | 284.15 | 98833 | 7.2 | 270 | 5.1847 | 1504.8 | 2106 | 269.003 | 0 | 1 | 11
2394 | 4/10 | 17:00:00 | 283.15 | 98824 | 7.7 | 280 | 5.1851 | 907.2 | 1281.6 | 268.319 | 0 | 1 | 10
2395 | 4/10 | 18:00:00 | 282.15 | 98815 | 7.2 | 280 | 5.1856 | 396 | 496.8 | 267.371 | 0 | 1 | 9
2396 | 4/10 | 19:00:00 | 282.15 | 98815 | 5.7 | 270 | 5.1856 | 61.2 | 0 | 267.11 | 0 | 1 | 9
2397 | 4/10 | 20:00:00 | 281.15 | 98806 | 6.2 | 280 | 5.1861 | 0 | 0 | 266.163 | 0 | 1 | 8
2398 | 4/10 | 21:00:00 | 280.15 | 98798 | 6.7 | 290 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
2399 | 4/10 | 22:00:00 | 280.15 | 98798 | 5.1 | 280 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
2400 | 4/10 | 23:00:00 | 279.15 | 98789 | 4.6 | 300 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
2401 | 4/10 | 24:00:00 | 278.15 | 98780 | 5.7 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2402 | 4/11 | 01:00:00 | 278.15 | 98780 | 3.1 | 270 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
2403 | 4/11 | 02:00:00 | 278.15 | 98780 | 6.2 | 290 | 4.4968 | 0 | 0 | 262.865 | 0 | 1 | 5
2404 | 4/11 | 03:00:00 | 277.15 | 98771 | 5.7 | 270 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
2405 | 4/11 | 04:00:00 | 277.15 | 98771 | 5.1 | 270 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
2406 | 4/11 | 05:00:00 | 277.15 | 98771 | 3.6 | 280 | 4.8316 | 0 | 0 | 262.405 | 0 | 1 | 4
2407 | 4/11 | 06:00:00 | 278.15 | 98780 | 5.7 | 260 | 4.8311 | 18 | 0 | 263.095 | 0 | 1 | 5
2408 | 4/11 | 07:00:00 | 279.15 | 98789 | 4.6 | 250 | 5.187 | 309.6 | 403.2 | 264.269 | 0 | 1 | 6
2409 | 4/11 | 08:00:00 | 280.15 | 98798 | 6.2 | 260 | 5.1865 | 781.2 | 1231.2 | 265.476 | 0 | 1 | 7
2410 | 4/11 | 09:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.5656 | 1299.6 | 1674 | 266.653 | 0 | 1 | 8
2411 | 4/11 | 10:00:00 | 282.15 | 98815 | 7.7 | 270 | 5.1856 | 1760.4 | 2127.6 | 267.371 | 0 | 1 | 9
2412 | 4/11 | 11:00:00 | 282.15 | 98815 | 10.8 | 270 | 5.1856 | 2102.4 | 2347.2 | 267.371 | 0 | 1 | 9
2413 | 4/11 | 12:00:00 | 282.15 | 98815 | 10.3 | 270 | 5.1856 | 2289.6 | 2408.4 | 267.371 | 0 | 1 | 9
2414 | 4/11 | 13:00:00 | 284.15 | 98833 | 10.8 | 260 | 5.1847 | 2311.2 | 2415.6 | 269.266 | 0 | 1 | 11
2415 | 4/11 | 14:00:00 | 283.15 | 98824 | 7.2 | 260 | 5.1851 | 2167.2 | 1890 | 268.319 | 0 | 1 | 10
2416 | 4/11 | 15:00:00 | 282.15 | 98815 | 6.2 | 260 | 5.1856 | 1033.2 | 259.2 | 267.844 | 0 | 1 | 9
2417 | 4/11 | 16:00:00 | 282.15 | 98815 | 10.3 | 260 | 5.1856 | 1432.8 | 1501.2 | 267.371 | 0 | 1 | 9
2418 | 4/11 | 17:00:00 | 282.15 | 98815 | 12.4 | 260 | 5.1856 | 921.6 | 1339.2 | 267.371 | 0 | 1 | 9
2419 | 4/11 | 18:00:00 | 281.15 | 98806 | 12.9 | 260 | 5.1861 | 410.4 | 511.2 | 266.423 | 0 | 1 | 8
2420 | 4/11 | 19:00:00 | 281.15 | 98806 | 8.2 | 260 | 5.5656 | 61.2 | 0 | 266.653 | 0 | 1 | 8
2421 | 4/11 | 20:00:00 | 281.15 | 98806 | 11.3 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
2422 | 4/11 | 21:00:00 | 281.15 | 98806 | 10.8 | 280 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
2423 | 4/11 | 22:00:00 | 281.15 | 98806 | 9.3 | 270 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
2424 | 4/11 | 23:00:00 | 281.15 | 98806 | 10.8 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
2425 | 4/11 | 24:00:00 | 281.15 | 98806 | 10.8 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
2426 | 4/12 | 01:00:00 | 281.15 | 98806 | 10.8 | 280 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
2427 | 4/12 | 02:00:00 | 280.65 | 98802 | 8.8 | 239 | 5.7648 | 0 | 0 | 266.764 | 0 | 1 | 7.5
2428 | 4/12 | 03:00:00 | 280.15 | 98798 | 6.7 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2429 | 4/12 | 04:00:00 | 280.15 | 98798 | 6.2 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2430 | 4/12 | 05:00:00 | 280.15 | 98798 | 6.7 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2431 | 4/12 | 06:00:00 | 280.15 | 98798 | 7.7 | 260 | 5.9703 | 14.4 | 0 | 266.402 | 0 | 1 | 7
2432 | 4/12 | 07:00:00 | 280.15 | 98798 | 6.7 | 250 | 5.9703 | 169.2 | 0 | 266.402 | 0 | 1 | 7
2433 | 4/12 | 08:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.9703 | 442.8 | 32.4 | 266.402 | 0 | 1 | 7
2434 | 4/12 | 09:00:00 | 281.15 | 98806 | 9.3 | 260 | 5.9698 | 730.8 | 61.2 | 267.353 | 0 | 1 | 8
2435 | 4/12 | 10:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.4 | 982.8 | 151.2 | 267.58 | 0 | 1 | 8
2436 | 4/12 | 11:00:00 | 282.15 | 98815 | 9.3 | 270 | 6.3994 | 1170 | 226.8 | 268.532 | 0 | 1 | 9
2437 | 4/12 | 12:00:00 | 282.15 | 98815 | 9.3 | 270 | 6.3994 | 1274.4 | 234 | 268.532 | 0 | 1 | 9
2438 | 4/12 | 13:00:00 | 282.15 | 98815 | 8.2 | 270 | 6.8571 | 1285.2 | 201.6 | 268.758 | 0 | 1 | 9
2439 | 4/12 | 14:00:00 | 282.15 | 98815 | 6.7 | 270 | 6.8571 | 2170.8 | 1911.6 | 268.283 | 0 | 1 | 9
2440 | 4/12 | 15:00:00 | 283.15 | 98824 | 13.4 | 280 | 5.9687 | 1875.6 | 2109.6 | 268.779 | 0 | 1 | 10
2441 | 4/12 | 16:00:00 | 284.15 | 98833 | 14.4 | 280 | 4.8285 | 1540.8 | 2296.8 | 268.77 | 0 | 1 | 11
2442 | 4/12 | 17:00:00 | 283.15 | 98824 | 12.9 | 280 | 4.4948 | 997.2 | 1645.2 | 267.59 | 0 | 1 | 10
2443 | 4/12 | 18:00:00 | 282.15 | 98815 | 14.4 | 290 | 4.4952 | 450 | 820.8 | 266.645 | 0 | 1 | 9
2444 | 4/12 | 19:00:00 | 281.15 | 98806 | 9.8 | 280 | 4.8299 | 72 | 0 | 265.932 | 0 | 1 | 8
2445 | 4/12 | 20:00:00 | 280.15 | 98798 | 8.2 | 280 | 4.8303 | 0 | 0 | 264.986 | 0 | 1 | 7
2446 | 4/12 | 21:00:00 | 279.15 | 98789 | 7.7 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
2447 | 4/12 | 22:00:00 | 279.15 | 98789 | 6.2 | 290 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
2448 | 4/12 | 23:00:00 | 279.15 | 98789 | 6.2 | 290 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
2449 | 4/12 | 24:00:00 | 278.15 | 98780 | 6.7 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2450 | 4/13 | 01:00:00 | 278.15 | 98780 | 6.7 | 290 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2451 | 4/13 | 02:00:00 | 278.15 | 98780 | 7.7 | 300 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
2452 | 4/13 | 03:00:00 | 278.15 | 98780 | 9.3 | 300 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
2453 | 4/13 | 04:00:00 | 277.15 | 98771 | 6.2 | 280 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
2454 | 4/13 | 05:00:00 | 278.15 | 98780 | 7.7 | 290 | 4.4968 | 0 | 0 | 262.865 | 0 | 1 | 5
2455 | 4/13 | 06:00:00 | 278.15 | 98780 | 6.2 | 290 | 4.8311 | 32.4 | 0 | 263.095 | 0 | 1 | 5
2456 | 4/13 | 07:00:00 | 278.15 | 98780 | 4.6 | 280 | 4.8311 | 342 | 396 | 263.095 | 0 | 1 | 5
2457 | 4/13 | 08:00:00 | 279.15 | 98789 | 6.7 | 290 | 5.187 | 817.2 | 1270.8 | 264.528 | 0 | 1 | 6
2458 | 4/13 | 09:00:00 | 281.15 | 98806 | 5.7 | 300 | 5.1861 | 1342.8 | 1702.8 | 266.423 | 0 | 1 | 8
2459 | 4/13 | 10:00:00 | 281.15 | 98806 | 5.1 | 290 | 4.8299 | 1803.6 | 2095.2 | 266.193 | 0 | 1 | 8
2460 | 4/13 | 11:00:00 | 282.15 | 98815 | 6.7 | 280 | 5.1856 | 2138.4 | 2354.4 | 267.371 | 0 | 1 | 9
2461 | 4/13 | 12:00:00 | 283.15 | 98824 | 7.2 | 270 | 5.1851 | 2325.6 | 1936.8 | 268.319 | 0 | 1 | 10
2462 | 4/13 | 13:00:00 | 281.15 | 98806 | 7.2 | 280 | 5.1861 | 1303.2 | 284.4 | 266.895 | 0 | 1 | 8
2463 | 4/13 | 14:00:00 | 281.15 | 98806 | 6.7 | 280 | 5.1861 | 2199.6 | 1350 | 266.423 | 0 | 1 | 8
2464 | 4/13 | 15:00:00 | 282.15 | 98815 | 7.2 | 280 | 4.8294 | 1054.8 | 190.8 | 267.612 | 0 | 1 | 9
2465 | 4/13 | 16:00:00 | 282.15 | 98815 | 7.2 | 270 | 4.8294 | 813.6 | 68.4 | 267.612 | 0 | 1 | 9
2466 | 4/13 | 17:00:00 | 281.15 | 98806 | 7.2 | 280 | 4.8299 | 529.2 | 21.6 | 266.664 | 0 | 1 | 8
2467 | 4/13 | 18:00:00 | 281.15 | 98806 | 5.7 | 270 | 5.1861 | 241.2 | 0 | 266.895 | 0 | 1 | 8
2468 | 4/13 | 19:00:00 | 280.15 | 98798 | 6.2 | 270 | 5.1865 | 39.6 | 0 | 265.946 | 0 | 1 | 7
2469 | 4/13 | 20:00:00 | 280.15 | 98798 | 5.7 | 270 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
2470 | 4/13 | 21:00:00 | 280.15 | 98798 | 4.6 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
2471 | 4/13 | 22:00:00 | 280.15 | 98798 | 6.2 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
2472 | 4/13 | 23:00:00 | 280.15 | 98798 | 5.7 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
2473 | 4/13 | 24:00:00 | 280.15 | 98798 | 4.6 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
2474 | 4/14 | 01:00:00 | 280.15 | 98798 | 6.2 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2475 | 4/14 | 02:00:00 | 280.15 | 98798 | 9.3 | 270 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
2476 | 4/14 | 03:00:00 | 280.15 | 98798 | 5.1 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2477 | 4/14 | 04:00:00 | 280.15 | 98798 | 4.1 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2478 | 4/14 | 05:00:00 | 280.15 | 98798 | 2.1 | 210 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2479 | 4/14 | 06:00:00 | 279.15 | 98789 | 1.5 | 108 | 5.5666 | 21.6 | 0 | 265.224 | 0 | 1 | 6
2480 | 4/14 | 07:00:00 | 279.15 | 98789 | 2.1 | 210 | 5.9708 | 187.2 | 0 | 265.451 | 0 | 1 | 6
2481 | 4/14 | 08:00:00 | 280.15 | 98798 | 2.1 | 200 | 5.9703 | 464.4 | 36 | 266.402 | 0 | 1 | 7
2482 | 4/14 | 09:00:00 | 281.15 | 98806 | 3.1 | 220 | 6.4 | 752.4 | 61.2 | 267.58 | 0 | 1 | 8
2483 | 4/14 | 10:00:00 | 281.15 | 98806 | 3.1 | 220 | 6.4 | 1004.4 | 208.8 | 267.58 | 0 | 1 | 8
2484 | 4/14 | 11:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.8577 | 1188 | 194.4 | 267.805 | 0 | 1 | 8
2485 | 4/14 | 12:00:00 | 283.15 | 98824 | 5.1 | 250 | 6.8564 | 2329.2 | 1339.2 | 269.234 | 0 | 1 | 10
2486 | 4/14 | 13:00:00 | 283.15 | 98824 | 5.1 | 260 | 7.3431 | 1299.6 | 273.6 | 269.936 | 0 | 1 | 10
2487 | 4/14 | 14:00:00 | 283.15 | 98824 | 7.7 | 260 | 6.3988 | 2206.8 | 1267.2 | 269.007 | 0 | 1 | 10
2488 | 4/14 | 15:00:00 | 283.15 | 98824 | 7.2 | 260 | 6.3988 | 1054.8 | 183.6 | 269.483 | 0 | 1 | 10
2489 | 4/14 | 16:00:00 | 282.15 | 98815 | 6.7 | 270 | 5.9692 | 817.2 | 68.4 | 268.304 | 0 | 1 | 9
2490 | 4/14 | 17:00:00 | 282.15 | 98815 | 5.1 | 270 | 5.9692 | 532.8 | 21.6 | 268.304 | 0 | 1 | 9
2491 | 4/14 | 18:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.3994 | 248.4 | 0 | 268.532 | 0 | 1 | 9
2492 | 4/14 | 19:00:00 | 281.15 | 98806 | 4.6 | 290 | 6.4 | 75.6 | 0 | 267.107 | 0 | 1 | 8
2493 | 4/14 | 20:00:00 | 280.15 | 98798 | 5.1 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
2494 | 4/14 | 21:00:00 | 280.15 | 98798 | 4.1 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
2495 | 4/14 | 22:00:00 | 280.15 | 98798 | 4.6 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
2496 | 4/14 | 23:00:00 | 280.15 | 98798 | 4.1 | 290 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
2497 | 4/14 | 24:00:00 | 279.15 | 98789 | 2.6 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
2498 | 4/15 | 01:00:00 | 279.15 | 98789 | 4.1 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
2499 | 4/15 | 02:00:00 | 278.15 | 98780 | 3.6 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
2500 | 4/15 | 03:00:00 | 278.15 | 98780 | 5.1 | 300 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
2501 | 4/15 | 04:00:00 | 278.15 | 98780 | 6.2 | 280 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
2502 | 4/15 | 05:00:00 | 277.15 | 98771 | 9.3 | 280 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
2503 | 4/15 | 06:00:00 | 277.15 | 98771 | 9.8 | 270 | 4.4973 | 46.8 | 0 | 261.92 | 0 | 1 | 4
2504 | 4/15 | 07:00:00 | 278.15 | 98780 | 9.8 | 270 | 4.4968 | 374.4 | 525.6 | 262.865 | 0 | 1 | 5
2505 | 4/15 | 08:00:00 | 278.15 | 98780 | 8.2 | 270 | 4.8311 | 907.2 | 1576.8 | 263.095 | 0 | 1 | 5
2506 | 4/15 | 09:00:00 | 279.15 | 98789 | 8.8 | 270 | 4.8307 | 1382.4 | 1796.4 | 264.299 | 0 | 1 | 6
2507 | 4/15 | 10:00:00 | 280.15 | 98798 | 8.8 | 280 | 4.8303 | 1839.6 | 2102.4 | 265.246 | 0 | 1 | 7
2508 | 4/15 | 11:00:00 | 282.15 | 98815 | 8.8 | 280 | 4.8294 | 2178 | 2372.4 | 267.139 | 0 | 1 | 9
2509 | 4/15 | 12:00:00 | 282.15 | 98815 | 9.8 | 280 | 4.8294 | 2361.6 | 2422.8 | 267.139 | 0 | 1 | 9
2510 | 4/15 | 13:00:00 | 282.15 | 98815 | 10.3 | 270 | 4.8294 | 2383.2 | 2426.4 | 267.139 | 0 | 1 | 9
2511 | 4/15 | 14:00:00 | 283.15 | 98824 | 10.8 | 270 | 4.4948 | 2239.2 | 2404.8 | 267.852 | 0 | 1 | 10
2512 | 4/15 | 15:00:00 | 282.15 | 98815 | 11.3 | 280 | 4.1819 | 1936.8 | 1846.8 | 266.672 | 0 | 1 | 9
2513 | 4/15 | 16:00:00 | 282.15 | 98815 | 10.3 | 280 | 4.4952 | 1497.6 | 1659.6 | 266.906 | 0 | 1 | 9
2514 | 4/15 | 17:00:00 | 282.15 | 98815 | 8.8 | 280 | 4.4952 | 1040.4 | 1677.6 | 266.645 | 0 | 1 | 9
2515 | 4/15 | 18:00:00 | 281.15 | 98806 | 9.8 | 280 | 3.8882 | 489.6 | 748.8 | 265.232 | 0 | 1 | 8
2516 | 4/15 | 19:00:00 | 280.15 | 98798 | 10.3 | 280 | 3.8885 | 86.4 | 0 | 264.289 | 0 | 1 | 7
2517 | 4/15 | 20:00:00 | 279.15 | 98789 | 9.3 | 280 | 4.183 | 0 | 0 | 263.578 | 0 | 1 | 6
2518 | 4/15 | 21:00:00 | 278.15 | 98780 | 5.7 | 280 | 4.1834 | 0 | 0 | 263.132 | 0 | 1 | 5
2519 | 4/15 | 22:00:00 | 278.15 | 98780 | 4.1 | 280 | 3.8892 | 0 | 0 | 262.781 | 0 | 1 | 5
2520 | 4/15 | 23:00:00 | 277.15 | 98771 | 5.1 | 270 | 3.5793 | 0 | 0 | 261.603 | 0 | 1 | 4
2521 | 4/15 | 24:00:00 | 277.15 | 98771 | 5.7 | 300 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
2522 | 4/16 | 01:00:00 | 277.15 | 98771 | 6.2 | 290 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
2523 | 4/16 | 02:00:00 | 277.15 | 98771 | 6.2 | 280 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
2524 | 4/16 | 03:00:00 | 278.15 | 98780 | 6.7 | 280 | 4.1834 | 0 | 0 | 263.132 | 0 | 1 | 5
2525 | 4/16 | 04:00:00 | 277.15 | 98771 | 6.2 | 280 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
2526 | 4/16 | 05:00:00 | 277.15 | 98771 | 4.6 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2527 | 4/16 | 06:00:00 | 277.15 | 98771 | 4.1 | 280 | 4.4973 | 50.4 | 0 | 261.92 | 0 | 1 | 4
2528 | 4/16 | 07:00:00 | 277.15 | 98771 | 5.1 | 280 | 4.4973 | 388.8 | 457.2 | 261.92 | 0 | 1 | 4
2529 | 4/16 | 08:00:00 | 279.15 | 98789 | 5.1 | 290 | 4.8307 | 874.8 | 1270.8 | 264.299 | 0 | 1 | 6
2530 | 4/16 | 09:00:00 | 279.15 | 98789 | 4.6 | 300 | 5.187 | 1400.4 | 1728 | 264.528 | 0 | 1 | 6
2531 | 4/16 | 10:00:00 | 280.15 | 98798 | 4.6 | 260 | 5.1865 | 1854 | 2098.8 | 265.476 | 0 | 1 | 7
2532 | 4/16 | 11:00:00 | 280.15 | 98798 | 4.1 | 270 | 5.5661 | 2188.8 | 1893.6 | 265.704 | 0 | 1 | 7
2533 | 4/16 | 12:00:00 | 280.15 | 98798 | 3.6 | 260 | 5.9703 | 1314 | 201.6 | 266.402 | 0 | 1 | 7
2534 | 4/16 | 13:00:00 | 280.15 | 98798 | 4.1 | 250 | 6.4005 | 1321.2 | 234 | 266.628 | 0 | 1 | 7
2535 | 4/16 | 14:00:00 | 281.15 | 98806 | 5.1 | 250 | 6.4 | 1242 | 230.4 | 267.58 | 0 | 1 | 8
2536 | 4/16 | 15:00:00 | 281.15 | 98806 | 5.7 | 260 | 6.8577 | 1069.2 | 212.4 | 267.805 | 0 | 1 | 8
2537 | 4/16 | 16:00:00 | 282.15 | 98815 | 5.7 | 260 | 6.8571 | 831.6 | 129.6 | 268.758 | 0 | 1 | 9
2538 | 4/16 | 17:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.8564 | 986.4 | 1152 | 269.234 | 0 | 1 | 10
2539 | 4/16 | 18:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.8571 | 468 | 568.8 | 268.283 | 0 | 1 | 9
2540 | 4/16 | 19:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.8571 | 82.8 | 0 | 268.283 | 0 | 1 | 9
2541 | 4/16 | 20:00:00 | 280.15 | 98798 | 3.1 | 360 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
2542 | 4/16 | 21:00:00 | 279.15 | 98789 | 3.6 | 30 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
2543 | 4/16 | 22:00:00 | 278.15 | 98780 | 3.6 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
2544 | 4/16 | 23:00:00 | 277.15 | 98771 | 2.6 | 50 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
2545 | 4/16 | 24:00:00 | 277.15 | 98771 | 2.6 | 60 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
2546 | 4/17 | 01:00:00 | 277.15 | 98771 | 2.1 | 40 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
2547 | 4/17 | 02:00:00 | 277.15 | 98771 | 1.5 | 349 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
2548 | 4/17 | 03:00:00 | 277.15 | 98771 | 2.6 | 30 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
2549 | 4/17 | 04:00:00 | 277.15 | 98771 | 1.5 | 101 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
2550 | 4/17 | 05:00:00 | 277.15 | 98771 | 2.1 | 30 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
2551 | 4/17 | 06:00:00 | 277.15 | 98771 | 1 | 299 | 5.1879 | 28.8 | 0 | 263.098 | 0 | 1 | 4
2552 | 4/17 | 07:00:00 | 277.15 | 98771 | 2.1 | 40 | 5.1879 | 212.4 | 0 | 263.098 | 0 | 1 | 4
2553 | 4/17 | 08:00:00 | 278.15 | 98780 | 2.1 | 30 | 4.8311 | 496.8 | 129.6 | 263.818 | 0 | 1 | 5
2554 | 4/17 | 09:00:00 | 279.15 | 98789 | 3.1 | 40 | 4.8307 | 1418.4 | 1468.8 | 264.299 | 0 | 1 | 6
2555 | 4/17 | 10:00:00 | 279.15 | 98789 | 3.1 | 40 | 4.183 | 1882.8 | 1818 | 263.837 | 0 | 1 | 6
2556 | 4/17 | 11:00:00 | 279.15 | 98789 | 1.5 | 230 | 4.183 | 2217.6 | 1850.4 | 263.837 | 0 | 1 | 6
2557 | 4/17 | 12:00:00 | 280.15 | 98798 | 2.1 | 60 | 4.496 | 1332 | 284.4 | 265.483 | 0 | 1 | 7
2558 | 4/17 | 13:00:00 | 280.15 | 98798 | 1.5 | 93 | 4.1826 | 2422.8 | 1936.8 | 264.782 | 0 | 1 | 7
2559 | 4/17 | 14:00:00 | 281.15 | 98806 | 1 | 76 | 4.4957 | 2268 | 2404.8 | 265.96 | 0 | 1 | 8
2560 | 4/17 | 15:00:00 | 281.15 | 98806 | 2.1 | 10 | 4.4957 | 1962 | 2160 | 265.96 | 0 | 1 | 8
2561 | 4/17 | 16:00:00 | 281.15 | 98806 | 0.5 | 206 | 4.4957 | 1530 | 1929.6 | 265.96 | 0 | 1 | 8
2562 | 4/17 | 17:00:00 | 281.15 | 98806 | 2.1 | 10 | 4.1823 | 1011.6 | 1198.8 | 265.727 | 0 | 1 | 8
2563 | 4/17 | 18:00:00 | 281.15 | 98806 | 1 | 163 | 4.1823 | 486 | 500.4 | 265.727 | 0 | 1 | 8
2564 | 4/17 | 19:00:00 | 280.15 | 98798 | 1 | 360 | 4.496 | 93.6 | 0 | 264.755 | 0 | 1 | 7
2565 | 4/17 | 20:00:00 | 279.15 | 98789 | 2.6 | 270 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
2566 | 4/17 | 21:00:00 | 279.15 | 98789 | 2.6 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
2567 | 4/17 | 22:00:00 | 279.15 | 98789 | 3.1 | 20 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
2568 | 4/17 | 23:00:00 | 277.15 | 98771 | 6.2 | 20 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2569 | 4/17 | 24:00:00 | 276.15 | 98762 | 3.1 | 20 | 3.8899 | 0 | 0 | 260.515 | 0 | 1 | 3
2570 | 4/18 | 01:00:00 | 275.15 | 98752 | 3.6 | 30 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
2571 | 4/18 | 02:00:00 | 275.15 | 98752 | 6.2 | 10 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
2572 | 4/18 | 03:00:00 | 274.15 | 98743 | 3.1 | 350 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
2573 | 4/18 | 04:00:00 | 274.15 | 98743 | 3.6 | 10 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
2574 | 4/18 | 05:00:00 | 273.15 | 98734 | 2.6 | 310 | 3.293 | 0 | 0 | 257.823 | 0 | 1 | 0
2575 | 4/18 | 06:00:00 | 272.15 | 98724 | 2.6 | 310 | 3.0271 | 43.2 | 0 | 256.647 | 0 | 1 | -1
2576 | 4/18 | 07:00:00 | 275.15 | 98752 | 3.6 | 360 | 3.2924 | 370.8 | 295.2 | 259.482 | 0 | 1 | 2
2577 | 4/18 | 08:00:00 | 276.15 | 98762 | 3.6 | 30 | 3.2921 | 900 | 1062 | 260.304 | 0 | 1 | 3
2578 | 4/18 | 09:00:00 | 278.15 | 98780 | 4.6 | 30 | 3.5789 | 1533.6 | 2055.6 | 262.168 | 0 | 1 | 5
2579 | 4/18 | 10:00:00 | 279.15 | 98789 | 4.6 | 40 | 3.5786 | 2019.6 | 2552.4 | 263.11 | 0 | 1 | 6
2580 | 4/18 | 11:00:00 | 280.15 | 98798 | 4.1 | 30 | 3.8885 | 2239.2 | 2214 | 264.547 | 0 | 1 | 7
2581 | 4/18 | 12:00:00 | 281.15 | 98806 | 3.6 | 40 | 4.1823 | 2419.2 | 2448 | 265.727 | 0 | 1 | 8
2582 | 4/18 | 13:00:00 | 281.15 | 98806 | 3.1 | 22 | 4.1823 | 2437.2 | 2451.6 | 265.727 | 0 | 1 | 8
2583 | 4/18 | 14:00:00 | 281.15 | 98806 | 3.6 | 50 | 3.578 | 2293.2 | 2444.4 | 265.255 | 0 | 1 | 8
2584 | 4/18 | 15:00:00 | 282.15 | 98815 | 1.5 | 221 | 3.2903 | 1990.8 | 2163.6 | 265.959 | 0 | 1 | 9
2585 | 4/18 | 16:00:00 | 282.15 | 98815 | 2.6 | 50 | 3.5777 | 1551.6 | 1501.2 | 266.199 | 0 | 1 | 9
2586 | 4/18 | 17:00:00 | 282.15 | 98815 | 2.6 | 90 | 3.5777 | 1090.8 | 1468.8 | 265.938 | 0 | 1 | 9
2587 | 4/18 | 18:00:00 | 281.15 | 98806 | 3.1 | 90 | 3.8882 | 529.2 | 799.2 | 265.232 | 0 | 1 | 8
2588 | 4/18 | 19:00:00 | 280.15 | 98798 | 3.1 | 100 | 4.1826 | 100.8 | 0 | 264.523 | 0 | 1 | 7
2589 | 4/18 | 20:00:00 | 279.15 | 98789 | 2.6 | 110 | 4.183 | 0 | 0 | 263.959 | 0 | 1 | 6
2590 | 4/18 | 21:00:00 | 279.15 | 98789 | 4.1 | 120 | 4.4964 | 0 | 0 | 264.31 | 0 | 1 | 6
2591 | 4/18 | 22:00:00 | 278.15 | 98780 | 4.1 | 120 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
2592 | 4/18 | 23:00:00 | 278.15 | 98780 | 2.6 | 130 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2593 | 4/18 | 24:00:00 | 277.15 | 98771 | 2.6 | 150 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
2594 | 4/19 | 01:00:00 | 276.15 | 98762 | 2.1 | 160 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2595 | 4/19 | 02:00:00 | 276.15 | 98762 | 2.1 | 150 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2596 | 4/19 | 03:00:00 | 277.15 | 98771 | 2.6 | 160 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
2597 | 4/19 | 04:00:00 | 277.15 | 98771 | 2.6 | 160 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
2598 | 4/19 | 05:00:00 | 276.15 | 98762 | 2.6 | 160 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
2599 | 4/19 | 06:00:00 | 276.15 | 98762 | 2.6 | 170 | 4.4977 | 28.8 | 0 | 261.799 | 0 | 1 | 3
2600 | 4/19 | 07:00:00 | 277.15 | 98771 | 2.6 | 180 | 4.8316 | 187.2 | 0 | 262.976 | 0 | 1 | 4
2601 | 4/19 | 08:00:00 | 278.15 | 98780 | 2.1 | 190 | 4.8311 | 597.6 | 208.8 | 263.818 | 0 | 1 | 5
2602 | 4/19 | 09:00:00 | 279.15 | 98789 | 2.6 | 190 | 4.8307 | 1152 | 716.4 | 264.656 | 0 | 1 | 6
2603 | 4/19 | 10:00:00 | 281.15 | 98806 | 3.6 | 200 | 4.8299 | 1818 | 1677.6 | 266.316 | 0 | 1 | 8
2604 | 4/19 | 11:00:00 | 281.15 | 98806 | 3.6 | 210 | 4.4957 | 2386.8 | 2246.4 | 265.7 | 0 | 1 | 8
2605 | 4/19 | 12:00:00 | 282.15 | 98815 | 3.1 | 210 | 4.4952 | 1350 | 208.8 | 267.379 | 0 | 1 | 9
2606 | 4/19 | 13:00:00 | 283.15 | 98824 | 2.6 | 250 | 4.4948 | 1357.2 | 90 | 268.326 | 0 | 1 | 10
2607 | 4/19 | 14:00:00 | 283.15 | 98824 | 4.1 | 260 | 4.4948 | 777.6 | 10.8 | 268.435 | 0 | 1 | 10
2608 | 4/19 | 15:00:00 | 283.15 | 98824 | 3.6 | 240 | 4.4948 | 673.2 | 14.4 | 268.435 | 0 | 1 | 10
2609 | 4/19 | 16:00:00 | 283.15 | 98824 | 3.6 | 230 | 4.4948 | 864 | 288 | 268.326 | 0 | 1 | 10
2610 | 4/19 | 17:00:00 | 284.15 | 98833 | 3.6 | 230 | 4.4944 | 1036.8 | 1213.2 | 268.798 | 0 | 1 | 11
2611 | 4/19 | 18:00:00 | 283.15 | 98824 | 4.6 | 260 | 4.829 | 284.4 | 0 | 268.561 | 0 | 1 | 10
2612 | 4/19 | 19:00:00 | 283.15 | 98824 | 4.6 | 260 | 4.829 | 100.8 | 0 | 268.086 | 0 | 1 | 10
2613 | 4/19 | 20:00:00 | 282.15 | 98815 | 4.6 | 260 | 5.1856 | 0 | 0 | 267.844 | 0 | 1 | 9
2614 | 4/19 | 21:00:00 | 282.15 | 98815 | 4.6 | 270 | 5.5651 | 0 | 0 | 268.075 | 0 | 1 | 9
2615 | 4/19 | 22:00:00 | 281.15 | 98806 | 4.6 | 260 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
2616 | 4/19 | 23:00:00 | 281.15 | 98806 | 4.1 | 250 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
2617 | 4/19 | 24:00:00 | 281.15 | 98806 | 4.6 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
2618 | 4/20 | 01:00:00 | 281.15 | 98806 | 5.1 | 260 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
2619 | 4/20 | 02:00:00 | 281.15 | 98806 | 4.1 | 260 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
2620 | 4/20 | 03:00:00 | 281.15 | 98806 | 5.1 | 260 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
2621 | 4/20 | 04:00:00 | 281.15 | 98806 | 4.6 | 270 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
2622 | 4/20 | 05:00:00 | 282.15 | 98815 | 4.1 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
2623 | 4/20 | 06:00:00 | 282.15 | 98815 | 5.7 | 280 | 7.3438 | 39.6 | 0 | 268.983 | 0 | 1 | 9
2624 | 4/20 | 07:00:00 | 282.15 | 98815 | 3.1 | 280 | 7.3438 | 234 | 0 | 268.983 | 0 | 1 | 9
2625 | 4/20 | 08:00:00 | 283.15 | 98824 | 5.1 | 280 | 7.3431 | 936 | 1087.2 | 269.46 | 0 | 1 | 10
2626 | 4/20 | 09:00:00 | 283.15 | 98824 | 4.1 | 270 | 7.3431 | 810 | 122.4 | 269.936 | 0 | 1 | 10
2627 | 4/20 | 10:00:00 | 284.15 | 98833 | 5.1 | 290 | 7.3425 | 1062 | 208.8 | 270.89 | 0 | 1 | 11
2628 | 4/20 | 11:00:00 | 284.15 | 98833 | 4.1 | 280 | 7.3425 | 1242 | 226.8 | 270.89 | 0 | 1 | 11
2629 | 4/20 | 12:00:00 | 284.15 | 98833 | 5.1 | 280 | 6.8558 | 1346.4 | 201.6 | 270.663 | 0 | 1 | 11
2630 | 4/20 | 13:00:00 | 285.15 | 98841 | 7.2 | 290 | 6.3977 | 2444.4 | 1976.4 | 270.907 | 0 | 1 | 12
2631 | 4/20 | 14:00:00 | 286.15 | 98850 | 7.7 | 280 | 6.8546 | 2293.2 | 2329.2 | 272.087 | 0 | 1 | 13
2632 | 4/20 | 15:00:00 | 285.15 | 98841 | 8.2 | 280 | 6.8552 | 1987.2 | 2106 | 271.136 | 0 | 1 | 12
2633 | 4/20 | 16:00:00 | 286.15 | 98850 | 7.7 | 290 | 6.8546 | 1555.2 | 1530 | 272.087 | 0 | 1 | 13
2634 | 4/20 | 17:00:00 | 285.15 | 98841 | 7.7 | 280 | 6.8552 | 579.6 | 169.2 | 271.616 | 0 | 1 | 12
2635 | 4/20 | 18:00:00 | 285.15 | 98841 | 7.2 | 270 | 6.8552 | 518.4 | 759.6 | 271.136 | 0 | 1 | 12
2636 | 4/20 | 19:00:00 | 284.15 | 98833 | 7.2 | 290 | 6.8558 | 108 | 0 | 270.185 | 0 | 1 | 11
2637 | 4/20 | 20:00:00 | 282.15 | 98815 | 5.7 | 280 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
2638 | 4/20 | 21:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
2639 | 4/20 | 22:00:00 | 281.15 | 98806 | 4.6 | 260 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
2640 | 4/20 | 23:00:00 | 281.15 | 98806 | 7.2 | 280 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
2641 | 4/20 | 24:00:00 | 281.15 | 98806 | 3.6 | 290 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
2642 | 4/21 | 01:00:00 | 280.15 | 98798 | 3.1 | 290 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
2643 | 4/21 | 02:00:00 | 279.15 | 98789 | 1.5 | 270 | 5.9708 | 0 | 0 | 264.723 | 0 | 1 | 6
2644 | 4/21 | 03:00:00 | 278.15 | 98780 | 2.6 | 280 | 5.5671 | 0 | 0 | 263.549 | 0 | 1 | 5
2645 | 4/21 | 04:00:00 | 280.15 | 98798 | 3.1 | 280 | 6.4005 | 0 | 0 | 266.157 | 0 | 1 | 7
2646 | 4/21 | 05:00:00 | 281.15 | 98806 | 2.1 | 280 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
2647 | 4/21 | 06:00:00 | 281.15 | 98806 | 4.1 | 270 | 6.4 | 75.6 | 0 | 267.107 | 0 | 1 | 8
2648 | 4/21 | 07:00:00 | 282.15 | 98815 | 3.1 | 260 | 6.3994 | 439.2 | 518.4 | 268.057 | 0 | 1 | 9
2649 | 4/21 | 08:00:00 | 282.15 | 98815 | 5.1 | 280 | 6.3994 | 957.6 | 1314 | 268.057 | 0 | 1 | 9
2650 | 4/21 | 09:00:00 | 283.15 | 98824 | 6.7 | 270 | 6.8564 | 1479.6 | 1731.6 | 269.234 | 0 | 1 | 10
2651 | 4/21 | 10:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.3988 | 1933.2 | 1918.8 | 269.007 | 0 | 1 | 10
2652 | 4/21 | 11:00:00 | 284.15 | 98833 | 6.2 | 280 | 6.3982 | 1256.4 | 198 | 270.435 | 0 | 1 | 11
2653 | 4/21 | 12:00:00 | 282.15 | 98815 | 6.2 | 280 | 6.8571 | 1353.6 | 201.6 | 268.758 | 0 | 1 | 9
2654 | 4/21 | 13:00:00 | 284.15 | 98833 | 7.2 | 280 | 6.8558 | 2455.2 | 1962 | 270.185 | 0 | 1 | 11
2655 | 4/21 | 14:00:00 | 286.15 | 98850 | 8.8 | 290 | 6.3971 | 2311.2 | 2336.4 | 271.858 | 0 | 1 | 13
2656 | 4/21 | 15:00:00 | 285.15 | 98841 | 9.8 | 280 | 6.3977 | 2005.2 | 2116.8 | 270.907 | 0 | 1 | 12
2657 | 4/21 | 16:00:00 | 285.15 | 98841 | 6.7 | 280 | 6.3977 | 1573.2 | 1904.4 | 270.907 | 0 | 1 | 12
2658 | 4/21 | 17:00:00 | 285.15 | 98841 | 9.3 | 280 | 6.3977 | 1058.4 | 1411.2 | 270.907 | 0 | 1 | 12
2659 | 4/21 | 18:00:00 | 284.15 | 98833 | 8.8 | 290 | 6.3982 | 529.2 | 633.6 | 269.957 | 0 | 1 | 11
2660 | 4/21 | 19:00:00 | 284.15 | 98833 | 7.2 | 280 | 6.3982 | 115.2 | 0 | 269.957 | 0 | 1 | 11
2661 | 4/21 | 20:00:00 | 283.15 | 98824 | 7.2 | 280 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
2662 | 4/21 | 21:00:00 | 282.15 | 98815 | 6.7 | 290 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
2663 | 4/21 | 22:00:00 | 281.15 | 98806 | 6.7 | 300 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
2664 | 4/21 | 23:00:00 | 280.15 | 98798 | 2.1 | 60 | 6.4005 | 0 | 0 | 266.157 | 0 | 1 | 7
2665 | 4/21 | 24:00:00 | 280.15 | 98798 | 1.5 | 122 | 6.4005 | 0 | 0 | 266.157 | 0 | 1 | 7
2666 | 4/22 | 01:00:00 | 279.15 | 98789 | 1 | 150 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
2667 | 4/22 | 02:00:00 | 280.15 | 98798 | 1 | 240 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
2668 | 4/22 | 03:00:00 | 280.15 | 98798 | 1.5 | 96 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
2669 | 4/22 | 04:00:00 | 279.15 | 98789 | 2.1 | 260 | 5.9708 | 0 | 0 | 264.982 | 0 | 1 | 6
2670 | 4/22 | 05:00:00 | 278.15 | 98780 | 2.6 | 290 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
2671 | 4/22 | 06:00:00 | 277.15 | 98771 | 2.1 | 280 | 4.8316 | 82.8 | 0 | 262.405 | 0 | 1 | 4
2672 | 4/22 | 07:00:00 | 279.15 | 98789 | 2.1 | 320 | 5.187 | 457.2 | 543.6 | 264.528 | 0 | 1 | 6
2673 | 4/22 | 08:00:00 | 279.15 | 98789 | 2.6 | 10 | 4.8307 | 979.2 | 1353.6 | 264.299 | 0 | 1 | 6
2674 | 4/22 | 09:00:00 | 279.15 | 98789 | 3.1 | 20 | 4.8307 | 1508.4 | 1875.6 | 264.299 | 0 | 1 | 6
2675 | 4/22 | 10:00:00 | 280.15 | 98798 | 2.1 | 40 | 5.1865 | 1958.4 | 2120.4 | 265.476 | 0 | 1 | 7
2676 | 4/22 | 11:00:00 | 281.15 | 98806 | 2.1 | 60 | 5.1861 | 2289.6 | 2365.2 | 266.423 | 0 | 1 | 8
2677 | 4/22 | 12:00:00 | 281.15 | 98806 | 2.1 | 60 | 5.1861 | 2469.6 | 2404.8 | 266.423 | 0 | 1 | 8
2678 | 4/22 | 13:00:00 | 283.15 | 98824 | 1 | 190 | 5.1851 | 2487.6 | 2408.4 | 268.319 | 0 | 1 | 10
2679 | 4/22 | 14:00:00 | 284.15 | 98833 | 1.5 | 15 | 4.8285 | 2336.4 | 2390.4 | 269.033 | 0 | 1 | 11
2680 | 4/22 | 15:00:00 | 284.15 | 98833 | 2.1 | 40 | 4.8285 | 2030.4 | 2156.4 | 269.033 | 0 | 1 | 11
2681 | 4/22 | 16:00:00 | 284.15 | 98833 | 2.1 | 56 | 5.1847 | 1594.8 | 1947.6 | 269.266 | 0 | 1 | 11
2682 | 4/22 | 17:00:00 | 283.15 | 98824 | 4.1 | 40 | 4.4948 | 1080 | 1454.4 | 267.852 | 0 | 1 | 10
2683 | 4/22 | 18:00:00 | 283.15 | 98824 | 2.6 | 30 | 4.4948 | 579.6 | 1011.6 | 267.59 | 0 | 1 | 10
2684 | 4/22 | 19:00:00 | 282.15 | 98815 | 4.1 | 70 | 4.8294 | 126 | 21.6 | 267.139 | 0 | 1 | 9
2685 | 4/22 | 20:00:00 | 280.15 | 98798 | 2.6 | 80 | 4.496 | 0 | 0 | 265.483 | 0 | 1 | 7
2686 | 4/22 | 21:00:00 | 280.15 | 98798 | 3.1 | 130 | 4.8303 | 0 | 0 | 265.715 | 0 | 1 | 7
2687 | 4/22 | 22:00:00 | 279.15 | 98789 | 2.6 | 140 | 4.183 | 0 | 0 | 264.303 | 0 | 1 | 6
2688 | 4/22 | 23:00:00 | 278.15 | 98780 | 2.1 | 160 | 4.1834 | 0 | 0 | 262.891 | 0 | 1 | 5
2689 | 4/22 | 24:00:00 | 276.15 | 98762 | 2.1 | 210 | 3.8899 | 0 | 0 | 260.515 | 0 | 1 | 3
2690 | 4/23 | 01:00:00 | 277.15 | 98771 | 2.6 | 210 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
2691 | 4/23 | 02:00:00 | 277.15 | 98771 | 3.1 | 240 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2692 | 4/23 | 03:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
2693 | 4/23 | 04:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
2694 | 4/23 | 05:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
2695 | 4/23 | 06:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.8316 | 39.6 | 0 | 262.976 | 0 | 1 | 4
2696 | 4/23 | 07:00:00 | 278.15 | 98780 | 5.1 | 270 | 5.1875 | 500.4 | 864 | 263.323 | 0 | 1 | 5
2697 | 4/23 | 08:00:00 | 280.15 | 98798 | 3.6 | 290 | 5.5661 | 1054.8 | 1634.4 | 265.444 | 0 | 1 | 7
2698 | 4/23 | 09:00:00 | 281.15 | 98806 | 4.6 | 280 | 5.1861 | 1616.4 | 2127.6 | 266.163 | 0 | 1 | 8
2699 | 4/23 | 10:00:00 | 283.15 | 98824 | 4.1 | 270 | 4.829 | 2098.8 | 2566.8 | 267.824 | 0 | 1 | 10
2700 | 4/23 | 11:00:00 | 283.15 | 98824 | 3.1 | 250 | 4.4948 | 2314.8 | 2221.2 | 267.852 | 0 | 1 | 10
2701 | 4/23 | 12:00:00 | 284.15 | 98833 | 3.6 | 270 | 4.8285 | 2491.2 | 2419.2 | 269.033 | 0 | 1 | 11
2702 | 4/23 | 13:00:00 | 285.15 | 98841 | 3.6 | 280 | 4.8281 | 2505.6 | 2268 | 269.98 | 0 | 1 | 12
2703 | 4/23 | 14:00:00 | 285.15 | 98841 | 5.7 | 280 | 4.8281 | 2494.8 | 2710.8 | 269.716 | 0 | 1 | 12
2704 | 4/23 | 15:00:00 | 285.15 | 98841 | 5.7 | 280 | 4.8281 | 2170.8 | 2595.6 | 269.716 | 0 | 1 | 12
2705 | 4/23 | 16:00:00 | 285.15 | 98841 | 7.7 | 280 | 4.8281 | 1710 | 2178 | 269.716 | 0 | 1 | 12
2706 | 4/23 | 17:00:00 | 283.15 | 98824 | 7.2 | 270 | 4.4948 | 1148.4 | 1717.2 | 267.724 | 0 | 1 | 10
2707 | 4/23 | 18:00:00 | 283.15 | 98824 | 7.2 | 270 | 4.1815 | 594 | 871.2 | 267.355 | 0 | 1 | 10
2708 | 4/23 | 19:00:00 | 282.15 | 98815 | 6.2 | 280 | 4.1819 | 140.4 | 64.8 | 266.544 | 0 | 1 | 9
2709 | 4/23 | 20:00:00 | 280.15 | 98798 | 6.7 | 280 | 4.8303 | 0 | 0 | 264.986 | 0 | 1 | 7
2710 | 4/23 | 21:00:00 | 280.15 | 98798 | 5.7 | 280 | 4.8303 | 0 | 0 | 264.986 | 0 | 1 | 7
2711 | 4/23 | 22:00:00 | 280.15 | 98798 | 2.6 | 250 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
2712 | 4/23 | 23:00:00 | 280.15 | 98798 | 6.2 | 250 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
2713 | 4/23 | 24:00:00 | 281.15 | 98806 | 6.2 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
2714 | 4/24 | 01:00:00 | 281.15 | 98806 | 6.2 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
2715 | 4/24 | 02:00:00 | 281.15 | 98806 | 7.2 | 260 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
2716 | 4/24 | 03:00:00 | 281.15 | 98806 | 7.7 | 260 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
2717 | 4/24 | 04:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
2718 | 4/24 | 05:00:00 | 281.15 | 98806 | 7.2 | 290 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
2719 | 4/24 | 06:00:00 | 281.15 | 98806 | 5.1 | 280 | 5.9698 | 93.6 | 0 | 266.881 | 0 | 1 | 8
2720 | 4/24 | 07:00:00 | 281.15 | 98806 | 4.6 | 260 | 5.5656 | 486 | 576 | 266.653 | 0 | 1 | 8
2721 | 4/24 | 08:00:00 | 281.15 | 98806 | 5.1 | 280 | 5.9698 | 1011.6 | 1360.8 | 266.881 | 0 | 1 | 8
2722 | 4/24 | 09:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.3994 | 1533.6 | 1504.8 | 268.057 | 0 | 1 | 9
2723 | 4/24 | 10:00:00 | 281.15 | 98806 | 7.7 | 300 | 5.9698 | 1101.6 | 255.6 | 267.353 | 0 | 1 | 8
2724 | 4/24 | 11:00:00 | 280.15 | 98798 | 3.1 | 290 | 5.5661 | 2318.4 | 1915.2 | 265.704 | 0 | 1 | 7
2725 | 4/24 | 12:00:00 | 281.15 | 98806 | 5.1 | 330 | 4.4957 | 2509.2 | 2430 | 265.96 | 0 | 1 | 8
2726 | 4/24 | 13:00:00 | 283.15 | 98824 | 8.8 | 310 | 3.8875 | 2527.2 | 2455.2 | 267.38 | 0 | 1 | 10
2727 | 4/24 | 14:00:00 | 283.15 | 98824 | 7.7 | 290 | 3.5773 | 2379.6 | 2440.8 | 267.142 | 0 | 1 | 10
2728 | 4/24 | 15:00:00 | 283.15 | 98824 | 10.8 | 280 | 3.8875 | 2066.4 | 2160 | 267.38 | 0 | 1 | 10
2729 | 4/24 | 16:00:00 | 282.15 | 98815 | 12.9 | 290 | 2.7781 | 1738.8 | 2149.2 | 265.217 | 0 | 1 | 9
2730 | 4/24 | 17:00:00 | 278.15 | 98780 | 10.8 | 310 | 3.5789 | 1108.8 | 1260 | 262.425 | 0 | 1 | 5
2731 | 4/24 | 18:00:00 | 279.15 | 98789 | 10.8 | 300 | 3.0251 | 612 | 900 | 262.637 | 0 | 1 | 6
2732 | 4/24 | 19:00:00 | 278.15 | 98780 | 9.8 | 290 | 3.0253 | 151.2 | 90 | 261.696 | 0 | 1 | 5
2733 | 4/24 | 20:00:00 | 276.15 | 98762 | 9.3 | 320 | 3.0259 | 0 | 0 | 259.814 | 0 | 1 | 3
2734 | 4/24 | 21:00:00 | 275.15 | 98752 | 7.7 | 310 | 3.2924 | 0 | 0 | 259.107 | 0 | 1 | 2
2735 | 4/24 | 22:00:00 | 274.15 | 98743 | 5.7 | 290 | 3.5803 | 0 | 0 | 258.398 | 0 | 1 | 1
2736 | 4/24 | 23:00:00 | 273.15 | 98734 | 6.7 | 300 | 3.293 | 0 | 0 | 257.224 | 0 | 1 | 0
2737 | 4/24 | 24:00:00 | 273.15 | 98734 | 6.2 | 290 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
2738 | 4/25 | 01:00:00 | 273.15 | 98734 | 5.1 | 290 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
2739 | 4/25 | 02:00:00 | 272.15 | 98724 | 6.2 | 310 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
2740 | 4/25 | 03:00:00 | 273.15 | 98734 | 6.2 | 310 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
2741 | 4/25 | 04:00:00 | 272.15 | 98724 | 5.7 | 310 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
2742 | 4/25 | 05:00:00 | 272.15 | 98724 | 6.7 | 330 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
2743 | 4/25 | 06:00:00 | 272.15 | 98724 | 5.7 | 310 | 2.7806 | 86.4 | 0 | 256.302 | 0 | 1 | -1
2744 | 4/25 | 07:00:00 | 273.15 | 98734 | 5.1 | 290 | 3.0267 | 428.4 | 302.4 | 257.478 | 0 | 1 | 0
2745 | 4/25 | 08:00:00 | 275.15 | 98752 | 6.2 | 300 | 3.0262 | 1101.6 | 1454.4 | 258.873 | 0 | 1 | 2
2746 | 4/25 | 09:00:00 | 277.15 | 98771 | 7.2 | 300 | 3.2918 | 1569.6 | 1591.2 | 261.246 | 0 | 1 | 4
2747 | 4/25 | 10:00:00 | 278.15 | 98780 | 7.7 | 320 | 3.0253 | 1123.2 | 28.8 | 262.415 | 0 | 1 | 5
2748 | 4/25 | 11:00:00 | 278.15 | 98780 | 8.2 | 330 | 3.0253 | 1310.4 | 93.6 | 262.415 | 0 | 1 | 5
2749 | 4/25 | 12:00:00 | 278.15 | 98780 | 6.2 | 320 | 3.2915 | 1407.6 | 198 | 262.653 | 0 | 1 | 5
2750 | 4/25 | 13:00:00 | 279.15 | 98789 | 6.7 | 340 | 3.2912 | 2548.8 | 1969.2 | 263.132 | 0 | 1 | 6
2751 | 4/25 | 14:00:00 | 281.15 | 98806 | 6.7 | 350 | 3.2906 | 2394 | 2448 | 265.017 | 0 | 1 | 8
2752 | 4/25 | 15:00:00 | 276.15 | 98762 | 4.1 | 350 | 4.1841 | 2077.2 | 2152.8 | 261.001 | 0 | 1 | 3
2753 | 4/25 | 16:00:00 | 277.15 | 98771 | 5.1 | 30 | 4.1838 | 1641.6 | 1519.2 | 261.946 | 0 | 1 | 4
2754 | 4/25 | 17:00:00 | 279.15 | 98789 | 4.6 | 360 | 4.183 | 1119.6 | 1252.8 | 263.837 | 0 | 1 | 6
2755 | 4/25 | 18:00:00 | 279.15 | 98789 | 5.7 | 20 | 3.8889 | 583.2 | 734.4 | 263.603 | 0 | 1 | 6
2756 | 4/25 | 19:00:00 | 278.15 | 98780 | 6.2 | 350 | 3.5789 | 151.2 | 46.8 | 262.425 | 0 | 1 | 5
2757 | 4/25 | 20:00:00 | 276.15 | 98762 | 5.1 | 340 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
2758 | 4/25 | 21:00:00 | 276.15 | 98762 | 7.2 | 360 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
2759 | 4/25 | 22:00:00 | 276.15 | 98762 | 4.1 | 330 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
2760 | 4/25 | 23:00:00 | 275.15 | 98752 | 5.7 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
2761 | 4/25 | 24:00:00 | 275.15 | 98752 | 5.7 | 320 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
2762 | 4/26 | 01:00:00 | 275.15 | 98752 | 6.2 | 350 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
2763 | 4/26 | 02:00:00 | 275.15 | 98752 | 6.2 | 350 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
2764 | 4/26 | 03:00:00 | 275.15 | 98752 | 6.2 | 340 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
2765 | 4/26 | 04:00:00 | 275.15 | 98752 | 4.6 | 340 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
2766 | 4/26 | 05:00:00 | 274.15 | 98743 | 4.6 | 320 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
2767 | 4/26 | 06:00:00 | 275.15 | 98752 | 5.7 | 320 | 3.5799 | 111.6 | 0 | 259.594 | 0 | 1 | 2
2768 | 4/26 | 07:00:00 | 275.15 | 98752 | 7.2 | 340 | 3.2924 | 522 | 518.4 | 259.361 | 0 | 1 | 2
2769 | 4/26 | 08:00:00 | 276.15 | 98762 | 6.2 | 350 | 3.2921 | 1054.8 | 1209.6 | 260.304 | 0 | 1 | 3
2770 | 4/26 | 09:00:00 | 277.15 | 98771 | 7.2 | 360 | 3.2918 | 1587.6 | 1497.6 | 261.246 | 0 | 1 | 4
2771 | 4/26 | 10:00:00 | 279.15 | 98789 | 6.2 | 10 | 3.5786 | 2037.6 | 2138.4 | 263.368 | 0 | 1 | 6
2772 | 4/26 | 11:00:00 | 279.15 | 98789 | 6.2 | 350 | 3.0251 | 2372.4 | 2451.6 | 262.894 | 0 | 1 | 6
2773 | 4/26 | 12:00:00 | 280.15 | 98798 | 5.1 | 30 | 3.5783 | 2545.2 | 2462.4 | 264.312 | 0 | 1 | 7
2774 | 4/26 | 13:00:00 | 279.15 | 98789 | 5.1 | 10 | 3.0251 | 2566.8 | 2487.6 | 262.894 | 0 | 1 | 6
2775 | 4/26 | 14:00:00 | 281.15 | 98806 | 5.1 | 20 | 3.2906 | 2408.4 | 2448 | 265.017 | 0 | 1 | 8
2776 | 4/26 | 15:00:00 | 280.15 | 98798 | 5.1 | 20 | 2.7786 | 2106 | 2163.6 | 263.595 | 0 | 1 | 7
2777 | 4/26 | 16:00:00 | 280.15 | 98798 | 4.6 | 30 | 3.5783 | 1659.6 | 1540.8 | 264.312 | 0 | 1 | 7
2778 | 4/26 | 17:00:00 | 279.15 | 98789 | 4.6 | 40 | 3.5786 | 1137.6 | 1270.8 | 263.368 | 0 | 1 | 6
2779 | 4/26 | 18:00:00 | 279.15 | 98789 | 3.1 | 20 | 3.5786 | 633.6 | 918 | 263.11 | 0 | 1 | 6
2780 | 4/26 | 19:00:00 | 277.15 | 98771 | 1.5 | 328 | 4.1838 | 158.4 | 72 | 261.946 | 0 | 1 | 4
2781 | 4/26 | 20:00:00 | 277.15 | 98771 | 1 | 147 | 3.8896 | 0 | 0 | 261.458 | 0 | 1 | 4
2782 | 4/26 | 21:00:00 | 276.15 | 98762 | 1.5 | 270 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
2783 | 4/26 | 22:00:00 | 276.15 | 98762 | 1.5 | 260 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
2784 | 4/26 | 23:00:00 | 276.15 | 98762 | 2.6 | 250 | 3.8899 | 0 | 0 | 260.515 | 0 | 1 | 3
2785 | 4/26 | 24:00:00 | 276.15 | 98762 | 3.1 | 260 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
2786 | 4/27 | 01:00:00 | 276.15 | 98762 | 3.6 | 260 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
2787 | 4/27 | 02:00:00 | 276.15 | 98762 | 4.1 | 260 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
2788 | 4/27 | 03:00:00 | 276.15 | 98762 | 4.1 | 270 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
2789 | 4/27 | 04:00:00 | 276.15 | 98762 | 4.6 | 270 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
2790 | 4/27 | 05:00:00 | 276.15 | 98762 | 3.6 | 260 | 3.5796 | 0 | 0 | 260.283 | 0 | 1 | 3
2791 | 4/27 | 06:00:00 | 277.15 | 98771 | 4.6 | 280 | 4.1838 | 68.4 | 0 | 262.41 | 0 | 1 | 4
2792 | 4/27 | 07:00:00 | 277.15 | 98771 | 6.7 | 280 | 4.4973 | 295.2 | 0 | 262.64 | 0 | 1 | 4
2793 | 4/27 | 08:00:00 | 278.15 | 98780 | 6.2 | 270 | 5.1875 | 1062 | 1188 | 263.581 | 0 | 1 | 5
2794 | 4/27 | 09:00:00 | 280.15 | 98798 | 5.7 | 280 | 5.1865 | 1587.6 | 1918.8 | 265.476 | 0 | 1 | 7
2795 | 4/27 | 10:00:00 | 281.15 | 98806 | 7.7 | 300 | 5.1861 | 2037.6 | 2131.2 | 266.423 | 0 | 1 | 8
2796 | 4/27 | 11:00:00 | 282.15 | 98815 | 6.7 | 290 | 5.1856 | 2365.2 | 2365.2 | 267.371 | 0 | 1 | 9
2797 | 4/27 | 12:00:00 | 283.15 | 98824 | 6.2 | 300 | 5.1851 | 2541.6 | 2397.6 | 268.319 | 0 | 1 | 10
2798 | 4/27 | 13:00:00 | 284.15 | 98833 | 7.2 | 300 | 5.1847 | 2556 | 2401.2 | 269.266 | 0 | 1 | 11
2799 | 4/27 | 14:00:00 | 284.15 | 98833 | 6.7 | 290 | 5.1847 | 2401.2 | 2372.4 | 269.266 | 0 | 1 | 11
2800 | 4/27 | 15:00:00 | 282.15 | 98815 | 3.6 | 330 | 5.5651 | 2091.6 | 2142 | 267.601 | 0 | 1 | 9
2801 | 4/27 | 16:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.3994 | 1652.4 | 1947.6 | 268.057 | 0 | 1 | 9
2802 | 4/27 | 17:00:00 | 283.15 | 98824 | 5.1 | 270 | 6.3988 | 1137.6 | 1454.4 | 269.007 | 0 | 1 | 10
2803 | 4/27 | 18:00:00 | 283.15 | 98824 | 5.7 | 280 | 6.3988 | 601.2 | 698.4 | 269.007 | 0 | 1 | 10
2804 | 4/27 | 19:00:00 | 280.15 | 98798 | 4.1 | 10 | 6.4005 | 93.6 | 0 | 266.628 | 0 | 1 | 7
2805 | 4/27 | 20:00:00 | 279.15 | 98789 | 4.6 | 20 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
2806 | 4/27 | 21:00:00 | 279.15 | 98789 | 2.1 | 30 | 5.9708 | 0 | 0 | 264.982 | 0 | 1 | 6
2807 | 4/27 | 22:00:00 | 279.15 | 98789 | 3.1 | 30 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
2808 | 4/27 | 23:00:00 | 279.15 | 98789 | 1.5 | 214 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
2809 | 4/27 | 24:00:00 | 278.15 | 98780 | 2.1 | 20 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
2810 | 4/28 | 01:00:00 | 278.15 | 98780 | 3.1 | 350 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
2811 | 4/28 | 02:00:00 | 278.15 | 98780 | 2.6 | 340 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
2812 | 4/28 | 03:00:00 | 278.15 | 98780 | 3.1 | 360 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
2813 | 4/28 | 04:00:00 | 276.15 | 98762 | 3.1 | 320 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
2814 | 4/28 | 05:00:00 | 275.15 | 98752 | 3.6 | 310 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
2815 | 4/28 | 06:00:00 | 276.15 | 98762 | 2.6 | 310 | 4.1841 | 82.8 | 0 | 261.463 | 0 | 1 | 3
2816 | 4/28 | 07:00:00 | 277.15 | 98771 | 2.6 | 290 | 4.4973 | 302.4 | 0 | 262.64 | 0 | 1 | 4
2817 | 4/28 | 08:00:00 | 279.15 | 98789 | 3.6 | 320 | 4.4964 | 597.6 | 180 | 264.536 | 0 | 1 | 6
2818 | 4/28 | 09:00:00 | 279.15 | 98789 | 2.1 | 360 | 4.4964 | 1609.2 | 1580.4 | 264.069 | 0 | 1 | 6
2819 | 4/28 | 10:00:00 | 281.15 | 98806 | 3.1 | 10 | 4.4957 | 2059.2 | 1976.4 | 265.96 | 0 | 1 | 8
2820 | 4/28 | 11:00:00 | 281.15 | 98806 | 2.6 | 326 | 4.1823 | 1324.8 | 190.8 | 266.197 | 0 | 1 | 8
2821 | 4/28 | 12:00:00 | 282.15 | 98815 | 3.1 | 14 | 4.1819 | 1422 | 194.4 | 267.144 | 0 | 1 | 9
2822 | 4/28 | 13:00:00 | 283.15 | 98824 | 1 | 194 | 4.4948 | 2574 | 1443.6 | 267.852 | 0 | 1 | 10
2823 | 4/28 | 14:00:00 | 284.15 | 98833 | 2.1 | 42 | 4.4944 | 1342.8 | 205.2 | 269.274 | 0 | 1 | 11
2824 | 4/28 | 15:00:00 | 283.15 | 98824 | 1.5 | 26 | 4.829 | 1170 | 223.2 | 268.561 | 0 | 1 | 10
2825 | 4/28 | 16:00:00 | 283.15 | 98824 | 2.1 | 258 | 4.4948 | 932.4 | 72 | 268.326 | 0 | 1 | 10
2826 | 4/28 | 17:00:00 | 283.15 | 98824 | 3.1 | 280 | 4.829 | 640.8 | 93.6 | 268.561 | 0 | 1 | 10
2827 | 4/28 | 18:00:00 | 282.15 | 98815 | 2.1 | 280 | 5.1856 | 619.2 | 720 | 267.371 | 0 | 1 | 9
2828 | 4/28 | 19:00:00 | 282.15 | 98815 | 2.6 | 270 | 5.1856 | 176.4 | 100.8 | 267.371 | 0 | 1 | 9
2829 | 4/28 | 20:00:00 | 281.15 | 98806 | 2.1 | 300 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
2830 | 4/28 | 21:00:00 | 281.15 | 98806 | 2.1 | 300 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
2831 | 4/28 | 22:00:00 | 280.15 | 98798 | 3.1 | 290 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
2832 | 4/28 | 23:00:00 | 280.15 | 98798 | 3.6 | 280 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
2833 | 4/28 | 24:00:00 | 280.15 | 98798 | 2.6 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2834 | 4/29 | 01:00:00 | 280.15 | 98798 | 1 | 210 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2835 | 4/29 | 02:00:00 | 279.15 | 98789 | 1 | 230 | 5.5666 | 0 | 0 | 264.075 | 0 | 1 | 6
2836 | 4/29 | 03:00:00 | 279.15 | 98789 | 1 | 290 | 5.5666 | 0 | 0 | 264.075 | 0 | 1 | 6
2837 | 4/29 | 04:00:00 | 279.15 | 98789 | 1.5 | 250 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
2838 | 4/29 | 05:00:00 | 279.15 | 98789 | 0.5 | 312 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
2839 | 4/29 | 06:00:00 | 279.15 | 98789 | 0 | 246 | 5.5666 | 79.2 | 0 | 265.224 | 0 | 1 | 6
2840 | 4/29 | 07:00:00 | 280.15 | 98798 | 0.5 | 273 | 5.5661 | 309.6 | 0 | 266.174 | 0 | 1 | 7
2841 | 4/29 | 08:00:00 | 280.15 | 98798 | 1 | 82 | 5.5661 | 604.8 | 176.4 | 266.174 | 0 | 1 | 7
2842 | 4/29 | 09:00:00 | 281.15 | 98806 | 1 | 168 | 5.5656 | 1616.4 | 1562.4 | 266.653 | 0 | 1 | 8
2843 | 4/29 | 10:00:00 | 281.15 | 98806 | 0.5 | 164 | 5.5656 | 2062.8 | 2124 | 266.653 | 0 | 1 | 8
2844 | 4/29 | 11:00:00 | 282.15 | 98815 | 1.5 | 161 | 5.1856 | 2394 | 2361.6 | 267.371 | 0 | 1 | 9
2845 | 4/29 | 12:00:00 | 283.15 | 98824 | 1 | 11 | 5.1851 | 2570.4 | 2397.6 | 268.319 | 0 | 1 | 10
2846 | 4/29 | 13:00:00 | 283.15 | 98824 | 3.1 | 210 | 5.1851 | 2581.2 | 2397.6 | 268.319 | 0 | 1 | 10
2847 | 4/29 | 14:00:00 | 284.15 | 98833 | 3.1 | 160 | 5.1847 | 2426.4 | 1929.6 | 269.266 | 0 | 1 | 11
2848 | 4/29 | 15:00:00 | 284.15 | 98833 | 3.6 | 170 | 5.1847 | 1177.2 | 190.8 | 269.743 | 0 | 1 | 11
2849 | 4/29 | 16:00:00 | 284.15 | 98833 | 4.6 | 150 | 4.4944 | 939.6 | 72 | 269.274 | 0 | 1 | 11
2850 | 4/29 | 17:00:00 | 283.15 | 98824 | 5.1 | 160 | 4.4948 | 648 | 50.4 | 268.326 | 0 | 1 | 10
2851 | 4/29 | 18:00:00 | 283.15 | 98824 | 3.1 | 160 | 4.4948 | 349.2 | 7.2 | 268.326 | 0 | 1 | 10
2852 | 4/29 | 19:00:00 | 283.15 | 98824 | 3.1 | 140 | 4.829 | 61.2 | 0 | 268.669 | 0 | 1 | 10
2853 | 4/29 | 20:00:00 | 283.15 | 98824 | 3.6 | 130 | 4.829 | 0 | 0 | 268.561 | 0 | 1 | 10
2854 | 4/29 | 21:00:00 | 282.15 | 98815 | 3.1 | 120 | 5.1856 | 0 | 0 | 267.844 | 0 | 1 | 9
2855 | 4/29 | 22:00:00 | 282.15 | 98815 | 5.1 | 120 | 5.5651 | 0 | 0 | 268.075 | 0 | 1 | 9
2856 | 4/29 | 23:00:00 | 282.15 | 98815 | 4.6 | 120 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
2857 | 4/29 | 24:00:00 | 281.15 | 98806 | 5.1 | 130 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
2858 | 4/30 | 01:00:00 | 280.15 | 98798 | 4.6 | 130 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
2859 | 4/30 | 02:00:00 | 279.15 | 98789 | 5.1 | 120 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
2860 | 4/30 | 03:00:00 | 279.15 | 98789 | 5.1 | 110 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
2861 | 4/30 | 04:00:00 | 279.15 | 98789 | 6.2 | 110 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
2862 | 4/30 | 05:00:00 | 279.15 | 98789 | 5.7 | 100 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
2863 | 4/30 | 06:00:00 | 279.15 | 98789 | 6.2 | 110 | 5.187 | 162 | 172.8 | 263.847 | 0 | 1 | 6
2864 | 4/30 | 07:00:00 | 280.15 | 98798 | 6.7 | 110 | 5.1865 | 615.6 | 1062 | 264.793 | 0 | 1 | 7
2865 | 4/30 | 08:00:00 | 281.15 | 98806 | 7.7 | 110 | 5.1861 | 1191.6 | 1803.6 | 265.738 | 0 | 1 | 8
2866 | 4/30 | 09:00:00 | 283.15 | 98824 | 6.7 | 110 | 5.5646 | 1731.6 | 2188.8 | 268.287 | 0 | 1 | 10
2867 | 4/30 | 10:00:00 | 284.15 | 98833 | 6.2 | 80 | 5.9681 | 1972.8 | 1778.4 | 269.854 | 0 | 1 | 11
2868 | 4/30 | 11:00:00 | 285.15 | 98841 | 8.2 | 90 | 5.9676 | 2401.2 | 2127.6 | 270.678 | 0 | 1 | 12
2869 | 4/30 | 12:00:00 | 285.15 | 98841 | 6.7 | 100 | 5.9676 | 2732.4 | 2793.6 | 270.413 | 0 | 1 | 12
2870 | 4/30 | 13:00:00 | 286.15 | 98850 | 7.7 | 80 | 6.3971 | 2739.6 | 2887.2 | 271.592 | 0 | 1 | 13
2871 | 4/30 | 14:00:00 | 286.15 | 98850 | 9.3 | 90 | 5.5631 | 2584.8 | 2869.2 | 271.13 | 0 | 1 | 13
2872 | 4/30 | 15:00:00 | 286.15 | 98850 | 9.8 | 100 | 5.1837 | 2264.4 | 2602.8 | 270.896 | 0 | 1 | 13
2873 | 4/30 | 16:00:00 | 285.15 | 98841 | 9.3 | 90 | 5.9676 | 1796.4 | 2386.8 | 270.413 | 0 | 1 | 12
2874 | 4/30 | 17:00:00 | 284.15 | 98833 | 8.2 | 90 | 6.3982 | 1245.6 | 1782 | 269.693 | 0 | 1 | 11
2875 | 4/30 | 18:00:00 | 284.15 | 98833 | 6.7 | 90 | 7.8598 | 673.2 | 878.4 | 270.371 | 0 | 1 | 11
2876 | 4/30 | 19:00:00 | 282.35 | 98817 | 4.2 | 67 | 7.0966 | 64.8 | 0 | 269.17 | 0 | 1 | 9.2
2877 | 4/30 | 20:00:00 | 281.95 | 98813 | 4 | 57 | 6.4888 | 0 | 0 | 268.495 | 0 | 1 | 8.8
2878 | 4/30 | 21:00:00 | 281.35 | 98808 | 3.6 | 52 | 6.0536 | 0 | 0 | 267.697 | 0 | 1 | 8.2
2879 | 4/30 | 22:00:00 | 281.75 | 98812 | 3 | 79 | 6.1383 | 0 | 0 | 267.902 | 0 | 1 | 8.6
2880 | 4/30 | 23:00:00 | 282.35 | 98817 | 2.6 | 143 | 6.6246 | 0 | 0 | 268.723 | 0 | 1 | 9.2
2881 | 4/30 | 24:00:00 | 282.95 | 98822 | 2.3 | 165 | 7.145 | 0 | 0 | 269.656 | 0 | 1 | 9.8
2882 | 5/1 | 01:00:00 | 283.45 | 98827 | 2.3 | 192 | 7.4948 | 0 | 0 | 270.399 | 0 | 1 | 10.3
2883 | 5/1 | 02:00:00 | 283.25 | 98825 | 2.3 | 188 | 7.3934 | 0 | 0 | 270.164 | 0 | 1 | 10.1
2884 | 5/1 | 03:00:00 | 283.45 | 98827 | 2.5 | 154 | 7.3932 | 0 | 0 | 270.354 | 0 | 1 | 10.3
2885 | 5/1 | 04:00:00 | 283.65 | 98829 | 2.7 | 170 | 7.3427 | 0 | 0 | 269.671 | 0 | 1 | 10.5
2886 | 5/1 | 05:00:00 | 284.15 | 98833 | 3.2 | 182 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
2887 | 5/1 | 06:00:00 | 284.65 | 98837 | 3.8 | 192 | 7.3422 | 169.2 | 108 | 270.622 | 0 | 1 | 11.5
2888 | 5/1 | 07:00:00 | 284.15 | 98833 | 3.1 | 190 | 7.3425 | 583.2 | 658.8 | 270.411 | 0 | 1 | 11
2889 | 5/1 | 08:00:00 | 285.15 | 98841 | 4.6 | 210 | 7.3418 | 1112.4 | 1407.6 | 271.363 | 0 | 1 | 12
2890 | 5/1 | 09:00:00 | 285.15 | 98841 | 4.6 | 200 | 7.3418 | 1634.4 | 1818 | 271.363 | 0 | 1 | 12
2891 | 5/1 | 10:00:00 | 286.15 | 98850 | 4.6 | 210 | 7.3412 | 2206.8 | 2480.4 | 272.048 | 0 | 1 | 13
2892 | 5/1 | 11:00:00 | 288.15 | 98867 | 6.2 | 200 | 6.8534 | 2404.8 | 2250 | 273.988 | 0 | 1 | 15
2893 | 5/1 | 12:00:00 | 289.15 | 98875 | 6.2 | 200 | 6.3955 | 2581.2 | 2289.6 | 274.708 | 0 | 1 | 16
2894 | 5/1 | 13:00:00 | 289.15 | 98875 | 6.7 | 210 | 5.1824 | 2797.2 | 2750.4 | 273.596 | 0 | 1 | 16
2895 | 5/1 | 14:00:00 | 287.15 | 98858 | 5.1 | 230 | 4.4933 | 2458.8 | 2084.4 | 271.636 | 0 | 1 | 14
2896 | 5/1 | 15:00:00 | 284.15 | 98833 | 5.1 | 240 | 5.5641 | 2271.6 | 2440.8 | 269.234 | 0 | 1 | 11
2897 | 5/1 | 16:00:00 | 284.15 | 98833 | 4.1 | 210 | 6.8558 | 1699.2 | 1879.2 | 270.185 | 0 | 1 | 11
2898 | 5/1 | 17:00:00 | 285.15 | 98841 | 6.2 | 220 | 6.3977 | 1184.4 | 1479.6 | 270.907 | 0 | 1 | 12
2899 | 5/1 | 18:00:00 | 285.15 | 98841 | 5.1 | 240 | 6.3977 | 648 | 918 | 270.907 | 0 | 1 | 12
2900 | 5/1 | 19:00:00 | 285.15 | 98841 | 5.1 | 220 | 6.8552 | 212.4 | 187.2 | 270.871 | 0 | 1 | 12
2901 | 5/1 | 20:00:00 | 284.15 | 98833 | 2.1 | 240 | 6.8558 | 0 | 0 | 269.921 | 0 | 1 | 11
2902 | 5/1 | 21:00:00 | 283.15 | 98824 | 3.1 | 250 | 6.3988 | 0 | 0 | 268.744 | 0 | 1 | 10
2903 | 5/1 | 22:00:00 | 282.15 | 98815 | 2.6 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
2904 | 5/1 | 23:00:00 | 280.15 | 98798 | 1.5 | 209 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
2905 | 5/1 | 24:00:00 | 281.15 | 98806 | 2.1 | 240 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
2906 | 5/2 | 01:00:00 | 281.15 | 98806 | 2.6 | 220 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
2907 | 5/2 | 02:00:00 | 281.15 | 98806 | 2.6 | 230 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
2908 | 5/2 | 03:00:00 | 280.15 | 98798 | 1 | 229 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
2909 | 5/2 | 04:00:00 | 279.15 | 98789 | 1 | 282 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2910 | 5/2 | 05:00:00 | 279.15 | 98789 | 1.5 | 111 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
2911 | 5/2 | 06:00:00 | 278.15 | 98780 | 1.5 | 240 | 5.5671 | 180 | 126 | 263.549 | 0 | 1 | 5
2912 | 5/2 | 07:00:00 | 281.15 | 98806 | 1.5 | 95 | 5.9698 | 637.2 | 1040.4 | 266.62 | 0 | 1 | 8
2913 | 5/2 | 08:00:00 | 282.15 | 98815 | 4.1 | 270 | 5.9692 | 1202.4 | 1735.2 | 267.568 | 0 | 1 | 9
2914 | 5/2 | 09:00:00 | 284.15 | 98833 | 3.6 | 270 | 5.5641 | 1659.6 | 1947.6 | 269.498 | 0 | 1 | 11
2915 | 5/2 | 10:00:00 | 283.15 | 98824 | 3.6 | 300 | 5.5646 | 2235.6 | 2422.8 | 268.287 | 0 | 1 | 10
2916 | 5/2 | 11:00:00 | 284.15 | 98833 | 3.1 | 250 | 4.8285 | 2584.8 | 2883.6 | 268.77 | 0 | 1 | 11
2917 | 5/2 | 12:00:00 | 286.15 | 98850 | 5.1 | 250 | 4.8277 | 2768.4 | 2937.6 | 270.662 | 0 | 1 | 13
2918 | 5/2 | 13:00:00 | 285.15 | 98841 | 5.7 | 260 | 4.494 | 2782.8 | 2952 | 269.481 | 0 | 1 | 12
2919 | 5/2 | 14:00:00 | 287.15 | 98858 | 5.1 | 230 | 4.8273 | 2617.2 | 2894.4 | 271.608 | 0 | 1 | 14
2920 | 5/2 | 15:00:00 | 287.15 | 98858 | 5.7 | 260 | 4.4933 | 2293.2 | 2592 | 271.371 | 0 | 1 | 14
2921 | 5/2 | 16:00:00 | 285.15 | 98841 | 4.6 | 280 | 4.494 | 1832.4 | 2394 | 269.481 | 0 | 1 | 12
2922 | 5/2 | 17:00:00 | 285.15 | 98841 | 4.6 | 280 | 4.8281 | 1278 | 1828.8 | 269.716 | 0 | 1 | 12
2923 | 5/2 | 18:00:00 | 285.15 | 98841 | 5.1 | 270 | 4.8281 | 705.6 | 1159.2 | 269.716 | 0 | 1 | 12
2924 | 5/2 | 19:00:00 | 285.15 | 98841 | 5.1 | 270 | 4.8281 | 223.2 | 208.8 | 269.716 | 0 | 1 | 12
2925 | 5/2 | 20:00:00 | 283.15 | 98824 | 3.6 | 260 | 4.4948 | 3.6 | 0 | 267.724 | 0 | 1 | 10
2926 | 5/2 | 21:00:00 | 281.15 | 98806 | 4.1 | 270 | 4.4957 | 0 | 0 | 265.96 | 0 | 1 | 8
2927 | 5/2 | 22:00:00 | 281.15 | 98806 | 2.1 | 260 | 4.8299 | 0 | 0 | 266.316 | 0 | 1 | 8
2928 | 5/2 | 23:00:00 | 280.15 | 98798 | 3.1 | 260 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
2929 | 5/2 | 24:00:00 | 281.15 | 98806 | 3.6 | 270 | 4.8299 | 0 | 0 | 266.316 | 0 | 1 | 8
2930 | 5/3 | 01:00:00 | 280.15 | 98798 | 2.6 | 250 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
2931 | 5/3 | 02:00:00 | 281.15 | 98806 | 4.6 | 230 | 4.8299 | 0 | 0 | 266.316 | 0 | 1 | 8
2932 | 5/3 | 03:00:00 | 281.15 | 98806 | 2.1 | 230 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
2933 | 5/3 | 04:00:00 | 281.15 | 98806 | 5.1 | 230 | 4.8299 | 0 | 0 | 266.664 | 0 | 1 | 8
2934 | 5/3 | 05:00:00 | 279.15 | 98789 | 4.1 | 290 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
2935 | 5/3 | 06:00:00 | 278.15 | 98780 | 5.1 | 260 | 5.1875 | 180 | 93.6 | 263.581 | 0 | 1 | 5
2936 | 5/3 | 07:00:00 | 280.15 | 98798 | 7.2 | 280 | 5.5661 | 612 | 867.6 | 265.704 | 0 | 1 | 7
2937 | 5/3 | 08:00:00 | 280.15 | 98798 | 8.2 | 290 | 5.5661 | 1148.4 | 1404 | 265.704 | 0 | 1 | 7
2938 | 5/3 | 09:00:00 | 282.15 | 98815 | 9.3 | 300 | 4.8294 | 1782 | 2178 | 266.878 | 0 | 1 | 9
2939 | 5/3 | 10:00:00 | 282.15 | 98815 | 9.8 | 300 | 4.4952 | 2257.2 | 2574 | 266.645 | 0 | 1 | 9
2940 | 5/3 | 11:00:00 | 283.15 | 98824 | 8.7 | 290 | 4.1815 | 2606.4 | 2912.4 | 267.355 | 0 | 1 | 10
2941 | 5/3 | 12:00:00 | 283.15 | 98824 | 9.3 | 300 | 4.1815 | 2790 | 2962.8 | 267.355 | 0 | 1 | 10
2942 | 5/3 | 13:00:00 | 284.15 | 98833 | 9.8 | 300 | 4.1811 | 2800.8 | 2750.4 | 268.3 | 0 | 1 | 11
2943 | 5/3 | 14:00:00 | 282.15 | 98815 | 8.7 | 310 | 4.4952 | 2480.4 | 2221.2 | 266.906 | 0 | 1 | 9
2944 | 5/3 | 15:00:00 | 283.15 | 98824 | 8.7 | 290 | 4.1815 | 2178 | 2149.2 | 267.617 | 0 | 1 | 10
2945 | 5/3 | 16:00:00 | 283.15 | 98824 | 8.2 | 290 | 4.4948 | 1738.8 | 1767.6 | 267.852 | 0 | 1 | 10
2946 | 5/3 | 17:00:00 | 284.15 | 98833 | 8.7 | 290 | 4.1811 | 1296 | 1569.6 | 268.3 | 0 | 1 | 11
2947 | 5/3 | 18:00:00 | 283.15 | 98824 | 8.2 | 290 | 4.1815 | 720 | 997.2 | 267.355 | 0 | 1 | 10
2948 | 5/3 | 19:00:00 | 282.15 | 98815 | 7.7 | 270 | 4.1819 | 234 | 172.8 | 266.411 | 0 | 1 | 9
2949 | 5/3 | 20:00:00 | 280.15 | 98798 | 7.7 | 280 | 4.1826 | 7.2 | 0 | 264.523 | 0 | 1 | 7
2950 | 5/3 | 21:00:00 | 279.15 | 98789 | 5.1 | 280 | 4.4964 | 0 | 0 | 264.31 | 0 | 1 | 6
2951 | 5/3 | 22:00:00 | 278.15 | 98780 | 3.6 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2952 | 5/3 | 23:00:00 | 278.15 | 98780 | 3.6 | 260 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
2953 | 5/3 | 24:00:00 | 278.15 | 98780 | 4.1 | 260 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
2954 | 5/4 | 01:00:00 | 279.15 | 98789 | 6.2 | 270 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
2955 | 5/4 | 02:00:00 | 279.15 | 98789 | 5.1 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
2956 | 5/4 | 03:00:00 | 279.15 | 98789 | 7.2 | 260 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
2957 | 5/4 | 04:00:00 | 279.15 | 98789 | 7.7 | 260 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
2958 | 5/4 | 05:00:00 | 280.15 | 98798 | 4.6 | 250 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
2959 | 5/4 | 06:00:00 | 280.15 | 98798 | 4.6 | 260 | 5.5661 | 187.2 | 108 | 265.704 | 0 | 1 | 7
2960 | 5/4 | 07:00:00 | 280.15 | 98798 | 3.6 | 240 | 5.5661 | 626.4 | 885.6 | 265.704 | 0 | 1 | 7
2961 | 5/4 | 08:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.5661 | 1162.8 | 1461.6 | 265.704 | 0 | 1 | 7
2962 | 5/4 | 09:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.5661 | 1688.4 | 1591.2 | 265.704 | 0 | 1 | 7
2963 | 5/4 | 10:00:00 | 280.15 | 98798 | 6.7 | 250 | 5.1865 | 1184.4 | 82.8 | 265.946 | 0 | 1 | 7
2964 | 5/4 | 11:00:00 | 281.15 | 98806 | 9.3 | 250 | 5.1861 | 1364.4 | 234 | 266.895 | 0 | 1 | 8
2965 | 5/4 | 12:00:00 | 282.15 | 98815 | 9.3 | 250 | 5.5651 | 1458 | 72 | 268.075 | 0 | 1 | 9
2966 | 5/4 | 13:00:00 | 281.15 | 98806 | 6.7 | 230 | 5.5656 | 1461.6 | 72 | 267.125 | 0 | 1 | 8
2967 | 5/4 | 14:00:00 | 282.15 | 98815 | 6.7 | 240 | 5.9692 | 1375.2 | 230.4 | 268.304 | 0 | 1 | 9
2968 | 5/4 | 15:00:00 | 283.15 | 98824 | 5.7 | 240 | 6.3988 | 1202.4 | 219.6 | 269.483 | 0 | 1 | 10
2969 | 5/4 | 16:00:00 | 283.15 | 98824 | 8.7 | 260 | 6.8564 | 964.8 | 72 | 269.71 | 0 | 1 | 10
2970 | 5/4 | 17:00:00 | 282.15 | 98815 | 6.2 | 240 | 7.3438 | 676.8 | 50.4 | 268.983 | 0 | 1 | 9
2971 | 5/4 | 18:00:00 | 282.15 | 98815 | 5.1 | 230 | 7.3438 | 378 | 10.8 | 268.983 | 0 | 1 | 9
2972 | 5/4 | 19:00:00 | 282.15 | 98815 | 3.6 | 250 | 7.3438 | 126 | 0 | 268.983 | 0 | 1 | 9
2973 | 5/4 | 20:00:00 | 283.15 | 98824 | 11.3 | 270 | 7.3431 | 3.6 | 0 | 269.936 | 0 | 1 | 10
2974 | 5/4 | 21:00:00 | 283.15 | 98824 | 9.8 | 270 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
2975 | 5/4 | 22:00:00 | 283.15 | 98824 | 6.7 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
2976 | 5/4 | 23:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
2977 | 5/4 | 24:00:00 | 283.15 | 98824 | 5.7 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
2978 | 5/5 | 01:00:00 | 282.15 | 98815 | 5.7 | 290 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
2979 | 5/5 | 02:00:00 | 282.15 | 98815 | 6.7 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
2980 | 5/5 | 03:00:00 | 282.15 | 98815 | 5.7 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
2981 | 5/5 | 04:00:00 | 282.15 | 98815 | 5.7 | 260 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
2982 | 5/5 | 05:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
2983 | 5/5 | 06:00:00 | 282.15 | 98815 | 5.1 | 260 | 6.3994 | 108 | 0 | 268.532 | 0 | 1 | 9
2984 | 5/5 | 07:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.8577 | 352.8 | 3.6 | 267.805 | 0 | 1 | 8
2985 | 5/5 | 08:00:00 | 282.15 | 98815 | 5.1 | 260 | 7.3438 | 648 | 46.8 | 268.983 | 0 | 1 | 9
2986 | 5/5 | 09:00:00 | 283.15 | 98824 | 4.1 | 260 | 7.3431 | 939.6 | 68.4 | 269.936 | 0 | 1 | 10
2987 | 5/5 | 10:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.8605 | 1180.8 | 212.4 | 270.161 | 0 | 1 | 10
2988 | 5/5 | 11:00:00 | 284.15 | 98833 | 7.2 | 270 | 7.3425 | 1360.8 | 226.8 | 270.89 | 0 | 1 | 11
2989 | 5/5 | 12:00:00 | 283.15 | 98824 | 7.7 | 260 | 7.3431 | 1454.4 | 72 | 269.936 | 0 | 1 | 10
2990 | 5/5 | 13:00:00 | 284.15 | 98833 | 8.7 | 260 | 7.3425 | 1458 | 72 | 270.89 | 0 | 1 | 11
2991 | 5/5 | 14:00:00 | 284.15 | 98833 | 9.3 | 260 | 6.8558 | 1375.2 | 226.8 | 270.663 | 0 | 1 | 11
2992 | 5/5 | 15:00:00 | 284.15 | 98833 | 8.2 | 250 | 6.8558 | 1209.6 | 219.6 | 270.663 | 0 | 1 | 11
2993 | 5/5 | 16:00:00 | 284.15 | 98833 | 8.2 | 250 | 6.8558 | 968.4 | 50.4 | 270.663 | 0 | 1 | 11
2994 | 5/5 | 17:00:00 | 284.15 | 98833 | 8.2 | 250 | 6.8558 | 684 | 50.4 | 270.663 | 0 | 1 | 11
2995 | 5/5 | 18:00:00 | 284.15 | 98833 | 8.2 | 250 | 6.8558 | 385.2 | 10.8 | 270.663 | 0 | 1 | 11
2996 | 5/5 | 19:00:00 | 284.15 | 98833 | 8.7 | 250 | 6.8558 | 133.2 | 0 | 270.663 | 0 | 1 | 11
2997 | 5/5 | 20:00:00 | 284.15 | 98833 | 9.3 | 250 | 6.3982 | 14.4 | 0 | 269.957 | 0 | 1 | 11
2998 | 5/5 | 21:00:00 | 284.15 | 98833 | 8.7 | 250 | 6.8558 | 0 | 0 | 270.663 | 0 | 1 | 11
2999 | 5/5 | 22:00:00 | 284.15 | 98833 | 10.8 | 250 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
3000 | 5/5 | 23:00:00 | 284.15 | 98833 | 11.8 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
3001 | 5/5 | 24:00:00 | 284.15 | 98833 | 12.9 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
3002 | 5/6 | 01:00:00 | 284.15 | 98833 | 12.3 | 260 | 6.8558 | 0 | 0 | 270.663 | 0 | 1 | 11
3003 | 5/6 | 02:00:00 | 283.15 | 98824 | 10.3 | 260 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
3004 | 5/6 | 03:00:00 | 283.15 | 98824 | 8.2 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
3005 | 5/6 | 04:00:00 | 283.15 | 98824 | 7.7 | 260 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
3006 | 5/6 | 05:00:00 | 283.15 | 98824 | 5.7 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
3007 | 5/6 | 06:00:00 | 283.15 | 98824 | 4.6 | 280 | 7.3431 | 115.2 | 0 | 269.936 | 0 | 1 | 10
3008 | 5/6 | 07:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.8605 | 648 | 709.2 | 269.684 | 0 | 1 | 10
3009 | 5/6 | 08:00:00 | 284.15 | 98833 | 7.7 | 280 | 7.3425 | 655.2 | 90 | 270.89 | 0 | 1 | 11
3010 | 5/6 | 09:00:00 | 284.15 | 98833 | 6.7 | 270 | 7.3425 | 943.2 | 68.4 | 270.89 | 0 | 1 | 11
3011 | 5/6 | 10:00:00 | 285.15 | 98841 | 8.2 | 260 | 7.8591 | 1188 | 212.4 | 272.069 | 0 | 1 | 12
3012 | 5/6 | 11:00:00 | 285.15 | 98841 | 9.3 | 250 | 7.8591 | 1364.4 | 223.2 | 272.069 | 0 | 1 | 12
3013 | 5/6 | 12:00:00 | 285.15 | 98841 | 8.2 | 260 | 7.8591 | 1458 | 72 | 272.069 | 0 | 1 | 12
3014 | 5/6 | 13:00:00 | 285.15 | 98841 | 7.7 | 250 | 7.3418 | 1465.2 | 223.2 | 271.843 | 0 | 1 | 12
3015 | 5/6 | 14:00:00 | 285.15 | 98841 | 6.7 | 250 | 7.8591 | 2484 | 1897.2 | 271.588 | 0 | 1 | 12
3016 | 5/6 | 15:00:00 | 287.15 | 98858 | 7.7 | 250 | 7.3406 | 2185.2 | 2102.4 | 273.266 | 0 | 1 | 14
3017 | 5/6 | 16:00:00 | 287.15 | 98858 | 6.2 | 240 | 6.854 | 1864.8 | 2278.8 | 272.77 | 0 | 1 | 14
3018 | 5/6 | 17:00:00 | 286.15 | 98850 | 8.7 | 240 | 6.8546 | 1242 | 1501.2 | 272.087 | 0 | 1 | 13
3019 | 5/6 | 18:00:00 | 286.15 | 98850 | 9.3 | 240 | 6.3971 | 748.8 | 1188 | 271.592 | 0 | 1 | 13
3020 | 5/6 | 19:00:00 | 286.15 | 98850 | 7.7 | 240 | 5.9671 | 244.8 | 313.2 | 271.627 | 0 | 1 | 13
3021 | 5/6 | 20:00:00 | 285.15 | 98841 | 7.2 | 230 | 6.3977 | 18 | 0 | 270.907 | 0 | 1 | 12
3022 | 5/6 | 21:00:00 | 285.15 | 98841 | 7.7 | 240 | 5.5636 | 0 | 0 | 270.447 | 0 | 1 | 12
3023 | 5/6 | 22:00:00 | 284.15 | 98833 | 7.2 | 230 | 6.3982 | 0 | 0 | 269.957 | 0 | 1 | 11
3024 | 5/6 | 23:00:00 | 284.15 | 98833 | 8.7 | 230 | 6.3982 | 0 | 0 | 269.957 | 0 | 1 | 11
3025 | 5/6 | 24:00:00 | 283.15 | 98824 | 8.7 | 230 | 6.3988 | 0 | 0 | 269.483 | 0 | 1 | 10
3026 | 5/7 | 01:00:00 | 282.15 | 98815 | 7.7 | 230 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
3027 | 5/7 | 02:00:00 | 282.15 | 98815 | 9.3 | 250 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
3028 | 5/7 | 03:00:00 | 281.15 | 98806 | 7.2 | 260 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
3029 | 5/7 | 04:00:00 | 280.15 | 98798 | 8.2 | 260 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
3030 | 5/7 | 05:00:00 | 280.15 | 98798 | 9.3 | 260 | 5.5661 | 3.6 | 0 | 266.174 | 0 | 1 | 7
3031 | 5/7 | 06:00:00 | 280.15 | 98798 | 9.8 | 260 | 5.1865 | 230.4 | 208.8 | 265.216 | 0 | 1 | 7
3032 | 5/7 | 07:00:00 | 280.15 | 98798 | 9.3 | 250 | 4.8303 | 705.6 | 1137.6 | 264.986 | 0 | 1 | 7
3033 | 5/7 | 08:00:00 | 281.15 | 98806 | 11.3 | 260 | 4.8299 | 1278 | 1803.6 | 265.932 | 0 | 1 | 8
3034 | 5/7 | 09:00:00 | 282.15 | 98815 | 11.3 | 250 | 4.4952 | 1731.6 | 1746 | 266.906 | 0 | 1 | 9
3035 | 5/7 | 10:00:00 | 283.15 | 98824 | 8.7 | 260 | 4.4948 | 2178 | 2134.8 | 267.852 | 0 | 1 | 10
3036 | 5/7 | 11:00:00 | 283.15 | 98824 | 7.7 | 260 | 4.4948 | 2498.4 | 2376 | 267.852 | 0 | 1 | 10
3037 | 5/7 | 12:00:00 | 285.15 | 98841 | 7.2 | 240 | 4.1808 | 2674.8 | 2415.6 | 269.507 | 0 | 1 | 12
3038 | 5/7 | 13:00:00 | 285.15 | 98841 | 7.2 | 240 | 4.1808 | 2682 | 2235.6 | 269.507 | 0 | 1 | 12
3039 | 5/7 | 14:00:00 | 286.15 | 98850 | 7.2 | 250 | 4.4936 | 2678.4 | 2710.8 | 270.426 | 0 | 1 | 13
3040 | 5/7 | 15:00:00 | 287.15 | 98858 | 6.7 | 230 | 4.4933 | 2354.4 | 2592 | 271.371 | 0 | 1 | 14
3041 | 5/7 | 16:00:00 | 287.15 | 98858 | 7.2 | 220 | 4.4933 | 1893.6 | 2404.8 | 271.371 | 0 | 1 | 14
3042 | 5/7 | 17:00:00 | 287.15 | 98858 | 7.7 | 230 | 4.1801 | 1342.8 | 1602 | 271.132 | 0 | 1 | 14
3043 | 5/7 | 18:00:00 | 286.15 | 98850 | 8.2 | 220 | 4.4936 | 766.8 | 1231.2 | 270.426 | 0 | 1 | 13
3044 | 5/7 | 19:00:00 | 285.15 | 98841 | 6.7 | 220 | 4.494 | 270 | 277.2 | 269.481 | 0 | 1 | 12
3045 | 5/7 | 20:00:00 | 284.15 | 98833 | 8.7 | 230 | 4.1811 | 21.6 | 0 | 268.3 | 0 | 1 | 11
3046 | 5/7 | 21:00:00 | 283.15 | 98824 | 6.7 | 230 | 4.4948 | 0 | 0 | 267.852 | 0 | 1 | 10
3047 | 5/7 | 22:00:00 | 283.15 | 98824 | 9.3 | 230 | 4.4948 | 0 | 0 | 267.852 | 0 | 1 | 10
3048 | 5/7 | 23:00:00 | 282.15 | 98815 | 7.2 | 230 | 3.8878 | 0 | 0 | 266.436 | 0 | 1 | 9
3049 | 5/7 | 24:00:00 | 282.15 | 98815 | 7.7 | 210 | 4.4952 | 0 | 0 | 266.906 | 0 | 1 | 9
3050 | 5/8 | 01:00:00 | 281.15 | 98806 | 8.7 | 210 | 4.4957 | 0 | 0 | 265.96 | 0 | 1 | 8
3051 | 5/8 | 02:00:00 | 280.15 | 98798 | 7.7 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3052 | 5/8 | 03:00:00 | 280.15 | 98798 | 6.7 | 230 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
3053 | 5/8 | 04:00:00 | 279.15 | 98789 | 6.2 | 230 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
3054 | 5/8 | 05:00:00 | 279.15 | 98789 | 7.2 | 220 | 4.4964 | 10.8 | 0 | 263.81 | 0 | 1 | 6
3055 | 5/8 | 06:00:00 | 279.15 | 98789 | 7.2 | 230 | 4.4964 | 241.2 | 223.2 | 263.81 | 0 | 1 | 6
3056 | 5/8 | 07:00:00 | 280.15 | 98798 | 7.7 | 230 | 4.496 | 680.4 | 950.4 | 265.014 | 0 | 1 | 7
3057 | 5/8 | 08:00:00 | 281.15 | 98806 | 8.2 | 230 | 4.1823 | 1296 | 1548 | 265.467 | 0 | 1 | 8
3058 | 5/8 | 09:00:00 | 282.15 | 98815 | 8.2 | 240 | 4.4952 | 1746 | 1753.2 | 266.906 | 0 | 1 | 9
3059 | 5/8 | 10:00:00 | 284.15 | 98833 | 14.4 | 240 | 3.577 | 2199.6 | 2127.6 | 268.085 | 0 | 1 | 11
3060 | 5/8 | 11:00:00 | 283.15 | 98824 | 12.9 | 250 | 4.4948 | 2509.2 | 1926 | 267.852 | 0 | 1 | 10
3061 | 5/8 | 12:00:00 | 281.15 | 98806 | 11.3 | 250 | 5.5656 | 1479.6 | 226.8 | 267.125 | 0 | 1 | 8
3062 | 5/8 | 13:00:00 | 283.15 | 98824 | 9.8 | 250 | 5.1851 | 1486.8 | 72 | 268.793 | 0 | 1 | 10
3063 | 5/8 | 14:00:00 | 284.15 | 98833 | 10.8 | 250 | 4.8285 | 1404 | 201.6 | 269.509 | 0 | 1 | 11
3064 | 5/8 | 15:00:00 | 283.15 | 98824 | 10.8 | 260 | 5.5646 | 2221.2 | 1843.2 | 268.55 | 0 | 1 | 10
3065 | 5/8 | 16:00:00 | 284.15 | 98833 | 9.8 | 250 | 4.8285 | 1904.4 | 2404.8 | 268.77 | 0 | 1 | 11
3066 | 5/8 | 17:00:00 | 283.15 | 98824 | 8.7 | 260 | 5.9687 | 1346.4 | 1854 | 268.516 | 0 | 1 | 10
3067 | 5/8 | 18:00:00 | 284.15 | 98833 | 10.3 | 260 | 4.8285 | 777.6 | 1234.8 | 268.77 | 0 | 1 | 11
3068 | 5/8 | 19:00:00 | 284.15 | 98833 | 7.7 | 250 | 5.1847 | 280.8 | 288 | 269.003 | 0 | 1 | 11
3069 | 5/8 | 20:00:00 | 282.15 | 98815 | 9.3 | 260 | 4.8294 | 25.2 | 0 | 266.878 | 0 | 1 | 9
3070 | 5/8 | 21:00:00 | 281.15 | 98806 | 5.1 | 240 | 5.1861 | 0 | 0 | 266.163 | 0 | 1 | 8
3071 | 5/8 | 22:00:00 | 281.15 | 98806 | 5.7 | 240 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
3072 | 5/8 | 23:00:00 | 280.15 | 98798 | 3.6 | 240 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
3073 | 5/8 | 24:00:00 | 280.15 | 98798 | 4.6 | 230 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
3074 | 5/9 | 01:00:00 | 279.15 | 98789 | 4.1 | 210 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3075 | 5/9 | 02:00:00 | 279.15 | 98789 | 4.1 | 210 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3076 | 5/9 | 03:00:00 | 279.15 | 98789 | 3.1 | 210 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3077 | 5/9 | 04:00:00 | 279.15 | 98789 | 2.6 | 220 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3078 | 5/9 | 05:00:00 | 279.15 | 98789 | 1.5 | 69 | 5.187 | 14.4 | 0 | 264.269 | 0 | 1 | 6
3079 | 5/9 | 06:00:00 | 279.15 | 98789 | 3.6 | 210 | 5.187 | 248.4 | 237.6 | 264.269 | 0 | 1 | 6
3080 | 5/9 | 07:00:00 | 281.15 | 98806 | 5.7 | 220 | 5.5656 | 730.8 | 1155.6 | 266.392 | 0 | 1 | 8
3081 | 5/9 | 08:00:00 | 282.15 | 98815 | 5.1 | 230 | 5.1856 | 1303.2 | 1814.4 | 267.11 | 0 | 1 | 9
3082 | 5/9 | 09:00:00 | 283.15 | 98824 | 7.7 | 220 | 4.829 | 1861.2 | 2379.6 | 267.824 | 0 | 1 | 10
3083 | 5/9 | 10:00:00 | 284.15 | 98833 | 7.2 | 230 | 4.1811 | 2340 | 2574 | 268.3 | 0 | 1 | 11
3084 | 5/9 | 11:00:00 | 285.15 | 98841 | 8.2 | 230 | 4.494 | 2520 | 2210.4 | 269.744 | 0 | 1 | 12
3085 | 5/9 | 12:00:00 | 284.15 | 98833 | 7.2 | 230 | 4.4944 | 2692.8 | 2401.2 | 268.798 | 0 | 1 | 11
3086 | 5/9 | 13:00:00 | 285.15 | 98841 | 9.3 | 230 | 4.494 | 2700 | 2401.2 | 269.744 | 0 | 1 | 12
3087 | 5/9 | 14:00:00 | 285.15 | 98841 | 7.7 | 210 | 4.494 | 2545.2 | 2379.6 | 269.744 | 0 | 1 | 12
3088 | 5/9 | 15:00:00 | 285.15 | 98841 | 5.7 | 220 | 5.1842 | 2232 | 2156.4 | 270.214 | 0 | 1 | 12
3089 | 5/9 | 16:00:00 | 281.15 | 98806 | 9.8 | 270 | 5.9698 | 1796.4 | 2098.8 | 266.881 | 0 | 1 | 8
3090 | 5/9 | 17:00:00 | 282.15 | 98815 | 8.2 | 260 | 5.9692 | 1357.2 | 1944 | 267.568 | 0 | 1 | 9
3091 | 5/9 | 18:00:00 | 283.15 | 98824 | 7.2 | 280 | 4.829 | 788.4 | 1249.2 | 267.824 | 0 | 1 | 10
3092 | 5/9 | 19:00:00 | 282.15 | 98815 | 6.7 | 270 | 4.4952 | 291.6 | 306 | 266.645 | 0 | 1 | 9
3093 | 5/9 | 20:00:00 | 281.15 | 98806 | 3.1 | 260 | 4.8299 | 28.8 | 0 | 265.932 | 0 | 1 | 8
3094 | 5/9 | 21:00:00 | 280.15 | 98798 | 6.2 | 250 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
3095 | 5/9 | 22:00:00 | 280.15 | 98798 | 5.1 | 260 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
3096 | 5/9 | 23:00:00 | 280.15 | 98798 | 5.7 | 250 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
3097 | 5/9 | 24:00:00 | 279.15 | 98789 | 4.1 | 250 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
3098 | 5/10 | 01:00:00 | 280.15 | 98798 | 3.1 | 250 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
3099 | 5/10 | 02:00:00 | 279.15 | 98789 | 0.5 | 90 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3100 | 5/10 | 03:00:00 | 279.15 | 98789 | 0.5 | 190 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3101 | 5/10 | 04:00:00 | 279.15 | 98789 | 1.5 | 160 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
3102 | 5/10 | 05:00:00 | 279.15 | 98789 | 1.5 | 230 | 5.187 | 21.6 | 0 | 264.269 | 0 | 1 | 6
3103 | 5/10 | 06:00:00 | 280.15 | 98798 | 1 | 230 | 5.5661 | 259.2 | 248.4 | 265.444 | 0 | 1 | 7
3104 | 5/10 | 07:00:00 | 280.15 | 98798 | 1.5 | 214 | 5.5661 | 741.6 | 1170 | 265.444 | 0 | 1 | 7
3105 | 5/10 | 08:00:00 | 281.15 | 98806 | 1.5 | 249 | 5.9698 | 1314 | 1807.2 | 266.62 | 0 | 1 | 8
3106 | 5/10 | 09:00:00 | 282.15 | 98815 | 2.1 | 310 | 5.9692 | 1864.8 | 2383.2 | 267.568 | 0 | 1 | 9
3107 | 5/10 | 10:00:00 | 283.15 | 98824 | 2.6 | 300 | 5.9687 | 2332.8 | 2610 | 268.516 | 0 | 1 | 10
3108 | 5/10 | 11:00:00 | 284.15 | 98833 | 2.6 | 310 | 5.5641 | 2674.8 | 2725.2 | 269.234 | 0 | 1 | 11
3109 | 5/10 | 12:00:00 | 283.15 | 98824 | 3.1 | 290 | 4.4948 | 2703.6 | 2138.4 | 267.852 | 0 | 1 | 10
3110 | 5/10 | 13:00:00 | 283.15 | 98824 | 0.5 | 190 | 5.1851 | 2865.6 | 2768.4 | 268.056 | 0 | 1 | 10
3111 | 5/10 | 14:00:00 | 283.15 | 98824 | 2.1 | 10 | 5.1851 | 2703.6 | 2876.4 | 268.056 | 0 | 1 | 10
3112 | 5/10 | 15:00:00 | 284.15 | 98833 | 1.5 | 170 | 4.8285 | 2383.2 | 2602.8 | 268.77 | 0 | 1 | 11
3113 | 5/10 | 16:00:00 | 283.15 | 98824 | 2.1 | 20 | 5.1851 | 1922.4 | 1987.2 | 268.056 | 0 | 1 | 10
3114 | 5/10 | 17:00:00 | 283.15 | 98824 | 3.1 | 70 | 6.3988 | 716.4 | 212.4 | 269.483 | 0 | 1 | 10
3115 | 5/10 | 18:00:00 | 283.15 | 98824 | 3.1 | 80 | 6.3988 | 414 | 18 | 269.483 | 0 | 1 | 10
3116 | 5/10 | 19:00:00 | 282.15 | 98815 | 3.1 | 80 | 5.9692 | 154.8 | 0 | 268.304 | 0 | 1 | 9
3117 | 5/10 | 20:00:00 | 282.15 | 98815 | 2.1 | 70 | 5.9692 | 25.2 | 0 | 268.191 | 0 | 1 | 9
3118 | 5/10 | 21:00:00 | 281.15 | 98806 | 1.5 | 90 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
3119 | 5/10 | 22:00:00 | 280.15 | 98798 | 2.1 | 70 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
3120 | 5/10 | 23:00:00 | 279.15 | 98789 | 2.6 | 70 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3121 | 5/10 | 24:00:00 | 278.15 | 98780 | 2.6 | 50 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
3122 | 5/11 | 01:00:00 | 278.15 | 98780 | 2.6 | 60 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
3123 | 5/11 | 02:00:00 | 277.15 | 98771 | 3.1 | 20 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
3124 | 5/11 | 03:00:00 | 277.15 | 98771 | 2.6 | 20 | 5.1879 | 0 | 0 | 262.633 | 0 | 1 | 4
3125 | 5/11 | 04:00:00 | 277.15 | 98771 | 3.1 | 20 | 5.1879 | 0 | 0 | 262.633 | 0 | 1 | 4
3126 | 5/11 | 05:00:00 | 277.15 | 98771 | 3.6 | 30 | 4.8316 | 25.2 | 0 | 262.149 | 0 | 1 | 4
3127 | 5/11 | 06:00:00 | 278.15 | 98780 | 4.1 | 30 | 5.1875 | 266.4 | 262.8 | 263.323 | 0 | 1 | 5
3128 | 5/11 | 07:00:00 | 279.15 | 98789 | 4.6 | 40 | 5.5666 | 752.4 | 1177.2 | 264.497 | 0 | 1 | 6
3129 | 5/11 | 08:00:00 | 280.15 | 98798 | 5.1 | 50 | 5.1865 | 1328.4 | 1828.8 | 265.216 | 0 | 1 | 7
3130 | 5/11 | 09:00:00 | 281.15 | 98806 | 5.1 | 70 | 5.5656 | 1879.2 | 2383.2 | 266.392 | 0 | 1 | 8
3131 | 5/11 | 10:00:00 | 283.15 | 98824 | 5.7 | 60 | 4.829 | 2354.4 | 2584.8 | 267.824 | 0 | 1 | 10
3132 | 5/11 | 11:00:00 | 284.15 | 98833 | 6.2 | 50 | 4.8285 | 2692.8 | 2883.6 | 268.77 | 0 | 1 | 11
3133 | 5/11 | 12:00:00 | 285.15 | 98841 | 7.2 | 50 | 4.494 | 2876.4 | 2944.8 | 269.481 | 0 | 1 | 12
3134 | 5/11 | 13:00:00 | 285.15 | 98841 | 6.7 | 60 | 4.1808 | 2887.2 | 2959.2 | 269.244 | 0 | 1 | 12
3135 | 5/11 | 14:00:00 | 285.15 | 98841 | 7.7 | 60 | 4.8281 | 2718 | 2890.8 | 269.716 | 0 | 1 | 12
3136 | 5/11 | 15:00:00 | 285.15 | 98841 | 7.7 | 70 | 4.494 | 2397.6 | 2595.6 | 269.481 | 0 | 1 | 12
3137 | 5/11 | 16:00:00 | 284.15 | 98833 | 7.7 | 70 | 4.4944 | 1940.4 | 2408.4 | 268.535 | 0 | 1 | 11
3138 | 5/11 | 17:00:00 | 283.15 | 98824 | 7.7 | 70 | 4.4948 | 1389.6 | 1922.4 | 267.59 | 0 | 1 | 10
3139 | 5/11 | 18:00:00 | 283.15 | 98824 | 7.2 | 60 | 4.829 | 810 | 1267.2 | 267.824 | 0 | 1 | 10
3140 | 5/11 | 19:00:00 | 282.15 | 98815 | 6.7 | 60 | 4.4952 | 309.6 | 342 | 266.645 | 0 | 1 | 9
3141 | 5/11 | 20:00:00 | 280.15 | 98798 | 6.2 | 70 | 4.496 | 39.6 | 0 | 264.755 | 0 | 1 | 7
3142 | 5/11 | 21:00:00 | 279.15 | 98789 | 5.1 | 60 | 4.4964 | 0 | 0 | 264.069 | 0 | 1 | 6
3143 | 5/11 | 22:00:00 | 278.15 | 98780 | 4.1 | 60 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
3144 | 5/11 | 23:00:00 | 278.15 | 98780 | 4.1 | 60 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
3145 | 5/11 | 24:00:00 | 278.15 | 98780 | 4.6 | 60 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
3146 | 5/12 | 01:00:00 | 277.15 | 98771 | 4.6 | 60 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
3147 | 5/12 | 02:00:00 | 277.15 | 98771 | 4.6 | 50 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
3148 | 5/12 | 03:00:00 | 277.15 | 98771 | 5.1 | 50 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
3149 | 5/12 | 04:00:00 | 277.15 | 98771 | 4.6 | 50 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
3150 | 5/12 | 05:00:00 | 278.15 | 98780 | 3.6 | 60 | 4.8311 | 14.4 | 0 | 263.818 | 0 | 1 | 5
3151 | 5/12 | 06:00:00 | 278.15 | 98780 | 4.6 | 60 | 4.8311 | 144 | 0 | 263.818 | 0 | 1 | 5
3152 | 5/12 | 07:00:00 | 279.15 | 98789 | 4.6 | 70 | 4.8307 | 399.6 | 14.4 | 264.767 | 0 | 1 | 6
3153 | 5/12 | 08:00:00 | 280.15 | 98798 | 4.6 | 60 | 5.1865 | 702 | 208.8 | 265.946 | 0 | 1 | 7
3154 | 5/12 | 09:00:00 | 281.15 | 98806 | 7.2 | 60 | 4.8299 | 1789.2 | 1803.6 | 266.193 | 0 | 1 | 8
3155 | 5/12 | 10:00:00 | 282.15 | 98815 | 7.7 | 60 | 4.8294 | 2228.4 | 2138.4 | 267.139 | 0 | 1 | 9
3156 | 5/12 | 11:00:00 | 284.15 | 98833 | 7.2 | 60 | 5.1847 | 2545.2 | 2343.6 | 269.266 | 0 | 1 | 11
3157 | 5/12 | 12:00:00 | 285.15 | 98841 | 7.2 | 70 | 5.5636 | 2710.8 | 2361.6 | 270.447 | 0 | 1 | 12
3158 | 5/12 | 13:00:00 | 285.15 | 98841 | 8.2 | 80 | 5.1842 | 2721.6 | 2246.4 | 270.214 | 0 | 1 | 12
3159 | 5/12 | 14:00:00 | 285.15 | 98841 | 8.2 | 70 | 5.1842 | 2721.6 | 2721.6 | 269.95 | 0 | 1 | 12
3160 | 5/12 | 15:00:00 | 286.15 | 98850 | 8.7 | 80 | 5.1837 | 2401.2 | 2610 | 270.896 | 0 | 1 | 13
3161 | 5/12 | 16:00:00 | 286.15 | 98850 | 8.7 | 80 | 5.5631 | 1940.4 | 2412 | 271.13 | 0 | 1 | 13
3162 | 5/12 | 17:00:00 | 286.15 | 98850 | 9.3 | 80 | 4.8277 | 1396.8 | 1922.4 | 270.662 | 0 | 1 | 13
3163 | 5/12 | 18:00:00 | 285.15 | 98841 | 8.7 | 80 | 4.8281 | 820.8 | 1278 | 269.716 | 0 | 1 | 12
3164 | 5/12 | 19:00:00 | 284.15 | 98833 | 8.2 | 80 | 5.1847 | 306 | 306 | 269.137 | 0 | 1 | 11
3165 | 5/12 | 20:00:00 | 282.15 | 98815 | 5.7 | 70 | 7.3438 | 14.4 | 0 | 269.092 | 0 | 1 | 9
3166 | 5/12 | 21:00:00 | 280.15 | 98798 | 5.7 | 60 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
3167 | 5/12 | 22:00:00 | 279.15 | 98789 | 4.6 | 60 | 5.9708 | 0 | 0 | 265.559 | 0 | 1 | 6
3168 | 5/12 | 23:00:00 | 279.15 | 98789 | 4.1 | 60 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3169 | 5/12 | 24:00:00 | 278.15 | 98780 | 4.1 | 60 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
3170 | 5/13 | 01:00:00 | 278.15 | 98780 | 4.6 | 50 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
3171 | 5/13 | 02:00:00 | 278.15 | 98780 | 5.1 | 50 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
3172 | 5/13 | 03:00:00 | 278.15 | 98780 | 5.1 | 50 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
3173 | 5/13 | 04:00:00 | 278.15 | 98780 | 5.1 | 50 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
3174 | 5/13 | 05:00:00 | 278.15 | 98780 | 5.1 | 40 | 4.8311 | 18 | 0 | 263.818 | 0 | 1 | 5
3175 | 5/13 | 06:00:00 | 279.15 | 98789 | 5.1 | 50 | 5.187 | 172.8 | 0 | 264.996 | 0 | 1 | 6
3176 | 5/13 | 07:00:00 | 280.15 | 98798 | 6.2 | 50 | 5.5661 | 471.6 | 104.4 | 266.174 | 0 | 1 | 7
3177 | 5/13 | 08:00:00 | 282.15 | 98815 | 5.7 | 60 | 5.9692 | 1346.4 | 1548 | 267.568 | 0 | 1 | 9
3178 | 5/13 | 09:00:00 | 285.15 | 98841 | 7.7 | 80 | 5.9676 | 1900.8 | 2390.4 | 270.413 | 0 | 1 | 12
3179 | 5/13 | 10:00:00 | 286.15 | 98850 | 7.2 | 70 | 6.3971 | 2361.6 | 2620.8 | 271.592 | 0 | 1 | 13
3180 | 5/13 | 11:00:00 | 287.15 | 98858 | 8.7 | 90 | 5.9666 | 2545.2 | 2232 | 272.576 | 0 | 1 | 14
3181 | 5/13 | 12:00:00 | 287.15 | 98858 | 10.3 | 90 | 5.5627 | 2718 | 2250 | 272.343 | 0 | 1 | 14
3182 | 5/13 | 13:00:00 | 286.15 | 98850 | 10.8 | 90 | 5.1837 | 2894.4 | 2768.4 | 270.896 | 0 | 1 | 13
3183 | 5/13 | 14:00:00 | 285.15 | 98841 | 10.8 | 90 | 5.1842 | 2732.4 | 2876.4 | 269.95 | 0 | 1 | 12
3184 | 5/13 | 15:00:00 | 285.15 | 98841 | 9.8 | 80 | 4.8281 | 2415.6 | 2214 | 269.716 | 0 | 1 | 12
3185 | 5/13 | 16:00:00 | 284.15 | 98833 | 8.2 | 90 | 4.4944 | 1026 | 172.8 | 269.274 | 0 | 1 | 11
3186 | 5/13 | 17:00:00 | 283.15 | 98824 | 7.7 | 80 | 5.1851 | 734.4 | 54 | 268.793 | 0 | 1 | 10
3187 | 5/13 | 18:00:00 | 282.15 | 98815 | 6.7 | 80 | 5.5651 | 435.6 | 21.6 | 268.075 | 0 | 1 | 9
3188 | 5/13 | 19:00:00 | 282.15 | 98815 | 5.1 | 70 | 5.5651 | 169.2 | 0 | 268.075 | 0 | 1 | 9
3189 | 5/13 | 20:00:00 | 282.15 | 98815 | 5.1 | 60 | 5.5651 | 25.2 | 0 | 268.075 | 0 | 1 | 9
3190 | 5/13 | 21:00:00 | 281.15 | 98806 | 5.1 | 60 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
3191 | 5/13 | 22:00:00 | 281.15 | 98806 | 5.1 | 60 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
3192 | 5/13 | 23:00:00 | 281.15 | 98806 | 4.6 | 60 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
3193 | 5/13 | 24:00:00 | 280.15 | 98798 | 5.7 | 50 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
3194 | 5/14 | 01:00:00 | 280.15 | 98798 | 4.6 | 50 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
3195 | 5/14 | 02:00:00 | 280.15 | 98798 | 4.6 | 50 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
3196 | 5/14 | 03:00:00 | 281.15 | 98806 | 4.6 | 50 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
3197 | 5/14 | 04:00:00 | 280.15 | 98798 | 4.1 | 40 | 6.4005 | 0 | 0 | 265.897 | 0 | 1 | 7
3198 | 5/14 | 05:00:00 | 281.15 | 98806 | 3.6 | 50 | 6.4 | 32.4 | 0 | 267.107 | 0 | 1 | 8
3199 | 5/14 | 06:00:00 | 281.15 | 98806 | 4.6 | 50 | 6.4 | 154.8 | 0 | 267.58 | 0 | 1 | 8
3200 | 5/14 | 07:00:00 | 281.15 | 98806 | 4.1 | 50 | 6.8577 | 410.4 | 14.4 | 267.805 | 0 | 1 | 8
3201 | 5/14 | 08:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.8577 | 709.2 | 50.4 | 267.805 | 0 | 1 | 8
3202 | 5/14 | 09:00:00 | 282.15 | 98815 | 5.1 | 60 | 6.8571 | 997.2 | 50.4 | 268.758 | 0 | 1 | 9
3203 | 5/14 | 10:00:00 | 283.15 | 98824 | 5.1 | 60 | 7.3431 | 1234.8 | 183.6 | 269.936 | 0 | 1 | 10
3204 | 5/14 | 11:00:00 | 283.15 | 98824 | 5.7 | 60 | 7.3431 | 2545.2 | 1904.4 | 269.46 | 0 | 1 | 10
3205 | 5/14 | 12:00:00 | 284.15 | 98833 | 6.7 | 60 | 6.8558 | 2880 | 2793.6 | 269.921 | 0 | 1 | 11
3206 | 5/14 | 13:00:00 | 285.15 | 98841 | 6.2 | 60 | 6.8552 | 2887.2 | 2397.6 | 270.871 | 0 | 1 | 12
3207 | 5/14 | 14:00:00 | 285.15 | 98841 | 6.7 | 70 | 6.3977 | 1429.2 | 939.6 | 271.387 | 0 | 1 | 12
3208 | 5/14 | 15:00:00 | 286.15 | 98850 | 6.7 | 70 | 5.9671 | 2275.2 | 1861.2 | 271.627 | 0 | 1 | 13
3209 | 5/14 | 16:00:00 | 286.15 | 98850 | 7.2 | 80 | 5.5631 | 1962 | 2415.6 | 271.13 | 0 | 1 | 13
3210 | 5/14 | 17:00:00 | 285.15 | 98841 | 6.7 | 80 | 5.5636 | 1414.8 | 1915.2 | 270.182 | 0 | 1 | 12
3211 | 5/14 | 18:00:00 | 284.15 | 98833 | 5.1 | 60 | 6.3982 | 838.8 | 1274.4 | 269.693 | 0 | 1 | 11
3212 | 5/14 | 19:00:00 | 283.15 | 98824 | 6.7 | 60 | 5.9687 | 334.8 | 374.4 | 268.516 | 0 | 1 | 10
3213 | 5/14 | 20:00:00 | 282.15 | 98815 | 4.1 | 60 | 6.3994 | 46.8 | 0 | 268.057 | 0 | 1 | 9
3214 | 5/14 | 21:00:00 | 282.15 | 98815 | 5.1 | 60 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
3215 | 5/14 | 22:00:00 | 281.15 | 98806 | 4.6 | 50 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
3216 | 5/14 | 23:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
3217 | 5/14 | 24:00:00 | 281.15 | 98806 | 4.1 | 60 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
3218 | 5/15 | 01:00:00 | 281.15 | 98806 | 5.7 | 40 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
3219 | 5/15 | 02:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
3220 | 5/15 | 03:00:00 | 281.15 | 98806 | 5.7 | 40 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
3221 | 5/15 | 04:00:00 | 281.15 | 98806 | 5.1 | 40 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
3222 | 5/15 | 05:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.8577 | 21.6 | 0 | 267.805 | 0 | 1 | 8
3223 | 5/15 | 06:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.8577 | 158.4 | 0 | 267.805 | 0 | 1 | 8
3224 | 5/15 | 07:00:00 | 281.15 | 98806 | 3.6 | 60 | 6.8577 | 414 | 21.6 | 267.805 | 0 | 1 | 8
3225 | 5/15 | 08:00:00 | 281.15 | 98806 | 5.1 | 40 | 6.8577 | 435.6 | 0 | 267.914 | 0 | 1 | 8
3226 | 5/15 | 09:00:00 | 281.15 | 98806 | 4.1 | 40 | 6.8577 | 612 | 3.6 | 267.914 | 0 | 1 | 8
3227 | 5/15 | 10:00:00 | 281.15 | 98806 | 4.6 | 50 | 6.8577 | 1242 | 82.8 | 267.805 | 0 | 1 | 8
3228 | 5/15 | 11:00:00 | 282.15 | 98815 | 4.6 | 40 | 6.8571 | 1418.4 | 68.4 | 268.758 | 0 | 1 | 9
3229 | 5/15 | 12:00:00 | 282.15 | 98815 | 4.1 | 50 | 7.3438 | 1508.4 | 72 | 268.983 | 0 | 1 | 9
3230 | 5/15 | 13:00:00 | 282.15 | 98815 | 2.6 | 50 | 7.3438 | 1512 | 72 | 268.983 | 0 | 1 | 9
3231 | 5/15 | 14:00:00 | 282.15 | 98815 | 2.1 | 50 | 7.3438 | 1429.2 | 68.4 | 268.983 | 0 | 1 | 9
3232 | 5/15 | 15:00:00 | 283.15 | 98824 | 1.5 | 7 | 7.3431 | 1260 | 216 | 269.936 | 0 | 1 | 10
3233 | 5/15 | 16:00:00 | 283.15 | 98824 | 1.5 | 281 | 7.3431 | 1026 | 194.4 | 269.936 | 0 | 1 | 10
3234 | 5/15 | 17:00:00 | 284.15 | 98833 | 1.5 | 130 | 7.8598 | 741.6 | 100.8 | 271.115 | 0 | 1 | 11
3235 | 5/15 | 18:00:00 | 284.15 | 98833 | 2.1 | 100 | 7.8598 | 846 | 1015.2 | 270.371 | 0 | 1 | 11
3236 | 5/15 | 19:00:00 | 284.15 | 98833 | 2.6 | 100 | 7.8598 | 342 | 378 | 270.371 | 0 | 1 | 11
3237 | 5/15 | 20:00:00 | 284.15 | 98833 | 2.1 | 41 | 7.8598 | 50.4 | 0 | 270.636 | 0 | 1 | 11
3238 | 5/15 | 21:00:00 | 283.15 | 98824 | 1.5 | 276 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
3239 | 5/15 | 22:00:00 | 282.15 | 98815 | 0.5 | 111 | 6.8571 | 0 | 0 | 267.593 | 0 | 1 | 9
3240 | 5/15 | 23:00:00 | 282.15 | 98815 | 1 | 204 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
3241 | 5/15 | 24:00:00 | 282.15 | 98815 | 0.5 | 90 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3242 | 5/16 | 01:00:00 | 282.15 | 98815 | 1.5 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3243 | 5/16 | 02:00:00 | 282.15 | 98815 | 5.1 | 230 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3244 | 5/16 | 03:00:00 | 281.15 | 98806 | 5.1 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
3245 | 5/16 | 04:00:00 | 280.15 | 98798 | 5.1 | 250 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
3246 | 5/16 | 05:00:00 | 279.15 | 98789 | 3.1 | 240 | 5.187 | 39.6 | 0 | 264.528 | 0 | 1 | 6
3247 | 5/16 | 06:00:00 | 279.15 | 98789 | 1 | 304 | 5.5666 | 313.2 | 414 | 264.497 | 0 | 1 | 6
3248 | 5/16 | 07:00:00 | 280.15 | 98798 | 3.1 | 140 | 5.9703 | 345.6 | 0 | 266.51 | 0 | 1 | 7
3249 | 5/16 | 08:00:00 | 281.15 | 98806 | 5.1 | 150 | 6.4 | 720 | 28.8 | 267.58 | 0 | 1 | 8
3250 | 5/16 | 09:00:00 | 281.15 | 98806 | 5.1 | 140 | 6.4 | 1008 | 54 | 267.58 | 0 | 1 | 8
3251 | 5/16 | 10:00:00 | 281.15 | 98806 | 4.1 | 140 | 6.8577 | 1249.2 | 187.2 | 267.805 | 0 | 1 | 8
3252 | 5/16 | 11:00:00 | 284.15 | 98833 | 5.1 | 150 | 7.3425 | 2559.6 | 1904.4 | 270.411 | 0 | 1 | 11
3253 | 5/16 | 12:00:00 | 286.15 | 98850 | 6.2 | 170 | 8.408 | 2721.6 | 2311.2 | 272.766 | 0 | 1 | 13
3254 | 5/16 | 13:00:00 | 285.15 | 98841 | 8.2 | 180 | 7.3418 | 2736 | 2257.2 | 271.363 | 0 | 1 | 12
3255 | 5/16 | 14:00:00 | 286.15 | 98850 | 5.7 | 160 | 7.3412 | 2739.6 | 2750.4 | 272.048 | 0 | 1 | 13
3256 | 5/16 | 15:00:00 | 286.15 | 98850 | 6.2 | 180 | 7.3412 | 2422.8 | 2512.8 | 272.048 | 0 | 1 | 13
3257 | 5/16 | 16:00:00 | 286.15 | 98850 | 6.2 | 170 | 6.3971 | 1864.8 | 1962 | 271.858 | 0 | 1 | 13
3258 | 5/16 | 17:00:00 | 286.15 | 98850 | 5.1 | 180 | 6.3971 | 1432.8 | 1990.8 | 271.592 | 0 | 1 | 13
3259 | 5/16 | 18:00:00 | 286.15 | 98850 | 5.7 | 200 | 5.9671 | 860.4 | 1303.2 | 271.361 | 0 | 1 | 13
3260 | 5/16 | 19:00:00 | 284.15 | 98833 | 4.1 | 160 | 5.5641 | 352.8 | 399.6 | 269.234 | 0 | 1 | 11
3261 | 5/16 | 20:00:00 | 284.15 | 98833 | 5.7 | 180 | 5.5641 | 54 | 0 | 269.234 | 0 | 1 | 11
3262 | 5/16 | 21:00:00 | 284.15 | 98833 | 7.2 | 210 | 5.5641 | 0 | 0 | 269.234 | 0 | 1 | 11
3263 | 5/16 | 22:00:00 | 280.15 | 98798 | 5.1 | 180 | 4.8303 | 0 | 0 | 265.246 | 0 | 1 | 7
3264 | 5/16 | 23:00:00 | 279.15 | 98789 | 3.6 | 180 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
3265 | 5/16 | 24:00:00 | 278.65 | 98784 | 3.1 | 236 | 5.1872 | 0 | 0 | 264.522 | 0 | 1 | 5.5
3266 | 5/17 | 01:00:00 | 278.15 | 98780 | 2.6 | 160 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
3267 | 5/17 | 02:00:00 | 276.15 | 98762 | 3.1 | 150 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
3268 | 5/17 | 03:00:00 | 277.15 | 98771 | 4.1 | 160 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
3269 | 5/17 | 04:00:00 | 278.15 | 98780 | 3.6 | 160 | 4.4968 | 0 | 0 | 262.445 | 0 | 1 | 5
3270 | 5/17 | 05:00:00 | 277.15 | 98771 | 2.6 | 110 | 4.8316 | 46.8 | 0 | 261.73 | 0 | 1 | 4
3271 | 5/17 | 06:00:00 | 276.15 | 98762 | 2.6 | 90 | 4.1841 | 320.4 | 295.2 | 260.746 | 0 | 1 | 3
3272 | 5/17 | 07:00:00 | 277.15 | 98771 | 3.1 | 100 | 4.8316 | 774 | 1033.2 | 262.405 | 0 | 1 | 4
3273 | 5/17 | 08:00:00 | 279.15 | 98789 | 3.1 | 110 | 5.187 | 1314 | 1537.2 | 264.528 | 0 | 1 | 6
3274 | 5/17 | 09:00:00 | 282.15 | 98815 | 5.1 | 120 | 6.8571 | 1825.2 | 1929.6 | 268.283 | 0 | 1 | 9
3275 | 5/17 | 10:00:00 | 282.15 | 98815 | 7.2 | 120 | 6.8571 | 2260.8 | 2095.2 | 268.283 | 0 | 1 | 9
3276 | 5/17 | 11:00:00 | 283.15 | 98824 | 6.7 | 120 | 6.8564 | 2574 | 2296.8 | 269.234 | 0 | 1 | 10
3277 | 5/17 | 12:00:00 | 285.15 | 98841 | 6.7 | 120 | 6.3977 | 2743.2 | 1958.4 | 270.907 | 0 | 1 | 12
3278 | 5/17 | 13:00:00 | 284.15 | 98833 | 7.7 | 120 | 5.9681 | 1530 | 223.2 | 270.206 | 0 | 1 | 11
3279 | 5/17 | 14:00:00 | 283.15 | 98824 | 6.7 | 110 | 6.3988 | 1443.6 | 219.6 | 269.483 | 0 | 1 | 10
3280 | 5/17 | 15:00:00 | 283.15 | 98824 | 6.2 | 120 | 6.8564 | 2296.8 | 1929.6 | 269.234 | 0 | 1 | 10
3281 | 5/17 | 16:00:00 | 284.15 | 98833 | 6.2 | 130 | 6.8558 | 1872 | 1796.4 | 270.185 | 0 | 1 | 11
3282 | 5/17 | 17:00:00 | 282.15 | 98815 | 4.6 | 160 | 6.8571 | 752.4 | 219.6 | 268.758 | 0 | 1 | 9
3283 | 5/17 | 18:00:00 | 282.15 | 98815 | 4.6 | 110 | 6.8571 | 453.6 | 36 | 268.758 | 0 | 1 | 9
3284 | 5/17 | 19:00:00 | 282.15 | 98815 | 4.6 | 160 | 7.3438 | 360 | 496.8 | 268.245 | 0 | 1 | 9
3285 | 5/17 | 20:00:00 | 283.15 | 98824 | 3.6 | 200 | 7.3431 | 54 | 0 | 269.46 | 0 | 1 | 10
3286 | 5/17 | 21:00:00 | 282.15 | 98815 | 4.1 | 190 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
3287 | 5/17 | 22:00:00 | 282.15 | 98815 | 4.1 | 190 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3288 | 5/17 | 23:00:00 | 282.15 | 98815 | 4.6 | 180 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3289 | 5/17 | 24:00:00 | 281.15 | 98806 | 4.6 | 180 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
3290 | 5/18 | 01:00:00 | 281.15 | 98806 | 4.6 | 180 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
3291 | 5/18 | 02:00:00 | 280.15 | 98798 | 3.6 | 170 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
3292 | 5/18 | 03:00:00 | 281.15 | 98806 | 3.1 | 170 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
3293 | 5/18 | 04:00:00 | 281.15 | 98806 | 2.6 | 160 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
3294 | 5/18 | 05:00:00 | 280.15 | 98798 | 3.1 | 140 | 5.9703 | 46.8 | 0 | 265.931 | 0 | 1 | 7
3295 | 5/18 | 06:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.4 | 309.6 | 270 | 267.107 | 0 | 1 | 8
3296 | 5/18 | 07:00:00 | 282.15 | 98815 | 6.7 | 170 | 5.9692 | 781.2 | 824.4 | 267.83 | 0 | 1 | 9
3297 | 5/18 | 08:00:00 | 282.15 | 98815 | 6.7 | 170 | 6.3994 | 730.8 | 212.4 | 268.532 | 0 | 1 | 9
3298 | 5/18 | 09:00:00 | 282.15 | 98815 | 4.1 | 180 | 6.8571 | 1832.4 | 1760.4 | 268.283 | 0 | 1 | 9
3299 | 5/18 | 10:00:00 | 283.15 | 98824 | 4.6 | 190 | 6.8564 | 1256.4 | 82.8 | 269.71 | 0 | 1 | 10
3300 | 5/18 | 11:00:00 | 285.15 | 98841 | 6.7 | 200 | 6.3977 | 1432.8 | 219.6 | 271.387 | 0 | 1 | 12
3301 | 5/18 | 12:00:00 | 285.15 | 98841 | 7.7 | 210 | 6.3977 | 2754 | 1958.4 | 270.907 | 0 | 1 | 12
3302 | 5/18 | 13:00:00 | 286.15 | 98850 | 6.7 | 210 | 6.8546 | 2757.6 | 2325.6 | 272.087 | 0 | 1 | 13
3303 | 5/18 | 14:00:00 | 286.15 | 98850 | 8.7 | 200 | 6.3971 | 2610 | 2307.6 | 271.858 | 0 | 1 | 13
3304 | 5/18 | 15:00:00 | 285.15 | 98841 | 8.7 | 220 | 6.3977 | 2307.6 | 2174.4 | 270.907 | 0 | 1 | 12
3305 | 5/18 | 16:00:00 | 285.15 | 98841 | 8.2 | 210 | 6.8552 | 1879.2 | 1958.4 | 271.136 | 0 | 1 | 12
3306 | 5/18 | 17:00:00 | 285.15 | 98841 | 7.7 | 230 | 6.8552 | 1368 | 1551.6 | 271.136 | 0 | 1 | 12
3307 | 5/18 | 18:00:00 | 284.15 | 98833 | 5.1 | 220 | 7.3425 | 828 | 1022.4 | 270.411 | 0 | 1 | 11
3308 | 5/18 | 19:00:00 | 284.15 | 98833 | 5.1 | 210 | 7.3425 | 349.2 | 320.4 | 270.411 | 0 | 1 | 11
3309 | 5/18 | 20:00:00 | 283.15 | 98824 | 6.2 | 220 | 6.8564 | 57.6 | 0 | 269.234 | 0 | 1 | 10
3310 | 5/18 | 21:00:00 | 283.15 | 98824 | 5.1 | 210 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
3311 | 5/18 | 22:00:00 | 282.15 | 98815 | 4.6 | 210 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
3312 | 5/18 | 23:00:00 | 282.15 | 98815 | 5.1 | 210 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3313 | 5/18 | 24:00:00 | 282.15 | 98815 | 5.1 | 200 | 5.9692 | 0 | 0 | 268.191 | 0 | 1 | 9
3314 | 5/19 | 01:00:00 | 281.15 | 98806 | 5.1 | 200 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
3315 | 5/19 | 02:00:00 | 281.15 | 98806 | 4.1 | 200 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
3316 | 5/19 | 03:00:00 | 281.15 | 98806 | 4.1 | 210 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
3317 | 5/19 | 04:00:00 | 281.15 | 98806 | 4.1 | 210 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
3318 | 5/19 | 05:00:00 | 281.15 | 98806 | 5.1 | 200 | 5.5656 | 39.6 | 0 | 267.013 | 0 | 1 | 8
3319 | 5/19 | 06:00:00 | 281.15 | 98806 | 3.6 | 160 | 5.9698 | 334.8 | 367.2 | 266.62 | 0 | 1 | 8
3320 | 5/19 | 07:00:00 | 282.15 | 98815 | 3.1 | 170 | 5.9692 | 788.4 | 828 | 267.83 | 0 | 1 | 9
3321 | 5/19 | 08:00:00 | 282.15 | 98815 | 3.6 | 170 | 6.3994 | 734.4 | 216 | 268.532 | 0 | 1 | 9
3322 | 5/19 | 09:00:00 | 283.15 | 98824 | 4.1 | 190 | 6.3988 | 1843.2 | 1785.6 | 269.007 | 0 | 1 | 10
3323 | 5/19 | 10:00:00 | 284.15 | 98833 | 4.6 | 200 | 5.9681 | 2282.4 | 2113.2 | 269.728 | 0 | 1 | 11
3324 | 5/19 | 11:00:00 | 284.15 | 98833 | 6.2 | 180 | 6.3982 | 2592 | 2300.4 | 269.957 | 0 | 1 | 11
3325 | 5/19 | 12:00:00 | 285.15 | 98841 | 6.2 | 180 | 6.8552 | 2754 | 2257.2 | 271.136 | 0 | 1 | 12
3326 | 5/19 | 13:00:00 | 285.15 | 98841 | 6.7 | 200 | 6.3977 | 2937.6 | 2797.2 | 270.643 | 0 | 1 | 12
3327 | 5/19 | 14:00:00 | 285.15 | 98841 | 5.1 | 170 | 6.3977 | 2775.6 | 2754 | 270.643 | 0 | 1 | 12
3328 | 5/19 | 15:00:00 | 285.15 | 98841 | 4.6 | 160 | 6.8552 | 2311.2 | 2088 | 271.136 | 0 | 1 | 12
3329 | 5/19 | 16:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.8564 | 2001.6 | 2307.6 | 268.971 | 0 | 1 | 10
3330 | 5/19 | 17:00:00 | 284.15 | 98833 | 3.6 | 220 | 6.8558 | 1378.8 | 1555.2 | 270.185 | 0 | 1 | 11
3331 | 5/19 | 18:00:00 | 285.15 | 98841 | 2.6 | 230 | 7.3418 | 835.2 | 1029.6 | 271.363 | 0 | 1 | 12
3332 | 5/19 | 19:00:00 | 283.15 | 98824 | 5.1 | 230 | 6.8564 | 356.4 | 331.2 | 269.234 | 0 | 1 | 10
3333 | 5/19 | 20:00:00 | 283.15 | 98824 | 1.5 | 48 | 6.8564 | 61.2 | 0 | 269.234 | 0 | 1 | 10
3334 | 5/19 | 21:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
3335 | 5/19 | 22:00:00 | 282.15 | 98815 | 4.1 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3336 | 5/19 | 23:00:00 | 281.15 | 98806 | 1.5 | 230 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
3337 | 5/19 | 24:00:00 | 282.15 | 98815 | 5.1 | 220 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3338 | 5/20 | 01:00:00 | 282.15 | 98815 | 2.6 | 210 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
3339 | 5/20 | 02:00:00 | 281.15 | 98806 | 2.1 | 210 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
3340 | 5/20 | 03:00:00 | 280.65 | 98802 | 1.8 | 39 | 6.1818 | 0 | 0 | 267.099 | 0 | 1 | 7.5
3341 | 5/20 | 04:00:00 | 280.15 | 98798 | 1.5 | 98 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
3342 | 5/20 | 05:00:00 | 280.15 | 98798 | 1.5 | 59 | 5.9703 | 54 | 0 | 265.671 | 0 | 1 | 7
3343 | 5/20 | 06:00:00 | 281.15 | 98806 | 4.6 | 210 | 6.4 | 342 | 374.4 | 266.846 | 0 | 1 | 8
3344 | 5/20 | 07:00:00 | 282.15 | 98815 | 5.1 | 220 | 6.3994 | 842.4 | 1260 | 267.795 | 0 | 1 | 9
3345 | 5/20 | 08:00:00 | 283.15 | 98824 | 4.6 | 230 | 6.3988 | 1418.4 | 1875.6 | 268.744 | 0 | 1 | 10
3346 | 5/20 | 09:00:00 | 284.15 | 98833 | 7.7 | 230 | 6.3982 | 1965.6 | 2404.8 | 269.693 | 0 | 1 | 11
3347 | 5/20 | 10:00:00 | 285.15 | 98841 | 6.7 | 230 | 6.3977 | 2426.4 | 2624.4 | 270.643 | 0 | 1 | 12
3348 | 5/20 | 11:00:00 | 287.15 | 98858 | 6.7 | 230 | 6.3966 | 2599.2 | 2232 | 272.808 | 0 | 1 | 14
3349 | 5/20 | 12:00:00 | 286.15 | 98850 | 5.7 | 240 | 5.9671 | 2772 | 2250 | 271.627 | 0 | 1 | 13
3350 | 5/20 | 13:00:00 | 286.15 | 98850 | 3.6 | 250 | 6.3971 | 2944.8 | 2797.2 | 271.592 | 0 | 1 | 13
3351 | 5/20 | 14:00:00 | 285.15 | 98841 | 4.1 | 240 | 7.3418 | 2775.6 | 2347.2 | 271.097 | 0 | 1 | 12
3352 | 5/20 | 15:00:00 | 286.15 | 98850 | 4.1 | 260 | 6.8546 | 1288.8 | 259.2 | 272.568 | 0 | 1 | 13
3353 | 5/20 | 16:00:00 | 285.15 | 98841 | 3.6 | 230 | 7.3418 | 1893.6 | 1792.8 | 271.363 | 0 | 1 | 12
3354 | 5/20 | 17:00:00 | 285.15 | 98841 | 5.7 | 250 | 7.3418 | 1386 | 1551.6 | 271.363 | 0 | 1 | 12
3355 | 5/20 | 18:00:00 | 284.15 | 98833 | 2.1 | 270 | 7.3425 | 846 | 1036.8 | 270.411 | 0 | 1 | 11
3356 | 5/20 | 19:00:00 | 284.15 | 98833 | 1.5 | 230 | 7.3425 | 363.6 | 338.4 | 270.411 | 0 | 1 | 11
3357 | 5/20 | 20:00:00 | 284.15 | 98833 | 1 | 221 | 7.3425 | 64.8 | 0 | 270.411 | 0 | 1 | 11
3358 | 5/20 | 21:00:00 | 284.15 | 98833 | 0.5 | 100 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
3359 | 5/20 | 22:00:00 | 282.15 | 98815 | 1.5 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
3360 | 5/20 | 23:00:00 | 282.15 | 98815 | 1.5 | 124 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
3361 | 5/20 | 24:00:00 | 282.15 | 98815 | 1.5 | 160 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
3362 | 5/21 | 01:00:00 | 281.15 | 98806 | 1 | 210 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
3363 | 5/21 | 02:00:00 | 282.15 | 98815 | 1 | 74 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
3364 | 5/21 | 03:00:00 | 282.15 | 98815 | 0.5 | 301 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
3365 | 5/21 | 04:00:00 | 281.15 | 98806 | 1.5 | 220 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
3366 | 5/21 | 05:00:00 | 281.15 | 98806 | 0 | 7 | 6.8577 | 54 | 0 | 267.332 | 0 | 1 | 8
3367 | 5/21 | 06:00:00 | 282.15 | 98815 | 2.6 | 230 | 6.8571 | 331.2 | 295.2 | 268.283 | 0 | 1 | 9
3368 | 5/21 | 07:00:00 | 282.15 | 98815 | 3.6 | 230 | 7.3438 | 849.6 | 1256.4 | 268.245 | 0 | 1 | 9
3369 | 5/21 | 08:00:00 | 283.15 | 98824 | 3.6 | 240 | 7.3431 | 1422 | 1936.8 | 269.196 | 0 | 1 | 10
3370 | 5/21 | 09:00:00 | 283.15 | 98824 | 4.6 | 270 | 7.3431 | 1854 | 2066.4 | 269.46 | 0 | 1 | 10
3371 | 5/21 | 10:00:00 | 280.15 | 98798 | 2.6 | 270 | 5.9703 | 2296.8 | 2037.6 | 265.931 | 0 | 1 | 7
3372 | 5/21 | 11:00:00 | 283.15 | 98824 | 2.6 | 250 | 6.8564 | 2761.2 | 2743.2 | 268.971 | 0 | 1 | 10
3373 | 5/21 | 12:00:00 | 285.15 | 98841 | 3.1 | 250 | 7.8591 | 2930.4 | 2858.4 | 271.323 | 0 | 1 | 12
3374 | 5/21 | 13:00:00 | 286.15 | 98850 | 6.7 | 280 | 7.3412 | 2941.2 | 2865.6 | 272.048 | 0 | 1 | 13
3375 | 5/21 | 14:00:00 | 287.15 | 98858 | 6.7 | 270 | 6.854 | 2786.4 | 2750.4 | 272.77 | 0 | 1 | 14
3376 | 5/21 | 15:00:00 | 286.15 | 98850 | 7.7 | 280 | 5.9671 | 2336.4 | 2167.2 | 271.627 | 0 | 1 | 13
3377 | 5/21 | 16:00:00 | 287.15 | 98858 | 8.2 | 280 | 5.9666 | 1911.6 | 2127.6 | 272.576 | 0 | 1 | 14
3378 | 5/21 | 17:00:00 | 286.15 | 98850 | 6.7 | 270 | 5.1837 | 1490.4 | 2062.8 | 270.896 | 0 | 1 | 13
3379 | 5/21 | 18:00:00 | 285.15 | 98841 | 6.7 | 280 | 5.1842 | 914.4 | 1303.2 | 269.95 | 0 | 1 | 12
3380 | 5/21 | 19:00:00 | 285.15 | 98841 | 6.7 | 270 | 4.8281 | 396 | 460.8 | 269.716 | 0 | 1 | 12
3381 | 5/21 | 20:00:00 | 284.15 | 98833 | 6.7 | 280 | 5.1847 | 72 | 0 | 269.003 | 0 | 1 | 11
3382 | 5/21 | 21:00:00 | 283.15 | 98824 | 6.2 | 270 | 5.9687 | 0 | 0 | 268.516 | 0 | 1 | 10
3383 | 5/21 | 22:00:00 | 282.15 | 98815 | 3.1 | 270 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
3384 | 5/21 | 23:00:00 | 282.15 | 98815 | 2.6 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3385 | 5/21 | 24:00:00 | 282.15 | 98815 | 3.6 | 250 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
3386 | 5/22 | 01:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3387 | 5/22 | 02:00:00 | 282.15 | 98815 | 3.6 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3388 | 5/22 | 03:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3389 | 5/22 | 04:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
3390 | 5/22 | 05:00:00 | 281.15 | 98806 | 2.1 | 270 | 5.9698 | 61.2 | 0 | 266.62 | 0 | 1 | 8
3391 | 5/22 | 06:00:00 | 281.15 | 98806 | 3.1 | 260 | 5.9698 | 360 | 392.4 | 266.62 | 0 | 1 | 8
3392 | 5/22 | 07:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.3994 | 860.4 | 1263.6 | 267.795 | 0 | 1 | 9
3393 | 5/22 | 08:00:00 | 282.15 | 98815 | 5.1 | 260 | 6.8571 | 1350 | 1591.2 | 268.283 | 0 | 1 | 9
3394 | 5/22 | 09:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.8564 | 1864.8 | 1936.8 | 269.234 | 0 | 1 | 10
3395 | 5/22 | 10:00:00 | 284.15 | 98833 | 5.7 | 270 | 6.8558 | 2296.8 | 2091.6 | 270.185 | 0 | 1 | 11
3396 | 5/22 | 11:00:00 | 284.15 | 98833 | 6.2 | 250 | 5.9681 | 2617.2 | 1929.6 | 269.728 | 0 | 1 | 11
3397 | 5/22 | 12:00:00 | 285.15 | 98841 | 6.2 | 270 | 6.8552 | 1540.8 | 219.6 | 271.616 | 0 | 1 | 12
3398 | 5/22 | 13:00:00 | 285.15 | 98841 | 5.7 | 260 | 6.8552 | 1544.4 | 72 | 271.616 | 0 | 1 | 12
3399 | 5/22 | 14:00:00 | 286.15 | 98850 | 6.7 | 270 | 7.3412 | 1458 | 216 | 272.796 | 0 | 1 | 13
3400 | 5/22 | 15:00:00 | 287.15 | 98858 | 7.7 | 260 | 7.3406 | 2332.8 | 1918.8 | 273.266 | 0 | 1 | 14
3401 | 5/22 | 16:00:00 | 286.15 | 98850 | 6.2 | 280 | 7.3412 | 1911.6 | 1954.8 | 272.314 | 0 | 1 | 13
3402 | 5/22 | 17:00:00 | 285.15 | 98841 | 4.6 | 240 | 7.3418 | 1404 | 1558.8 | 271.363 | 0 | 1 | 12
3403 | 5/22 | 18:00:00 | 286.15 | 98850 | 4.6 | 260 | 7.3412 | 864 | 921.6 | 272.314 | 0 | 1 | 13
3404 | 5/22 | 19:00:00 | 286.15 | 98850 | 3.6 | 250 | 7.3412 | 208.8 | 0 | 272.796 | 0 | 1 | 13
3405 | 5/22 | 20:00:00 | 285.15 | 98841 | 3.1 | 250 | 7.3418 | 39.6 | 0 | 271.843 | 0 | 1 | 12
3406 | 5/22 | 21:00:00 | 285.15 | 98841 | 3.1 | 240 | 7.3418 | 0 | 0 | 271.843 | 0 | 1 | 12
3407 | 5/22 | 22:00:00 | 284.15 | 98833 | 1.5 | 210 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
3408 | 5/22 | 23:00:00 | 284.15 | 98833 | 2.6 | 200 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
3409 | 5/22 | 24:00:00 | 284.15 | 98833 | 2.1 | 210 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
3410 | 5/23 | 01:00:00 | 284.15 | 98833 | 3.1 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
3411 | 5/23 | 02:00:00 | 284.15 | 98833 | 1.5 | 210 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
3412 | 5/23 | 03:00:00 | 282.15 | 98815 | 1 | 220 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3413 | 5/23 | 04:00:00 | 283.15 | 98824 | 3.1 | 220 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
3414 | 5/23 | 05:00:00 | 282.15 | 98815 | 2.1 | 190 | 6.8571 | 61.2 | 0 | 268.021 | 0 | 1 | 9
3415 | 5/23 | 06:00:00 | 283.15 | 98824 | 2.1 | 170 | 7.3431 | 363.6 | 399.6 | 269.196 | 0 | 1 | 10
3416 | 5/23 | 07:00:00 | 284.15 | 98833 | 2.6 | 180 | 7.8598 | 867.6 | 1256.4 | 270.371 | 0 | 1 | 11
3417 | 5/23 | 08:00:00 | 286.15 | 98850 | 3.1 | 210 | 7.8584 | 1353.6 | 1465.2 | 272.541 | 0 | 1 | 13
3418 | 5/23 | 09:00:00 | 286.15 | 98850 | 2.6 | 180 | 7.8584 | 1036.8 | 72 | 273.023 | 0 | 1 | 13
3419 | 5/23 | 10:00:00 | 287.15 | 98858 | 4.1 | 190 | 8.4073 | 1274.4 | 277.2 | 274.203 | 0 | 1 | 14
3420 | 5/23 | 11:00:00 | 286.15 | 98850 | 3.1 | 130 | 8.408 | 2606.4 | 1875.6 | 272.766 | 0 | 1 | 13
3421 | 5/23 | 12:00:00 | 289.15 | 98875 | 3.6 | 180 | 8.9895 | 2768.4 | 2300.4 | 275.852 | 0 | 1 | 16
3422 | 5/23 | 13:00:00 | 290.15 | 98883 | 5.1 | 170 | 7.8557 | 2782.8 | 2311.2 | 276.351 | 0 | 1 | 17
3423 | 5/23 | 14:00:00 | 289.15 | 98875 | 5.7 | 190 | 7.3393 | 2638.8 | 2293.2 | 275.169 | 0 | 1 | 16
3424 | 5/23 | 15:00:00 | 290.15 | 98883 | 6.2 | 210 | 7.3387 | 2340 | 2091.6 | 276.121 | 0 | 1 | 17
3425 | 5/23 | 16:00:00 | 288.15 | 98867 | 4.1 | 280 | 7.3399 | 2037.6 | 2437.2 | 273.95 | 0 | 1 | 15
3426 | 5/23 | 17:00:00 | 289.15 | 98875 | 6.7 | 270 | 7.8564 | 1497.6 | 1933.2 | 275.129 | 0 | 1 | 16
3427 | 5/23 | 18:00:00 | 288.15 | 98867 | 6.2 | 260 | 5.9661 | 932.4 | 1310.4 | 273.258 | 0 | 1 | 15
3428 | 5/23 | 19:00:00 | 287.15 | 98858 | 5.7 | 270 | 5.1833 | 417.6 | 489.6 | 271.843 | 0 | 1 | 14
3429 | 5/23 | 20:00:00 | 285.15 | 98841 | 5.1 | 270 | 5.9676 | 72 | 0 | 270.678 | 0 | 1 | 12
3430 | 5/23 | 21:00:00 | 284.15 | 98833 | 5.7 | 270 | 6.8558 | 0 | 0 | 270.185 | 0 | 1 | 11
3431 | 5/23 | 22:00:00 | 283.15 | 98824 | 5.7 | 270 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
3432 | 5/23 | 23:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3433 | 5/23 | 24:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
3434 | 5/24 | 01:00:00 | 282.15 | 98815 | 3.1 | 300 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
3435 | 5/24 | 02:00:00 | 281.15 | 98806 | 3.6 | 250 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
3436 | 5/24 | 03:00:00 | 281.15 | 98806 | 5.7 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
3437 | 5/24 | 04:00:00 | 280.15 | 98798 | 5.7 | 290 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
3438 | 5/24 | 05:00:00 | 280.15 | 98798 | 5.1 | 300 | 5.5661 | 39.6 | 0 | 266.174 | 0 | 1 | 7
3439 | 5/24 | 06:00:00 | 280.15 | 98798 | 5.7 | 310 | 5.9703 | 158.4 | 0 | 266.51 | 0 | 1 | 7
3440 | 5/24 | 07:00:00 | 281.15 | 98806 | 5.7 | 300 | 6.4 | 878.4 | 1083.6 | 266.846 | 0 | 1 | 8
3441 | 5/24 | 08:00:00 | 283.15 | 98824 | 5.7 | 300 | 5.9687 | 1206 | 972 | 269.025 | 0 | 1 | 10
3442 | 5/24 | 09:00:00 | 285.15 | 98841 | 6.2 | 290 | 5.9676 | 1868.4 | 1803.6 | 270.678 | 0 | 1 | 12
3443 | 5/24 | 10:00:00 | 287.15 | 98858 | 4.1 | 250 | 5.9666 | 2419.2 | 2347.2 | 272.445 | 0 | 1 | 14
3444 | 5/24 | 11:00:00 | 288.15 | 98867 | 3.1 | 250 | 6.396 | 2786.4 | 2829.6 | 273.49 | 0 | 1 | 15
3445 | 5/24 | 12:00:00 | 289.15 | 98875 | 3.6 | 240 | 5.9656 | 2970 | 2883.6 | 274.206 | 0 | 1 | 16
3446 | 5/24 | 13:00:00 | 289.15 | 98875 | 5.1 | 280 | 5.9656 | 2977.2 | 2887.2 | 274.206 | 0 | 1 | 16
3447 | 5/24 | 14:00:00 | 290.15 | 98883 | 4.1 | 260 | 5.9651 | 2818.8 | 2847.6 | 275.155 | 0 | 1 | 17
3448 | 5/24 | 15:00:00 | 291.15 | 98892 | 4.6 | 270 | 5.9645 | 2530.8 | 2844 | 275.961 | 0 | 1 | 18
3449 | 5/24 | 16:00:00 | 291.15 | 98892 | 3.1 | 250 | 5.9645 | 2077.2 | 2527.2 | 275.961 | 0 | 1 | 18
3450 | 5/24 | 17:00:00 | 291.15 | 98892 | 4.6 | 300 | 5.5607 | 1537.2 | 2012.4 | 275.578 | 0 | 1 | 18
3451 | 5/24 | 18:00:00 | 290.15 | 98883 | 3.6 | 300 | 5.5612 | 950.4 | 1371.6 | 274.778 | 0 | 1 | 17
3452 | 5/24 | 19:00:00 | 290.15 | 98883 | 2.6 | 310 | 5.5612 | 424.8 | 511.2 | 274.778 | 0 | 1 | 17
3453 | 5/24 | 20:00:00 | 289.15 | 98875 | 3.1 | 310 | 5.9656 | 79.2 | 0 | 274.206 | 0 | 1 | 16
3454 | 5/24 | 21:00:00 | 287.15 | 98858 | 0.5 | 10 | 6.854 | 0 | 0 | 273.038 | 0 | 1 | 14
3455 | 5/24 | 22:00:00 | 286.15 | 98850 | 0.5 | 340 | 6.3971 | 0 | 0 | 271.858 | 0 | 1 | 13
3456 | 5/24 | 23:00:00 | 285.15 | 98841 | 1 | 320 | 6.3977 | 0 | 0 | 271.033 | 0 | 1 | 12
3457 | 5/24 | 24:00:00 | 284.15 | 98833 | 2.1 | 270 | 6.3982 | 0 | 0 | 270.204 | 0 | 1 | 11
3458 | 5/25 | 01:00:00 | 283.15 | 98824 | 2.1 | 310 | 5.9687 | 0 | 0 | 269.025 | 0 | 1 | 10
3459 | 5/25 | 02:00:00 | 283.15 | 98824 | 1 | 300 | 5.9687 | 0 | 0 | 269.025 | 0 | 1 | 10
3460 | 5/25 | 03:00:00 | 281.15 | 98806 | 1 | 310 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
3461 | 5/25 | 04:00:00 | 282.15 | 98815 | 0 | 101 | 5.9692 | 0 | 0 | 268.191 | 0 | 1 | 9
3462 | 5/25 | 05:00:00 | 281.15 | 98806 | 1 | 40 | 5.9698 | 39.6 | 0 | 267.353 | 0 | 1 | 8
3463 | 5/25 | 06:00:00 | 282.15 | 98815 | 0.5 | 63 | 6.3994 | 230.4 | 0 | 268.532 | 0 | 1 | 9
3464 | 5/25 | 07:00:00 | 283.15 | 98824 | 2.6 | 90 | 6.8564 | 536.4 | 115.2 | 269.71 | 0 | 1 | 10
3465 | 5/25 | 08:00:00 | 286.15 | 98850 | 1.5 | 76 | 7.3412 | 1184.4 | 853.2 | 272.563 | 0 | 1 | 13
3466 | 5/25 | 09:00:00 | 288.15 | 98867 | 2.1 | 120 | 7.3399 | 1868.4 | 1778.4 | 274.218 | 0 | 1 | 15
3467 | 5/25 | 10:00:00 | 290.15 | 98883 | 3.6 | 130 | 7.8557 | 2361.6 | 2311.2 | 276.351 | 0 | 1 | 17
3468 | 5/25 | 11:00:00 | 291.15 | 98892 | 3.1 | 140 | 8.4044 | 2656.8 | 2340 | 277.532 | 0 | 1 | 18
3469 | 5/25 | 12:00:00 | 292.15 | 98900 | 3.6 | 160 | 8.4037 | 2952 | 2779.2 | 278.213 | 0 | 1 | 19
3470 | 5/25 | 13:00:00 | 294.15 | 98916 | 3.6 | 170 | 8.4023 | 2962.8 | 2858.4 | 280.117 | 0 | 1 | 21
3471 | 5/25 | 14:00:00 | 293.15 | 98908 | 2.6 | 180 | 7.8537 | 2808 | 2746.8 | 278.935 | 0 | 1 | 20
3472 | 5/25 | 15:00:00 | 293.15 | 98908 | 4.6 | 150 | 7.8537 | 2354.4 | 2066.4 | 279.208 | 0 | 1 | 20
3473 | 5/25 | 16:00:00 | 291.15 | 98892 | 4.1 | 160 | 7.855 | 2052 | 2437.2 | 277.032 | 0 | 1 | 18
3474 | 5/25 | 17:00:00 | 291.15 | 98892 | 4.1 | 150 | 7.855 | 1515.6 | 1944 | 277.032 | 0 | 1 | 18
3475 | 5/25 | 18:00:00 | 289.15 | 98875 | 3.6 | 160 | 8.4059 | 889.2 | 1054.8 | 275.626 | 0 | 1 | 16
3476 | 5/25 | 19:00:00 | 288.15 | 98867 | 3.6 | 150 | 8.4065 | 424.8 | 547.2 | 274.404 | 0 | 1 | 15
3477 | 5/25 | 20:00:00 | 287.15 | 98858 | 1.5 | 244 | 8.4073 | 82.8 | 0 | 273.451 | 0 | 1 | 14
3478 | 5/25 | 21:00:00 | 287.15 | 98858 | 0.5 | 298 | 8.991 | 0 | 0 | 273.944 | 0 | 1 | 14
3479 | 5/25 | 22:00:00 | 285.15 | 98841 | 3.1 | 290 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
3480 | 5/25 | 23:00:00 | 284.15 | 98833 | 2.6 | 300 | 6.3982 | 0 | 0 | 270.435 | 0 | 1 | 11
3481 | 5/25 | 24:00:00 | 284.15 | 98833 | 3.6 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
3482 | 5/26 | 01:00:00 | 283.15 | 98824 | 3.1 | 280 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
3483 | 5/26 | 02:00:00 | 283.15 | 98824 | 4.1 | 280 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
3484 | 5/26 | 03:00:00 | 283.15 | 98824 | 4.6 | 280 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
3485 | 5/26 | 04:00:00 | 283.15 | 98824 | 7.7 | 270 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
3486 | 5/26 | 05:00:00 | 283.15 | 98824 | 6.2 | 280 | 7.8605 | 36 | 0 | 270.161 | 0 | 1 | 10
3487 | 5/26 | 06:00:00 | 282.15 | 98815 | 8.2 | 290 | 6.8571 | 201.6 | 0 | 268.758 | 0 | 1 | 9
3488 | 5/26 | 07:00:00 | 282.15 | 98815 | 7.2 | 290 | 6.8571 | 464.4 | 79.2 | 268.758 | 0 | 1 | 9
3489 | 5/26 | 08:00:00 | 282.15 | 98815 | 9.8 | 300 | 5.9692 | 1465.2 | 1623.6 | 267.568 | 0 | 1 | 9
3490 | 5/26 | 09:00:00 | 283.15 | 98824 | 9.3 | 300 | 5.5646 | 2016 | 2404.8 | 268.287 | 0 | 1 | 10
3491 | 5/26 | 10:00:00 | 284.15 | 98833 | 10.3 | 290 | 6.3982 | 2469.6 | 2624.4 | 269.693 | 0 | 1 | 11
3492 | 5/26 | 11:00:00 | 285.15 | 98841 | 10.3 | 300 | 7.3418 | 2631.6 | 2221.2 | 271.363 | 0 | 1 | 12
3493 | 5/26 | 12:00:00 | 285.15 | 98841 | 11.3 | 290 | 7.8591 | 2793.6 | 2304 | 271.588 | 0 | 1 | 12
3494 | 5/26 | 13:00:00 | 286.15 | 98850 | 10.8 | 280 | 8.408 | 2797.2 | 2300.4 | 272.766 | 0 | 1 | 13
3495 | 5/26 | 14:00:00 | 286.15 | 98850 | 10.8 | 280 | 8.408 | 2649.6 | 2275.2 | 272.766 | 0 | 1 | 13
3496 | 5/26 | 15:00:00 | 285.15 | 98841 | 11.8 | 270 | 8.4088 | 2354.4 | 2145.6 | 271.813 | 0 | 1 | 12
3497 | 5/26 | 16:00:00 | 285.15 | 98841 | 11.3 | 280 | 8.4088 | 2055.6 | 2433.6 | 271.547 | 0 | 1 | 12
3498 | 5/26 | 17:00:00 | 285.15 | 98841 | 10.3 | 270 | 8.4088 | 1519.2 | 2070 | 271.547 | 0 | 1 | 12
3499 | 5/26 | 18:00:00 | 285.15 | 98841 | 9.8 | 270 | 4.8281 | 961.2 | 1346.4 | 269.716 | 0 | 1 | 12
3500 | 5/26 | 19:00:00 | 284.15 | 98833 | 8.2 | 260 | 4.8285 | 439.2 | 511.2 | 268.77 | 0 | 1 | 11
3501 | 5/26 | 20:00:00 | 283.15 | 98824 | 6.7 | 260 | 5.1851 | 86.4 | 0 | 268.056 | 0 | 1 | 10
3502 | 5/26 | 21:00:00 | 282.15 | 98815 | 4.6 | 260 | 5.1856 | 0 | 0 | 267.11 | 0 | 1 | 9
3503 | 5/26 | 22:00:00 | 281.15 | 98806 | 3.6 | 240 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
3504 | 5/26 | 23:00:00 | 281.15 | 98806 | 2.6 | 250 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
3505 | 5/26 | 24:00:00 | 282.15 | 98815 | 3.6 | 230 | 5.5651 | 0 | 0 | 267.846 | 0 | 1 | 9
3506 | 5/27 | 01:00:00 | 282.15 | 98815 | 3.1 | 230 | 5.9692 | 0 | 0 | 268.191 | 0 | 1 | 9
3507 | 5/27 | 02:00:00 | 282.15 | 98815 | 4.6 | 240 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
3508 | 5/27 | 03:00:00 | 281.15 | 98806 | 6.2 | 250 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
3509 | 5/27 | 04:00:00 | 281.15 | 98806 | 4.1 | 240 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
3510 | 5/27 | 05:00:00 | 281.15 | 98806 | 4.6 | 220 | 5.5656 | 72 | 0 | 266.392 | 0 | 1 | 8
3511 | 5/27 | 06:00:00 | 281.15 | 98806 | 3.6 | 210 | 5.5656 | 392.4 | 540 | 266.392 | 0 | 1 | 8
3512 | 5/27 | 07:00:00 | 282.15 | 98815 | 5.1 | 210 | 5.9692 | 471.6 | 39.6 | 268.304 | 0 | 1 | 9
3513 | 5/27 | 08:00:00 | 282.15 | 98815 | 5.7 | 210 | 6.3994 | 770.4 | 223.2 | 268.532 | 0 | 1 | 9
3514 | 5/27 | 09:00:00 | 282.15 | 98815 | 6.2 | 210 | 6.3994 | 1900.8 | 1782 | 268.057 | 0 | 1 | 9
3515 | 5/27 | 10:00:00 | 282.15 | 98815 | 5.7 | 200 | 6.8571 | 1292.4 | 82.8 | 268.758 | 0 | 1 | 9
3516 | 5/27 | 11:00:00 | 283.15 | 98824 | 6.7 | 210 | 6.8564 | 1465.2 | 68.4 | 269.71 | 0 | 1 | 10
3517 | 5/27 | 12:00:00 | 283.15 | 98824 | 4.6 | 220 | 7.3431 | 1555.2 | 68.4 | 269.936 | 0 | 1 | 10
3518 | 5/27 | 13:00:00 | 284.15 | 98833 | 4.1 | 240 | 7.8598 | 1558.8 | 68.4 | 271.115 | 0 | 1 | 11
3519 | 5/27 | 14:00:00 | 286.15 | 98850 | 6.2 | 260 | 8.408 | 1472.4 | 158.4 | 273.248 | 0 | 1 | 13
3520 | 5/27 | 15:00:00 | 287.15 | 98858 | 7.2 | 260 | 8.4073 | 1310.4 | 111.6 | 274.203 | 0 | 1 | 14
3521 | 5/27 | 16:00:00 | 286.15 | 98850 | 8.7 | 270 | 8.408 | 1080 | 111.6 | 273.248 | 0 | 1 | 13
3522 | 5/27 | 17:00:00 | 287.15 | 98858 | 6.7 | 260 | 8.4073 | 1440 | 1314 | 273.719 | 0 | 1 | 14
3523 | 5/27 | 18:00:00 | 288.15 | 98867 | 7.2 | 270 | 8.4065 | 903.6 | 1065.6 | 274.672 | 0 | 1 | 15
3524 | 5/27 | 19:00:00 | 287.15 | 98858 | 8.7 | 270 | 7.8578 | 417.6 | 396 | 273.493 | 0 | 1 | 14
3525 | 5/27 | 20:00:00 | 287.15 | 98858 | 8.7 | 270 | 7.8578 | 90 | 0 | 273.226 | 0 | 1 | 14
3526 | 5/27 | 21:00:00 | 286.15 | 98850 | 4.6 | 280 | 8.408 | 0 | 0 | 272.499 | 0 | 1 | 13
3527 | 5/27 | 22:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
3528 | 5/27 | 23:00:00 | 285.15 | 98841 | 5.1 | 270 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
3529 | 5/27 | 24:00:00 | 285.15 | 98841 | 6.7 | 260 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
3530 | 5/28 | 01:00:00 | 285.15 | 98841 | 7.2 | 270 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
3531 | 5/28 | 02:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
3532 | 5/28 | 03:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
3533 | 5/28 | 04:00:00 | 285.15 | 98841 | 8.7 | 280 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
3534 | 5/28 | 05:00:00 | 285.15 | 98841 | 7.2 | 270 | 8.4088 | 39.6 | 0 | 272.294 | 0 | 1 | 12
3535 | 5/28 | 06:00:00 | 286.15 | 98850 | 6.7 | 280 | 8.9918 | 205.2 | 0 | 273.473 | 0 | 1 | 13
3536 | 5/28 | 07:00:00 | 286.15 | 98850 | 3.1 | 290 | 8.9918 | 468 | 25.2 | 273.473 | 0 | 1 | 13
3537 | 5/28 | 08:00:00 | 286.15 | 98850 | 5.7 | 280 | 8.9918 | 766.8 | 72 | 273.473 | 0 | 1 | 13
3538 | 5/28 | 09:00:00 | 287.15 | 98858 | 6.2 | 290 | 8.991 | 1047.6 | 97.2 | 274.428 | 0 | 1 | 14
3539 | 5/28 | 10:00:00 | 287.15 | 98858 | 7.2 | 280 | 8.991 | 1288.8 | 108 | 274.428 | 0 | 1 | 14
3540 | 5/28 | 11:00:00 | 288.15 | 98867 | 7.2 | 270 | 8.9902 | 1458 | 370.8 | 275.384 | 0 | 1 | 15
3541 | 5/28 | 12:00:00 | 289.15 | 98875 | 10.3 | 270 | 8.9895 | 2793.6 | 1904.4 | 275.852 | 0 | 1 | 16
3542 | 5/28 | 13:00:00 | 290.15 | 98883 | 10.3 | 270 | 8.9887 | 2804.4 | 2296.8 | 276.806 | 0 | 1 | 17
3543 | 5/28 | 14:00:00 | 289.15 | 98875 | 10.8 | 270 | 8.9895 | 2656.8 | 2217.6 | 275.852 | 0 | 1 | 16
3544 | 5/28 | 15:00:00 | 290.15 | 98883 | 10.8 | 280 | 8.9887 | 2509.2 | 2534.4 | 276.535 | 0 | 1 | 17
3545 | 5/28 | 16:00:00 | 290.15 | 98883 | 10.3 | 270 | 8.9887 | 1947.6 | 1911.6 | 276.806 | 0 | 1 | 17
3546 | 5/28 | 17:00:00 | 288.15 | 98867 | 6.2 | 270 | 8.9902 | 1447.2 | 1659.6 | 274.898 | 0 | 1 | 15
3547 | 5/28 | 18:00:00 | 289.15 | 98875 | 4.6 | 260 | 8.9895 | 910.8 | 1065.6 | 275.852 | 0 | 1 | 16
3548 | 5/28 | 19:00:00 | 288.15 | 98867 | 5.7 | 270 | 8.4065 | 421.2 | 482.4 | 274.672 | 0 | 1 | 15
3549 | 5/28 | 20:00:00 | 288.15 | 98867 | 3.6 | 280 | 8.9902 | 86.4 | 0 | 274.898 | 0 | 1 | 15
3550 | 5/28 | 21:00:00 | 287.15 | 98858 | 2.1 | 270 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
3551 | 5/28 | 22:00:00 | 285.15 | 98841 | 2.1 | 300 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
3552 | 5/28 | 23:00:00 | 285.15 | 98841 | 1 | 355 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
3553 | 5/28 | 24:00:00 | 285.15 | 98841 | 0.5 | 34 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
3554 | 5/29 | 01:00:00 | 286.15 | 98850 | 3.1 | 260 | 8.408 | 0 | 0 | 272.499 | 0 | 1 | 13
3555 | 5/29 | 02:00:00 | 285.15 | 98841 | 6.2 | 300 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
3556 | 5/29 | 03:00:00 | 285.15 | 98841 | 4.1 | 290 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
3557 | 5/29 | 04:00:00 | 283.15 | 98824 | 2.1 | 250 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
3558 | 5/29 | 05:00:00 | 282.15 | 98815 | 2.1 | 290 | 6.8571 | 32.4 | 0 | 268.867 | 0 | 1 | 9
3559 | 5/29 | 06:00:00 | 285.15 | 98841 | 1 | 92 | 7.8591 | 230.4 | 0 | 272.069 | 0 | 1 | 12
3560 | 5/29 | 07:00:00 | 285.15 | 98841 | 1.5 | 246 | 8.4088 | 903.6 | 1080 | 271.547 | 0 | 1 | 12
3561 | 5/29 | 08:00:00 | 287.15 | 98858 | 2.1 | 120 | 8.4073 | 1389.6 | 1623.6 | 273.719 | 0 | 1 | 14
3562 | 5/29 | 09:00:00 | 289.15 | 98875 | 1.5 | 167 | 8.9895 | 2012.4 | 2318.4 | 275.582 | 0 | 1 | 16
3563 | 5/29 | 10:00:00 | 290.15 | 98883 | 2.6 | 140 | 9.6084 | 2462.4 | 2610 | 276.76 | 0 | 1 | 17
3564 | 5/29 | 11:00:00 | 292.15 | 98900 | 3.6 | 140 | 9.6067 | 2790 | 2797.2 | 278.668 | 0 | 1 | 19
3565 | 5/29 | 12:00:00 | 293.15 | 98908 | 4.1 | 130 | 10.2634 | 2962.8 | 2851.2 | 279.848 | 0 | 1 | 20
3566 | 5/29 | 13:00:00 | 294.15 | 98916 | 4.1 | 140 | 10.2625 | 2973.6 | 2854.8 | 280.803 | 0 | 1 | 21
3567 | 5/29 | 14:00:00 | 295.15 | 98924 | 3.6 | 140 | 9.6043 | 2822.4 | 2808 | 281.529 | 0 | 1 | 22
3568 | 5/29 | 15:00:00 | 295.15 | 98924 | 4.6 | 140 | 9.6043 | 2512.8 | 2631.6 | 281.529 | 0 | 1 | 22
3569 | 5/29 | 16:00:00 | 295.15 | 98924 | 5.1 | 110 | 10.2617 | 2070 | 2437.2 | 281.757 | 0 | 1 | 22
3570 | 5/29 | 17:00:00 | 294.15 | 98916 | 5.7 | 100 | 10.2625 | 1537.2 | 2052 | 280.803 | 0 | 1 | 21
3571 | 5/29 | 18:00:00 | 293.15 | 98908 | 5.7 | 110 | 9.6059 | 972 | 1296 | 279.622 | 0 | 1 | 20
3572 | 5/29 | 19:00:00 | 292.15 | 98900 | 6.2 | 110 | 9.6067 | 453.6 | 612 | 278.668 | 0 | 1 | 19
3573 | 5/29 | 20:00:00 | 290.15 | 98883 | 5.1 | 100 | 8.9887 | 97.2 | 0 | 276.535 | 0 | 1 | 17
3574 | 5/29 | 21:00:00 | 287.15 | 98858 | 4.6 | 90 | 8.4073 | 0 | 0 | 274.088 | 0 | 1 | 14
3575 | 5/29 | 22:00:00 | 285.15 | 98841 | 4.1 | 80 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
3576 | 5/29 | 23:00:00 | 283.15 | 98824 | 3.6 | 80 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
3577 | 5/29 | 24:00:00 | 282.15 | 98815 | 3.6 | 70 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
3578 | 5/30 | 01:00:00 | 281.15 | 98806 | 3.6 | 80 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
3579 | 5/30 | 02:00:00 | 280.15 | 98798 | 3.1 | 70 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3580 | 5/30 | 03:00:00 | 279.15 | 98789 | 3.6 | 70 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
3581 | 5/30 | 04:00:00 | 279.15 | 98789 | 3.6 | 60 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
3582 | 5/30 | 05:00:00 | 280.15 | 98798 | 3.1 | 60 | 5.9703 | 32.4 | 0 | 266.51 | 0 | 1 | 7
3583 | 5/30 | 06:00:00 | 281.15 | 98806 | 2.1 | 40 | 5.9698 | 248.4 | 0 | 267.353 | 0 | 1 | 8
3584 | 5/30 | 07:00:00 | 283.15 | 98824 | 2.1 | 70 | 6.3988 | 662.4 | 360 | 269.37 | 0 | 1 | 10
3585 | 5/30 | 08:00:00 | 284.15 | 98833 | 2.1 | 80 | 6.8558 | 1076.4 | 550.8 | 270.549 | 0 | 1 | 11
3586 | 5/30 | 09:00:00 | 286.15 | 98850 | 3.1 | 70 | 7.3412 | 2026.8 | 2170.8 | 272.048 | 0 | 1 | 13
3587 | 5/30 | 10:00:00 | 288.15 | 98867 | 3.1 | 70 | 7.857 | 2476.8 | 2613.6 | 274.177 | 0 | 1 | 15
3588 | 5/30 | 11:00:00 | 289.15 | 98875 | 3.6 | 90 | 7.8564 | 2808 | 2808 | 275.129 | 0 | 1 | 16
3589 | 5/30 | 12:00:00 | 291.15 | 98892 | 4.6 | 110 | 7.338 | 2988 | 2858.4 | 276.802 | 0 | 1 | 18
3590 | 5/30 | 13:00:00 | 292.15 | 98900 | 6.2 | 100 | 6.8511 | 3006 | 2865.6 | 277.52 | 0 | 1 | 19
3591 | 5/30 | 14:00:00 | 292.15 | 98900 | 6.2 | 90 | 6.3938 | 2883.6 | 2923.2 | 277.144 | 0 | 1 | 19
3592 | 5/30 | 15:00:00 | 292.15 | 98900 | 6.2 | 100 | 4.8252 | 2588.4 | 2718 | 275.896 | 0 | 1 | 19
3593 | 5/30 | 16:00:00 | 291.15 | 98892 | 5.7 | 110 | 4.8256 | 2109.6 | 2426.4 | 275.391 | 0 | 1 | 18
3594 | 5/30 | 17:00:00 | 291.15 | 98892 | 5.1 | 90 | 6.8517 | 1558.8 | 1987.2 | 276.57 | 0 | 1 | 18
3595 | 5/30 | 18:00:00 | 290.15 | 98883 | 5.7 | 90 | 6.3949 | 986.4 | 1346.4 | 275.388 | 0 | 1 | 17
3596 | 5/30 | 19:00:00 | 288.15 | 98867 | 5.7 | 90 | 5.9661 | 464.4 | 529.2 | 273.258 | 0 | 1 | 15
3597 | 5/30 | 20:00:00 | 286.15 | 98850 | 6.2 | 90 | 5.9671 | 97.2 | 0 | 271.496 | 0 | 1 | 13
3598 | 5/30 | 21:00:00 | 285.15 | 98841 | 3.6 | 80 | 6.8552 | 0 | 0 | 271.384 | 0 | 1 | 12
3599 | 5/30 | 22:00:00 | 283.15 | 98824 | 2.1 | 60 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
3600 | 5/30 | 23:00:00 | 283.15 | 98824 | 3.1 | 70 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
3601 | 5/30 | 24:00:00 | 282.15 | 98815 | 3.6 | 70 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
3602 | 5/31 | 01:00:00 | 282.15 | 98815 | 3.1 | 40 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
3603 | 5/31 | 02:00:00 | 282.15 | 98815 | 2.1 | 30 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
3604 | 5/31 | 03:00:00 | 281.15 | 98806 | 3.1 | 60 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
3605 | 5/31 | 04:00:00 | 281.15 | 98806 | 2.6 | 30 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
3606 | 5/31 | 05:00:00 | 282.15 | 98815 | 2.6 | 20 | 6.3994 | 46.8 | 0 | 268.532 | 0 | 1 | 9
3607 | 5/31 | 06:00:00 | 283.15 | 98824 | 2.6 | 10 | 6.8564 | 248.4 | 0 | 269.71 | 0 | 1 | 10
3608 | 5/31 | 07:00:00 | 285.15 | 98841 | 3.1 | 40 | 6.8552 | 763.2 | 626.4 | 271.384 | 0 | 1 | 12
3609 | 5/31 | 08:00:00 | 286.15 | 98850 | 4.1 | 40 | 7.3412 | 1213.2 | 856.8 | 272.563 | 0 | 1 | 13
3610 | 5/31 | 09:00:00 | 288.15 | 98867 | 4.1 | 50 | 7.3399 | 1897.2 | 1778.4 | 274.218 | 0 | 1 | 15
3611 | 5/31 | 10:00:00 | 290.15 | 98883 | 4.6 | 60 | 7.3387 | 2448 | 2476.8 | 275.988 | 0 | 1 | 17
3612 | 5/31 | 11:00:00 | 291.15 | 98892 | 7.2 | 80 | 7.855 | 2768.4 | 2581.2 | 277.17 | 0 | 1 | 18
3613 | 5/31 | 12:00:00 | 293.15 | 98908 | 6.7 | 80 | 7.3368 | 3020.4 | 2923.2 | 278.56 | 0 | 1 | 20
3614 | 5/31 | 13:00:00 | 294.15 | 98916 | 6.7 | 70 | 7.8531 | 3027.6 | 2923.2 | 279.742 | 0 | 1 | 21
3615 | 5/31 | 14:00:00 | 294.15 | 98916 | 6.7 | 70 | 7.3362 | 2880 | 2908.8 | 279.51 | 0 | 1 | 21
3616 | 5/31 | 15:00:00 | 294.15 | 98916 | 6.2 | 70 | 6.85 | 2574 | 2826 | 279.127 | 0 | 1 | 21
3617 | 5/31 | 16:00:00 | 294.15 | 98916 | 6.7 | 90 | 6.3928 | 2131.2 | 2545.2 | 278.892 | 0 | 1 | 21
3618 | 5/31 | 17:00:00 | 293.15 | 98908 | 5.7 | 70 | 5.9636 | 1591.2 | 2048.4 | 277.708 | 0 | 1 | 20
3619 | 5/31 | 18:00:00 | 293.15 | 98908 | 6.2 | 80 | 5.5598 | 1011.6 | 1422 | 277.319 | 0 | 1 | 20
3620 | 5/31 | 19:00:00 | 288.95 | 98873 | 3.5 | 75 | 5.6406 | 478.8 | 572.4 | 273.543 | 0 | 1 | 15.8
3621 | 5/31 | 20:00:00 | 287.65 | 98863 | 2.6 | 65 | 5.8835 | 108 | 0 | 272.597 | 0 | 1 | 14.5
3622 | 5/31 | 21:00:00 | 286.35 | 98852 | 2.1 | 132 | 5.8841 | 0 | 0 | 271.505 | 0 | 1 | 13.2
3623 | 5/31 | 22:00:00 | 285.65 | 98846 | 1.8 | 117 | 5.7622 | 0 | 0 | 270.906 | 0 | 1 | 12.5
3624 | 5/31 | 23:00:00 | 285.15 | 98841 | 1.9 | 107 | 5.6424 | 0 | 0 | 270.363 | 0 | 1 | 12
3625 | 5/31 | 24:00:00 | 284.65 | 98837 | 1.8 | 104 | 5.5639 | 0 | 0 | 269.842 | 0 | 1 | 11.5
3626 | 6/1 | 01:00:00 | 284.35 | 98835 | 1.9 | 17 | 5.6428 | 0 | 0 | 269.604 | 0 | 1 | 11.2
3627 | 6/1 | 02:00:00 | 284.15 | 98833 | 2.3 | 105 | 5.7629 | 0 | 0 | 269.613 | 0 | 1 | 11
3628 | 6/1 | 03:00:00 | 284.35 | 98835 | 2.3 | 105 | 5.8852 | 0 | 0 | 269.872 | 0 | 1 | 11.2
3629 | 6/1 | 04:00:00 | 284.95 | 98839 | 2.6 | 102 | 5.9678 | 0 | 0 | 270.614 | 0 | 1 | 11.8
3630 | 6/1 | 05:00:00 | 285.95 | 98848 | 2.8 | 110 | 5.9672 | 72 | 0 | 271.563 | 0 | 1 | 12.8
3631 | 6/1 | 06:00:00 | 287.35 | 98860 | 3 | 30 | 5.9665 | 388.8 | 349.2 | 272.766 | 0 | 1 | 14.2
3632 | 6/1 | 07:00:00 | 286.15 | 98850 | 2.6 | 20 | 5.9671 | 900 | 1152 | 271.496 | 0 | 1 | 13
3633 | 6/1 | 08:00:00 | 288.15 | 98867 | 3.1 | 40 | 5.9661 | 1497.6 | 1918.8 | 273.258 | 0 | 1 | 15
3634 | 6/1 | 09:00:00 | 290.15 | 98883 | 3.6 | 40 | 5.9651 | 2062.8 | 2480.4 | 275.013 | 0 | 1 | 17
3635 | 6/1 | 10:00:00 | 291.15 | 98892 | 3.6 | 60 | 5.5607 | 2538 | 2844 | 275.578 | 0 | 1 | 18
3636 | 6/1 | 11:00:00 | 292.15 | 98900 | 4.1 | 60 | 6.8511 | 2851.2 | 2887.2 | 277.377 | 0 | 1 | 19
3637 | 6/1 | 12:00:00 | 293.15 | 98908 | 4.6 | 70 | 6.8506 | 3034.8 | 2952 | 278.327 | 0 | 1 | 20
3638 | 6/1 | 13:00:00 | 294.15 | 98916 | 3.6 | 70 | 6.85 | 3052.8 | 2966.4 | 279.127 | 0 | 1 | 21
3639 | 6/1 | 14:00:00 | 294.15 | 98916 | 4.6 | 90 | 5.9631 | 2905.2 | 2952 | 278.502 | 0 | 1 | 21
3640 | 6/1 | 15:00:00 | 295.15 | 98924 | 3.1 | 70 | 6.3923 | 2588.4 | 2757.6 | 279.686 | 0 | 1 | 22
3641 | 6/1 | 16:00:00 | 295.15 | 98924 | 3.6 | 80 | 6.3923 | 2138.4 | 2548.8 | 279.686 | 0 | 1 | 22
3642 | 6/1 | 17:00:00 | 295.15 | 98924 | 3.1 | 80 | 6.3923 | 1598.4 | 2070 | 279.686 | 0 | 1 | 22
3643 | 6/1 | 18:00:00 | 294.15 | 98916 | 4.1 | 100 | 5.9631 | 1018.8 | 1425.6 | 278.502 | 0 | 1 | 21
3644 | 6/1 | 19:00:00 | 293.15 | 98908 | 3.6 | 80 | 6.3933 | 486 | 576 | 277.944 | 0 | 1 | 20
3645 | 6/1 | 20:00:00 | 291.15 | 98892 | 2.6 | 110 | 6.3944 | 111.6 | 0 | 276.195 | 0 | 1 | 18
3646 | 6/1 | 21:00:00 | 289.15 | 98875 | 2.1 | 110 | 5.9656 | 0 | 0 | 274.206 | 0 | 1 | 16
3647 | 6/1 | 22:00:00 | 286.15 | 98850 | 3.1 | 130 | 5.9671 | 0 | 0 | 271.496 | 0 | 1 | 13
3648 | 6/1 | 23:00:00 | 287.15 | 98858 | 1 | 13 | 5.9666 | 0 | 0 | 272.445 | 0 | 1 | 14
3649 | 6/1 | 24:00:00 | 286.15 | 98850 | 1.5 | 200 | 5.5631 | 0 | 0 | 271.264 | 0 | 1 | 13
3650 | 6/2 | 01:00:00 | 285.15 | 98841 | 1 | 180 | 5.1842 | 0 | 0 | 270.084 | 0 | 1 | 12
3651 | 6/2 | 02:00:00 | 285.15 | 98841 | 1 | 190 | 5.5636 | 0 | 0 | 270.316 | 0 | 1 | 12
3652 | 6/2 | 03:00:00 | 284.15 | 98833 | 1.5 | 220 | 5.5641 | 0 | 0 | 269.498 | 0 | 1 | 11
3653 | 6/2 | 04:00:00 | 284.15 | 98833 | 1 | 260 | 5.9681 | 0 | 0 | 269.854 | 0 | 1 | 11
3654 | 6/2 | 05:00:00 | 284.15 | 98833 | 2.1 | 290 | 5.9681 | 72 | 0 | 269.854 | 0 | 1 | 11
3655 | 6/2 | 06:00:00 | 285.15 | 98841 | 2.1 | 280 | 6.8552 | 349.2 | 244.8 | 271.384 | 0 | 1 | 12
3656 | 6/2 | 07:00:00 | 288.15 | 98867 | 3.1 | 300 | 6.8534 | 896.4 | 1119.6 | 273.988 | 0 | 1 | 15
3657 | 6/2 | 08:00:00 | 290.15 | 98883 | 1.5 | 188 | 7.3387 | 1472.4 | 1789.2 | 275.988 | 0 | 1 | 17
3658 | 6/2 | 09:00:00 | 292.15 | 98900 | 1.5 | 324 | 7.8544 | 2026.8 | 2268 | 277.983 | 0 | 1 | 19
3659 | 6/2 | 10:00:00 | 293.15 | 98908 | 1.5 | 122 | 7.3368 | 2516.4 | 2692.8 | 278.56 | 0 | 1 | 20
3660 | 6/2 | 11:00:00 | 294.15 | 98916 | 1.5 | 181 | 7.8531 | 2844 | 2876.4 | 279.742 | 0 | 1 | 21
3661 | 6/2 | 12:00:00 | 295.15 | 98924 | 1.5 | 85 | 7.8525 | 2998.8 | 2851.2 | 280.838 | 0 | 1 | 22
3662 | 6/2 | 13:00:00 | 296.15 | 98932 | 2.1 | 330 | 7.335 | 3013.2 | 2862 | 281.555 | 0 | 1 | 23
3663 | 6/2 | 14:00:00 | 296.15 | 98932 | 2.1 | 60 | 7.8518 | 2854.8 | 2818.8 | 281.789 | 0 | 1 | 23
3664 | 6/2 | 15:00:00 | 296.15 | 98932 | 1.5 | 195 | 8.4009 | 2545.2 | 2635.2 | 282.022 | 0 | 1 | 23
3665 | 6/2 | 16:00:00 | 295.15 | 98924 | 1.5 | 268 | 8.4016 | 2106 | 2440.8 | 281.07 | 0 | 1 | 22
3666 | 6/2 | 17:00:00 | 294.15 | 98916 | 1 | 154 | 8.9857 | 1569.6 | 2095.2 | 280.347 | 0 | 1 | 21
3667 | 6/2 | 18:00:00 | 291.15 | 98892 | 5.1 | 10 | 8.9879 | 1004.4 | 1324.8 | 277.488 | 0 | 1 | 18
3668 | 6/2 | 19:00:00 | 289.15 | 98875 | 5.1 | 20 | 7.8564 | 482.4 | 547.2 | 275.129 | 0 | 1 | 16
3669 | 6/2 | 20:00:00 | 288.15 | 98867 | 2.6 | 30 | 7.3399 | 115.2 | 0 | 273.95 | 0 | 1 | 15
3670 | 6/2 | 21:00:00 | 286.15 | 98850 | 4.1 | 30 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
3671 | 6/2 | 22:00:00 | 284.15 | 98833 | 3.6 | 30 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
3672 | 6/2 | 23:00:00 | 283.15 | 98824 | 3.1 | 30 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
3673 | 6/2 | 24:00:00 | 283.15 | 98824 | 3.1 | 30 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
3674 | 6/3 | 01:00:00 | 283.15 | 98824 | 2.6 | 30 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
3675 | 6/3 | 02:00:00 | 284.15 | 98833 | 3.6 | 20 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
3676 | 6/3 | 03:00:00 | 284.15 | 98833 | 3.1 | 30 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
3677 | 6/3 | 04:00:00 | 283.15 | 98824 | 3.6 | 30 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
3678 | 6/3 | 05:00:00 | 283.15 | 98824 | 3.1 | 30 | 7.3431 | 79.2 | 0 | 269.46 | 0 | 1 | 10
3679 | 6/3 | 06:00:00 | 283.15 | 98824 | 3.1 | 30 | 7.3431 | 219.6 | 0 | 269.936 | 0 | 1 | 10
3680 | 6/3 | 07:00:00 | 283.15 | 98824 | 4.1 | 20 | 6.8564 | 486 | 10.8 | 269.71 | 0 | 1 | 10
3681 | 6/3 | 08:00:00 | 283.15 | 98824 | 4.1 | 30 | 6.3988 | 788.4 | 223.2 | 269.483 | 0 | 1 | 10
3682 | 6/3 | 09:00:00 | 283.15 | 98824 | 4.6 | 30 | 5.9687 | 1933.2 | 1800 | 268.779 | 0 | 1 | 10
3683 | 6/3 | 10:00:00 | 284.15 | 98833 | 3.6 | 40 | 5.5641 | 2368.8 | 1839.6 | 269.498 | 0 | 1 | 11
3684 | 6/3 | 11:00:00 | 285.15 | 98841 | 3.6 | 30 | 5.1842 | 1490.4 | 943.2 | 270.692 | 0 | 1 | 12
3685 | 6/3 | 12:00:00 | 286.15 | 98850 | 3.1 | 60 | 5.5631 | 3024 | 2440.8 | 271.13 | 0 | 1 | 13
3686 | 6/3 | 13:00:00 | 287.15 | 98858 | 3.6 | 30 | 5.1833 | 3038.4 | 2754 | 271.843 | 0 | 1 | 14
3687 | 6/3 | 14:00:00 | 287.15 | 98858 | 4.1 | 30 | 5.1833 | 2718 | 2098.8 | 272.109 | 0 | 1 | 14
3688 | 6/3 | 15:00:00 | 287.15 | 98858 | 3.6 | 50 | 5.1833 | 2574 | 2613.6 | 271.843 | 0 | 1 | 14
3689 | 6/3 | 16:00:00 | 287.15 | 98858 | 4.1 | 50 | 4.8273 | 2134.8 | 2242.8 | 271.608 | 0 | 1 | 14
3690 | 6/3 | 17:00:00 | 287.15 | 98858 | 3.6 | 60 | 4.8273 | 1508.4 | 1630.8 | 271.873 | 0 | 1 | 14
3691 | 6/3 | 18:00:00 | 286.15 | 98850 | 4.1 | 30 | 5.5631 | 1018.8 | 1429.2 | 271.13 | 0 | 1 | 13
3692 | 6/3 | 19:00:00 | 285.15 | 98841 | 4.1 | 30 | 5.1842 | 493.2 | 568.8 | 269.95 | 0 | 1 | 12
3693 | 6/3 | 20:00:00 | 284.15 | 98833 | 4.1 | 40 | 5.1847 | 118.8 | 0 | 269.003 | 0 | 1 | 11
3694 | 6/3 | 21:00:00 | 282.15 | 98815 | 3.1 | 40 | 4.8294 | 0 | 0 | 267.139 | 0 | 1 | 9
3695 | 6/3 | 22:00:00 | 281.15 | 98806 | 3.6 | 30 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
3696 | 6/3 | 23:00:00 | 280.15 | 98798 | 3.1 | 20 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
3697 | 6/3 | 24:00:00 | 280.15 | 98798 | 1.5 | 340 | 4.8303 | 0 | 0 | 264.986 | 0 | 1 | 7
3698 | 6/4 | 01:00:00 | 279.15 | 98789 | 2.6 | 330 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
3699 | 6/4 | 02:00:00 | 278.15 | 98780 | 2.6 | 290 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
3700 | 6/4 | 03:00:00 | 279.15 | 98789 | 2.6 | 350 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
3701 | 6/4 | 04:00:00 | 280.15 | 98798 | 2.1 | 340 | 4.8303 | 0 | 0 | 265.715 | 0 | 1 | 7
3702 | 6/4 | 05:00:00 | 279.15 | 98789 | 0.5 | 37 | 4.8307 | 28.8 | 0 | 264.874 | 0 | 1 | 6
3703 | 6/4 | 06:00:00 | 280.15 | 98798 | 2.1 | 300 | 5.1865 | 428.4 | 529.2 | 265.216 | 0 | 1 | 7
3704 | 6/4 | 07:00:00 | 281.15 | 98806 | 1 | 154 | 4.8299 | 493.2 | 46.8 | 266.664 | 0 | 1 | 8
3705 | 6/4 | 08:00:00 | 281.15 | 98806 | 1 | 35 | 5.1861 | 792 | 57.6 | 266.895 | 0 | 1 | 8
3706 | 6/4 | 09:00:00 | 282.15 | 98815 | 1.5 | 329 | 4.8294 | 1080 | 201.6 | 267.612 | 0 | 1 | 9
3707 | 6/4 | 10:00:00 | 283.15 | 98824 | 1 | 138 | 4.829 | 1317.6 | 223.2 | 268.561 | 0 | 1 | 10
3708 | 6/4 | 11:00:00 | 283.15 | 98824 | 1.5 | 78 | 5.1851 | 1490.4 | 72 | 268.793 | 0 | 1 | 10
3709 | 6/4 | 12:00:00 | 284.15 | 98833 | 3.6 | 260 | 5.1847 | 1584 | 223.2 | 269.743 | 0 | 1 | 11
3710 | 6/4 | 13:00:00 | 285.15 | 98841 | 1 | 36 | 5.9676 | 2862 | 1958.4 | 270.678 | 0 | 1 | 12
3711 | 6/4 | 14:00:00 | 286.15 | 98850 | 3.6 | 320 | 5.5631 | 2721.6 | 2304 | 271.395 | 0 | 1 | 13
3712 | 6/4 | 15:00:00 | 284.15 | 98833 | 3.1 | 50 | 5.9681 | 2426.4 | 2242.8 | 269.728 | 0 | 1 | 11
3713 | 6/4 | 16:00:00 | 285.15 | 98841 | 2.6 | 70 | 5.9676 | 2008.8 | 1990.8 | 270.678 | 0 | 1 | 12
3714 | 6/4 | 17:00:00 | 284.15 | 98833 | 3.1 | 50 | 5.9681 | 1504.8 | 1612.8 | 269.728 | 0 | 1 | 11
3715 | 6/4 | 18:00:00 | 284.15 | 98833 | 4.1 | 60 | 5.9681 | 964.8 | 993.6 | 269.728 | 0 | 1 | 11
3716 | 6/4 | 19:00:00 | 282.15 | 98815 | 4.6 | 60 | 5.5651 | 259.2 | 0 | 268.075 | 0 | 1 | 9
3717 | 6/4 | 20:00:00 | 280.15 | 98798 | 3.1 | 50 | 5.9703 | 115.2 | 0 | 265.931 | 0 | 1 | 7
3718 | 6/4 | 21:00:00 | 280.15 | 98798 | 1.5 | 124 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3719 | 6/4 | 22:00:00 | 280.15 | 98798 | 0 | 269 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3720 | 6/4 | 23:00:00 | 280.15 | 98798 | 0.5 | 172 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3721 | 6/4 | 24:00:00 | 280.15 | 98798 | 1 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3722 | 6/5 | 01:00:00 | 280.15 | 98798 | 1 | 220 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
3723 | 6/5 | 02:00:00 | 280.15 | 98798 | 1 | 210 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3724 | 6/5 | 03:00:00 | 279.15 | 98789 | 1.5 | 200 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
3725 | 6/5 | 04:00:00 | 279.15 | 98789 | 0.5 | 230 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
3726 | 6/5 | 05:00:00 | 279.15 | 98789 | 0 | 271 | 5.187 | 54 | 0 | 264.996 | 0 | 1 | 6
3727 | 6/5 | 06:00:00 | 280.15 | 98798 | 0.5 | 339 | 5.5661 | 262.8 | 0 | 266.174 | 0 | 1 | 7
3728 | 6/5 | 07:00:00 | 281.15 | 98806 | 2.1 | 170 | 5.1861 | 784.8 | 702 | 266.667 | 0 | 1 | 8
3729 | 6/5 | 08:00:00 | 282.15 | 98815 | 0.5 | 238 | 4.4952 | 1483.2 | 1728 | 266.778 | 0 | 1 | 9
3730 | 6/5 | 09:00:00 | 283.15 | 98824 | 2.6 | 120 | 4.4948 | 2052 | 2134.8 | 267.724 | 0 | 1 | 10
3731 | 6/5 | 10:00:00 | 285.15 | 98841 | 1 | 38 | 4.494 | 2530.8 | 2574 | 269.481 | 0 | 1 | 12
3732 | 6/5 | 11:00:00 | 286.15 | 98850 | 1.5 | 98 | 4.8277 | 2692.8 | 2174.4 | 270.927 | 0 | 1 | 13
3733 | 6/5 | 12:00:00 | 287.15 | 98858 | 2.6 | 70 | 4.8273 | 2865.6 | 2343.6 | 271.873 | 0 | 1 | 14
3734 | 6/5 | 13:00:00 | 285.15 | 98841 | 4.1 | 80 | 4.494 | 2880 | 2354.4 | 269.744 | 0 | 1 | 12
3735 | 6/5 | 14:00:00 | 282.15 | 98815 | 4.6 | 20 | 5.9692 | 2718 | 2289.6 | 267.83 | 0 | 1 | 9
3736 | 6/5 | 15:00:00 | 282.15 | 98815 | 5.7 | 30 | 5.9692 | 2430 | 2239.2 | 267.83 | 0 | 1 | 9
3737 | 6/5 | 16:00:00 | 280.15 | 98798 | 6.7 | 30 | 6.4005 | 2012.4 | 1821.6 | 266.157 | 0 | 1 | 7
3738 | 6/5 | 17:00:00 | 279.15 | 98789 | 6.2 | 30 | 5.5666 | 838.8 | 241.2 | 265.224 | 0 | 1 | 6
3739 | 6/5 | 18:00:00 | 279.15 | 98789 | 5.1 | 30 | 5.9708 | 540 | 14.4 | 265.451 | 0 | 1 | 6
3740 | 6/5 | 19:00:00 | 278.15 | 98780 | 5.7 | 30 | 5.5671 | 262.8 | 0 | 264.274 | 0 | 1 | 5
3741 | 6/5 | 20:00:00 | 278.15 | 98780 | 4.6 | 30 | 5.5671 | 64.8 | 0 | 264.274 | 0 | 1 | 5
3742 | 6/5 | 21:00:00 | 278.15 | 98780 | 5.7 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
3743 | 6/5 | 22:00:00 | 278.15 | 98780 | 5.7 | 30 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
3744 | 6/5 | 23:00:00 | 278.15 | 98780 | 6.2 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
3745 | 6/5 | 24:00:00 | 278.15 | 98780 | 5.7 | 30 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
3746 | 6/6 | 01:00:00 | 278.15 | 98780 | 6.7 | 30 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
3747 | 6/6 | 02:00:00 | 278.15 | 98780 | 5.1 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
3748 | 6/6 | 03:00:00 | 279.15 | 98789 | 4.1 | 80 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
3749 | 6/6 | 04:00:00 | 279.15 | 98789 | 3.6 | 60 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
3750 | 6/6 | 05:00:00 | 279.15 | 98789 | 3.1 | 70 | 5.9708 | 46.8 | 0 | 265.451 | 0 | 1 | 6
3751 | 6/6 | 06:00:00 | 279.15 | 98789 | 3.1 | 70 | 5.9708 | 226.8 | 0 | 265.451 | 0 | 1 | 6
3752 | 6/6 | 07:00:00 | 279.15 | 98789 | 4.1 | 70 | 5.9708 | 493.2 | 10.8 | 265.451 | 0 | 1 | 6
3753 | 6/6 | 08:00:00 | 280.15 | 98798 | 3.6 | 80 | 6.4005 | 792 | 54 | 266.628 | 0 | 1 | 7
3754 | 6/6 | 09:00:00 | 281.15 | 98806 | 6.2 | 70 | 6.4 | 1076.4 | 169.2 | 267.58 | 0 | 1 | 8
3755 | 6/6 | 10:00:00 | 282.15 | 98815 | 6.2 | 70 | 6.3994 | 2368.8 | 1911.6 | 268.057 | 0 | 1 | 9
3756 | 6/6 | 11:00:00 | 282.15 | 98815 | 9.3 | 80 | 5.9692 | 2685.6 | 2199.6 | 267.83 | 0 | 1 | 9
3757 | 6/6 | 12:00:00 | 283.15 | 98824 | 6.7 | 70 | 5.5646 | 3031.2 | 2757.6 | 268.287 | 0 | 1 | 10
3758 | 6/6 | 13:00:00 | 283.15 | 98824 | 6.2 | 60 | 5.9687 | 3042 | 2779.2 | 268.516 | 0 | 1 | 10
3759 | 6/6 | 14:00:00 | 283.15 | 98824 | 6.7 | 70 | 5.5646 | 2728.8 | 2196 | 268.55 | 0 | 1 | 10
3760 | 6/6 | 15:00:00 | 284.15 | 98833 | 6.2 | 70 | 5.5641 | 2437.2 | 2250 | 269.498 | 0 | 1 | 11
3761 | 6/6 | 16:00:00 | 283.15 | 98824 | 7.2 | 80 | 5.1851 | 2026.8 | 2008.8 | 268.319 | 0 | 1 | 10
3762 | 6/6 | 17:00:00 | 283.15 | 98824 | 7.2 | 60 | 5.5646 | 1519.2 | 1612.8 | 268.55 | 0 | 1 | 10
3763 | 6/6 | 18:00:00 | 283.15 | 98824 | 5.7 | 70 | 5.5646 | 979.2 | 1144.8 | 268.55 | 0 | 1 | 10
3764 | 6/6 | 19:00:00 | 283.15 | 98824 | 5.1 | 60 | 5.5646 | 478.8 | 464.4 | 268.55 | 0 | 1 | 10
3765 | 6/6 | 20:00:00 | 282.15 | 98815 | 4.6 | 60 | 5.1856 | 122.4 | 0 | 267.371 | 0 | 1 | 9
3766 | 6/6 | 21:00:00 | 281.15 | 98806 | 4.1 | 60 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
3767 | 6/6 | 22:00:00 | 281.15 | 98806 | 4.1 | 50 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
3768 | 6/6 | 23:00:00 | 281.15 | 98806 | 4.1 | 50 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
3769 | 6/6 | 24:00:00 | 281.15 | 98806 | 4.6 | 50 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
3770 | 6/7 | 01:00:00 | 280.15 | 98798 | 5.1 | 40 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
3771 | 6/7 | 02:00:00 | 280.15 | 98798 | 5.1 | 40 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
3772 | 6/7 | 03:00:00 | 280.15 | 98798 | 5.7 | 50 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
3773 | 6/7 | 04:00:00 | 280.15 | 98798 | 5.7 | 50 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
3774 | 6/7 | 05:00:00 | 280.15 | 98798 | 5.1 | 50 | 5.9703 | 86.4 | 0 | 265.931 | 0 | 1 | 7
3775 | 6/7 | 06:00:00 | 280.15 | 98798 | 5.1 | 50 | 6.4005 | 410.4 | 374.4 | 266.157 | 0 | 1 | 7
3776 | 6/7 | 07:00:00 | 281.15 | 98806 | 6.2 | 40 | 6.4 | 946.8 | 1116 | 266.846 | 0 | 1 | 8
3777 | 6/7 | 08:00:00 | 282.15 | 98815 | 6.7 | 50 | 6.3994 | 792 | 108 | 268.532 | 0 | 1 | 9
3778 | 6/7 | 09:00:00 | 284.15 | 98833 | 7.7 | 60 | 5.9681 | 1080 | 169.2 | 270.206 | 0 | 1 | 11
3779 | 6/7 | 10:00:00 | 284.15 | 98833 | 7.2 | 60 | 5.9681 | 2376 | 1839.6 | 269.728 | 0 | 1 | 11
3780 | 6/7 | 11:00:00 | 284.15 | 98833 | 7.2 | 60 | 5.5641 | 2692.8 | 2293.2 | 269.498 | 0 | 1 | 11
3781 | 6/7 | 12:00:00 | 285.15 | 98841 | 7.7 | 50 | 5.1842 | 2865.6 | 2329.2 | 270.214 | 0 | 1 | 12
3782 | 6/7 | 13:00:00 | 285.15 | 98841 | 8.2 | 60 | 5.5636 | 2872.8 | 2322 | 270.447 | 0 | 1 | 12
3783 | 6/7 | 14:00:00 | 286.15 | 98850 | 7.7 | 50 | 5.5631 | 2732.4 | 2300.4 | 271.395 | 0 | 1 | 13
3784 | 6/7 | 15:00:00 | 285.15 | 98841 | 7.7 | 50 | 5.1842 | 2444.4 | 2260.8 | 270.214 | 0 | 1 | 12
3785 | 6/7 | 16:00:00 | 285.15 | 98841 | 7.7 | 60 | 5.1842 | 2030.4 | 2008.8 | 270.214 | 0 | 1 | 12
3786 | 6/7 | 17:00:00 | 285.15 | 98841 | 7.2 | 50 | 5.1842 | 1526.4 | 1627.2 | 270.214 | 0 | 1 | 12
3787 | 6/7 | 18:00:00 | 284.15 | 98833 | 6.7 | 50 | 5.5641 | 986.4 | 1148.4 | 269.498 | 0 | 1 | 11
3788 | 6/7 | 19:00:00 | 284.15 | 98833 | 7.2 | 60 | 5.5641 | 486 | 468 | 269.498 | 0 | 1 | 11
3789 | 6/7 | 20:00:00 | 283.15 | 98824 | 5.7 | 50 | 5.5646 | 126 | 0 | 268.55 | 0 | 1 | 10
3790 | 6/7 | 21:00:00 | 282.15 | 98815 | 4.6 | 50 | 5.5651 | 0 | 0 | 267.601 | 0 | 1 | 9
3791 | 6/7 | 22:00:00 | 282.15 | 98815 | 4.1 | 40 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
3792 | 6/7 | 23:00:00 | 281.15 | 98806 | 4.1 | 20 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
3793 | 6/7 | 24:00:00 | 280.15 | 98798 | 4.1 | 20 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
3794 | 6/8 | 01:00:00 | 280.15 | 98798 | 4.1 | 20 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
3795 | 6/8 | 02:00:00 | 280.15 | 98798 | 3.6 | 20 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
3796 | 6/8 | 03:00:00 | 280.15 | 98798 | 2.6 | 30 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
3797 | 6/8 | 04:00:00 | 280.15 | 98798 | 3.1 | 20 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
3798 | 6/8 | 05:00:00 | 280.15 | 98798 | 3.1 | 20 | 5.9703 | 93.6 | 0 | 265.671 | 0 | 1 | 7
3799 | 6/8 | 06:00:00 | 280.15 | 98798 | 3.1 | 30 | 5.9703 | 410.4 | 374.4 | 265.931 | 0 | 1 | 7
3800 | 6/8 | 07:00:00 | 281.15 | 98806 | 3.6 | 30 | 5.9698 | 892.8 | 1051.2 | 266.881 | 0 | 1 | 8
3801 | 6/8 | 08:00:00 | 283.15 | 98824 | 4.1 | 50 | 6.3988 | 1429.2 | 1544.4 | 269.007 | 0 | 1 | 10
3802 | 6/8 | 09:00:00 | 283.15 | 98824 | 3.6 | 70 | 5.9687 | 2062.8 | 2257.2 | 268.516 | 0 | 1 | 10
3803 | 6/8 | 10:00:00 | 284.15 | 98833 | 4.1 | 60 | 5.9681 | 2376 | 2134.8 | 269.728 | 0 | 1 | 11
3804 | 6/8 | 11:00:00 | 285.15 | 98841 | 4.1 | 50 | 5.5636 | 2692.8 | 2289.6 | 270.447 | 0 | 1 | 12
3805 | 6/8 | 12:00:00 | 286.15 | 98850 | 4.6 | 60 | 5.5631 | 2862 | 2318.4 | 271.395 | 0 | 1 | 13
3806 | 6/8 | 13:00:00 | 286.15 | 98850 | 5.7 | 80 | 5.9671 | 2872.8 | 2311.2 | 271.627 | 0 | 1 | 13
3807 | 6/8 | 14:00:00 | 287.15 | 98858 | 4.6 | 70 | 5.5627 | 2736 | 2296.8 | 272.343 | 0 | 1 | 14
3808 | 6/8 | 15:00:00 | 287.15 | 98858 | 6.2 | 50 | 5.5627 | 2444.4 | 2246.4 | 272.343 | 0 | 1 | 14
3809 | 6/8 | 16:00:00 | 286.15 | 98850 | 5.7 | 70 | 5.5631 | 2030.4 | 2145.6 | 271.395 | 0 | 1 | 13
3810 | 6/8 | 17:00:00 | 285.15 | 98841 | 5.7 | 70 | 5.5636 | 1623.6 | 2124 | 270.182 | 0 | 1 | 12
3811 | 6/8 | 18:00:00 | 285.15 | 98841 | 5.7 | 80 | 5.5636 | 1051.2 | 1396.8 | 270.182 | 0 | 1 | 12
3812 | 6/8 | 19:00:00 | 284.15 | 98833 | 4.6 | 70 | 5.5641 | 518.4 | 590.4 | 269.234 | 0 | 1 | 11
3813 | 6/8 | 20:00:00 | 283.15 | 98824 | 4.6 | 50 | 5.5646 | 136.8 | 18 | 268.287 | 0 | 1 | 10
3814 | 6/8 | 21:00:00 | 283.15 | 98824 | 2.6 | 60 | 5.9687 | 0 | 0 | 268.779 | 0 | 1 | 10
3815 | 6/8 | 22:00:00 | 282.15 | 98815 | 3.1 | 70 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
3816 | 6/8 | 23:00:00 | 281.15 | 98806 | 2.6 | 60 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
3817 | 6/8 | 24:00:00 | 280.15 | 98798 | 3.1 | 40 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
3818 | 6/9 | 01:00:00 | 280.15 | 98798 | 3.6 | 20 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
3819 | 6/9 | 02:00:00 | 280.15 | 98798 | 4.1 | 20 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
3820 | 6/9 | 03:00:00 | 280.15 | 98798 | 4.6 | 20 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
3821 | 6/9 | 04:00:00 | 279.15 | 98789 | 4.1 | 20 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
3822 | 6/9 | 05:00:00 | 280.15 | 98798 | 4.6 | 10 | 5.9703 | 93.6 | 0 | 265.671 | 0 | 1 | 7
3823 | 6/9 | 06:00:00 | 281.15 | 98806 | 4.6 | 20 | 5.9698 | 439.2 | 482.4 | 266.62 | 0 | 1 | 8
3824 | 6/9 | 07:00:00 | 282.15 | 98815 | 4.6 | 30 | 6.3994 | 896.4 | 1047.6 | 268.057 | 0 | 1 | 9
3825 | 6/9 | 08:00:00 | 282.15 | 98815 | 5.7 | 10 | 6.3994 | 795.6 | 223.2 | 268.532 | 0 | 1 | 9
3826 | 6/9 | 09:00:00 | 283.15 | 98824 | 6.2 | 20 | 6.3988 | 1944 | 1785.6 | 269.007 | 0 | 1 | 10
3827 | 6/9 | 10:00:00 | 283.15 | 98824 | 6.7 | 20 | 6.8564 | 2372.4 | 2217.6 | 269.234 | 0 | 1 | 10
3828 | 6/9 | 11:00:00 | 285.15 | 98841 | 6.7 | 20 | 6.8552 | 2685.6 | 1897.2 | 271.136 | 0 | 1 | 12
3829 | 6/9 | 12:00:00 | 285.15 | 98841 | 7.7 | 20 | 6.8552 | 1584 | 932.4 | 271.616 | 0 | 1 | 12
3830 | 6/9 | 13:00:00 | 284.15 | 98833 | 5.7 | 20 | 6.8558 | 2869.2 | 1929.6 | 270.185 | 0 | 1 | 11
3831 | 6/9 | 14:00:00 | 285.15 | 98841 | 7.7 | 10 | 6.3977 | 2728.8 | 2278.8 | 270.907 | 0 | 1 | 12
3832 | 6/9 | 15:00:00 | 285.15 | 98841 | 7.7 | 20 | 6.8552 | 2437.2 | 2156.4 | 271.136 | 0 | 1 | 12
3833 | 6/9 | 16:00:00 | 285.15 | 98841 | 6.7 | 20 | 6.3977 | 2152.8 | 2448 | 270.643 | 0 | 1 | 12
3834 | 6/9 | 17:00:00 | 285.15 | 98841 | 6.7 | 20 | 6.3977 | 1623.6 | 2026.8 | 270.643 | 0 | 1 | 12
3835 | 6/9 | 18:00:00 | 284.15 | 98833 | 5.7 | 20 | 6.3982 | 1054.8 | 1389.6 | 269.693 | 0 | 1 | 11
3836 | 6/9 | 19:00:00 | 283.15 | 98824 | 5.7 | 30 | 6.8564 | 522 | 590.4 | 268.971 | 0 | 1 | 10
3837 | 6/9 | 20:00:00 | 283.15 | 98824 | 4.6 | 30 | 6.3988 | 140.4 | 25.2 | 268.744 | 0 | 1 | 10
3838 | 6/9 | 21:00:00 | 282.15 | 98815 | 4.6 | 20 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3839 | 6/9 | 22:00:00 | 282.15 | 98815 | 3.6 | 20 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3840 | 6/9 | 23:00:00 | 282.15 | 98815 | 3.1 | 10 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
3841 | 6/9 | 24:00:00 | 282.15 | 98815 | 3.1 | 360 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
3842 | 6/10 | 01:00:00 | 281.15 | 98806 | 2.1 | 340 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
3843 | 6/10 | 02:00:00 | 281.15 | 98806 | 1 | 285 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
3844 | 6/10 | 03:00:00 | 281.15 | 98806 | 1.5 | 350 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
3845 | 6/10 | 04:00:00 | 281.15 | 98806 | 1.5 | 12 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
3846 | 6/10 | 05:00:00 | 281.15 | 98806 | 2.1 | 30 | 6.4 | 97.2 | 0 | 266.846 | 0 | 1 | 8
3847 | 6/10 | 06:00:00 | 281.15 | 98806 | 2.1 | 30 | 6.4 | 230.4 | 0 | 267.58 | 0 | 1 | 8
3848 | 6/10 | 07:00:00 | 282.15 | 98815 | 2.1 | 40 | 6.3994 | 496.8 | 10.8 | 268.532 | 0 | 1 | 9
3849 | 6/10 | 08:00:00 | 282.15 | 98815 | 2.1 | 50 | 6.3994 | 795.6 | 54 | 268.532 | 0 | 1 | 9
3850 | 6/10 | 09:00:00 | 284.15 | 98833 | 2.1 | 80 | 6.8558 | 1076.4 | 194.4 | 270.663 | 0 | 1 | 11
3851 | 6/10 | 10:00:00 | 284.15 | 98833 | 2.1 | 70 | 6.8558 | 1317.6 | 216 | 270.663 | 0 | 1 | 11
3852 | 6/10 | 11:00:00 | 285.15 | 98841 | 2.1 | 100 | 6.8552 | 1490.4 | 216 | 271.616 | 0 | 1 | 12
3853 | 6/10 | 12:00:00 | 286.15 | 98850 | 3.1 | 140 | 6.3971 | 2858.4 | 1936.8 | 271.858 | 0 | 1 | 13
3854 | 6/10 | 13:00:00 | 287.15 | 98858 | 3.1 | 120 | 6.3966 | 2872.8 | 2304 | 272.808 | 0 | 1 | 14
3855 | 6/10 | 14:00:00 | 287.15 | 98858 | 2.1 | 110 | 6.3966 | 2732.4 | 2275.2 | 272.808 | 0 | 1 | 14
3856 | 6/10 | 15:00:00 | 287.15 | 98858 | 2.1 | 120 | 6.3966 | 2444.4 | 2224.8 | 272.808 | 0 | 1 | 14
3857 | 6/10 | 16:00:00 | 285.15 | 98841 | 5.1 | 80 | 7.3418 | 2030.4 | 1962 | 271.363 | 0 | 1 | 12
3858 | 6/10 | 17:00:00 | 285.15 | 98841 | 4.6 | 80 | 7.8591 | 1526.4 | 1587.6 | 271.588 | 0 | 1 | 12
3859 | 6/10 | 18:00:00 | 284.15 | 98833 | 5.1 | 90 | 7.3425 | 993.6 | 993.6 | 270.411 | 0 | 1 | 11
3860 | 6/10 | 19:00:00 | 283.15 | 98824 | 3.6 | 80 | 7.3431 | 273.6 | 0 | 269.936 | 0 | 1 | 10
3861 | 6/10 | 20:00:00 | 283.15 | 98824 | 3.1 | 80 | 7.8605 | 75.6 | 0 | 270.161 | 0 | 1 | 10
3862 | 6/10 | 21:00:00 | 283.15 | 98824 | 3.1 | 70 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
3863 | 6/10 | 22:00:00 | 282.15 | 98815 | 2.1 | 70 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3864 | 6/10 | 23:00:00 | 282.15 | 98815 | 1 | 195 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3865 | 6/10 | 24:00:00 | 282.15 | 98815 | 2.1 | 70 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3866 | 6/11 | 01:00:00 | 282.15 | 98815 | 2.6 | 40 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3867 | 6/11 | 02:00:00 | 282.15 | 98815 | 1.5 | 58 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
3868 | 6/11 | 03:00:00 | 281.15 | 98806 | 1 | 115 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
3869 | 6/11 | 04:00:00 | 281.15 | 98806 | 1 | 310 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
3870 | 6/11 | 05:00:00 | 281.15 | 98806 | 1 | 83 | 6.4 | 97.2 | 0 | 266.846 | 0 | 1 | 8
3871 | 6/11 | 06:00:00 | 282.15 | 98815 | 2.6 | 260 | 6.8571 | 442.8 | 475.2 | 268.021 | 0 | 1 | 9
3872 | 6/11 | 07:00:00 | 282.15 | 98815 | 4.1 | 270 | 6.8571 | 950.4 | 1267.2 | 268.021 | 0 | 1 | 9
3873 | 6/11 | 08:00:00 | 282.15 | 98815 | 3.6 | 260 | 7.3438 | 1515.6 | 1897.2 | 268.245 | 0 | 1 | 9
3874 | 6/11 | 09:00:00 | 284.15 | 98833 | 5.1 | 270 | 6.8558 | 2062.8 | 2394 | 269.921 | 0 | 1 | 11
3875 | 6/11 | 10:00:00 | 285.15 | 98841 | 7.2 | 280 | 5.9676 | 2379.6 | 2131.2 | 270.678 | 0 | 1 | 12
3876 | 6/11 | 11:00:00 | 286.15 | 98850 | 7.2 | 250 | 5.5631 | 2700 | 2286 | 271.395 | 0 | 1 | 13
3877 | 6/11 | 12:00:00 | 286.15 | 98850 | 7.7 | 270 | 5.5631 | 2869.2 | 2214 | 271.395 | 0 | 1 | 13
3878 | 6/11 | 13:00:00 | 287.15 | 98858 | 8.2 | 270 | 5.5627 | 3060 | 2764.8 | 272.077 | 0 | 1 | 14
3879 | 6/11 | 14:00:00 | 288.15 | 98867 | 8.7 | 280 | 4.8269 | 2919.6 | 2865.6 | 272.553 | 0 | 1 | 15
3880 | 6/11 | 15:00:00 | 287.15 | 98858 | 8.2 | 280 | 4.8273 | 2613.6 | 2599.2 | 271.608 | 0 | 1 | 14
3881 | 6/11 | 16:00:00 | 287.15 | 98858 | 9.8 | 290 | 5.9666 | 2167.2 | 2300.4 | 272.31 | 0 | 1 | 14
3882 | 6/11 | 17:00:00 | 287.15 | 98858 | 7.2 | 280 | 5.5627 | 1544.4 | 1623.6 | 272.343 | 0 | 1 | 14
3883 | 6/11 | 18:00:00 | 286.15 | 98850 | 7.7 | 280 | 5.5631 | 1065.6 | 1458 | 271.13 | 0 | 1 | 13
3884 | 6/11 | 19:00:00 | 286.15 | 98850 | 6.2 | 270 | 5.1837 | 532.8 | 608.4 | 270.896 | 0 | 1 | 13
3885 | 6/11 | 20:00:00 | 285.15 | 98841 | 4.1 | 270 | 5.5636 | 147.6 | 54 | 270.182 | 0 | 1 | 12
3886 | 6/11 | 21:00:00 | 283.15 | 98824 | 3.6 | 270 | 5.1851 | 0 | 0 | 268.056 | 0 | 1 | 10
3887 | 6/11 | 22:00:00 | 282.15 | 98815 | 4.1 | 260 | 5.1856 | 0 | 0 | 267.11 | 0 | 1 | 9
3888 | 6/11 | 23:00:00 | 281.15 | 98806 | 5.7 | 280 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
3889 | 6/11 | 24:00:00 | 281.15 | 98806 | 5.7 | 260 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
3890 | 6/12 | 01:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3891 | 6/12 | 02:00:00 | 280.15 | 98798 | 5.7 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
3892 | 6/12 | 03:00:00 | 280.15 | 98798 | 4.6 | 270 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
3893 | 6/12 | 04:00:00 | 279.15 | 98789 | 5.7 | 300 | 5.9708 | 0 | 0 | 265.559 | 0 | 1 | 6
3894 | 6/12 | 05:00:00 | 280.15 | 98798 | 4.1 | 280 | 5.9703 | 43.2 | 0 | 266.51 | 0 | 1 | 7
3895 | 6/12 | 06:00:00 | 281.15 | 98806 | 5.1 | 300 | 6.4 | 190.8 | 0 | 267.688 | 0 | 1 | 8
3896 | 6/12 | 07:00:00 | 283.15 | 98824 | 3.6 | 270 | 6.3988 | 954 | 1116 | 268.744 | 0 | 1 | 10
3897 | 6/12 | 08:00:00 | 283.15 | 98824 | 2.1 | 270 | 6.3988 | 1436.4 | 1609.2 | 269.007 | 0 | 1 | 10
3898 | 6/12 | 09:00:00 | 285.15 | 98841 | 2.1 | 360 | 5.9676 | 1951.2 | 1951.2 | 270.678 | 0 | 1 | 12
3899 | 6/12 | 10:00:00 | 286.15 | 98850 | 1.5 | 293 | 5.9671 | 2383.2 | 2131.2 | 271.627 | 0 | 1 | 13
3900 | 6/12 | 11:00:00 | 287.15 | 98858 | 1 | 141 | 5.1833 | 2703.6 | 2296.8 | 272.109 | 0 | 1 | 14
3901 | 6/12 | 12:00:00 | 288.15 | 98867 | 1.5 | 158 | 5.5621 | 2872.8 | 2217.6 | 273.292 | 0 | 1 | 15
3902 | 6/12 | 13:00:00 | 288.15 | 98867 | 2.6 | 90 | 5.5621 | 3063.6 | 2768.4 | 273.025 | 0 | 1 | 15
3903 | 6/12 | 14:00:00 | 289.15 | 98875 | 1.5 | 279 | 5.5617 | 2912.4 | 2840.4 | 273.972 | 0 | 1 | 16
3904 | 6/12 | 15:00:00 | 290.15 | 98883 | 2.1 | 170 | 5.182 | 2613.6 | 2761.2 | 274.683 | 0 | 1 | 17
3905 | 6/12 | 16:00:00 | 290.15 | 98883 | 3.6 | 160 | 5.5612 | 2174.4 | 2433.6 | 274.92 | 0 | 1 | 17
3906 | 6/12 | 17:00:00 | 290.15 | 98883 | 2.6 | 160 | 5.5612 | 1663.2 | 2055.6 | 274.778 | 0 | 1 | 17
3907 | 6/12 | 18:00:00 | 290.15 | 98883 | 3.1 | 150 | 5.5612 | 1083.6 | 1465.2 | 274.778 | 0 | 1 | 17
3908 | 6/12 | 19:00:00 | 289.15 | 98875 | 3.6 | 120 | 5.9656 | 536.4 | 608.4 | 274.206 | 0 | 1 | 16
3909 | 6/12 | 20:00:00 | 288.15 | 98867 | 5.1 | 100 | 6.8534 | 151.2 | 36 | 273.72 | 0 | 1 | 15
3910 | 6/12 | 21:00:00 | 286.15 | 98850 | 5.1 | 110 | 6.8546 | 0 | 0 | 272.087 | 0 | 1 | 13
3911 | 6/12 | 22:00:00 | 285.15 | 98841 | 4.6 | 110 | 6.8552 | 0 | 0 | 271.136 | 0 | 1 | 12
3912 | 6/12 | 23:00:00 | 284.15 | 98833 | 4.6 | 120 | 6.3982 | 0 | 0 | 270.435 | 0 | 1 | 11
3913 | 6/12 | 24:00:00 | 284.15 | 98833 | 4.1 | 130 | 6.3982 | 0 | 0 | 270.435 | 0 | 1 | 11
3914 | 6/13 | 01:00:00 | 283.15 | 98824 | 2.6 | 110 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
3915 | 6/13 | 02:00:00 | 283.15 | 98824 | 2.1 | 110 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
3916 | 6/13 | 03:00:00 | 283.15 | 98824 | 0 | 224 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
3917 | 6/13 | 04:00:00 | 283.15 | 98824 | 1 | 185 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
3918 | 6/13 | 05:00:00 | 283.15 | 98824 | 0.5 | 162 | 7.3431 | 93.6 | 0 | 269.46 | 0 | 1 | 10
3919 | 6/13 | 06:00:00 | 285.15 | 98841 | 0.5 | 224 | 7.8591 | 230.4 | 0 | 272.069 | 0 | 1 | 12
3920 | 6/13 | 07:00:00 | 286.15 | 98850 | 2.1 | 270 | 7.8584 | 896.4 | 900 | 272.541 | 0 | 1 | 13
3921 | 6/13 | 08:00:00 | 287.15 | 98858 | 3.6 | 270 | 7.8578 | 1429.2 | 1281.6 | 273.493 | 0 | 1 | 14
3922 | 6/13 | 09:00:00 | 287.15 | 98858 | 2.6 | 260 | 7.3406 | 1076.4 | 165.6 | 273.75 | 0 | 1 | 14
3923 | 6/13 | 10:00:00 | 288.15 | 98867 | 2.1 | 240 | 7.3399 | 2372.4 | 1886.4 | 274.218 | 0 | 1 | 15
3924 | 6/13 | 11:00:00 | 290.15 | 98883 | 3.6 | 210 | 6.8523 | 2689.2 | 2260.8 | 275.89 | 0 | 1 | 17
3925 | 6/13 | 12:00:00 | 290.15 | 98883 | 2.6 | 260 | 6.3949 | 2865.6 | 2296.8 | 275.658 | 0 | 1 | 17
3926 | 6/13 | 13:00:00 | 291.15 | 98892 | 3.6 | 260 | 6.3944 | 2880 | 2239.2 | 276.608 | 0 | 1 | 18
3927 | 6/13 | 14:00:00 | 292.15 | 98900 | 4.1 | 240 | 6.3938 | 2908.8 | 2739.6 | 277.286 | 0 | 1 | 19
3928 | 6/13 | 15:00:00 | 291.15 | 98892 | 3.6 | 270 | 6.3944 | 2606.4 | 2721.6 | 276.337 | 0 | 1 | 18
3929 | 6/13 | 16:00:00 | 292.15 | 98900 | 3.6 | 260 | 6.3938 | 2170.8 | 2448 | 277.286 | 0 | 1 | 19
3930 | 6/13 | 17:00:00 | 292.15 | 98900 | 4.1 | 280 | 7.3374 | 1638 | 2012.4 | 277.752 | 0 | 1 | 19
3931 | 6/13 | 18:00:00 | 291.15 | 98892 | 2.6 | 260 | 6.8517 | 1069.2 | 1393.2 | 276.57 | 0 | 1 | 18
3932 | 6/13 | 19:00:00 | 291.15 | 98892 | 3.6 | 310 | 6.8517 | 540 | 604.8 | 276.57 | 0 | 1 | 18
3933 | 6/13 | 20:00:00 | 289.15 | 98875 | 4.6 | 310 | 7.3393 | 151.2 | 39.6 | 274.9 | 0 | 1 | 16
3934 | 6/13 | 21:00:00 | 288.15 | 98867 | 3.6 | 320 | 7.3399 | 0 | 0 | 274.218 | 0 | 1 | 15
3935 | 6/13 | 22:00:00 | 287.15 | 98858 | 4.6 | 310 | 7.3406 | 0 | 0 | 273.393 | 0 | 1 | 14
3936 | 6/13 | 23:00:00 | 286.15 | 98850 | 3.6 | 290 | 7.3412 | 0 | 0 | 272.563 | 0 | 1 | 13
3937 | 6/13 | 24:00:00 | 285.15 | 98841 | 3.6 | 290 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
3938 | 6/14 | 01:00:00 | 285.15 | 98841 | 3.1 | 270 | 7.3418 | 0 | 0 | 271.729 | 0 | 1 | 12
3939 | 6/14 | 02:00:00 | 284.15 | 98833 | 1.5 | 310 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
3940 | 6/14 | 03:00:00 | 284.15 | 98833 | 1 | 350 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
3941 | 6/14 | 04:00:00 | 282.15 | 98815 | 2.6 | 250 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
3942 | 6/14 | 05:00:00 | 282.15 | 98815 | 3.6 | 300 | 6.8571 | 100.8 | 0 | 268.021 | 0 | 1 | 9
3943 | 6/14 | 06:00:00 | 284.15 | 98833 | 1.5 | 209 | 7.3425 | 442.8 | 475.2 | 270.147 | 0 | 1 | 11
3944 | 6/14 | 07:00:00 | 285.15 | 98841 | 3.1 | 270 | 7.8591 | 950.4 | 1256.4 | 271.323 | 0 | 1 | 12
3945 | 6/14 | 08:00:00 | 287.15 | 98858 | 5.7 | 270 | 7.8578 | 1515.6 | 1886.4 | 273.226 | 0 | 1 | 14
3946 | 6/14 | 09:00:00 | 288.15 | 98867 | 6.7 | 260 | 7.3399 | 2059.2 | 2390.4 | 273.95 | 0 | 1 | 15
3947 | 6/14 | 10:00:00 | 289.15 | 98875 | 5.7 | 280 | 6.8529 | 2520 | 2602.8 | 274.67 | 0 | 1 | 16
3948 | 6/14 | 11:00:00 | 290.15 | 98883 | 4.1 | 270 | 7.3387 | 2685.6 | 2196 | 276.121 | 0 | 1 | 17
3949 | 6/14 | 12:00:00 | 289.15 | 98875 | 5.7 | 310 | 6.8529 | 2862 | 2289.6 | 274.939 | 0 | 1 | 16
3950 | 6/14 | 13:00:00 | 290.15 | 98883 | 5.1 | 320 | 7.3387 | 2872.8 | 2228.4 | 276.121 | 0 | 1 | 17
3951 | 6/14 | 14:00:00 | 290.15 | 98883 | 5.7 | 320 | 6.8523 | 2905.2 | 2736 | 275.62 | 0 | 1 | 17
3952 | 6/14 | 15:00:00 | 292.15 | 98900 | 4.6 | 280 | 7.3374 | 2602.8 | 2635.2 | 277.752 | 0 | 1 | 19
3953 | 6/14 | 16:00:00 | 292.15 | 98900 | 4.6 | 270 | 6.8511 | 2048.4 | 1976.4 | 277.792 | 0 | 1 | 19
3954 | 6/14 | 17:00:00 | 292.15 | 98900 | 4.6 | 280 | 6.8511 | 1645.2 | 2109.6 | 277.52 | 0 | 1 | 19
3955 | 6/14 | 18:00:00 | 292.15 | 98900 | 5.1 | 270 | 6.3938 | 1076.4 | 1404 | 277.286 | 0 | 1 | 19
3956 | 6/14 | 19:00:00 | 291.15 | 98892 | 5.1 | 290 | 6.8517 | 543.6 | 612 | 276.57 | 0 | 1 | 18
3957 | 6/14 | 20:00:00 | 290.15 | 98883 | 3.6 | 320 | 6.3949 | 154.8 | 50.4 | 275.388 | 0 | 1 | 17
3958 | 6/14 | 21:00:00 | 288.15 | 98867 | 2.6 | 330 | 6.8534 | 0 | 0 | 273.988 | 0 | 1 | 15
3959 | 6/14 | 22:00:00 | 287.15 | 98858 | 3.6 | 330 | 6.3966 | 0 | 0 | 272.808 | 0 | 1 | 14
3960 | 6/14 | 23:00:00 | 286.15 | 98850 | 2.6 | 350 | 7.3412 | 0 | 0 | 272.563 | 0 | 1 | 13
3961 | 6/14 | 24:00:00 | 285.15 | 98841 | 3.1 | 310 | 7.3418 | 0 | 0 | 271.729 | 0 | 1 | 12
3962 | 6/15 | 01:00:00 | 285.15 | 98841 | 3.6 | 230 | 7.3418 | 0 | 0 | 271.363 | 0 | 1 | 12
3963 | 6/15 | 02:00:00 | 284.15 | 98833 | 2.1 | 310 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
3964 | 6/15 | 03:00:00 | 284.15 | 98833 | 1.5 | 200 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
3965 | 6/15 | 04:00:00 | 284.15 | 98833 | 1 | 125 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
3966 | 6/15 | 05:00:00 | 284.15 | 98833 | 2.1 | 220 | 7.8598 | 39.6 | 0 | 271.225 | 0 | 1 | 11
3967 | 6/15 | 06:00:00 | 284.15 | 98833 | 0 | 176 | 8.4095 | 442.8 | 687.6 | 270.595 | 0 | 1 | 11
3968 | 6/15 | 07:00:00 | 285.15 | 98841 | 1.5 | 300 | 8.4088 | 950.4 | 1242 | 271.547 | 0 | 1 | 12
3969 | 6/15 | 08:00:00 | 286.15 | 98850 | 2.1 | 310 | 8.408 | 1515.6 | 2005.2 | 272.499 | 0 | 1 | 13
3970 | 6/15 | 09:00:00 | 287.15 | 98858 | 3.6 | 320 | 7.8578 | 2059.2 | 2386.8 | 273.226 | 0 | 1 | 14
3971 | 6/15 | 10:00:00 | 289.15 | 98875 | 2.1 | 360 | 7.8564 | 2512.8 | 2595.6 | 275.129 | 0 | 1 | 16
3972 | 6/15 | 11:00:00 | 290.15 | 98883 | 3.1 | 100 | 7.8557 | 2847.6 | 2790 | 276.08 | 0 | 1 | 17
3973 | 6/15 | 12:00:00 | 290.15 | 98883 | 2.6 | 90 | 7.3387 | 3031.2 | 2768.4 | 275.851 | 0 | 1 | 17
3974 | 6/15 | 13:00:00 | 285.15 | 98841 | 4.6 | 270 | 7.8591 | 2872.8 | 2221.2 | 271.588 | 0 | 1 | 12
3975 | 6/15 | 14:00:00 | 286.15 | 98850 | 1.5 | 29 | 8.408 | 2728.8 | 2196 | 272.766 | 0 | 1 | 13
3976 | 6/15 | 15:00:00 | 288.15 | 98867 | 3.1 | 60 | 7.857 | 2599.2 | 2631.6 | 274.177 | 0 | 1 | 15
3977 | 6/15 | 16:00:00 | 289.15 | 98875 | 1.5 | 170 | 6.8529 | 2174.4 | 2448 | 274.67 | 0 | 1 | 16
3978 | 6/15 | 17:00:00 | 288.15 | 98867 | 2.1 | 50 | 6.8534 | 1648.8 | 2026.8 | 273.72 | 0 | 1 | 15
3979 | 6/15 | 18:00:00 | 287.15 | 98858 | 3.6 | 70 | 7.8578 | 1076.4 | 1389.6 | 273.226 | 0 | 1 | 14
3980 | 6/15 | 19:00:00 | 286.15 | 98850 | 3.6 | 20 | 7.3412 | 514.8 | 489.6 | 272.314 | 0 | 1 | 13
3981 | 6/15 | 20:00:00 | 285.15 | 98841 | 1.5 | 249 | 7.8591 | 147.6 | 7.2 | 271.588 | 0 | 1 | 12
3982 | 6/15 | 21:00:00 | 285.15 | 98841 | 3.1 | 30 | 7.8591 | 3.6 | 0 | 271.323 | 0 | 1 | 12
3983 | 6/15 | 22:00:00 | 284.15 | 98833 | 3.1 | 360 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
3984 | 6/15 | 23:00:00 | 284.15 | 98833 | 2.6 | 340 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
3985 | 6/15 | 24:00:00 | 284.15 | 98833 | 3.1 | 10 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
3986 | 6/16 | 01:00:00 | 284.15 | 98833 | 2.6 | 350 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
3987 | 6/16 | 02:00:00 | 284.15 | 98833 | 3.1 | 330 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
3988 | 6/16 | 03:00:00 | 283.15 | 98824 | 2.6 | 330 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
3989 | 6/16 | 04:00:00 | 281.15 | 98806 | 2.6 | 300 | 6.8577 | 0 | 0 | 266.644 | 0 | 1 | 8
3990 | 6/16 | 05:00:00 | 283.15 | 98824 | 2.6 | 330 | 7.3431 | 100.8 | 0 | 268.766 | 0 | 1 | 10
3991 | 6/16 | 06:00:00 | 283.15 | 98824 | 1.5 | 320 | 7.3431 | 450 | 500.4 | 268.766 | 0 | 1 | 10
3992 | 6/16 | 07:00:00 | 284.15 | 98833 | 2.1 | 10 | 7.8598 | 950.4 | 1299.6 | 270.371 | 0 | 1 | 11
3993 | 6/16 | 08:00:00 | 286.15 | 98850 | 1.5 | 108 | 7.8584 | 1429.2 | 1580.4 | 272.541 | 0 | 1 | 13
3994 | 6/16 | 09:00:00 | 286.15 | 98850 | 1 | 120 | 7.8584 | 1940.4 | 1911.6 | 272.541 | 0 | 1 | 13
3995 | 6/16 | 10:00:00 | 288.15 | 98867 | 0.5 | 64 | 7.857 | 2368.8 | 2030.4 | 274.446 | 0 | 1 | 15
3996 | 6/16 | 11:00:00 | 290.15 | 98883 | 1 | 165 | 7.3387 | 2851.2 | 2718 | 275.851 | 0 | 1 | 17
3997 | 6/16 | 12:00:00 | 289.15 | 98875 | 0.5 | 202 | 7.3393 | 3031.2 | 2844 | 274.9 | 0 | 1 | 16
3998 | 6/16 | 13:00:00 | 290.15 | 98883 | 2.6 | 130 | 7.3387 | 3052.8 | 2851.2 | 275.851 | 0 | 1 | 17
3999 | 6/16 | 14:00:00 | 290.15 | 98883 | 1.5 | 213 | 6.8523 | 2912.4 | 2815.2 | 275.62 | 0 | 1 | 17
4000 | 6/16 | 15:00:00 | 291.15 | 98892 | 2.1 | 170 | 7.338 | 2606.4 | 2710.8 | 276.802 | 0 | 1 | 18
4001 | 6/16 | 16:00:00 | 292.15 | 98900 | 3.1 | 160 | 6.8511 | 2178 | 2448 | 277.52 | 0 | 1 | 19
4002 | 6/16 | 17:00:00 | 291.15 | 98892 | 3.1 | 160 | 6.8517 | 1652.4 | 2034 | 276.57 | 0 | 1 | 18
4003 | 6/16 | 18:00:00 | 292.15 | 98900 | 3.6 | 170 | 6.8511 | 1022.4 | 1159.2 | 277.792 | 0 | 1 | 19
4004 | 6/16 | 19:00:00 | 292.15 | 98900 | 4.6 | 160 | 6.8511 | 550.8 | 622.8 | 277.52 | 0 | 1 | 19
4005 | 6/16 | 20:00:00 | 290.15 | 98883 | 2.6 | 160 | 7.3387 | 158.4 | 54 | 275.851 | 0 | 1 | 17
4006 | 6/16 | 21:00:00 | 290.15 | 98883 | 2.6 | 140 | 7.8557 | 3.6 | 0 | 276.08 | 0 | 1 | 17
4007 | 6/16 | 22:00:00 | 287.15 | 98858 | 3.1 | 120 | 8.4073 | 0 | 0 | 273.451 | 0 | 1 | 14
4008 | 6/16 | 23:00:00 | 287.15 | 98858 | 4.1 | 130 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
4009 | 6/16 | 24:00:00 | 286.15 | 98850 | 2.6 | 140 | 8.408 | 0 | 0 | 272.766 | 0 | 1 | 13
4010 | 6/17 | 01:00:00 | 286.15 | 98850 | 2.6 | 150 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
4011 | 6/17 | 02:00:00 | 286.15 | 98850 | 2.1 | 160 | 7.8584 | 0 | 0 | 272.909 | 0 | 1 | 13
4012 | 6/17 | 03:00:00 | 285.15 | 98841 | 2.1 | 170 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4013 | 6/17 | 04:00:00 | 285.15 | 98841 | 2.1 | 170 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
4014 | 6/17 | 05:00:00 | 285.15 | 98841 | 2.1 | 190 | 7.8591 | 93.6 | 0 | 271.588 | 0 | 1 | 12
4015 | 6/17 | 06:00:00 | 285.15 | 98841 | 3.1 | 150 | 8.4088 | 442.8 | 568.8 | 271.547 | 0 | 1 | 12
4016 | 6/17 | 07:00:00 | 286.15 | 98850 | 3.6 | 190 | 8.408 | 950.4 | 1242 | 272.499 | 0 | 1 | 13
4017 | 6/17 | 08:00:00 | 286.15 | 98850 | 5.1 | 180 | 7.8584 | 1515.6 | 1965.6 | 272.274 | 0 | 1 | 13
4018 | 6/17 | 09:00:00 | 286.15 | 98850 | 5.7 | 180 | 7.3412 | 1944 | 2059.2 | 272.314 | 0 | 1 | 13
4019 | 6/17 | 10:00:00 | 286.15 | 98850 | 6.7 | 190 | 7.3412 | 2372.4 | 1882.8 | 272.314 | 0 | 1 | 13
4020 | 6/17 | 11:00:00 | 286.15 | 98850 | 5.7 | 210 | 7.8584 | 1486.8 | 212.4 | 273.023 | 0 | 1 | 13
4021 | 6/17 | 12:00:00 | 285.15 | 98841 | 4.1 | 180 | 8.4088 | 1580.4 | 158.4 | 272.294 | 0 | 1 | 12
4022 | 6/17 | 13:00:00 | 285.15 | 98841 | 7.2 | 180 | 7.8591 | 1594.8 | 68.4 | 272.069 | 0 | 1 | 12
4023 | 6/17 | 14:00:00 | 285.15 | 98841 | 7.2 | 190 | 8.4088 | 1515.6 | 158.4 | 272.294 | 0 | 1 | 12
4024 | 6/17 | 15:00:00 | 286.15 | 98850 | 5.7 | 190 | 8.9918 | 1357.2 | 108 | 273.473 | 0 | 1 | 13
4025 | 6/17 | 16:00:00 | 287.15 | 98858 | 6.7 | 210 | 8.991 | 1134 | 100.8 | 274.428 | 0 | 1 | 14
4026 | 6/17 | 17:00:00 | 287.15 | 98858 | 7.2 | 210 | 8.991 | 860.4 | 104.4 | 274.428 | 0 | 1 | 14
4027 | 6/17 | 18:00:00 | 286.15 | 98850 | 7.7 | 270 | 8.9918 | 1018.8 | 1130.4 | 272.99 | 0 | 1 | 13
4028 | 6/17 | 19:00:00 | 286.15 | 98850 | 7.7 | 270 | 7.8584 | 554.4 | 619.2 | 272.274 | 0 | 1 | 13
4029 | 6/17 | 20:00:00 | 286.15 | 98850 | 5.7 | 270 | 7.8584 | 162 | 54 | 272.274 | 0 | 1 | 13
4030 | 6/17 | 21:00:00 | 285.15 | 98841 | 6.7 | 260 | 7.8591 | 3.6 | 0 | 271.323 | 0 | 1 | 12
4031 | 6/17 | 22:00:00 | 285.15 | 98841 | 5.1 | 260 | 7.3418 | 0 | 0 | 271.363 | 0 | 1 | 12
4032 | 6/17 | 23:00:00 | 284.15 | 98833 | 3.1 | 230 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
4033 | 6/17 | 24:00:00 | 283.15 | 98824 | 3.1 | 250 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4034 | 6/18 | 01:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
4035 | 6/18 | 02:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
4036 | 6/18 | 03:00:00 | 283.15 | 98824 | 4.1 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
4037 | 6/18 | 04:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
4038 | 6/18 | 05:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.3994 | 93.6 | 0 | 268.057 | 0 | 1 | 9
4039 | 6/18 | 06:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.3988 | 421.2 | 378 | 269.007 | 0 | 1 | 10
4040 | 6/18 | 07:00:00 | 284.15 | 98833 | 5.1 | 250 | 6.3982 | 900 | 1044 | 269.957 | 0 | 1 | 11
4041 | 6/18 | 08:00:00 | 284.15 | 98833 | 5.7 | 240 | 6.3982 | 1436.4 | 1540.8 | 269.957 | 0 | 1 | 11
4042 | 6/18 | 09:00:00 | 284.15 | 98833 | 5.1 | 240 | 6.3982 | 1947.6 | 1936.8 | 269.957 | 0 | 1 | 11
4043 | 6/18 | 10:00:00 | 285.15 | 98841 | 7.2 | 250 | 6.3977 | 2379.6 | 2070 | 270.907 | 0 | 1 | 12
4044 | 6/18 | 11:00:00 | 286.15 | 98850 | 6.2 | 240 | 5.9671 | 2700 | 2271.6 | 271.627 | 0 | 1 | 13
4045 | 6/18 | 12:00:00 | 286.15 | 98850 | 7.7 | 250 | 6.3971 | 2869.2 | 2296.8 | 271.858 | 0 | 1 | 13
4046 | 6/18 | 13:00:00 | 287.15 | 98858 | 8.7 | 250 | 5.9666 | 2890.8 | 2311.2 | 272.576 | 0 | 1 | 14
4047 | 6/18 | 14:00:00 | 289.15 | 98875 | 8.2 | 250 | 5.9656 | 2754 | 2282.4 | 274.475 | 0 | 1 | 16
4048 | 6/18 | 15:00:00 | 288.15 | 98867 | 8.7 | 250 | 5.9661 | 2473.2 | 2232 | 273.525 | 0 | 1 | 15
4049 | 6/18 | 16:00:00 | 289.15 | 98875 | 7.2 | 240 | 6.3955 | 2062.8 | 1987.2 | 274.708 | 0 | 1 | 16
4050 | 6/18 | 17:00:00 | 288.15 | 98867 | 8.2 | 250 | 5.9661 | 1569.6 | 1638 | 273.525 | 0 | 1 | 15
4051 | 6/18 | 18:00:00 | 287.15 | 98858 | 7.2 | 250 | 6.3966 | 1029.6 | 1213.2 | 272.808 | 0 | 1 | 14
4052 | 6/18 | 19:00:00 | 287.15 | 98858 | 7.7 | 250 | 6.3966 | 525.6 | 507.6 | 272.808 | 0 | 1 | 14
4053 | 6/18 | 20:00:00 | 286.15 | 98850 | 9.3 | 250 | 6.3971 | 154.8 | 18 | 271.858 | 0 | 1 | 13
4054 | 6/18 | 21:00:00 | 284.15 | 98833 | 8.7 | 280 | 6.3982 | 3.6 | 0 | 269.693 | 0 | 1 | 11
4055 | 6/18 | 22:00:00 | 284.15 | 98833 | 5.7 | 260 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
4056 | 6/18 | 23:00:00 | 283.15 | 98824 | 5.1 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
4057 | 6/18 | 24:00:00 | 283.15 | 98824 | 4.6 | 266 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
4058 | 6/19 | 01:00:00 | 284.15 | 98833 | 6.7 | 260 | 6.3982 | 0 | 0 | 269.957 | 0 | 1 | 11
4059 | 6/19 | 02:00:00 | 283.15 | 98824 | 8.2 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
4060 | 6/19 | 03:00:00 | 283.15 | 98824 | 7.2 | 260 | 6.3988 | 0 | 0 | 269.483 | 0 | 1 | 10
4061 | 6/19 | 04:00:00 | 283.15 | 98824 | 7.7 | 280 | 6.3988 | 0 | 0 | 269.483 | 0 | 1 | 10
4062 | 6/19 | 05:00:00 | 283.15 | 98824 | 7.2 | 280 | 6.8564 | 54 | 0 | 269.71 | 0 | 1 | 10
4063 | 6/19 | 06:00:00 | 283.15 | 98824 | 7.2 | 280 | 6.8564 | 417.6 | 460.8 | 269.234 | 0 | 1 | 10
4064 | 6/19 | 07:00:00 | 283.15 | 98824 | 5.7 | 270 | 6.8564 | 896.4 | 1033.2 | 269.234 | 0 | 1 | 10
4065 | 6/19 | 08:00:00 | 284.15 | 98833 | 7.7 | 270 | 6.3982 | 1432.8 | 1537.2 | 269.957 | 0 | 1 | 11
4066 | 6/19 | 09:00:00 | 285.15 | 98841 | 9.8 | 280 | 6.3977 | 1944 | 1933.2 | 270.907 | 0 | 1 | 12
4067 | 6/19 | 10:00:00 | 286.15 | 98850 | 8.7 | 280 | 6.3971 | 2379.6 | 2066.4 | 271.858 | 0 | 1 | 13
4068 | 6/19 | 11:00:00 | 287.15 | 98858 | 11.3 | 270 | 6.3966 | 2692.8 | 2260.8 | 272.808 | 0 | 1 | 14
4069 | 6/19 | 12:00:00 | 288.15 | 98867 | 11.8 | 270 | 6.8534 | 2865.6 | 2289.6 | 273.988 | 0 | 1 | 15
4070 | 6/19 | 13:00:00 | 286.15 | 98850 | 10.3 | 270 | 8.9918 | 2865.6 | 2271.6 | 272.99 | 0 | 1 | 13
4071 | 6/19 | 14:00:00 | 287.15 | 98858 | 11.3 | 280 | 10.2686 | 2721.6 | 2246.4 | 274.389 | 0 | 1 | 14
4072 | 6/19 | 15:00:00 | 288.15 | 98867 | 11.3 | 280 | 6.8534 | 2466 | 2214 | 273.988 | 0 | 1 | 15
4073 | 6/19 | 16:00:00 | 287.15 | 98858 | 10.8 | 280 | 6.3966 | 2062.8 | 1983.6 | 272.808 | 0 | 1 | 14
4074 | 6/19 | 17:00:00 | 286.15 | 98850 | 11.8 | 280 | 6.8546 | 1566 | 1681.2 | 272.087 | 0 | 1 | 13
4075 | 6/19 | 18:00:00 | 286.15 | 98850 | 11.8 | 280 | 6.3971 | 1094.4 | 1468.8 | 271.592 | 0 | 1 | 13
4076 | 6/19 | 19:00:00 | 286.15 | 98850 | 11.8 | 280 | 5.9671 | 561.6 | 633.6 | 271.361 | 0 | 1 | 13
4077 | 6/19 | 20:00:00 | 285.15 | 98841 | 8.2 | 270 | 5.9676 | 165.6 | 61.2 | 270.413 | 0 | 1 | 12
4078 | 6/19 | 21:00:00 | 284.15 | 98833 | 7.2 | 290 | 6.3982 | 7.2 | 0 | 269.693 | 0 | 1 | 11
4079 | 6/19 | 22:00:00 | 284.15 | 98833 | 6.7 | 280 | 5.9681 | 0 | 0 | 269.465 | 0 | 1 | 11
4080 | 6/19 | 23:00:00 | 284.15 | 98833 | 6.7 | 280 | 5.9681 | 0 | 0 | 269.465 | 0 | 1 | 11
4081 | 6/19 | 24:00:00 | 283.15 | 98824 | 4.1 | 300 | 5.9687 | 0 | 0 | 268.088 | 0 | 1 | 10
4082 | 6/20 | 01:00:00 | 283.15 | 98824 | 5.7 | 300 | 6.3988 | 0 | 0 | 268.744 | 0 | 1 | 10
4083 | 6/20 | 02:00:00 | 283.15 | 98824 | 5.1 | 290 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
4084 | 6/20 | 03:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
4085 | 6/20 | 04:00:00 | 282.15 | 98815 | 5.1 | 270 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
4086 | 6/20 | 05:00:00 | 283.15 | 98824 | 4.6 | 280 | 7.3431 | 93.6 | 0 | 269.46 | 0 | 1 | 10
4087 | 6/20 | 06:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.3431 | 417.6 | 370.8 | 269.46 | 0 | 1 | 10
4088 | 6/20 | 07:00:00 | 284.15 | 98833 | 6.2 | 260 | 7.3425 | 892.8 | 1029.6 | 270.411 | 0 | 1 | 11
4089 | 6/20 | 08:00:00 | 285.15 | 98841 | 5.7 | 280 | 7.3418 | 1429.2 | 1519.2 | 271.363 | 0 | 1 | 12
4090 | 6/20 | 09:00:00 | 285.15 | 98841 | 6.7 | 270 | 7.3418 | 1936.8 | 1900.8 | 271.363 | 0 | 1 | 12
4091 | 6/20 | 10:00:00 | 286.15 | 98850 | 7.2 | 270 | 7.8584 | 2509.2 | 2480.4 | 272.274 | 0 | 1 | 13
4092 | 6/20 | 11:00:00 | 287.15 | 98858 | 8.7 | 280 | 7.3406 | 2685.6 | 2188.8 | 273.266 | 0 | 1 | 14
4093 | 6/20 | 12:00:00 | 286.15 | 98850 | 5.7 | 270 | 8.408 | 2851.2 | 2271.6 | 272.766 | 0 | 1 | 13
4094 | 6/20 | 13:00:00 | 289.15 | 98875 | 8.2 | 280 | 7.8564 | 2876.4 | 2282.4 | 275.398 | 0 | 1 | 16
4095 | 6/20 | 14:00:00 | 288.15 | 98867 | 8.2 | 280 | 7.3399 | 2743.2 | 2260.8 | 274.218 | 0 | 1 | 15
4096 | 6/20 | 15:00:00 | 289.15 | 98875 | 7.7 | 290 | 7.3393 | 2466 | 2210.4 | 275.169 | 0 | 1 | 16
4097 | 6/20 | 16:00:00 | 288.15 | 98867 | 7.7 | 290 | 7.3399 | 2059.2 | 2109.6 | 274.218 | 0 | 1 | 15
4098 | 6/20 | 17:00:00 | 288.15 | 98867 | 8.7 | 290 | 6.8534 | 1663.2 | 2124 | 273.72 | 0 | 1 | 15
4099 | 6/20 | 18:00:00 | 287.15 | 98858 | 8.7 | 280 | 7.3406 | 1094.4 | 1407.6 | 272.999 | 0 | 1 | 14
4100 | 6/20 | 19:00:00 | 286.15 | 98850 | 8.2 | 280 | 7.3412 | 561.6 | 630 | 272.048 | 0 | 1 | 13
4101 | 6/20 | 20:00:00 | 286.15 | 98850 | 8.2 | 280 | 7.3412 | 165.6 | 64.8 | 272.048 | 0 | 1 | 13
4102 | 6/20 | 21:00:00 | 285.15 | 98841 | 5.7 | 280 | 7.3418 | 7.2 | 0 | 271.097 | 0 | 1 | 12
4103 | 6/20 | 22:00:00 | 284.15 | 98833 | 5.7 | 280 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
4104 | 6/20 | 23:00:00 | 284.15 | 98833 | 5.7 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
4105 | 6/20 | 24:00:00 | 284.15 | 98833 | 5.1 | 290 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
4106 | 6/21 | 01:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
4107 | 6/21 | 02:00:00 | 284.15 | 98833 | 5.7 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
4108 | 6/21 | 03:00:00 | 284.15 | 98833 | 6.2 | 280 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
4109 | 6/21 | 04:00:00 | 284.15 | 98833 | 4.6 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
4110 | 6/21 | 05:00:00 | 283.15 | 98824 | 4.1 | 290 | 7.3431 | 97.2 | 0 | 269.196 | 0 | 1 | 10
4111 | 6/21 | 06:00:00 | 283.15 | 98824 | 4.6 | 280 | 7.3431 | 439.2 | 468 | 269.196 | 0 | 1 | 10
4112 | 6/21 | 07:00:00 | 285.15 | 98841 | 6.2 | 300 | 7.3418 | 946.8 | 1252.8 | 271.097 | 0 | 1 | 12
4113 | 6/21 | 08:00:00 | 286.15 | 98850 | 4.6 | 310 | 7.3412 | 1512 | 1965.6 | 272.048 | 0 | 1 | 13
4114 | 6/21 | 09:00:00 | 287.15 | 98858 | 3.6 | 320 | 6.854 | 1940.4 | 2062.8 | 273.038 | 0 | 1 | 14
4115 | 6/21 | 10:00:00 | 288.15 | 98867 | 3.6 | 320 | 6.8534 | 2372.4 | 2059.2 | 273.988 | 0 | 1 | 15
4116 | 6/21 | 11:00:00 | 289.15 | 98875 | 3.1 | 187 | 6.8529 | 2689.2 | 2257.2 | 274.939 | 0 | 1 | 16
4117 | 6/21 | 12:00:00 | 290.15 | 98883 | 3.1 | 290 | 6.3949 | 2869.2 | 2293.2 | 275.658 | 0 | 1 | 17
4118 | 6/21 | 13:00:00 | 290.15 | 98883 | 3.1 | 270 | 6.8523 | 2883.6 | 2293.2 | 275.89 | 0 | 1 | 17
4119 | 6/21 | 14:00:00 | 290.15 | 98883 | 3.6 | 280 | 6.8523 | 2750.4 | 2268 | 275.89 | 0 | 1 | 17
4120 | 6/21 | 15:00:00 | 290.15 | 98883 | 3.1 | 280 | 7.3387 | 2466 | 2149.2 | 276.121 | 0 | 1 | 17
4121 | 6/21 | 16:00:00 | 290.15 | 98883 | 4.1 | 270 | 7.3387 | 2188.8 | 2448 | 275.851 | 0 | 1 | 17
4122 | 6/21 | 17:00:00 | 290.15 | 98883 | 5.7 | 290 | 7.8557 | 1659.6 | 2019.6 | 276.08 | 0 | 1 | 17
4123 | 6/21 | 18:00:00 | 290.15 | 98883 | 6.7 | 280 | 7.8557 | 1094.4 | 1404 | 276.08 | 0 | 1 | 17
4124 | 6/21 | 19:00:00 | 289.15 | 98875 | 5.7 | 280 | 7.8564 | 561.6 | 630 | 275.129 | 0 | 1 | 16
4125 | 6/21 | 20:00:00 | 288.15 | 98867 | 4.1 | 280 | 7.857 | 169.2 | 64.8 | 274.177 | 0 | 1 | 15
4126 | 6/21 | 21:00:00 | 286.15 | 98850 | 4.1 | 280 | 7.8584 | 7.2 | 0 | 272.274 | 0 | 1 | 13
4127 | 6/21 | 22:00:00 | 286.15 | 98850 | 3.6 | 270 | 7.8584 | 0 | 0 | 272.541 | 0 | 1 | 13
4128 | 6/21 | 23:00:00 | 286.15 | 98850 | 3.1 | 290 | 7.8584 | 0 | 0 | 273.023 | 0 | 1 | 13
4129 | 6/21 | 24:00:00 | 285.15 | 98841 | 4.1 | 280 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
4130 | 6/22 | 01:00:00 | 285.15 | 98841 | 3.1 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4131 | 6/22 | 02:00:00 | 285.15 | 98841 | 3.6 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4132 | 6/22 | 03:00:00 | 285.15 | 98841 | 3.1 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4133 | 6/22 | 04:00:00 | 285.15 | 98841 | 4.1 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4134 | 6/22 | 05:00:00 | 285.15 | 98841 | 4.1 | 270 | 8.4088 | 50.4 | 0 | 272.294 | 0 | 1 | 12
4135 | 6/22 | 06:00:00 | 285.15 | 98841 | 4.1 | 260 | 8.4088 | 230.4 | 0 | 272.294 | 0 | 1 | 12
4136 | 6/22 | 07:00:00 | 286.15 | 98850 | 4.1 | 270 | 8.9918 | 493.2 | 28.8 | 273.473 | 0 | 1 | 13
4137 | 6/22 | 08:00:00 | 287.15 | 98858 | 4.1 | 290 | 9.6108 | 784.8 | 72 | 274.652 | 0 | 1 | 14
4138 | 6/22 | 09:00:00 | 289.15 | 98875 | 6.2 | 280 | 9.6091 | 1065.6 | 241.2 | 276.565 | 0 | 1 | 16
4139 | 6/22 | 10:00:00 | 290.15 | 98883 | 4.6 | 270 | 9.6084 | 2354.4 | 1836 | 277.031 | 0 | 1 | 17
4140 | 6/22 | 11:00:00 | 291.15 | 98892 | 4.6 | 280 | 10.265 | 2664 | 2235.6 | 278.211 | 0 | 1 | 18
4141 | 6/22 | 12:00:00 | 293.15 | 98908 | 5.7 | 290 | 10.2634 | 2836.8 | 2264.4 | 280.122 | 0 | 1 | 20
4142 | 6/22 | 13:00:00 | 293.15 | 98908 | 3.6 | 300 | 10.2634 | 2858.4 | 2264.4 | 280.122 | 0 | 1 | 20
4143 | 6/22 | 14:00:00 | 294.15 | 98916 | 5.1 | 310 | 10.2625 | 2725.2 | 2246.4 | 281.078 | 0 | 1 | 21
4144 | 6/22 | 15:00:00 | 294.15 | 98916 | 4.6 | 310 | 10.96 | 2444.4 | 2084.4 | 281.303 | 0 | 1 | 21
4145 | 6/22 | 16:00:00 | 294.15 | 98916 | 4.6 | 280 | 10.96 | 2170.8 | 2458.8 | 281.028 | 0 | 1 | 21
4146 | 6/22 | 17:00:00 | 294.15 | 98916 | 2.6 | 300 | 10.96 | 1648.8 | 2106 | 281.028 | 0 | 1 | 21
4147 | 6/22 | 18:00:00 | 291.15 | 98892 | 4.1 | 330 | 11.7026 | 1087.2 | 1357.2 | 278.384 | 0 | 1 | 18
4148 | 6/22 | 19:00:00 | 290.15 | 98883 | 2.6 | 310 | 10.9637 | 529.2 | 594 | 277.478 | 0 | 1 | 17
4149 | 6/22 | 20:00:00 | 289.15 | 98875 | 3.6 | 290 | 10.9646 | 158.4 | 14.4 | 276.522 | 0 | 1 | 16
4150 | 6/22 | 21:00:00 | 290.15 | 98883 | 4.1 | 300 | 11.7037 | 7.2 | 0 | 277.428 | 0 | 1 | 17
4151 | 6/22 | 22:00:00 | 290.15 | 98883 | 4.1 | 300 | 10.9637 | 0 | 0 | 277.207 | 0 | 1 | 17
4152 | 6/22 | 23:00:00 | 289.15 | 98875 | 4.6 | 300 | 10.9646 | 0 | 0 | 276.251 | 0 | 1 | 16
4153 | 6/22 | 24:00:00 | 289.15 | 98875 | 3.6 | 300 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
4154 | 6/23 | 01:00:00 | 289.15 | 98875 | 3.6 | 290 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
4155 | 6/23 | 02:00:00 | 288.15 | 98867 | 2.1 | 310 | 10.2677 | 0 | 0 | 275.344 | 0 | 1 | 15
4156 | 6/23 | 03:00:00 | 288.15 | 98867 | 3.1 | 290 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4157 | 6/23 | 04:00:00 | 288.15 | 98867 | 2.1 | 310 | 10.2677 | 0 | 0 | 275.344 | 0 | 1 | 15
4158 | 6/23 | 05:00:00 | 287.15 | 98858 | 2.6 | 290 | 10.2686 | 50.4 | 0 | 274.874 | 0 | 1 | 14
4159 | 6/23 | 06:00:00 | 288.15 | 98867 | 1 | 129 | 10.9655 | 226.8 | 0 | 276.053 | 0 | 1 | 15
4160 | 6/23 | 07:00:00 | 289.15 | 98875 | 1 | 199 | 10.9646 | 489.6 | 25.2 | 277.011 | 0 | 1 | 16
4161 | 6/23 | 08:00:00 | 290.15 | 98883 | 1 | 212 | 11.7037 | 781.2 | 72 | 278.191 | 0 | 1 | 17
4162 | 6/23 | 09:00:00 | 291.15 | 98892 | 1.5 | 322 | 11.7026 | 1062 | 93.6 | 279.15 | 0 | 1 | 18
4163 | 6/23 | 10:00:00 | 291.15 | 98892 | 1.5 | 49 | 12.4871 | 1296 | 316.8 | 279.371 | 0 | 1 | 18
4164 | 6/23 | 11:00:00 | 292.15 | 98900 | 1.5 | 201 | 12.4861 | 2649.6 | 2109.6 | 279.836 | 0 | 1 | 19
4165 | 6/23 | 12:00:00 | 294.15 | 98916 | 1.5 | 205 | 12.484 | 2826 | 2314.8 | 281.751 | 0 | 1 | 21
4166 | 6/23 | 13:00:00 | 294.15 | 98916 | 2.6 | 70 | 12.484 | 2847.6 | 2314.8 | 281.751 | 0 | 1 | 21
4167 | 6/23 | 14:00:00 | 296.15 | 98932 | 3.1 | 100 | 11.6978 | 2718 | 2278.8 | 283.442 | 0 | 1 | 23
4168 | 6/23 | 15:00:00 | 295.15 | 98924 | 6.2 | 90 | 11.6988 | 2440.8 | 2001.6 | 282.485 | 0 | 1 | 22
4169 | 6/23 | 16:00:00 | 295.15 | 98924 | 5.7 | 90 | 11.6988 | 2044.8 | 1976.4 | 282.485 | 0 | 1 | 22
4170 | 6/23 | 17:00:00 | 294.15 | 98916 | 5.7 | 80 | 11.6997 | 1555.2 | 1666.8 | 281.528 | 0 | 1 | 21
4171 | 6/23 | 18:00:00 | 293.15 | 98908 | 4.1 | 70 | 11.7007 | 1087.2 | 1515.6 | 280.296 | 0 | 1 | 20
4172 | 6/23 | 19:00:00 | 292.15 | 98900 | 3.1 | 80 | 10.9618 | 561.6 | 745.2 | 279.117 | 0 | 1 | 19
4173 | 6/23 | 20:00:00 | 292.15 | 98900 | 3.6 | 80 | 10.2642 | 169.2 | 86.4 | 278.893 | 0 | 1 | 19
4174 | 6/23 | 21:00:00 | 290.15 | 98883 | 3.6 | 100 | 9.6084 | 7.2 | 0 | 276.76 | 0 | 1 | 17
4175 | 6/23 | 22:00:00 | 288.15 | 98867 | 2.6 | 80 | 8.9902 | 0 | 0 | 275.269 | 0 | 1 | 15
4176 | 6/23 | 23:00:00 | 287.15 | 98858 | 4.1 | 90 | 7.8578 | 0 | 0 | 273.743 | 0 | 1 | 14
4177 | 6/23 | 24:00:00 | 285.15 | 98841 | 3.1 | 70 | 6.8552 | 0 | 0 | 271.384 | 0 | 1 | 12
4178 | 6/24 | 01:00:00 | 284.15 | 98833 | 2.6 | 70 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
4179 | 6/24 | 02:00:00 | 283.15 | 98824 | 2.6 | 70 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
4180 | 6/24 | 03:00:00 | 283.15 | 98824 | 2.6 | 60 | 7.3431 | 0 | 0 | 268.766 | 0 | 1 | 10
4181 | 6/24 | 04:00:00 | 282.15 | 98815 | 2.1 | 50 | 7.3438 | 0 | 0 | 267.817 | 0 | 1 | 9
4182 | 6/24 | 05:00:00 | 283.15 | 98824 | 2.1 | 70 | 7.3431 | 39.6 | 0 | 270.046 | 0 | 1 | 10
4183 | 6/24 | 06:00:00 | 283.15 | 98824 | 2.1 | 60 | 7.8605 | 136.8 | 0 | 270.27 | 0 | 1 | 10
4184 | 6/24 | 07:00:00 | 283.15 | 98824 | 2.1 | 60 | 7.8605 | 298.8 | 0 | 270.27 | 0 | 1 | 10
4185 | 6/24 | 08:00:00 | 283.15 | 98824 | 2.1 | 80 | 7.8605 | 784.8 | 216 | 270.161 | 0 | 1 | 10
4186 | 6/24 | 09:00:00 | 285.15 | 98841 | 3.6 | 80 | 8.4088 | 1926 | 1724.4 | 271.813 | 0 | 1 | 12
4187 | 6/24 | 10:00:00 | 288.15 | 98867 | 3.6 | 90 | 8.4065 | 2358 | 2106 | 274.672 | 0 | 1 | 15
4188 | 6/24 | 11:00:00 | 290.15 | 98883 | 3.6 | 70 | 8.4052 | 2671.2 | 2242.8 | 276.579 | 0 | 1 | 17
4189 | 6/24 | 12:00:00 | 291.15 | 98892 | 5.1 | 100 | 8.4044 | 2847.6 | 2271.6 | 277.532 | 0 | 1 | 18
4190 | 6/24 | 13:00:00 | 292.15 | 98900 | 6.2 | 90 | 8.4037 | 2872.8 | 2275.2 | 278.485 | 0 | 1 | 19
4191 | 6/24 | 14:00:00 | 292.15 | 98900 | 6.2 | 80 | 8.4037 | 2739.6 | 2253.6 | 278.485 | 0 | 1 | 19
4192 | 6/24 | 15:00:00 | 293.15 | 98908 | 6.2 | 90 | 8.403 | 2462.4 | 2124 | 279.439 | 0 | 1 | 20
4193 | 6/24 | 16:00:00 | 292.15 | 98900 | 6.7 | 80 | 8.4037 | 2185.2 | 2444.4 | 278.213 | 0 | 1 | 19
4194 | 6/24 | 17:00:00 | 292.15 | 98900 | 6.2 | 80 | 8.4037 | 1663.2 | 2152.8 | 278.213 | 0 | 1 | 19
4195 | 6/24 | 18:00:00 | 291.15 | 98892 | 5.7 | 90 | 8.9879 | 1098 | 1386 | 277.488 | 0 | 1 | 18
4196 | 6/24 | 19:00:00 | 290.15 | 98883 | 6.7 | 90 | 8.9887 | 532.8 | 734.4 | 276.806 | 0 | 1 | 17
4197 | 6/24 | 20:00:00 | 287.15 | 98858 | 6.2 | 90 | 8.991 | 90 | 0 | 274.428 | 0 | 1 | 14
4198 | 6/24 | 21:00:00 | 286.15 | 98850 | 6.2 | 90 | 8.408 | 3.6 | 0 | 273.248 | 0 | 1 | 13
4199 | 6/24 | 22:00:00 | 286.15 | 98850 | 4.6 | 80 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
4200 | 6/24 | 23:00:00 | 285.15 | 98841 | 5.1 | 90 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
4201 | 6/24 | 24:00:00 | 285.15 | 98841 | 3.6 | 80 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
4202 | 6/25 | 01:00:00 | 285.15 | 98841 | 4.1 | 80 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
4203 | 6/25 | 02:00:00 | 285.15 | 98841 | 3.1 | 80 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
4204 | 6/25 | 03:00:00 | 285.15 | 98841 | 2.6 | 50 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
4205 | 6/25 | 04:00:00 | 284.15 | 98833 | 4.1 | 60 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
4206 | 6/25 | 05:00:00 | 284.15 | 98833 | 3.6 | 70 | 8.4095 | 50.4 | 0 | 271.339 | 0 | 1 | 11
4207 | 6/25 | 06:00:00 | 284.15 | 98833 | 4.1 | 60 | 7.8598 | 406.8 | 439.2 | 270.636 | 0 | 1 | 11
4208 | 6/25 | 07:00:00 | 284.15 | 98833 | 5.1 | 50 | 7.8598 | 489.6 | 39.6 | 271.115 | 0 | 1 | 11
4209 | 6/25 | 08:00:00 | 284.15 | 98833 | 3.6 | 50 | 7.8598 | 784.8 | 54 | 271.115 | 0 | 1 | 11
4210 | 6/25 | 09:00:00 | 286.15 | 98850 | 4.6 | 50 | 8.408 | 1065.6 | 244.8 | 273.248 | 0 | 1 | 13
4211 | 6/25 | 10:00:00 | 288.15 | 98867 | 4.6 | 40 | 8.9902 | 2350.8 | 1839.6 | 274.898 | 0 | 1 | 15
4212 | 6/25 | 11:00:00 | 290.15 | 98883 | 5.7 | 50 | 8.4052 | 2833.2 | 2707.2 | 276.308 | 0 | 1 | 17
4213 | 6/25 | 12:00:00 | 291.15 | 98892 | 6.2 | 50 | 8.9879 | 3016.8 | 2829.6 | 277.488 | 0 | 1 | 18
4214 | 6/25 | 13:00:00 | 293.15 | 98908 | 6.2 | 70 | 9.6059 | 3034.8 | 2833.2 | 279.622 | 0 | 1 | 20
4215 | 6/25 | 14:00:00 | 293.15 | 98908 | 5.7 | 90 | 8.9864 | 2901.6 | 2800.8 | 279.394 | 0 | 1 | 20
4216 | 6/25 | 15:00:00 | 293.15 | 98908 | 6.2 | 90 | 8.9864 | 2606.4 | 2685.6 | 279.394 | 0 | 1 | 20
4217 | 6/25 | 16:00:00 | 292.15 | 98900 | 6.2 | 80 | 9.6067 | 2178 | 2440.8 | 278.668 | 0 | 1 | 19
4218 | 6/25 | 17:00:00 | 293.15 | 98908 | 7.2 | 90 | 7.8537 | 1666.8 | 2019.6 | 278.935 | 0 | 1 | 20
4219 | 6/25 | 18:00:00 | 293.15 | 98908 | 6.7 | 80 | 7.8537 | 1101.6 | 1458 | 278.935 | 0 | 1 | 20
4220 | 6/25 | 19:00:00 | 292.15 | 98900 | 5.7 | 80 | 6.8511 | 572.4 | 658.8 | 277.377 | 0 | 1 | 19
4221 | 6/25 | 20:00:00 | 291.15 | 98892 | 5.7 | 80 | 7.338 | 169.2 | 64.8 | 276.802 | 0 | 1 | 18
4222 | 6/25 | 21:00:00 | 289.15 | 98875 | 3.6 | 70 | 7.8564 | 7.2 | 0 | 275.398 | 0 | 1 | 16
4223 | 6/25 | 22:00:00 | 287.15 | 98858 | 4.1 | 60 | 8.4073 | 0 | 0 | 274.088 | 0 | 1 | 14
4224 | 6/25 | 23:00:00 | 285.15 | 98841 | 3.6 | 50 | 8.9926 | 0 | 0 | 272.627 | 0 | 1 | 12
4225 | 6/25 | 24:00:00 | 285.15 | 98841 | 3.6 | 40 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
4226 | 6/26 | 01:00:00 | 285.15 | 98841 | 3.6 | 30 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4227 | 6/26 | 02:00:00 | 285.15 | 98841 | 3.6 | 40 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
4228 | 6/26 | 03:00:00 | 285.15 | 98841 | 3.6 | 40 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4229 | 6/26 | 04:00:00 | 284.15 | 98833 | 3.6 | 40 | 8.4095 | 0 | 0 | 270.859 | 0 | 1 | 11
4230 | 6/26 | 05:00:00 | 285.15 | 98841 | 4.1 | 40 | 8.9926 | 50.4 | 0 | 272.517 | 0 | 1 | 12
4231 | 6/26 | 06:00:00 | 286.15 | 98850 | 3.6 | 50 | 8.9918 | 223.2 | 0 | 273.473 | 0 | 1 | 13
4232 | 6/26 | 07:00:00 | 287.15 | 98858 | 3.6 | 40 | 9.6108 | 486 | 36 | 274.652 | 0 | 1 | 14
4233 | 6/26 | 08:00:00 | 288.15 | 98867 | 3.6 | 50 | 9.6099 | 1404 | 1245.6 | 275.122 | 0 | 1 | 15
4234 | 6/26 | 09:00:00 | 289.15 | 98875 | 4.6 | 50 | 10.2668 | 2026.8 | 2307.6 | 276.029 | 0 | 1 | 16
4235 | 6/26 | 10:00:00 | 291.15 | 98892 | 4.6 | 50 | 10.9627 | 2480.4 | 2595.6 | 278.162 | 0 | 1 | 18
4236 | 6/26 | 11:00:00 | 293.15 | 98908 | 6.2 | 50 | 10.2634 | 2656.8 | 2181.6 | 280.122 | 0 | 1 | 20
4237 | 6/26 | 12:00:00 | 292.15 | 98900 | 4.6 | 20 | 10.9618 | 2829.6 | 1882.8 | 279.391 | 0 | 1 | 19
4238 | 6/26 | 13:00:00 | 291.15 | 98892 | 4.6 | 30 | 10.265 | 1584 | 370.8 | 278.703 | 0 | 1 | 18
4239 | 6/26 | 14:00:00 | 291.15 | 98892 | 5.1 | 50 | 10.9627 | 1508.4 | 154.8 | 278.927 | 0 | 1 | 18
4240 | 6/26 | 15:00:00 | 290.15 | 98883 | 3.6 | 60 | 10.9637 | 1357.2 | 108 | 277.969 | 0 | 1 | 17
4241 | 6/26 | 16:00:00 | 289.15 | 98875 | 3.6 | 50 | 10.9646 | 1134 | 97.2 | 277.011 | 0 | 1 | 16
4242 | 6/26 | 17:00:00 | 289.15 | 98875 | 2.1 | 70 | 10.9646 | 864 | 79.2 | 277.011 | 0 | 1 | 16
4243 | 6/26 | 18:00:00 | 289.15 | 98875 | 2.6 | 60 | 10.9646 | 572.4 | 39.6 | 277.011 | 0 | 1 | 16
4244 | 6/26 | 19:00:00 | 289.15 | 98875 | 3.1 | 60 | 10.9646 | 295.2 | 0 | 277.011 | 0 | 1 | 16
4245 | 6/26 | 20:00:00 | 289.15 | 98875 | 2.6 | 50 | 10.9646 | 90 | 0 | 277.011 | 0 | 1 | 16
4246 | 6/26 | 21:00:00 | 288.15 | 98867 | 2.1 | 60 | 10.9655 | 3.6 | 0 | 276.053 | 0 | 1 | 15
4247 | 6/26 | 22:00:00 | 288.15 | 98867 | 2.1 | 60 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4248 | 6/26 | 23:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.9655 | 0 | 0 | 276.165 | 0 | 1 | 15
4249 | 6/26 | 24:00:00 | 288.15 | 98867 | 1.5 | 208 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4250 | 6/27 | 01:00:00 | 287.15 | 98858 | 2.1 | 80 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4251 | 6/27 | 02:00:00 | 287.15 | 98858 | 2.1 | 70 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4252 | 6/27 | 03:00:00 | 287.15 | 98858 | 2.1 | 70 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4253 | 6/27 | 04:00:00 | 287.15 | 98858 | 2.1 | 30 | 10.2686 | 0 | 0 | 274.985 | 0 | 1 | 14
4254 | 6/27 | 05:00:00 | 287.15 | 98858 | 1.5 | 171 | 10.2686 | 46.8 | 0 | 274.874 | 0 | 1 | 14
4255 | 6/27 | 06:00:00 | 287.15 | 98858 | 2.1 | 40 | 10.2686 | 223.2 | 0 | 274.874 | 0 | 1 | 14
4256 | 6/27 | 07:00:00 | 288.15 | 98867 | 2.6 | 50 | 10.2677 | 482.4 | 25.2 | 275.831 | 0 | 1 | 15
4257 | 6/27 | 08:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.9655 | 774 | 93.6 | 276.053 | 0 | 1 | 15
4258 | 6/27 | 09:00:00 | 289.15 | 98875 | 3.1 | 60 | 10.9646 | 1904.4 | 1684.8 | 276.522 | 0 | 1 | 16
4259 | 6/27 | 10:00:00 | 290.15 | 98883 | 2.1 | 40 | 10.9637 | 2332.8 | 1814.4 | 277.478 | 0 | 1 | 17
4260 | 6/27 | 11:00:00 | 291.15 | 98892 | 3.1 | 20 | 10.9627 | 1468.8 | 280.8 | 278.927 | 0 | 1 | 18
4261 | 6/27 | 12:00:00 | 292.15 | 98900 | 2.6 | 60 | 10.9618 | 2826 | 1882.8 | 279.391 | 0 | 1 | 19
4262 | 6/27 | 13:00:00 | 293.15 | 98908 | 3.1 | 60 | 11.7007 | 2847.6 | 2293.2 | 280.571 | 0 | 1 | 20
4263 | 6/27 | 14:00:00 | 293.15 | 98908 | 5.1 | 10 | 11.7007 | 2718 | 2275.2 | 280.571 | 0 | 1 | 20
4264 | 6/27 | 15:00:00 | 293.15 | 98908 | 4.1 | 40 | 11.7007 | 2440.8 | 1998 | 280.571 | 0 | 1 | 20
4265 | 6/27 | 16:00:00 | 292.15 | 98900 | 4.6 | 50 | 11.7017 | 2044.8 | 1976.4 | 279.614 | 0 | 1 | 19
4266 | 6/27 | 17:00:00 | 291.15 | 98892 | 4.1 | 50 | 11.7026 | 1555.2 | 1310.4 | 278.657 | 0 | 1 | 18
4267 | 6/27 | 18:00:00 | 290.15 | 98883 | 3.6 | 20 | 10.9637 | 572.4 | 57.6 | 277.969 | 0 | 1 | 17
4268 | 6/27 | 19:00:00 | 289.15 | 98875 | 3.6 | 20 | 10.9646 | 295.2 | 0 | 277.011 | 0 | 1 | 16
4269 | 6/27 | 20:00:00 | 288.15 | 98867 | 2.6 | 20 | 10.9655 | 54 | 0 | 276.165 | 0 | 1 | 15
4270 | 6/27 | 21:00:00 | 288.15 | 98867 | 3.1 | 20 | 10.9655 | 3.6 | 0 | 276.165 | 0 | 1 | 15
4271 | 6/27 | 22:00:00 | 288.15 | 98867 | 2.6 | 10 | 10.9655 | 0 | 0 | 276.165 | 0 | 1 | 15
4272 | 6/27 | 23:00:00 | 287.15 | 98858 | 2.6 | 10 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4273 | 6/27 | 24:00:00 | 287.15 | 98858 | 2.1 | 30 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4274 | 6/28 | 01:00:00 | 287.15 | 98858 | 2.1 | 30 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4275 | 6/28 | 02:00:00 | 287.15 | 98858 | 2.1 | 20 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4276 | 6/28 | 03:00:00 | 287.15 | 98858 | 2.6 | 40 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4277 | 6/28 | 04:00:00 | 287.15 | 98858 | 2.6 | 332 | 10.2686 | 0 | 0 | 274.985 | 0 | 1 | 14
4278 | 6/28 | 05:00:00 | 287.15 | 98858 | 2.6 | 179 | 10.2686 | 28.8 | 0 | 274.985 | 0 | 1 | 14
4279 | 6/28 | 06:00:00 | 287.15 | 98858 | 2.6 | 10 | 10.2686 | 133.2 | 0 | 274.985 | 0 | 1 | 14
4280 | 6/28 | 07:00:00 | 287.15 | 98858 | 2.6 | 30 | 10.2686 | 291.6 | 0 | 274.985 | 0 | 1 | 14
4281 | 6/28 | 08:00:00 | 287.15 | 98858 | 2.6 | 50 | 10.2686 | 471.6 | 0 | 274.985 | 0 | 1 | 14
4282 | 6/28 | 09:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.9655 | 644.4 | 3.6 | 276.165 | 0 | 1 | 15
4283 | 6/28 | 10:00:00 | 288.15 | 98867 | 1 | 246 | 10.9655 | 788.4 | 25.2 | 276.165 | 0 | 1 | 15
4284 | 6/28 | 11:00:00 | 288.15 | 98867 | 1.5 | 156 | 10.9655 | 1468.8 | 104.4 | 276.053 | 0 | 1 | 15
4285 | 6/28 | 12:00:00 | 288.15 | 98867 | 1 | 17 | 10.9655 | 1566 | 154.8 | 276.053 | 0 | 1 | 15
4286 | 6/28 | 13:00:00 | 289.15 | 98875 | 2.1 | 70 | 11.7047 | 1576.8 | 363.6 | 277.232 | 0 | 1 | 16
4287 | 6/28 | 14:00:00 | 291.15 | 98892 | 2.1 | 60 | 11.7026 | 2714.4 | 1897.2 | 278.657 | 0 | 1 | 18
4288 | 6/28 | 15:00:00 | 292.15 | 98900 | 2.1 | 80 | 11.7017 | 2440.8 | 1998 | 279.614 | 0 | 1 | 19
4289 | 6/28 | 16:00:00 | 294.15 | 98916 | 1.5 | 52 | 11.6997 | 2044.8 | 1976.4 | 281.528 | 0 | 1 | 21
4290 | 6/28 | 17:00:00 | 294.15 | 98916 | 4.1 | 70 | 10.96 | 1558.8 | 1674 | 281.303 | 0 | 1 | 21
4291 | 6/28 | 18:00:00 | 294.15 | 98916 | 3.6 | 50 | 10.96 | 1094.4 | 1522.8 | 281.028 | 0 | 1 | 21
4292 | 6/28 | 19:00:00 | 293.15 | 98908 | 3.6 | 70 | 10.9609 | 565.2 | 745.2 | 280.073 | 0 | 1 | 20
4293 | 6/28 | 20:00:00 | 291.15 | 98892 | 2.6 | 50 | 10.9627 | 169.2 | 86.4 | 278.162 | 0 | 1 | 18
4294 | 6/28 | 21:00:00 | 289.15 | 98875 | 2.6 | 70 | 10.2668 | 7.2 | 0 | 276.029 | 0 | 1 | 16
4295 | 6/28 | 22:00:00 | 289.15 | 98875 | 2.1 | 60 | 10.9646 | 0 | 0 | 276.251 | 0 | 1 | 16
4296 | 6/28 | 23:00:00 | 288.15 | 98867 | 2.1 | 60 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
4297 | 6/28 | 24:00:00 | 288.15 | 98867 | 2.1 | 80 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4298 | 6/29 | 01:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.9655 | 0 | 0 | 276.165 | 0 | 1 | 15
4299 | 6/29 | 02:00:00 | 288.15 | 98867 | 2.1 | 50 | 10.9655 | 0 | 0 | 276.165 | 0 | 1 | 15
4300 | 6/29 | 03:00:00 | 288.15 | 98867 | 1.5 | 30 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4301 | 6/29 | 04:00:00 | 288.15 | 98867 | 1 | 127 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4302 | 6/29 | 05:00:00 | 288.15 | 98867 | 2.1 | 60 | 10.9655 | 46.8 | 0 | 276.053 | 0 | 1 | 15
4303 | 6/29 | 06:00:00 | 288.15 | 98867 | 1.5 | 233 | 10.9655 | 216 | 0 | 276.053 | 0 | 1 | 15
4304 | 6/29 | 07:00:00 | 288.15 | 98867 | 2.1 | 100 | 10.9655 | 291.6 | 0 | 276.165 | 0 | 1 | 15
4305 | 6/29 | 08:00:00 | 288.15 | 98867 | 2.6 | 90 | 10.9655 | 471.6 | 0 | 276.165 | 0 | 1 | 15
4306 | 6/29 | 09:00:00 | 288.15 | 98867 | 2.6 | 100 | 10.9655 | 1051.2 | 104.4 | 276.053 | 0 | 1 | 15
4307 | 6/29 | 10:00:00 | 289.15 | 98875 | 1.5 | 209 | 11.7047 | 1288.8 | 104.4 | 277.232 | 0 | 1 | 16
4308 | 6/29 | 11:00:00 | 290.15 | 98883 | 2.1 | 90 | 11.7037 | 1465.2 | 151.2 | 278.191 | 0 | 1 | 17
4309 | 6/29 | 12:00:00 | 291.15 | 98892 | 2.1 | 80 | 11.7026 | 1562.4 | 363.6 | 279.15 | 0 | 1 | 18
4310 | 6/29 | 13:00:00 | 293.15 | 98908 | 2.6 | 100 | 11.7007 | 2844 | 1911.6 | 280.571 | 0 | 1 | 20
4311 | 6/29 | 14:00:00 | 294.15 | 98916 | 2.6 | 80 | 12.484 | 2876.4 | 2768.4 | 281.476 | 0 | 1 | 21
4312 | 6/29 | 15:00:00 | 295.15 | 98924 | 3.6 | 90 | 12.483 | 2584.8 | 2721.6 | 282.433 | 0 | 1 | 22
4313 | 6/29 | 16:00:00 | 295.15 | 98924 | 4.1 | 70 | 12.483 | 2163.6 | 2505.6 | 282.433 | 0 | 1 | 22
4314 | 6/29 | 17:00:00 | 295.15 | 98924 | 4.1 | 80 | 12.483 | 1648.8 | 2246.4 | 282.433 | 0 | 1 | 22
4315 | 6/29 | 18:00:00 | 295.15 | 98924 | 4.1 | 110 | 11.6988 | 1090.8 | 1515.6 | 282.209 | 0 | 1 | 22
4316 | 6/29 | 19:00:00 | 294.15 | 98916 | 5.1 | 100 | 11.6997 | 561.6 | 741.6 | 281.253 | 0 | 1 | 21
4317 | 6/29 | 20:00:00 | 293.15 | 98908 | 4.1 | 100 | 12.485 | 169.2 | 79.2 | 280.519 | 0 | 1 | 20
4318 | 6/29 | 21:00:00 | 291.15 | 98892 | 3.6 | 80 | 11.7026 | 3.6 | 0 | 279.15 | 0 | 1 | 18
4319 | 6/29 | 22:00:00 | 290.15 | 98883 | 4.1 | 90 | 10.9637 | 0 | 0 | 276.764 | 0 | 1 | 17
4320 | 6/29 | 23:00:00 | 289.15 | 98875 | 3.1 | 90 | 10.9646 | 0 | 0 | 275.81 | 0 | 1 | 16
4321 | 6/29 | 24:00:00 | 289.15 | 98875 | 3.1 | 80 | 10.9646 | 0 | 0 | 275.81 | 0 | 1 | 16
4322 | 6/30 | 01:00:00 | 288.15 | 98867 | 2.1 | 80 | 10.2677 | 0 | 0 | 274.636 | 0 | 1 | 15
4323 | 6/30 | 02:00:00 | 287.15 | 98858 | 2.6 | 60 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
4324 | 6/30 | 03:00:00 | 286.15 | 98850 | 2.6 | 80 | 9.6116 | 0 | 0 | 272.509 | 0 | 1 | 13
4325 | 6/30 | 04:00:00 | 286.15 | 98850 | 2.6 | 70 | 9.6116 | 0 | 0 | 272.509 | 0 | 1 | 13
4326 | 6/30 | 05:00:00 | 286.15 | 98850 | 2.1 | 70 | 9.6116 | 86.4 | 0 | 272.509 | 0 | 1 | 13
4327 | 6/30 | 06:00:00 | 286.15 | 98850 | 1 | 60 | 9.6116 | 133.2 | 0 | 273.806 | 0 | 1 | 13
4328 | 6/30 | 07:00:00 | 286.15 | 98850 | 0.5 | 111 | 9.6116 | 291.6 | 0 | 273.806 | 0 | 1 | 13
4329 | 6/30 | 08:00:00 | 287.15 | 98858 | 0.5 | 249 | 10.2686 | 770.4 | 93.6 | 274.874 | 0 | 1 | 14
4330 | 6/30 | 09:00:00 | 287.15 | 98858 | 0.5 | 83 | 10.2686 | 1051.2 | 237.6 | 274.874 | 0 | 1 | 14
4331 | 6/30 | 10:00:00 | 288.15 | 98867 | 0.5 | 216 | 10.9655 | 2325.6 | 1810.8 | 275.565 | 0 | 1 | 15
4332 | 6/30 | 11:00:00 | 289.15 | 98875 | 1.5 | 245 | 11.7047 | 2797.2 | 2728.8 | 276.472 | 0 | 1 | 16
4333 | 6/30 | 12:00:00 | 291.15 | 98892 | 1.5 | 290 | 11.7026 | 2988 | 2865.6 | 278.384 | 0 | 1 | 18
4334 | 6/30 | 13:00:00 | 292.15 | 98900 | 2.1 | 90 | 13.3174 | 3042 | 2746.8 | 279.335 | 0 | 1 | 19
4335 | 6/30 | 14:00:00 | 295.15 | 98924 | 2.1 | 70 | 13.3141 | 2905.2 | 2998.8 | 282.204 | 0 | 1 | 22
4336 | 6/30 | 15:00:00 | 296.15 | 98932 | 2.6 | 150 | 12.482 | 2617.2 | 2847.6 | 282.937 | 0 | 1 | 23
4337 | 6/30 | 16:00:00 | 296.15 | 98932 | 3.1 | 130 | 12.482 | 2192.4 | 2610 | 282.937 | 0 | 1 | 23
4338 | 6/30 | 17:00:00 | 296.15 | 98932 | 2.1 | 160 | 13.313 | 1645.2 | 2232 | 283.613 | 0 | 1 | 23
4339 | 6/30 | 18:00:00 | 295.15 | 98924 | 1 | 276 | 14.1948 | 1083.6 | 1605.6 | 282.876 | 0 | 1 | 22
4340 | 6/30 | 19:00:00 | 292.95 | 98906 | 1.6 | 225 | 13.1465 | 558 | 777.6 | 280.504 | 0 | 1 | 19.8
4341 | 6/30 | 20:00:00 | 292.15 | 98900 | 1.6 | 178 | 12.4861 | 169.2 | 75.6 | 279.562 | 0 | 1 | 19
4342 | 6/30 | 21:00:00 | 291.35 | 98894 | 2.2 | 118 | 11.8556 | 3.6 | 0 | 279.386 | 0 | 1 | 18.2
4343 | 6/30 | 22:00:00 | 289.15 | 98875 | 2.7 | 167 | 10.6106 | 0 | 0 | 276.9 | 0 | 1 | 16
4344 | 6/30 | 23:00:00 | 287.15 | 98858 | 3.2 | 175 | 9.4839 | 0 | 0 | 274.607 | 0 | 1 | 14
4345 | 6/30 | 24:00:00 | 285.15 | 98841 | 3.6 | 215 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
4346 | 7/1 | 01:00:00 | 283.35 | 98826 | 3.8 | 252 | 7.5977 | 0 | 0 | 269.762 | 0 | 1 | 10.2
4347 | 7/1 | 02:00:00 | 283.15 | 98824 | 3.6 | 252 | 7.4441 | 0 | 0 | 269.504 | 0 | 1 | 10
4348 | 7/1 | 03:00:00 | 283.15 | 98824 | 3.5 | 255 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4349 | 7/1 | 04:00:00 | 283.65 | 98828 | 3.2 | 255 | 7.4438 | 0 | 0 | 269.716 | 0 | 1 | 10.5
4350 | 7/1 | 05:00:00 | 284.35 | 98835 | 3.5 | 255 | 7.4433 | 86.4 | 0 | 270.382 | 0 | 1 | 11.2
4351 | 7/1 | 06:00:00 | 285.65 | 98846 | 4 | 255 | 7.3415 | 417.6 | 435.6 | 271.573 | 0 | 1 | 12.5
4352 | 7/1 | 07:00:00 | 285.15 | 98841 | 3.6 | 250 | 7.8591 | 864 | 1026 | 271.588 | 0 | 1 | 12
4353 | 7/1 | 08:00:00 | 286.15 | 98850 | 4.6 | 260 | 7.3412 | 1396.8 | 1494 | 272.314 | 0 | 1 | 13
4354 | 7/1 | 09:00:00 | 287.15 | 98858 | 4.6 | 250 | 6.854 | 1911.6 | 1908 | 273.038 | 0 | 1 | 14
4355 | 7/1 | 10:00:00 | 286.15 | 98850 | 4.6 | 270 | 6.3971 | 2350.8 | 2059.2 | 271.858 | 0 | 1 | 13
4356 | 7/1 | 11:00:00 | 287.15 | 98858 | 3.6 | 240 | 6.854 | 2667.6 | 2250 | 273.038 | 0 | 1 | 14
4357 | 7/1 | 12:00:00 | 286.15 | 98850 | 3.6 | 260 | 7.3412 | 2844 | 2275.2 | 272.314 | 0 | 1 | 13
4358 | 7/1 | 13:00:00 | 288.15 | 98867 | 4.1 | 220 | 6.8534 | 2876.4 | 2286 | 273.988 | 0 | 1 | 15
4359 | 7/1 | 14:00:00 | 289.15 | 98875 | 5.1 | 250 | 6.8529 | 2746.8 | 2260.8 | 274.939 | 0 | 1 | 16
4360 | 7/1 | 15:00:00 | 289.15 | 98875 | 5.1 | 260 | 6.8529 | 2469.6 | 2210.4 | 274.939 | 0 | 1 | 16
4361 | 7/1 | 16:00:00 | 287.15 | 98858 | 3.6 | 240 | 7.3406 | 2062.8 | 1965.6 | 273.266 | 0 | 1 | 14
4362 | 7/1 | 17:00:00 | 288.15 | 98867 | 5.7 | 230 | 7.3399 | 1573.2 | 1609.2 | 274.218 | 0 | 1 | 15
4363 | 7/1 | 18:00:00 | 287.15 | 98858 | 3.1 | 230 | 6.854 | 1040.4 | 1209.6 | 273.038 | 0 | 1 | 14
4364 | 7/1 | 19:00:00 | 286.15 | 98850 | 3.6 | 230 | 6.8546 | 568.8 | 637.2 | 271.821 | 0 | 1 | 13
4365 | 7/1 | 20:00:00 | 286.15 | 98850 | 4.1 | 220 | 7.3412 | 169.2 | 68.4 | 272.048 | 0 | 1 | 13
4366 | 7/1 | 21:00:00 | 285.15 | 98841 | 3.6 | 190 | 7.8591 | 7.2 | 0 | 271.588 | 0 | 1 | 12
4367 | 7/1 | 22:00:00 | 285.15 | 98841 | 3.6 | 180 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
4368 | 7/1 | 23:00:00 | 285.15 | 98841 | 4.1 | 190 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
4369 | 7/1 | 24:00:00 | 285.15 | 98841 | 5.1 | 230 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
4370 | 7/2 | 01:00:00 | 285.15 | 98841 | 5.7 | 250 | 8.9926 | 0 | 0 | 272.036 | 0 | 1 | 12
4371 | 7/2 | 02:00:00 | 285.15 | 98841 | 5.1 | 250 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
4372 | 7/2 | 03:00:00 | 285.15 | 98841 | 6.2 | 270 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
4373 | 7/2 | 04:00:00 | 284.15 | 98833 | 5.7 | 280 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
4374 | 7/2 | 05:00:00 | 284.15 | 98833 | 4.1 | 260 | 7.3425 | 82.8 | 0 | 270.147 | 0 | 1 | 11
4375 | 7/2 | 06:00:00 | 284.15 | 98833 | 4.6 | 250 | 7.8598 | 388.8 | 406.8 | 270.636 | 0 | 1 | 11
4376 | 7/2 | 07:00:00 | 284.15 | 98833 | 4.6 | 260 | 7.8598 | 475.2 | 75.6 | 271.115 | 0 | 1 | 11
4377 | 7/2 | 08:00:00 | 285.15 | 98841 | 4.6 | 240 | 7.8591 | 1389.6 | 1252.8 | 271.588 | 0 | 1 | 12
4378 | 7/2 | 09:00:00 | 286.15 | 98850 | 6.2 | 250 | 7.8584 | 1900.8 | 1882.8 | 272.541 | 0 | 1 | 13
4379 | 7/2 | 10:00:00 | 285.15 | 98841 | 5.1 | 250 | 7.3418 | 2340 | 2037.6 | 271.363 | 0 | 1 | 12
4380 | 7/2 | 11:00:00 | 287.15 | 98858 | 5.7 | 270 | 6.854 | 2664 | 2246.4 | 273.038 | 0 | 1 | 14
4381 | 7/2 | 12:00:00 | 287.15 | 98858 | 7.2 | 250 | 6.3966 | 2851.2 | 2282.4 | 272.808 | 0 | 1 | 14
4382 | 7/2 | 13:00:00 | 288.15 | 98867 | 5.7 | 260 | 6.396 | 2876.4 | 2289.6 | 273.758 | 0 | 1 | 15
4383 | 7/2 | 14:00:00 | 289.15 | 98875 | 5.1 | 230 | 6.8529 | 2743.2 | 2260.8 | 274.939 | 0 | 1 | 16
4384 | 7/2 | 15:00:00 | 288.15 | 98867 | 5.7 | 230 | 6.396 | 2469.6 | 2214 | 273.758 | 0 | 1 | 15
4385 | 7/2 | 16:00:00 | 285.15 | 98841 | 3.6 | 240 | 7.3418 | 2062.8 | 1962 | 271.363 | 0 | 1 | 12
4386 | 7/2 | 17:00:00 | 286.15 | 98850 | 6.2 | 260 | 6.8546 | 1573.2 | 1612.8 | 272.087 | 0 | 1 | 13
4387 | 7/2 | 18:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.8564 | 1036.8 | 1206 | 269.234 | 0 | 1 | 10
4388 | 7/2 | 19:00:00 | 285.15 | 98841 | 5.1 | 250 | 7.3418 | 532.8 | 504 | 271.363 | 0 | 1 | 12
4389 | 7/2 | 20:00:00 | 284.15 | 98833 | 6.7 | 250 | 6.8558 | 158.4 | 21.6 | 270.185 | 0 | 1 | 11
4390 | 7/2 | 21:00:00 | 282.15 | 98815 | 4.6 | 270 | 5.9692 | 7.2 | 0 | 267.83 | 0 | 1 | 9
4391 | 7/2 | 22:00:00 | 281.15 | 98806 | 3.1 | 260 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
4392 | 7/2 | 23:00:00 | 281.15 | 98806 | 5.1 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
4393 | 7/2 | 24:00:00 | 281.15 | 98806 | 2.6 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
4394 | 7/3 | 01:00:00 | 281.15 | 98806 | 3.1 | 230 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
4395 | 7/3 | 02:00:00 | 282.15 | 98815 | 4.1 | 260 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
4396 | 7/3 | 03:00:00 | 281.15 | 98806 | 3.1 | 260 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
4397 | 7/3 | 04:00:00 | 281.15 | 98806 | 3.6 | 260 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
4398 | 7/3 | 05:00:00 | 281.15 | 98806 | 4.1 | 230 | 6.4 | 75.6 | 0 | 267.107 | 0 | 1 | 8
4399 | 7/3 | 06:00:00 | 282.15 | 98815 | 5.7 | 250 | 6.8571 | 385.2 | 327.6 | 268.283 | 0 | 1 | 9
4400 | 7/3 | 07:00:00 | 283.15 | 98824 | 7.2 | 250 | 6.8564 | 907.2 | 1202.4 | 268.971 | 0 | 1 | 10
4401 | 7/3 | 08:00:00 | 283.15 | 98824 | 5.7 | 230 | 6.8564 | 1389.6 | 1440 | 269.234 | 0 | 1 | 10
4402 | 7/3 | 09:00:00 | 283.15 | 98824 | 5.1 | 230 | 7.3431 | 1054.8 | 72 | 269.936 | 0 | 1 | 10
4403 | 7/3 | 10:00:00 | 284.15 | 98833 | 7.2 | 260 | 7.3425 | 1296 | 180 | 270.89 | 0 | 1 | 11
4404 | 7/3 | 11:00:00 | 285.15 | 98841 | 7.7 | 250 | 7.8591 | 2653.2 | 1857.6 | 271.588 | 0 | 1 | 12
4405 | 7/3 | 12:00:00 | 285.15 | 98841 | 6.2 | 250 | 7.8591 | 2833.2 | 2268 | 271.588 | 0 | 1 | 12
4406 | 7/3 | 13:00:00 | 286.15 | 98850 | 5.7 | 260 | 7.8584 | 2862 | 2271.6 | 272.541 | 0 | 1 | 13
4407 | 7/3 | 14:00:00 | 287.15 | 98858 | 8.8 | 250 | 7.3406 | 2736 | 2253.6 | 273.266 | 0 | 1 | 14
4408 | 7/3 | 15:00:00 | 287.15 | 98858 | 8.8 | 250 | 6.854 | 2466 | 2210.4 | 273.038 | 0 | 1 | 14
4409 | 7/3 | 16:00:00 | 288.15 | 98867 | 10.8 | 260 | 6.8534 | 2062.8 | 1972.8 | 273.988 | 0 | 1 | 15
4410 | 7/3 | 17:00:00 | 287.15 | 98858 | 9.3 | 260 | 6.3966 | 1573.2 | 1623.6 | 272.808 | 0 | 1 | 14
4411 | 7/3 | 18:00:00 | 288.15 | 98867 | 10.3 | 270 | 6.396 | 1036.8 | 1209.6 | 273.758 | 0 | 1 | 15
4412 | 7/3 | 19:00:00 | 287.15 | 98858 | 10.8 | 270 | 6.3966 | 532.8 | 507.6 | 272.808 | 0 | 1 | 14
4413 | 7/3 | 20:00:00 | 286.15 | 98850 | 7.2 | 260 | 6.8546 | 158.4 | 18 | 272.087 | 0 | 1 | 13
4414 | 7/3 | 21:00:00 | 284.15 | 98833 | 6.2 | 270 | 7.3425 | 7.2 | 0 | 270.411 | 0 | 1 | 11
4415 | 7/3 | 22:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
4416 | 7/3 | 23:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4417 | 7/3 | 24:00:00 | 283.15 | 98824 | 5.1 | 250 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4418 | 7/4 | 01:00:00 | 283.15 | 98824 | 3.1 | 260 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4419 | 7/4 | 02:00:00 | 282.15 | 98815 | 3.1 | 240 | 7.3438 | 0 | 0 | 268.245 | 0 | 1 | 9
4420 | 7/4 | 03:00:00 | 282.15 | 98815 | 2.6 | 230 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
4421 | 7/4 | 04:00:00 | 282.15 | 98815 | 3.1 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
4422 | 7/4 | 05:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.8571 | 79.2 | 0 | 268.021 | 0 | 1 | 9
4423 | 7/4 | 06:00:00 | 283.15 | 98824 | 2.6 | 240 | 7.3431 | 378 | 320.4 | 269.46 | 0 | 1 | 10
4424 | 7/4 | 07:00:00 | 285.15 | 98841 | 3.1 | 240 | 7.8591 | 849.6 | 972 | 271.588 | 0 | 1 | 12
4425 | 7/4 | 08:00:00 | 286.15 | 98850 | 5.7 | 260 | 7.8584 | 1378.8 | 1476 | 272.541 | 0 | 1 | 13
4426 | 7/4 | 09:00:00 | 286.15 | 98850 | 5.7 | 250 | 6.8546 | 1897.2 | 1897.2 | 272.087 | 0 | 1 | 13
4427 | 7/4 | 10:00:00 | 287.15 | 98858 | 6.7 | 260 | 6.854 | 2336.4 | 2044.8 | 273.038 | 0 | 1 | 14
4428 | 7/4 | 11:00:00 | 287.15 | 98858 | 6.7 | 250 | 5.9666 | 2667.6 | 2260.8 | 272.576 | 0 | 1 | 14
4429 | 7/4 | 12:00:00 | 288.15 | 98867 | 6.7 | 260 | 5.9661 | 2847.6 | 2289.6 | 273.525 | 0 | 1 | 15
4430 | 7/4 | 13:00:00 | 289.15 | 98875 | 8.2 | 270 | 5.1824 | 2883.6 | 2318.4 | 274.004 | 0 | 1 | 16
4431 | 7/4 | 14:00:00 | 289.15 | 98875 | 8.8 | 270 | 5.5617 | 2750.4 | 2282.4 | 274.24 | 0 | 1 | 16
4432 | 7/4 | 15:00:00 | 289.15 | 98875 | 8.2 | 270 | 5.9656 | 2469.6 | 2224.8 | 274.475 | 0 | 1 | 16
4433 | 7/4 | 16:00:00 | 290.15 | 98883 | 8.2 | 270 | 5.9651 | 2070 | 2134.8 | 275.424 | 0 | 1 | 17
4434 | 7/4 | 17:00:00 | 289.15 | 98875 | 8.2 | 270 | 5.5617 | 1674 | 2145.6 | 273.972 | 0 | 1 | 16
4435 | 7/4 | 18:00:00 | 288.15 | 98867 | 8.8 | 290 | 5.1829 | 1116 | 1483.2 | 272.649 | 0 | 1 | 15
4436 | 7/4 | 19:00:00 | 288.15 | 98867 | 6.7 | 280 | 5.9661 | 561.6 | 630 | 273.258 | 0 | 1 | 15
4437 | 7/4 | 20:00:00 | 287.15 | 98858 | 5.1 | 290 | 6.3966 | 162 | 36 | 272.808 | 0 | 1 | 14
4438 | 7/4 | 21:00:00 | 285.15 | 98841 | 2.6 | 280 | 6.3977 | 3.6 | 0 | 271.033 | 0 | 1 | 12
4439 | 7/4 | 22:00:00 | 284.15 | 98833 | 2.1 | 270 | 6.3982 | 0 | 0 | 270.204 | 0 | 1 | 11
4440 | 7/4 | 23:00:00 | 283.15 | 98824 | 1.5 | 270 | 6.3988 | 0 | 0 | 269.37 | 0 | 1 | 10
4441 | 7/4 | 24:00:00 | 284.15 | 98833 | 1.5 | 310 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
4442 | 7/5 | 01:00:00 | 284.15 | 98833 | 1.5 | 260 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
4443 | 7/5 | 02:00:00 | 284.15 | 98833 | 0 | 262 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
4444 | 7/5 | 03:00:00 | 283.15 | 98824 | 1.5 | 190 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
4445 | 7/5 | 04:00:00 | 284.15 | 98833 | 1.5 | 200 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
4446 | 7/5 | 05:00:00 | 284.15 | 98833 | 2.1 | 190 | 6.8558 | 57.6 | 0 | 270.549 | 0 | 1 | 11
4447 | 7/5 | 06:00:00 | 284.15 | 98833 | 2.1 | 170 | 7.3425 | 241.2 | 0 | 270.89 | 0 | 1 | 11
4448 | 7/5 | 07:00:00 | 286.15 | 98850 | 2.1 | 180 | 7.3412 | 730.8 | 543.6 | 272.563 | 0 | 1 | 13
4449 | 7/5 | 08:00:00 | 287.15 | 98858 | 2.1 | 180 | 7.3406 | 1292.4 | 1152 | 273.393 | 0 | 1 | 14
4450 | 7/5 | 09:00:00 | 289.15 | 98875 | 3.6 | 190 | 6.8529 | 2008.8 | 2235.6 | 274.67 | 0 | 1 | 16
4451 | 7/5 | 10:00:00 | 290.15 | 98883 | 4.1 | 190 | 6.8523 | 2473.2 | 2574 | 275.62 | 0 | 1 | 17
4452 | 7/5 | 11:00:00 | 291.15 | 98892 | 4.1 | 190 | 6.3944 | 2660.4 | 2185.2 | 276.608 | 0 | 1 | 18
4453 | 7/5 | 12:00:00 | 292.15 | 98900 | 4.6 | 200 | 6.8511 | 2836.8 | 2278.8 | 277.792 | 0 | 1 | 19
4454 | 7/5 | 13:00:00 | 293.15 | 98908 | 4.6 | 200 | 6.8506 | 2865.6 | 2286 | 278.743 | 0 | 1 | 20
4455 | 7/5 | 14:00:00 | 293.15 | 98908 | 4.6 | 190 | 6.8506 | 2736 | 1897.2 | 278.743 | 0 | 1 | 20
4456 | 7/5 | 15:00:00 | 291.15 | 98892 | 3.6 | 220 | 7.338 | 1364.4 | 183.6 | 277.563 | 0 | 1 | 18
4457 | 7/5 | 16:00:00 | 290.15 | 98883 | 3.1 | 220 | 8.4052 | 1137.6 | 100.8 | 277.068 | 0 | 1 | 17
4458 | 7/5 | 17:00:00 | 290.15 | 98883 | 4.6 | 190 | 8.4052 | 867.6 | 108 | 277.068 | 0 | 1 | 17
4459 | 7/5 | 18:00:00 | 288.15 | 98867 | 3.1 | 200 | 10.2677 | 1022.4 | 982.8 | 275.344 | 0 | 1 | 15
4460 | 7/5 | 19:00:00 | 288.15 | 98867 | 3.6 | 200 | 10.2677 | 525.6 | 709.2 | 275.344 | 0 | 1 | 15
4461 | 7/5 | 20:00:00 | 288.15 | 98867 | 3.1 | 210 | 10.9655 | 86.4 | 0 | 276.053 | 0 | 1 | 15
4462 | 7/5 | 21:00:00 | 288.15 | 98867 | 2.6 | 220 | 10.2677 | 3.6 | 0 | 275.344 | 0 | 1 | 15
4463 | 7/5 | 22:00:00 | 288.15 | 98867 | 6.2 | 220 | 9.6099 | 0 | 0 | 275.122 | 0 | 1 | 15
4464 | 7/5 | 23:00:00 | 287.15 | 98858 | 5.7 | 240 | 9.6108 | 0 | 0 | 274.167 | 0 | 1 | 14
4465 | 7/5 | 24:00:00 | 287.15 | 98858 | 5.1 | 240 | 8.991 | 0 | 0 | 273.944 | 0 | 1 | 14
4466 | 7/6 | 01:00:00 | 286.15 | 98850 | 4.1 | 260 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
4467 | 7/6 | 02:00:00 | 286.15 | 98850 | 4.6 | 250 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
4468 | 7/6 | 03:00:00 | 286.15 | 98850 | 8.2 | 270 | 9.6116 | 0 | 0 | 273.695 | 0 | 1 | 13
4469 | 7/6 | 04:00:00 | 286.15 | 98850 | 4.6 | 290 | 9.6116 | 0 | 0 | 273.695 | 0 | 1 | 13
4470 | 7/6 | 05:00:00 | 285.15 | 98841 | 5.7 | 320 | 8.4088 | 72 | 0 | 271.813 | 0 | 1 | 12
4471 | 7/6 | 06:00:00 | 285.15 | 98841 | 4.6 | 330 | 7.8591 | 370.8 | 309.6 | 271.588 | 0 | 1 | 12
4472 | 7/6 | 07:00:00 | 285.15 | 98841 | 6.7 | 310 | 7.3418 | 838.8 | 964.8 | 271.363 | 0 | 1 | 12
4473 | 7/6 | 08:00:00 | 286.15 | 98850 | 8.8 | 310 | 7.3412 | 1454.4 | 1814.4 | 272.048 | 0 | 1 | 13
4474 | 7/6 | 09:00:00 | 287.15 | 98858 | 7.2 | 300 | 7.3406 | 1886.4 | 2016 | 273.266 | 0 | 1 | 14
4475 | 7/6 | 10:00:00 | 287.15 | 98858 | 6.7 | 310 | 7.3406 | 2322 | 2034 | 273.266 | 0 | 1 | 14
4476 | 7/6 | 11:00:00 | 289.15 | 98875 | 7.2 | 300 | 6.8529 | 2649.6 | 2246.4 | 274.939 | 0 | 1 | 16
4477 | 7/6 | 12:00:00 | 290.15 | 98883 | 7.2 | 300 | 7.3387 | 2829.6 | 2271.6 | 276.121 | 0 | 1 | 17
4478 | 7/6 | 13:00:00 | 289.15 | 98875 | 7.2 | 290 | 7.3393 | 2858.4 | 2275.2 | 275.169 | 0 | 1 | 16
4479 | 7/6 | 14:00:00 | 290.15 | 98883 | 7.2 | 280 | 7.3387 | 2728.8 | 2253.6 | 276.121 | 0 | 1 | 17
4480 | 7/6 | 15:00:00 | 291.15 | 98892 | 7.7 | 270 | 7.338 | 2455.2 | 2142 | 277.073 | 0 | 1 | 18
4481 | 7/6 | 16:00:00 | 289.15 | 98875 | 8.8 | 280 | 6.8529 | 2185.2 | 2440.8 | 274.67 | 0 | 1 | 16
4482 | 7/6 | 17:00:00 | 288.15 | 98867 | 9.8 | 270 | 6.396 | 1663.2 | 2037.6 | 273.49 | 0 | 1 | 15
4483 | 7/6 | 18:00:00 | 288.15 | 98867 | 8.2 | 280 | 6.8534 | 1094.4 | 1407.6 | 273.72 | 0 | 1 | 15
4484 | 7/6 | 19:00:00 | 288.15 | 98867 | 10.8 | 280 | 6.396 | 558 | 626.4 | 273.49 | 0 | 1 | 15
4485 | 7/6 | 20:00:00 | 287.15 | 98858 | 6.2 | 280 | 6.854 | 162 | 57.6 | 272.77 | 0 | 1 | 14
4486 | 7/6 | 21:00:00 | 285.15 | 98841 | 6.2 | 280 | 6.8552 | 3.6 | 0 | 270.871 | 0 | 1 | 12
4487 | 7/6 | 22:00:00 | 284.15 | 98833 | 6.7 | 290 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
4488 | 7/6 | 23:00:00 | 283.15 | 98824 | 5.7 | 290 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
4489 | 7/6 | 24:00:00 | 283.15 | 98824 | 3.1 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
4490 | 7/7 | 01:00:00 | 282.15 | 98815 | 4.6 | 290 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
4491 | 7/7 | 02:00:00 | 282.15 | 98815 | 6.2 | 290 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
4492 | 7/7 | 03:00:00 | 281.15 | 98806 | 4.6 | 270 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
4493 | 7/7 | 04:00:00 | 282.15 | 98815 | 5.1 | 280 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
4494 | 7/7 | 05:00:00 | 282.15 | 98815 | 5.1 | 280 | 6.8571 | 32.4 | 0 | 268.867 | 0 | 1 | 9
4495 | 7/7 | 06:00:00 | 282.15 | 98815 | 4.1 | 290 | 6.8571 | 165.6 | 0 | 268.867 | 0 | 1 | 9
4496 | 7/7 | 07:00:00 | 283.15 | 98824 | 3.6 | 270 | 7.3431 | 378 | 0 | 270.046 | 0 | 1 | 10
4497 | 7/7 | 08:00:00 | 285.15 | 98841 | 3.1 | 280 | 7.3418 | 1047.6 | 568.8 | 271.729 | 0 | 1 | 12
4498 | 7/7 | 09:00:00 | 286.15 | 98850 | 2.6 | 280 | 6.8546 | 1882.8 | 1789.2 | 272.087 | 0 | 1 | 13
4499 | 7/7 | 10:00:00 | 287.15 | 98858 | 3.6 | 280 | 6.3966 | 2325.6 | 2052 | 272.808 | 0 | 1 | 14
4500 | 7/7 | 11:00:00 | 288.15 | 98867 | 3.1 | 260 | 6.8534 | 2646 | 2242.8 | 273.988 | 0 | 1 | 15
4501 | 7/7 | 12:00:00 | 289.15 | 98875 | 4.1 | 260 | 7.3393 | 2826 | 2268 | 275.169 | 0 | 1 | 16
4502 | 7/7 | 13:00:00 | 289.15 | 98875 | 5.7 | 250 | 7.8564 | 2851.2 | 2271.6 | 275.398 | 0 | 1 | 16
4503 | 7/7 | 14:00:00 | 289.15 | 98875 | 5.1 | 260 | 7.8564 | 2721.6 | 2250 | 275.398 | 0 | 1 | 16
4504 | 7/7 | 15:00:00 | 289.15 | 98875 | 6.2 | 270 | 7.3393 | 2451.6 | 2206.8 | 275.169 | 0 | 1 | 16
4505 | 7/7 | 16:00:00 | 289.15 | 98875 | 4.6 | 250 | 7.3393 | 2052 | 2102.4 | 275.169 | 0 | 1 | 16
4506 | 7/7 | 17:00:00 | 289.15 | 98875 | 3.6 | 260 | 7.8564 | 1652.4 | 2091.6 | 275.129 | 0 | 1 | 16
4507 | 7/7 | 18:00:00 | 289.15 | 98875 | 2.1 | 260 | 8.4059 | 1083.6 | 1375.2 | 275.356 | 0 | 1 | 16
4508 | 7/7 | 19:00:00 | 289.15 | 98875 | 1 | 102 | 8.4059 | 522 | 590.4 | 275.626 | 0 | 1 | 16
4509 | 7/7 | 20:00:00 | 288.15 | 98867 | 1.5 | 117 | 8.9902 | 151.2 | 7.2 | 274.898 | 0 | 1 | 15
4510 | 7/7 | 21:00:00 | 288.15 | 98867 | 1.5 | 280 | 8.9902 | 3.6 | 0 | 274.629 | 0 | 1 | 15
4511 | 7/7 | 22:00:00 | 288.15 | 98867 | 2.1 | 210 | 8.9902 | 0 | 0 | 274.629 | 0 | 1 | 15
4512 | 7/7 | 23:00:00 | 288.15 | 98867 | 3.6 | 230 | 8.4065 | 0 | 0 | 274.404 | 0 | 1 | 15
4513 | 7/7 | 24:00:00 | 288.15 | 98867 | 4.1 | 240 | 8.4065 | 0 | 0 | 274.404 | 0 | 1 | 15
4514 | 7/8 | 01:00:00 | 287.15 | 98858 | 4.1 | 230 | 8.4073 | 0 | 0 | 274.203 | 0 | 1 | 14
4515 | 7/8 | 02:00:00 | 287.15 | 98858 | 4.6 | 230 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
4516 | 7/8 | 03:00:00 | 287.15 | 98858 | 4.1 | 240 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
4517 | 7/8 | 04:00:00 | 286.15 | 98850 | 4.6 | 250 | 8.9918 | 0 | 0 | 272.99 | 0 | 1 | 13
4518 | 7/8 | 05:00:00 | 286.15 | 98850 | 4.1 | 250 | 8.9918 | 68.4 | 0 | 272.99 | 0 | 1 | 13
4519 | 7/8 | 06:00:00 | 287.15 | 98858 | 4.1 | 250 | 8.991 | 360 | 349.2 | 273.944 | 0 | 1 | 14
4520 | 7/8 | 07:00:00 | 287.15 | 98858 | 4.6 | 240 | 9.6108 | 820.8 | 925.2 | 274.167 | 0 | 1 | 14
4521 | 7/8 | 08:00:00 | 288.15 | 98867 | 4.6 | 230 | 9.6099 | 1350 | 1533.6 | 275.122 | 0 | 1 | 15
4522 | 7/8 | 09:00:00 | 288.15 | 98867 | 5.7 | 240 | 9.6099 | 1861.2 | 1670.4 | 275.122 | 0 | 1 | 15
4523 | 7/8 | 10:00:00 | 290.15 | 98883 | 5.7 | 240 | 10.266 | 1274.4 | 115.2 | 277.746 | 0 | 1 | 17
4524 | 7/8 | 11:00:00 | 290.15 | 98883 | 6.7 | 230 | 10.266 | 1450.8 | 154.8 | 277.746 | 0 | 1 | 17
4525 | 7/8 | 12:00:00 | 289.15 | 98875 | 5.7 | 270 | 10.2668 | 1551.6 | 367.2 | 276.789 | 0 | 1 | 16
4526 | 7/8 | 13:00:00 | 290.15 | 98883 | 5.1 | 260 | 10.9637 | 2826 | 1526.4 | 277.478 | 0 | 1 | 17
4527 | 7/8 | 14:00:00 | 292.15 | 98900 | 5.7 | 260 | 10.2642 | 1501.2 | 280.8 | 279.66 | 0 | 1 | 19
4528 | 7/8 | 15:00:00 | 292.15 | 98900 | 5.7 | 260 | 9.6067 | 2433.6 | 1843.2 | 278.941 | 0 | 1 | 19
4529 | 7/8 | 16:00:00 | 292.15 | 98900 | 5.7 | 280 | 10.2642 | 2034 | 1983.6 | 279.166 | 0 | 1 | 19
4530 | 7/8 | 17:00:00 | 292.15 | 98900 | 3.6 | 260 | 10.2642 | 1544.4 | 1663.2 | 279.166 | 0 | 1 | 19
4531 | 7/8 | 18:00:00 | 292.15 | 98900 | 5.7 | 260 | 9.6067 | 1015.2 | 1242 | 278.941 | 0 | 1 | 19
4532 | 7/8 | 19:00:00 | 291.15 | 98892 | 5.1 | 270 | 9.6075 | 518.4 | 576 | 277.986 | 0 | 1 | 18
4533 | 7/8 | 20:00:00 | 291.15 | 98892 | 4.6 | 270 | 9.6075 | 147.6 | 3.6 | 277.986 | 0 | 1 | 18
4534 | 7/8 | 21:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.2668 | 0 | 0 | 276.3 | 0 | 1 | 16
4535 | 7/8 | 22:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
4536 | 7/8 | 23:00:00 | 288.15 | 98867 | 4.6 | 220 | 10.2677 | 0 | 0 | 275.831 | 0 | 1 | 15
4537 | 7/8 | 24:00:00 | 288.15 | 98867 | 4.6 | 220 | 10.2677 | 0 | 0 | 275.344 | 0 | 1 | 15
4538 | 7/9 | 01:00:00 | 288.15 | 98867 | 2.1 | 220 | 9.6099 | 0 | 0 | 274.852 | 0 | 1 | 15
4539 | 7/9 | 02:00:00 | 287.15 | 98858 | 3.6 | 220 | 9.6108 | 0 | 0 | 274.167 | 0 | 1 | 14
4540 | 7/9 | 03:00:00 | 288.15 | 98867 | 2.6 | 210 | 10.2677 | 0 | 0 | 275.831 | 0 | 1 | 15
4541 | 7/9 | 04:00:00 | 288.15 | 98867 | 3.6 | 210 | 10.2677 | 0 | 0 | 275.831 | 0 | 1 | 15
4542 | 7/9 | 05:00:00 | 287.15 | 98858 | 3.6 | 220 | 10.2686 | 36 | 0 | 274.874 | 0 | 1 | 14
4543 | 7/9 | 06:00:00 | 287.15 | 98858 | 6.2 | 250 | 10.2686 | 194.4 | 0 | 274.874 | 0 | 1 | 14
4544 | 7/9 | 07:00:00 | 287.15 | 98858 | 6.7 | 250 | 10.2686 | 450 | 18 | 274.874 | 0 | 1 | 14
4545 | 7/9 | 08:00:00 | 287.15 | 98858 | 5.1 | 250 | 9.6108 | 745.2 | 68.4 | 274.652 | 0 | 1 | 14
4546 | 7/9 | 09:00:00 | 287.15 | 98858 | 5.1 | 270 | 9.6108 | 1029.6 | 75.6 | 274.652 | 0 | 1 | 14
4547 | 7/9 | 10:00:00 | 287.15 | 98858 | 4.6 | 270 | 8.991 | 1274.4 | 104.4 | 274.428 | 0 | 1 | 14
4548 | 7/9 | 11:00:00 | 288.15 | 98867 | 7.2 | 260 | 9.6099 | 1450.8 | 154.8 | 275.608 | 0 | 1 | 15
4549 | 7/9 | 12:00:00 | 287.15 | 98858 | 6.2 | 270 | 9.6108 | 1551.6 | 154.8 | 274.652 | 0 | 1 | 14
4550 | 7/9 | 13:00:00 | 288.15 | 98867 | 8.2 | 260 | 8.9902 | 1573.2 | 158.4 | 275.384 | 0 | 1 | 15
4551 | 7/9 | 14:00:00 | 288.15 | 98867 | 7.7 | 280 | 8.4065 | 1504.8 | 370.8 | 275.158 | 0 | 1 | 15
4552 | 7/9 | 15:00:00 | 288.15 | 98867 | 8.8 | 270 | 8.4065 | 2437.2 | 1857.6 | 274.672 | 0 | 1 | 15
4553 | 7/9 | 16:00:00 | 290.15 | 98883 | 8.8 | 270 | 8.4052 | 2041.2 | 2008.8 | 276.579 | 0 | 1 | 17
4554 | 7/9 | 17:00:00 | 289.15 | 98875 | 8.2 | 260 | 8.4059 | 1548 | 1684.8 | 275.626 | 0 | 1 | 16
4555 | 7/9 | 18:00:00 | 289.15 | 98875 | 8.8 | 270 | 8.4059 | 1015.2 | 1249.2 | 275.626 | 0 | 1 | 16
4556 | 7/9 | 19:00:00 | 289.15 | 98875 | 5.1 | 270 | 8.4059 | 514.8 | 576 | 275.626 | 0 | 1 | 16
4557 | 7/9 | 20:00:00 | 289.15 | 98875 | 5.1 | 270 | 8.4059 | 147.6 | 3.6 | 275.626 | 0 | 1 | 16
4558 | 7/9 | 21:00:00 | 287.15 | 98858 | 2.1 | 270 | 8.4073 | 0 | 0 | 273.451 | 0 | 1 | 14
4559 | 7/9 | 22:00:00 | 286.15 | 98850 | 1.5 | 226 | 8.408 | 0 | 0 | 272.499 | 0 | 1 | 13
4560 | 7/9 | 23:00:00 | 285.15 | 98841 | 1.5 | 64 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
4561 | 7/9 | 24:00:00 | 285.15 | 98841 | 2.1 | 210 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
4562 | 7/10 | 01:00:00 | 286.15 | 98850 | 1.5 | 263 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
4563 | 7/10 | 02:00:00 | 287.15 | 98858 | 3.1 | 240 | 8.991 | 0 | 0 | 273.676 | 0 | 1 | 14
4564 | 7/10 | 03:00:00 | 287.15 | 98858 | 1 | 34 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
4565 | 7/10 | 04:00:00 | 287.15 | 98858 | 2.6 | 210 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
4566 | 7/10 | 05:00:00 | 287.15 | 98858 | 3.6 | 210 | 9.6108 | 36 | 0 | 274.652 | 0 | 1 | 14
4567 | 7/10 | 06:00:00 | 288.15 | 98867 | 3.1 | 210 | 9.6099 | 349.2 | 403.2 | 275.122 | 0 | 1 | 15
4568 | 7/10 | 07:00:00 | 288.15 | 98867 | 2.6 | 220 | 10.2677 | 446.4 | 25.2 | 275.831 | 0 | 1 | 15
4569 | 7/10 | 08:00:00 | 288.15 | 98867 | 2.6 | 210 | 10.2677 | 741.6 | 64.8 | 275.831 | 0 | 1 | 15
4570 | 7/10 | 09:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.2668 | 1026 | 75.6 | 276.789 | 0 | 1 | 16
4571 | 7/10 | 10:00:00 | 288.15 | 98867 | 4.1 | 210 | 10.9655 | 1267.2 | 104.4 | 276.053 | 0 | 1 | 15
4572 | 7/10 | 11:00:00 | 289.15 | 98875 | 4.1 | 200 | 11.7047 | 1443.6 | 151.2 | 277.232 | 0 | 1 | 16
4573 | 7/10 | 12:00:00 | 289.15 | 98875 | 3.6 | 230 | 10.9646 | 1544.4 | 154.8 | 277.011 | 0 | 1 | 16
4574 | 7/10 | 13:00:00 | 289.15 | 98875 | 3.1 | 220 | 11.7047 | 1558.8 | 154.8 | 277.232 | 0 | 1 | 16
4575 | 7/10 | 14:00:00 | 290.15 | 98883 | 3.1 | 210 | 11.7037 | 1490.4 | 360 | 278.191 | 0 | 1 | 17
4576 | 7/10 | 15:00:00 | 292.15 | 98900 | 5.1 | 210 | 12.4861 | 2412 | 1958.4 | 279.836 | 0 | 1 | 19
4577 | 7/10 | 16:00:00 | 293.15 | 98908 | 7.7 | 220 | 12.485 | 2019.6 | 2120.4 | 280.793 | 0 | 1 | 20
4578 | 7/10 | 17:00:00 | 292.15 | 98900 | 6.7 | 220 | 12.4861 | 1530 | 1760.4 | 279.836 | 0 | 1 | 19
4579 | 7/10 | 18:00:00 | 292.15 | 98900 | 6.2 | 220 | 12.4861 | 1004.4 | 1303.2 | 279.836 | 0 | 1 | 19
4580 | 7/10 | 19:00:00 | 291.15 | 98892 | 5.7 | 220 | 12.4871 | 507.6 | 594 | 278.878 | 0 | 1 | 18
4581 | 7/10 | 20:00:00 | 290.15 | 98883 | 6.7 | 220 | 12.4883 | 144 | 0 | 277.92 | 0 | 1 | 17
4582 | 7/10 | 21:00:00 | 290.15 | 98883 | 6.2 | 220 | 12.4883 | 0 | 0 | 277.92 | 0 | 1 | 17
4583 | 7/10 | 22:00:00 | 290.15 | 98883 | 8.2 | 220 | 11.7037 | 0 | 0 | 278.191 | 0 | 1 | 17
4584 | 7/10 | 23:00:00 | 289.15 | 98875 | 7.2 | 220 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
4585 | 7/10 | 24:00:00 | 289.15 | 98875 | 5.7 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
4586 | 7/11 | 01:00:00 | 289.15 | 98875 | 6.2 | 200 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
4587 | 7/11 | 02:00:00 | 289.15 | 98875 | 6.2 | 210 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
4588 | 7/11 | 03:00:00 | 289.15 | 98875 | 4.1 | 240 | 10.2668 | 0 | 0 | 276.3 | 0 | 1 | 16
4589 | 7/11 | 04:00:00 | 288.15 | 98867 | 5.7 | 240 | 9.6099 | 0 | 0 | 275.122 | 0 | 1 | 15
4590 | 7/11 | 05:00:00 | 288.15 | 98867 | 3.1 | 250 | 9.6099 | 64.8 | 0 | 275.122 | 0 | 1 | 15
4591 | 7/11 | 06:00:00 | 288.15 | 98867 | 3.1 | 250 | 9.6099 | 190.8 | 0 | 275.608 | 0 | 1 | 15
4592 | 7/11 | 07:00:00 | 288.15 | 98867 | 2.1 | 220 | 10.2677 | 799.2 | 792 | 275.344 | 0 | 1 | 15
4593 | 7/11 | 08:00:00 | 290.15 | 98883 | 5.1 | 230 | 10.266 | 1328.4 | 1508.4 | 277.255 | 0 | 1 | 17
4594 | 7/11 | 09:00:00 | 290.15 | 98883 | 5.1 | 230 | 9.6084 | 1843.2 | 1659.6 | 277.031 | 0 | 1 | 17
4595 | 7/11 | 10:00:00 | 291.15 | 98892 | 6.2 | 230 | 8.9879 | 1267.2 | 313.2 | 278.251 | 0 | 1 | 18
4596 | 7/11 | 11:00:00 | 290.15 | 98883 | 5.1 | 220 | 8.9887 | 2610 | 1828.8 | 276.806 | 0 | 1 | 17
4597 | 7/11 | 12:00:00 | 291.15 | 98892 | 4.6 | 230 | 9.6075 | 2790 | 2253.6 | 277.986 | 0 | 1 | 18
4598 | 7/11 | 13:00:00 | 291.15 | 98892 | 6.2 | 230 | 9.6075 | 2822.4 | 2257.2 | 277.986 | 0 | 1 | 18
4599 | 7/11 | 14:00:00 | 292.15 | 98900 | 6.2 | 240 | 9.6067 | 2696.4 | 2235.6 | 278.941 | 0 | 1 | 19
4600 | 7/11 | 15:00:00 | 292.15 | 98900 | 6.7 | 230 | 9.6067 | 2422.8 | 2019.6 | 278.941 | 0 | 1 | 19
4601 | 7/11 | 16:00:00 | 290.15 | 98883 | 5.7 | 220 | 10.266 | 2023.2 | 1980 | 277.255 | 0 | 1 | 17
4602 | 7/11 | 17:00:00 | 291.15 | 98892 | 4.6 | 230 | 10.265 | 1533.6 | 1656 | 278.211 | 0 | 1 | 18
4603 | 7/11 | 18:00:00 | 292.15 | 98900 | 3.6 | 250 | 9.6067 | 1004.4 | 1231.2 | 278.941 | 0 | 1 | 19
4604 | 7/11 | 19:00:00 | 290.15 | 98883 | 6.2 | 240 | 8.4052 | 507.6 | 568.8 | 276.579 | 0 | 1 | 17
4605 | 7/11 | 20:00:00 | 289.15 | 98875 | 4.6 | 220 | 8.9895 | 140.4 | 0 | 275.852 | 0 | 1 | 16
4606 | 7/11 | 21:00:00 | 289.15 | 98875 | 5.7 | 210 | 8.9895 | 0 | 0 | 275.852 | 0 | 1 | 16
4607 | 7/11 | 22:00:00 | 288.15 | 98867 | 4.6 | 200 | 8.9902 | 0 | 0 | 274.898 | 0 | 1 | 15
4608 | 7/11 | 23:00:00 | 288.15 | 98867 | 5.7 | 210 | 8.9902 | 0 | 0 | 274.898 | 0 | 1 | 15
4609 | 7/11 | 24:00:00 | 287.15 | 98858 | 5.7 | 210 | 8.991 | 0 | 0 | 273.944 | 0 | 1 | 14
4610 | 7/12 | 01:00:00 | 287.15 | 98858 | 6.7 | 210 | 8.991 | 0 | 0 | 273.944 | 0 | 1 | 14
4611 | 7/12 | 02:00:00 | 287.15 | 98858 | 5.7 | 220 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
4612 | 7/12 | 03:00:00 | 287.15 | 98858 | 5.7 | 220 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
4613 | 7/12 | 04:00:00 | 287.15 | 98858 | 6.2 | 220 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
4614 | 7/12 | 05:00:00 | 286.15 | 98850 | 6.2 | 220 | 9.6116 | 36 | 0 | 273.695 | 0 | 1 | 13
4615 | 7/12 | 06:00:00 | 286.15 | 98850 | 5.1 | 220 | 9.6116 | 187.2 | 0 | 273.695 | 0 | 1 | 13
4616 | 7/12 | 07:00:00 | 287.15 | 98858 | 5.1 | 250 | 9.6108 | 439.2 | 18 | 274.652 | 0 | 1 | 14
4617 | 7/12 | 08:00:00 | 287.15 | 98858 | 6.2 | 260 | 10.2686 | 734.4 | 64.8 | 274.874 | 0 | 1 | 14
4618 | 7/12 | 09:00:00 | 288.15 | 98867 | 6.2 | 260 | 10.2677 | 1018.8 | 230.4 | 275.831 | 0 | 1 | 15
4619 | 7/12 | 10:00:00 | 288.15 | 98867 | 7.2 | 260 | 10.2677 | 2271.6 | 1807.2 | 275.344 | 0 | 1 | 15
4620 | 7/12 | 11:00:00 | 287.15 | 98858 | 9.3 | 270 | 9.6108 | 2599.2 | 1814.4 | 274.167 | 0 | 1 | 14
4621 | 7/12 | 12:00:00 | 288.15 | 98867 | 7.7 | 270 | 9.6099 | 1544.4 | 367.2 | 275.608 | 0 | 1 | 15
4622 | 7/12 | 13:00:00 | 288.15 | 98867 | 7.7 | 270 | 10.2677 | 1558.8 | 367.2 | 275.831 | 0 | 1 | 15
4623 | 7/12 | 14:00:00 | 289.15 | 98875 | 8.2 | 260 | 10.2668 | 2689.2 | 1828.8 | 276.3 | 0 | 1 | 16
4624 | 7/12 | 15:00:00 | 289.15 | 98875 | 8.2 | 260 | 9.6091 | 2419.2 | 2016 | 276.076 | 0 | 1 | 16
4625 | 7/12 | 16:00:00 | 288.15 | 98867 | 9.3 | 270 | 9.6099 | 2023.2 | 1987.2 | 275.122 | 0 | 1 | 15
4626 | 7/12 | 17:00:00 | 289.15 | 98875 | 8.2 | 280 | 8.9895 | 1533.6 | 1670.4 | 275.852 | 0 | 1 | 16
4627 | 7/12 | 18:00:00 | 289.15 | 98875 | 9.3 | 270 | 8.4059 | 1004.4 | 1238.4 | 275.626 | 0 | 1 | 16
4628 | 7/12 | 19:00:00 | 288.15 | 98867 | 7.2 | 270 | 8.9902 | 504 | 558 | 274.898 | 0 | 1 | 15
4629 | 7/12 | 20:00:00 | 287.15 | 98858 | 6.7 | 270 | 8.991 | 140.4 | 0 | 273.944 | 0 | 1 | 14
4630 | 7/12 | 21:00:00 | 286.15 | 98850 | 5.1 | 270 | 8.408 | 0 | 0 | 272.499 | 0 | 1 | 13
4631 | 7/12 | 22:00:00 | 285.15 | 98841 | 3.6 | 270 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
4632 | 7/12 | 23:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
4633 | 7/12 | 24:00:00 | 284.15 | 98833 | 2.6 | 280 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
4634 | 7/13 | 01:00:00 | 283.15 | 98824 | 2.1 | 270 | 7.8605 | 0 | 0 | 269.684 | 0 | 1 | 10
4635 | 7/13 | 02:00:00 | 284.15 | 98833 | 4.6 | 280 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
4636 | 7/13 | 03:00:00 | 284.15 | 98833 | 4.1 | 280 | 8.4095 | 0 | 0 | 271.449 | 0 | 1 | 11
4637 | 7/13 | 04:00:00 | 284.15 | 98833 | 4.1 | 300 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
4638 | 7/13 | 05:00:00 | 284.15 | 98833 | 1.5 | 280 | 7.8598 | 64.8 | 0 | 270.371 | 0 | 1 | 11
4639 | 7/13 | 06:00:00 | 284.15 | 98833 | 3.6 | 290 | 7.8598 | 352.8 | 338.4 | 270.371 | 0 | 1 | 11
4640 | 7/13 | 07:00:00 | 285.15 | 98841 | 4.1 | 300 | 7.8591 | 838.8 | 1108.8 | 271.323 | 0 | 1 | 12
4641 | 7/13 | 08:00:00 | 286.15 | 98850 | 5.1 | 300 | 7.3412 | 1404 | 1818 | 272.048 | 0 | 1 | 13
4642 | 7/13 | 09:00:00 | 287.15 | 98858 | 3.6 | 320 | 6.854 | 1843.2 | 1994.4 | 273.038 | 0 | 1 | 14
4643 | 7/13 | 10:00:00 | 288.15 | 98867 | 4.1 | 320 | 6.8534 | 2286 | 1864.8 | 273.988 | 0 | 1 | 15
4644 | 7/13 | 11:00:00 | 288.15 | 98867 | 4.1 | 320 | 6.8534 | 1450.8 | 903.6 | 274.473 | 0 | 1 | 15
4645 | 7/13 | 12:00:00 | 289.15 | 98875 | 4.6 | 300 | 6.3955 | 2804.4 | 1911.6 | 274.708 | 0 | 1 | 16
4646 | 7/13 | 13:00:00 | 288.15 | 98867 | 6.7 | 310 | 6.396 | 2836.8 | 2275.2 | 273.758 | 0 | 1 | 15
4647 | 7/13 | 14:00:00 | 288.15 | 98867 | 6.2 | 280 | 5.9661 | 2714.4 | 2264.4 | 273.525 | 0 | 1 | 15
4648 | 7/13 | 15:00:00 | 288.15 | 98867 | 5.1 | 280 | 6.8534 | 2433.6 | 2210.4 | 273.988 | 0 | 1 | 15
4649 | 7/13 | 16:00:00 | 289.15 | 98875 | 6.2 | 300 | 6.3955 | 2034 | 1965.6 | 274.708 | 0 | 1 | 16
4650 | 7/13 | 17:00:00 | 288.15 | 98867 | 6.2 | 290 | 6.396 | 1540.8 | 1648.8 | 273.758 | 0 | 1 | 15
4651 | 7/13 | 18:00:00 | 288.15 | 98867 | 6.7 | 290 | 6.396 | 1065.6 | 1425.6 | 273.49 | 0 | 1 | 15
4652 | 7/13 | 19:00:00 | 287.15 | 98858 | 5.7 | 310 | 6.3966 | 500.4 | 468 | 272.808 | 0 | 1 | 14
4653 | 7/13 | 20:00:00 | 286.15 | 98850 | 5.1 | 300 | 6.3971 | 144 | 18 | 271.592 | 0 | 1 | 13
4654 | 7/13 | 21:00:00 | 285.15 | 98841 | 4.6 | 280 | 6.8552 | 0 | 0 | 270.871 | 0 | 1 | 12
4655 | 7/13 | 22:00:00 | 285.15 | 98841 | 4.6 | 280 | 6.3977 | 0 | 0 | 270.643 | 0 | 1 | 12
4656 | 7/13 | 23:00:00 | 284.15 | 98833 | 4.1 | 280 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
4657 | 7/13 | 24:00:00 | 284.15 | 98833 | 5.7 | 280 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
4658 | 7/14 | 01:00:00 | 284.15 | 98833 | 5.7 | 280 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
4659 | 7/14 | 02:00:00 | 284.15 | 98833 | 4.6 | 290 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
4660 | 7/14 | 03:00:00 | 284.15 | 98833 | 3.6 | 290 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
4661 | 7/14 | 04:00:00 | 284.15 | 98833 | 3.6 | 270 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
4662 | 7/14 | 05:00:00 | 283.15 | 98824 | 2.1 | 270 | 6.8564 | 61.2 | 0 | 268.971 | 0 | 1 | 10
4663 | 7/14 | 06:00:00 | 284.15 | 98833 | 2.6 | 280 | 6.8558 | 345.6 | 277.2 | 269.921 | 0 | 1 | 11
4664 | 7/14 | 07:00:00 | 284.15 | 98833 | 3.6 | 270 | 6.8558 | 604.8 | 302.4 | 270.549 | 0 | 1 | 11
4665 | 7/14 | 08:00:00 | 285.15 | 98841 | 4.1 | 280 | 7.3418 | 1396.8 | 1674 | 271.097 | 0 | 1 | 12
4666 | 7/14 | 09:00:00 | 285.15 | 98841 | 4.6 | 300 | 6.8552 | 1947.6 | 2311.2 | 270.871 | 0 | 1 | 12
4667 | 7/14 | 10:00:00 | 288.15 | 98867 | 6.2 | 300 | 6.8534 | 2278.8 | 2030.4 | 273.988 | 0 | 1 | 15
4668 | 7/14 | 11:00:00 | 289.15 | 98875 | 6.7 | 310 | 5.9656 | 2617.2 | 2163.6 | 274.475 | 0 | 1 | 16
4669 | 7/14 | 12:00:00 | 288.15 | 98867 | 7.7 | 290 | 6.396 | 2970 | 2617.2 | 273.49 | 0 | 1 | 15
4670 | 7/14 | 13:00:00 | 288.15 | 98867 | 7.2 | 280 | 6.8534 | 2826 | 2206.8 | 273.988 | 0 | 1 | 15
4671 | 7/14 | 14:00:00 | 289.15 | 98875 | 8.2 | 270 | 6.3955 | 2707.2 | 2257.2 | 274.708 | 0 | 1 | 16
4672 | 7/14 | 15:00:00 | 286.15 | 98850 | 7.7 | 270 | 7.8584 | 2419.2 | 2041.2 | 272.541 | 0 | 1 | 13
4673 | 7/14 | 16:00:00 | 286.15 | 98850 | 6.2 | 280 | 7.8584 | 2019.6 | 1933.2 | 272.541 | 0 | 1 | 13
4674 | 7/14 | 17:00:00 | 288.15 | 98867 | 8.2 | 280 | 7.3399 | 1530 | 1641.6 | 274.218 | 0 | 1 | 15
4675 | 7/14 | 18:00:00 | 288.15 | 98867 | 8.2 | 280 | 7.3399 | 1054.8 | 1407.6 | 273.95 | 0 | 1 | 15
4676 | 7/14 | 19:00:00 | 288.15 | 98867 | 8.8 | 280 | 6.8534 | 525.6 | 576 | 273.72 | 0 | 1 | 15
4677 | 7/14 | 20:00:00 | 286.15 | 98850 | 6.7 | 280 | 7.3412 | 140.4 | 18 | 272.048 | 0 | 1 | 13
4678 | 7/14 | 21:00:00 | 285.15 | 98841 | 8.2 | 270 | 7.3418 | 0 | 0 | 271.097 | 0 | 1 | 12
4679 | 7/14 | 22:00:00 | 284.15 | 98833 | 6.2 | 270 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
4680 | 7/14 | 23:00:00 | 284.15 | 98833 | 5.7 | 280 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
4681 | 7/14 | 24:00:00 | 283.15 | 98824 | 4.6 | 290 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4682 | 7/15 | 01:00:00 | 283.15 | 98824 | 5.1 | 290 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4683 | 7/15 | 02:00:00 | 283.15 | 98824 | 5.7 | 290 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4684 | 7/15 | 03:00:00 | 283.15 | 98824 | 5.1 | 290 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
4685 | 7/15 | 04:00:00 | 282.15 | 98815 | 3.1 | 280 | 7.3438 | 0 | 0 | 268.245 | 0 | 1 | 9
4686 | 7/15 | 05:00:00 | 282.15 | 98815 | 3.6 | 280 | 6.8571 | 57.6 | 0 | 268.021 | 0 | 1 | 9
4687 | 7/15 | 06:00:00 | 283.15 | 98824 | 4.1 | 280 | 7.3431 | 338.4 | 320.4 | 269.196 | 0 | 1 | 10
4688 | 7/15 | 07:00:00 | 284.15 | 98833 | 5.1 | 290 | 7.3425 | 824.4 | 1094.4 | 270.147 | 0 | 1 | 11
4689 | 7/15 | 08:00:00 | 286.15 | 98850 | 4.6 | 300 | 7.8584 | 1386 | 1717.2 | 272.274 | 0 | 1 | 13
4690 | 7/15 | 09:00:00 | 287.15 | 98858 | 4.6 | 310 | 7.8578 | 1933.2 | 2307.6 | 273.226 | 0 | 1 | 14
4691 | 7/15 | 10:00:00 | 288.15 | 98867 | 4.1 | 300 | 7.857 | 2404.8 | 2534.4 | 274.177 | 0 | 1 | 15
4692 | 7/15 | 11:00:00 | 288.15 | 98867 | 4.1 | 330 | 7.857 | 2595.6 | 2167.2 | 274.446 | 0 | 1 | 15
4693 | 7/15 | 12:00:00 | 288.15 | 98867 | 2.6 | 350 | 7.857 | 2782.8 | 2253.6 | 274.446 | 0 | 1 | 15
4694 | 7/15 | 13:00:00 | 290.15 | 98883 | 2.1 | 320 | 7.8557 | 2815.2 | 2260.8 | 276.351 | 0 | 1 | 17
4695 | 7/15 | 14:00:00 | 290.15 | 98883 | 4.1 | 270 | 7.3387 | 2692.8 | 2246.4 | 276.121 | 0 | 1 | 17
4696 | 7/15 | 15:00:00 | 292.15 | 98900 | 6.7 | 270 | 7.8544 | 2415.6 | 2041.2 | 278.256 | 0 | 1 | 19
4697 | 7/15 | 16:00:00 | 292.15 | 98900 | 6.2 | 280 | 7.8544 | 2138.4 | 2412 | 277.983 | 0 | 1 | 19
4698 | 7/15 | 17:00:00 | 291.15 | 98892 | 7.2 | 280 | 7.855 | 1616.4 | 1969.2 | 277.032 | 0 | 1 | 18
4699 | 7/15 | 18:00:00 | 290.15 | 98883 | 7.2 | 290 | 7.8557 | 1047.6 | 1346.4 | 276.08 | 0 | 1 | 17
4700 | 7/15 | 19:00:00 | 288.15 | 98867 | 7.2 | 270 | 7.3399 | 518.4 | 565.2 | 273.95 | 0 | 1 | 15
4701 | 7/15 | 20:00:00 | 287.15 | 98858 | 6.7 | 280 | 7.3406 | 136.8 | 10.8 | 272.999 | 0 | 1 | 14
4702 | 7/15 | 21:00:00 | 286.15 | 98850 | 6.2 | 270 | 7.8584 | 0 | 0 | 272.909 | 0 | 1 | 13
4703 | 7/15 | 22:00:00 | 285.15 | 98841 | 5.7 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4704 | 7/15 | 23:00:00 | 285.15 | 98841 | 6.7 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
4705 | 7/15 | 24:00:00 | 284.15 | 98833 | 5.1 | 280 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
4706 | 7/16 | 01:00:00 | 284.15 | 98833 | 5.1 | 280 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
4707 | 7/16 | 02:00:00 | 283.15 | 98824 | 3.6 | 280 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
4708 | 7/16 | 03:00:00 | 284.15 | 98833 | 4.1 | 290 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
4709 | 7/16 | 04:00:00 | 283.15 | 98824 | 2.1 | 240 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
4710 | 7/16 | 05:00:00 | 284.15 | 98833 | 3.1 | 250 | 7.8598 | 21.6 | 0 | 271.225 | 0 | 1 | 11
4711 | 7/16 | 06:00:00 | 285.15 | 98841 | 3.6 | 250 | 7.8591 | 194.4 | 0 | 272.069 | 0 | 1 | 12
4712 | 7/16 | 07:00:00 | 285.15 | 98841 | 2.6 | 240 | 7.8591 | 471.6 | 50.4 | 272.069 | 0 | 1 | 12
4713 | 7/16 | 08:00:00 | 286.15 | 98850 | 3.6 | 230 | 7.3412 | 1126.8 | 856.8 | 272.563 | 0 | 1 | 13
4714 | 7/16 | 09:00:00 | 286.15 | 98850 | 4.1 | 230 | 7.3412 | 1008 | 68.4 | 272.796 | 0 | 1 | 13
4715 | 7/16 | 10:00:00 | 287.15 | 98858 | 4.6 | 200 | 7.8578 | 1252.8 | 205.2 | 273.977 | 0 | 1 | 14
4716 | 7/16 | 11:00:00 | 287.15 | 98858 | 4.1 | 220 | 8.4073 | 1432.8 | 154.8 | 274.203 | 0 | 1 | 14
4717 | 7/16 | 12:00:00 | 288.15 | 98867 | 3.6 | 220 | 8.9902 | 1533.6 | 158.4 | 275.384 | 0 | 1 | 15
4718 | 7/16 | 13:00:00 | 288.15 | 98867 | 5.7 | 230 | 9.6099 | 1551.6 | 154.8 | 275.608 | 0 | 1 | 15
4719 | 7/16 | 14:00:00 | 288.15 | 98867 | 3.6 | 230 | 10.2677 | 1479.6 | 154.8 | 275.831 | 0 | 1 | 15
4720 | 7/16 | 15:00:00 | 290.15 | 98883 | 3.6 | 240 | 10.9637 | 1328.4 | 104.4 | 277.969 | 0 | 1 | 17
4721 | 7/16 | 16:00:00 | 289.15 | 98875 | 3.1 | 240 | 10.9646 | 1105.2 | 97.2 | 277.011 | 0 | 1 | 16
4722 | 7/16 | 17:00:00 | 290.15 | 98883 | 4.1 | 230 | 11.7037 | 835.2 | 75.6 | 278.191 | 0 | 1 | 17
4723 | 7/16 | 18:00:00 | 291.15 | 98892 | 3.6 | 250 | 12.4871 | 540 | 75.6 | 279.371 | 0 | 1 | 18
4724 | 7/16 | 19:00:00 | 291.15 | 98892 | 5.1 | 260 | 12.4871 | 266.4 | 0 | 279.371 | 0 | 1 | 18
4725 | 7/16 | 20:00:00 | 291.15 | 98892 | 4.6 | 230 | 12.4871 | 126 | 0 | 278.878 | 0 | 1 | 18
4726 | 7/16 | 21:00:00 | 290.15 | 98883 | 4.6 | 250 | 11.7037 | 0 | 0 | 277.428 | 0 | 1 | 17
4727 | 7/16 | 22:00:00 | 290.15 | 98883 | 4.1 | 220 | 11.7037 | 0 | 0 | 277.7 | 0 | 1 | 17
4728 | 7/16 | 23:00:00 | 290.15 | 98883 | 4.1 | 240 | 11.7037 | 0 | 0 | 277.7 | 0 | 1 | 17
4729 | 7/16 | 24:00:00 | 290.15 | 98883 | 5.1 | 240 | 10.9637 | 0 | 0 | 277.478 | 0 | 1 | 17
4730 | 7/17 | 01:00:00 | 289.15 | 98875 | 7.2 | 250 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
4731 | 7/17 | 02:00:00 | 289.15 | 98875 | 7.2 | 260 | 11.7047 | 0 | 0 | 276.743 | 0 | 1 | 16
4732 | 7/17 | 03:00:00 | 289.15 | 98875 | 6.2 | 260 | 11.7047 | 0 | 0 | 276.743 | 0 | 1 | 16
4733 | 7/17 | 04:00:00 | 289.15 | 98875 | 5.1 | 250 | 11.7047 | 0 | 0 | 277.232 | 0 | 1 | 16
4734 | 7/17 | 05:00:00 | 289.15 | 98875 | 3.6 | 260 | 10.9646 | 28.8 | 0 | 277.011 | 0 | 1 | 16
4735 | 7/17 | 06:00:00 | 288.15 | 98867 | 4.6 | 290 | 10.9655 | 169.2 | 0 | 276.053 | 0 | 1 | 15
4736 | 7/17 | 07:00:00 | 287.15 | 98858 | 5.1 | 280 | 10.2686 | 417.6 | 14.4 | 274.874 | 0 | 1 | 14
4737 | 7/17 | 08:00:00 | 288.15 | 98867 | 3.6 | 250 | 9.6099 | 712.8 | 61.2 | 275.608 | 0 | 1 | 15
4738 | 7/17 | 09:00:00 | 287.15 | 98858 | 3.6 | 250 | 9.6108 | 997.2 | 72 | 274.652 | 0 | 1 | 14
4739 | 7/17 | 10:00:00 | 287.15 | 98858 | 3.1 | 230 | 9.6108 | 1245.6 | 104.4 | 274.652 | 0 | 1 | 14
4740 | 7/17 | 11:00:00 | 288.15 | 98867 | 5.1 | 260 | 9.6099 | 1425.6 | 151.2 | 275.608 | 0 | 1 | 15
4741 | 7/17 | 12:00:00 | 289.15 | 98875 | 5.7 | 250 | 9.6091 | 1530 | 154.8 | 276.565 | 0 | 1 | 16
4742 | 7/17 | 13:00:00 | 290.15 | 98883 | 6.2 | 260 | 9.6084 | 1548 | 367.2 | 277.521 | 0 | 1 | 17
4743 | 7/17 | 14:00:00 | 291.15 | 98892 | 7.7 | 250 | 9.6075 | 2667.6 | 1832.4 | 277.986 | 0 | 1 | 18
4744 | 7/17 | 15:00:00 | 291.15 | 98892 | 8.2 | 250 | 9.6075 | 2394 | 2012.4 | 277.986 | 0 | 1 | 18
4745 | 7/17 | 16:00:00 | 290.15 | 98883 | 8.2 | 260 | 9.6084 | 1994.4 | 1972.8 | 277.031 | 0 | 1 | 17
4746 | 7/17 | 17:00:00 | 290.15 | 98883 | 7.7 | 260 | 9.6084 | 1504.8 | 1641.6 | 277.031 | 0 | 1 | 17
4747 | 7/17 | 18:00:00 | 290.15 | 98883 | 7.7 | 280 | 8.9887 | 972 | 1198.8 | 276.806 | 0 | 1 | 17
4748 | 7/17 | 19:00:00 | 289.15 | 98875 | 6.7 | 290 | 8.4059 | 478.8 | 522 | 275.626 | 0 | 1 | 16
4749 | 7/17 | 20:00:00 | 288.15 | 98867 | 7.7 | 280 | 8.4065 | 129.6 | 0 | 274.404 | 0 | 1 | 15
4750 | 7/17 | 21:00:00 | 287.15 | 98858 | 5.7 | 270 | 8.4073 | 0 | 0 | 273.451 | 0 | 1 | 14
4751 | 7/17 | 22:00:00 | 287.15 | 98858 | 5.7 | 260 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
4752 | 7/17 | 23:00:00 | 286.15 | 98850 | 5.7 | 260 | 8.9918 | 0 | 0 | 273.583 | 0 | 1 | 13
4753 | 7/17 | 24:00:00 | 286.15 | 98850 | 5.1 | 270 | 8.9918 | 0 | 0 | 273.583 | 0 | 1 | 13
4754 | 7/18 | 01:00:00 | 286.15 | 98850 | 5.1 | 280 | 9.6116 | 0 | 0 | 273.806 | 0 | 1 | 13
4755 | 7/18 | 02:00:00 | 287.15 | 98858 | 6.2 | 260 | 10.2686 | 0 | 0 | 274.985 | 0 | 1 | 14
4756 | 7/18 | 03:00:00 | 287.15 | 98858 | 5.7 | 260 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
4757 | 7/18 | 04:00:00 | 287.15 | 98858 | 6.2 | 260 | 8.991 | 0 | 0 | 273.676 | 0 | 1 | 14
4758 | 7/18 | 05:00:00 | 286.15 | 98850 | 7.2 | 270 | 8.9918 | 50.4 | 0 | 272.723 | 0 | 1 | 13
4759 | 7/18 | 06:00:00 | 286.15 | 98850 | 7.7 | 270 | 8.408 | 316.8 | 345.6 | 272.499 | 0 | 1 | 13
4760 | 7/18 | 07:00:00 | 286.15 | 98850 | 7.2 | 270 | 8.408 | 795.6 | 1047.6 | 272.499 | 0 | 1 | 13
4761 | 7/18 | 08:00:00 | 287.15 | 98858 | 8.8 | 270 | 8.4073 | 1281.6 | 1486.8 | 273.719 | 0 | 1 | 14
4762 | 7/18 | 09:00:00 | 288.15 | 98867 | 7.2 | 270 | 8.4065 | 1796.4 | 1782 | 274.672 | 0 | 1 | 15
4763 | 7/18 | 10:00:00 | 288.15 | 98867 | 9.3 | 270 | 8.4065 | 2379.6 | 2426.4 | 274.404 | 0 | 1 | 15
4764 | 7/18 | 11:00:00 | 289.15 | 98875 | 7.2 | 250 | 8.4059 | 2728.8 | 2732.4 | 275.356 | 0 | 1 | 16
4765 | 7/18 | 12:00:00 | 291.15 | 98892 | 7.2 | 260 | 8.4044 | 2926.8 | 2800.8 | 277.261 | 0 | 1 | 18
4766 | 7/18 | 13:00:00 | 290.15 | 98883 | 8.2 | 250 | 7.8557 | 2966.4 | 2811.6 | 276.08 | 0 | 1 | 17
4767 | 7/18 | 14:00:00 | 290.15 | 98883 | 7.7 | 280 | 8.4052 | 2829.6 | 2772 | 276.308 | 0 | 1 | 17
4768 | 7/18 | 15:00:00 | 291.15 | 98892 | 7.7 | 270 | 8.4044 | 2541.6 | 2595.6 | 277.261 | 0 | 1 | 18
4769 | 7/18 | 16:00:00 | 291.15 | 98892 | 7.2 | 270 | 8.9879 | 2113.2 | 2322 | 277.488 | 0 | 1 | 18
4770 | 7/18 | 17:00:00 | 292.15 | 98900 | 6.7 | 260 | 8.9872 | 1522.8 | 1720.8 | 278.714 | 0 | 1 | 19
4771 | 7/18 | 18:00:00 | 292.15 | 98900 | 8.2 | 270 | 8.4037 | 1008 | 1364.4 | 278.351 | 0 | 1 | 19
4772 | 7/18 | 19:00:00 | 291.15 | 98892 | 7.7 | 270 | 7.855 | 493.2 | 507.6 | 277.17 | 0 | 1 | 18
4773 | 7/18 | 20:00:00 | 290.15 | 98883 | 4.6 | 270 | 7.8557 | 122.4 | 0 | 276.351 | 0 | 1 | 17
4774 | 7/18 | 21:00:00 | 289.15 | 98875 | 3.6 | 270 | 8.4059 | 0 | 0 | 275.754 | 0 | 1 | 16
4775 | 7/18 | 22:00:00 | 288.15 | 98867 | 6.2 | 280 | 8.4065 | 0 | 0 | 274.924 | 0 | 1 | 15
4776 | 7/18 | 23:00:00 | 288.15 | 98867 | 4.1 | 290 | 8.9902 | 0 | 0 | 275.269 | 0 | 1 | 15
4777 | 7/18 | 24:00:00 | 288.15 | 98867 | 4.6 | 280 | 9.6099 | 0 | 0 | 275.608 | 0 | 1 | 15
4778 | 7/19 | 01:00:00 | 288.15 | 98867 | 2.1 | 270 | 10.2677 | 0 | 0 | 275.943 | 0 | 1 | 15
4779 | 7/19 | 02:00:00 | 288.15 | 98867 | 6.2 | 270 | 10.2677 | 0 | 0 | 275.943 | 0 | 1 | 15
4780 | 7/19 | 03:00:00 | 288.15 | 98867 | 6.2 | 270 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
4781 | 7/19 | 04:00:00 | 288.15 | 98867 | 7.7 | 270 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
4782 | 7/19 | 05:00:00 | 288.15 | 98867 | 8.2 | 270 | 10.9655 | 46.8 | 0 | 275.565 | 0 | 1 | 15
4783 | 7/19 | 06:00:00 | 289.15 | 98875 | 5.7 | 270 | 10.9646 | 162 | 0 | 277.011 | 0 | 1 | 16
4784 | 7/19 | 07:00:00 | 289.15 | 98875 | 4.6 | 260 | 11.7047 | 406.8 | 10.8 | 277.232 | 0 | 1 | 16
4785 | 7/19 | 08:00:00 | 289.15 | 98875 | 5.7 | 260 | 11.7047 | 698.4 | 61.2 | 277.232 | 0 | 1 | 16
4786 | 7/19 | 09:00:00 | 290.15 | 98883 | 5.7 | 260 | 12.4883 | 982.8 | 270 | 278.412 | 0 | 1 | 17
4787 | 7/19 | 10:00:00 | 292.15 | 98900 | 6.2 | 270 | 12.4861 | 2214 | 1918.8 | 279.836 | 0 | 1 | 19
4788 | 7/19 | 11:00:00 | 294.15 | 98916 | 7.7 | 260 | 12.484 | 2541.6 | 2275.2 | 281.751 | 0 | 1 | 21
4789 | 7/19 | 12:00:00 | 295.15 | 98924 | 6.2 | 260 | 13.3141 | 2890.8 | 2786.4 | 282.655 | 0 | 1 | 22
4790 | 7/19 | 13:00:00 | 296.15 | 98932 | 6.2 | 270 | 12.482 | 2930.4 | 2779.2 | 283.389 | 0 | 1 | 23
4791 | 7/19 | 14:00:00 | 296.15 | 98932 | 5.7 | 280 | 12.482 | 2638.8 | 2286 | 283.667 | 0 | 1 | 23
4792 | 7/19 | 15:00:00 | 297.15 | 98940 | 3.6 | 270 | 12.4809 | 2368.8 | 2170.8 | 284.625 | 0 | 1 | 24
4793 | 7/19 | 16:00:00 | 297.15 | 98940 | 3.1 | 260 | 12.4809 | 1972.8 | 2095.2 | 284.625 | 0 | 1 | 24
4794 | 7/19 | 17:00:00 | 297.15 | 98940 | 3.1 | 260 | 13.3119 | 1479.6 | 1717.2 | 284.849 | 0 | 1 | 24
4795 | 7/19 | 18:00:00 | 297.15 | 98940 | 3.1 | 260 | 12.4809 | 954 | 1245.6 | 284.625 | 0 | 1 | 24
4796 | 7/19 | 19:00:00 | 297.15 | 98940 | 3.1 | 300 | 13.3119 | 489.6 | 658.8 | 284.57 | 0 | 1 | 24
4797 | 7/19 | 20:00:00 | 295.15 | 98924 | 3.1 | 310 | 12.483 | 118.8 | 0 | 282.433 | 0 | 1 | 22
4798 | 7/19 | 21:00:00 | 294.15 | 98916 | 2.6 | 310 | 12.484 | 0 | 0 | 281.476 | 0 | 1 | 21
4799 | 7/19 | 22:00:00 | 292.15 | 98900 | 0.5 | 298 | 12.4861 | 0 | 0 | 280.331 | 0 | 1 | 19
4800 | 7/19 | 23:00:00 | 292.15 | 98900 | 0.5 | 350 | 12.4861 | 0 | 0 | 279.562 | 0 | 1 | 19
4801 | 7/19 | 24:00:00 | 291.15 | 98892 | 1.5 | 290 | 11.7026 | 0 | 0 | 279.15 | 0 | 1 | 18
4802 | 7/20 | 01:00:00 | 291.15 | 98892 | 0.5 | 320 | 11.7026 | 0 | 0 | 279.15 | 0 | 1 | 18
4803 | 7/20 | 02:00:00 | 290.15 | 98883 | 0 | 103 | 11.7037 | 0 | 0 | 278.304 | 0 | 1 | 17
4804 | 7/20 | 03:00:00 | 290.15 | 98883 | 0.5 | 199 | 11.7037 | 0 | 0 | 278.304 | 0 | 1 | 17
4805 | 7/20 | 04:00:00 | 290.15 | 98883 | 1 | 128 | 11.7037 | 0 | 0 | 278.304 | 0 | 1 | 17
4806 | 7/20 | 05:00:00 | 290.15 | 98883 | 1 | 58 | 11.7037 | 18 | 0 | 278.304 | 0 | 1 | 17
4807 | 7/20 | 06:00:00 | 291.15 | 98892 | 1.5 | 60 | 11.7026 | 176.4 | 0 | 279.15 | 0 | 1 | 18
4808 | 7/20 | 07:00:00 | 292.15 | 98900 | 1.5 | 36 | 12.4861 | 446.4 | 75.6 | 280.331 | 0 | 1 | 19
4809 | 7/20 | 08:00:00 | 294.15 | 98916 | 1.5 | 152 | 13.3152 | 932.4 | 511.2 | 282.354 | 0 | 1 | 21
4810 | 7/20 | 09:00:00 | 296.15 | 98932 | 2.1 | 120 | 13.313 | 1872 | 2181.6 | 283.613 | 0 | 1 | 23
4811 | 7/20 | 10:00:00 | 297.15 | 98940 | 2.6 | 130 | 13.3119 | 2336.4 | 2610 | 284.57 | 0 | 1 | 24
4812 | 7/20 | 11:00:00 | 298.15 | 98948 | 4.1 | 160 | 13.3108 | 2685.6 | 2790 | 285.528 | 0 | 1 | 25
4813 | 7/20 | 12:00:00 | 300.15 | 98964 | 4.1 | 150 | 12.4778 | 2887.2 | 2858.4 | 287.217 | 0 | 1 | 27
4814 | 7/20 | 13:00:00 | 300.15 | 98964 | 3.6 | 170 | 12.4778 | 2923.2 | 2872.8 | 287.217 | 0 | 1 | 27
4815 | 7/20 | 14:00:00 | 301.15 | 98971 | 3.6 | 170 | 10.9538 | 2800.8 | 2775.6 | 287.716 | 0 | 1 | 28
4816 | 7/20 | 15:00:00 | 301.15 | 98971 | 5.1 | 140 | 10.9538 | 2545.2 | 2754 | 287.568 | 0 | 1 | 28
4817 | 7/20 | 16:00:00 | 301.15 | 98971 | 5.7 | 130 | 10.9538 | 2116.8 | 2509.2 | 287.568 | 0 | 1 | 28
4818 | 7/20 | 17:00:00 | 301.15 | 98971 | 4.6 | 140 | 10.9538 | 1591.2 | 2106 | 287.568 | 0 | 1 | 28
4819 | 7/20 | 18:00:00 | 301.15 | 98971 | 5.7 | 140 | 11.6931 | 1015.2 | 1306.8 | 287.798 | 0 | 1 | 28
4820 | 7/20 | 19:00:00 | 300.15 | 98964 | 5.1 | 140 | 12.4778 | 482.4 | 655.2 | 287.217 | 0 | 1 | 27
4821 | 7/20 | 20:00:00 | 298.15 | 98948 | 4.6 | 100 | 14.1913 | 108 | 0 | 286.164 | 0 | 1 | 25
4822 | 7/20 | 21:00:00 | 297.15 | 98940 | 4.1 | 110 | 14.1924 | 0 | 0 | 285.205 | 0 | 1 | 24
4823 | 7/20 | 22:00:00 | 296.15 | 98932 | 4.6 | 120 | 13.313 | 0 | 0 | 284.022 | 0 | 1 | 23
4824 | 7/20 | 23:00:00 | 296.15 | 98932 | 4.6 | 130 | 13.313 | 0 | 0 | 284.022 | 0 | 1 | 23
4825 | 7/20 | 24:00:00 | 295.15 | 98924 | 4.6 | 130 | 13.3141 | 0 | 0 | 283.191 | 0 | 1 | 22
4826 | 7/21 | 01:00:00 | 294.15 | 98916 | 4.6 | 140 | 12.484 | 0 | 0 | 282.009 | 0 | 1 | 21
4827 | 7/21 | 02:00:00 | 293.15 | 98908 | 3.6 | 130 | 12.485 | 0 | 0 | 281.172 | 0 | 1 | 20
4828 | 7/21 | 03:00:00 | 292.15 | 98900 | 2.6 | 80 | 12.4861 | 0 | 0 | 280.331 | 0 | 1 | 19
4829 | 7/21 | 04:00:00 | 290.15 | 98883 | 2.6 | 70 | 11.7037 | 0 | 0 | 276.985 | 0 | 1 | 17
4830 | 7/21 | 05:00:00 | 290.15 | 98883 | 3.1 | 60 | 11.7037 | 46.8 | 0 | 276.985 | 0 | 1 | 17
4831 | 7/21 | 06:00:00 | 290.15 | 98883 | 4.6 | 70 | 11.7037 | 298.8 | 324 | 276.985 | 0 | 1 | 17
4832 | 7/21 | 07:00:00 | 291.15 | 98892 | 3.6 | 80 | 12.4871 | 774 | 1184.4 | 278.16 | 0 | 1 | 18
4833 | 7/21 | 08:00:00 | 293.15 | 98908 | 1.5 | 92 | 12.485 | 1317.6 | 1864.8 | 280.519 | 0 | 1 | 20
4834 | 7/21 | 09:00:00 | 294.15 | 98916 | 0 | 238 | 13.3152 | 1861.2 | 2383.2 | 281.697 | 0 | 1 | 21
4835 | 7/21 | 10:00:00 | 294.15 | 98916 | 3.6 | 340 | 13.3152 | 2329.2 | 2602.8 | 281.697 | 0 | 1 | 21
4836 | 7/21 | 11:00:00 | 295.15 | 98924 | 5.1 | 20 | 13.3141 | 2678.4 | 2732.4 | 282.655 | 0 | 1 | 22
4837 | 7/21 | 12:00:00 | 296.15 | 98932 | 5.1 | 20 | 10.9582 | 2725.2 | 2203.2 | 283.216 | 0 | 1 | 23
4838 | 7/21 | 13:00:00 | 295.15 | 98924 | 4.1 | 300 | 12.483 | 2750.4 | 2228.4 | 282.709 | 0 | 1 | 22
4839 | 7/21 | 14:00:00 | 297.15 | 98940 | 7.2 | 290 | 11.6968 | 2790 | 2725.2 | 284.121 | 0 | 1 | 24
4840 | 7/21 | 15:00:00 | 297.15 | 98940 | 6.7 | 290 | 10.9573 | 2505.6 | 2642.4 | 283.894 | 0 | 1 | 24
4841 | 7/21 | 16:00:00 | 297.15 | 98940 | 7.2 | 290 | 11.6968 | 2080.8 | 2433.6 | 284.121 | 0 | 1 | 24
4842 | 7/21 | 17:00:00 | 296.15 | 98932 | 7.7 | 270 | 10.9582 | 1562.4 | 2008.8 | 282.939 | 0 | 1 | 23
4843 | 7/21 | 18:00:00 | 295.15 | 98924 | 8.8 | 280 | 10.9591 | 1000.8 | 1263.6 | 281.984 | 0 | 1 | 22
4844 | 7/21 | 19:00:00 | 294.15 | 98916 | 6.7 | 280 | 10.96 | 478.8 | 608.4 | 281.028 | 0 | 1 | 21
4845 | 7/21 | 20:00:00 | 292.15 | 98900 | 6.2 | 270 | 10.9618 | 104.4 | 0 | 279.391 | 0 | 1 | 19
4846 | 7/21 | 21:00:00 | 290.15 | 98883 | 4.6 | 270 | 10.9637 | 0 | 0 | 277.207 | 0 | 1 | 17
4847 | 7/21 | 22:00:00 | 290.15 | 98883 | 3.1 | 260 | 10.266 | 0 | 0 | 277.255 | 0 | 1 | 17
4848 | 7/21 | 23:00:00 | 289.15 | 98875 | 5.7 | 280 | 10.2668 | 0 | 0 | 276.029 | 0 | 1 | 16
4849 | 7/21 | 24:00:00 | 288.15 | 98867 | 6.2 | 270 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
4850 | 7/22 | 01:00:00 | 287.15 | 98858 | 4.1 | 270 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14
4851 | 7/22 | 02:00:00 | 287.15 | 98858 | 4.6 | 260 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14
4852 | 7/22 | 03:00:00 | 287.15 | 98858 | 2.6 | 250 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14
4853 | 7/22 | 04:00:00 | 287.15 | 98858 | 2.1 | 250 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
4854 | 7/22 | 05:00:00 | 287.15 | 98858 | 1.5 | 314 | 9.6108 | 39.6 | 0 | 274.167 | 0 | 1 | 14
4855 | 7/22 | 06:00:00 | 287.15 | 98858 | 3.1 | 270 | 9.6108 | 288 | 295.2 | 273.899 | 0 | 1 | 14
4856 | 7/22 | 07:00:00 | 288.15 | 98867 | 3.6 | 270 | 10.2677 | 756 | 993.6 | 275.075 | 0 | 1 | 15
4857 | 7/22 | 08:00:00 | 289.15 | 98875 | 3.6 | 290 | 9.6091 | 1317.6 | 1753.2 | 275.806 | 0 | 1 | 16
4858 | 7/22 | 09:00:00 | 290.15 | 98883 | 4.1 | 250 | 9.6084 | 1864.8 | 2275.2 | 276.76 | 0 | 1 | 17
4859 | 7/22 | 10:00:00 | 292.15 | 98900 | 4.1 | 270 | 9.6067 | 2203.2 | 2048.4 | 278.941 | 0 | 1 | 19
4860 | 7/22 | 11:00:00 | 291.15 | 98892 | 2.6 | 240 | 8.9879 | 2538 | 1814.4 | 277.76 | 0 | 1 | 18
4861 | 7/22 | 12:00:00 | 292.15 | 98900 | 2.6 | 240 | 9.6067 | 2725.2 | 2242.8 | 278.941 | 0 | 1 | 19
4862 | 7/22 | 13:00:00 | 292.15 | 98900 | 3.1 | 250 | 9.6067 | 2757.6 | 2250 | 278.941 | 0 | 1 | 19
4863 | 7/22 | 14:00:00 | 293.15 | 98908 | 3.6 | 250 | 11.7007 | 2624.4 | 1789.2 | 280.571 | 0 | 1 | 20
4864 | 7/22 | 15:00:00 | 292.15 | 98900 | 3.6 | 250 | 12.4861 | 2347.2 | 2167.2 | 279.836 | 0 | 1 | 19
4865 | 7/22 | 16:00:00 | 292.15 | 98900 | 3.6 | 250 | 13.3174 | 1947.6 | 2073.6 | 280.056 | 0 | 1 | 19
4866 | 7/22 | 17:00:00 | 293.15 | 98908 | 2.6 | 250 | 14.1971 | 1454.4 | 1692 | 281.235 | 0 | 1 | 20
4867 | 7/22 | 18:00:00 | 292.15 | 98900 | 3.1 | 260 | 14.1983 | 928.8 | 1108.8 | 280.275 | 0 | 1 | 19
4868 | 7/22 | 19:00:00 | 292.15 | 98900 | 1.5 | 285 | 14.1983 | 442.8 | 489.6 | 280.275 | 0 | 1 | 19
4869 | 7/22 | 20:00:00 | 291.15 | 98892 | 1 | 240 | 13.3185 | 100.8 | 0 | 279.097 | 0 | 1 | 18
4870 | 7/22 | 21:00:00 | 291.15 | 98892 | 1 | 270 | 13.3185 | 0 | 0 | 279.097 | 0 | 1 | 18
4871 | 7/22 | 22:00:00 | 290.15 | 98883 | 2.1 | 270 | 12.4883 | 0 | 0 | 277.92 | 0 | 1 | 17
4872 | 7/22 | 23:00:00 | 290.15 | 98883 | 2.1 | 260 | 12.2481 | 0 | 0 | 277.854 | 0 | 1 | 17
4873 | 7/22 | 24:00:00 | 289.15 | 98875 | 2.1 | 280 | 11.7047 | 0 | 0 | 276.743 | 0 | 1 | 16
4874 | 7/23 | 01:00:00 | 289.15 | 98875 | 0 | 126 | 11.7047 | 0 | 0 | 277.345 | 0 | 1 | 16
4875 | 7/23 | 02:00:00 | 289.15 | 98875 | 1.5 | 270 | 11.7047 | 0 | 0 | 276.472 | 0 | 1 | 16
4876 | 7/23 | 03:00:00 | 289.15 | 98875 | 1.5 | 250 | 11.7047 | 0 | 0 | 276.472 | 0 | 1 | 16
4877 | 7/23 | 04:00:00 | 288.15 | 98867 | 1.5 | 150 | 10.9655 | 0 | 0 | 275.296 | 0 | 1 | 15
4878 | 7/23 | 05:00:00 | 288.15 | 98867 | 1 | 220 | 10.9655 | 10.8 | 0 | 276.165 | 0 | 1 | 15
4879 | 7/23 | 06:00:00 | 289.15 | 98875 | 1 | 260 | 11.7047 | 90 | 0 | 277.345 | 0 | 1 | 16
4880 | 7/23 | 07:00:00 | 290.15 | 98883 | 1 | 279 | 12.4883 | 702 | 889.2 | 277.92 | 0 | 1 | 17
4881 | 7/23 | 08:00:00 | 290.15 | 98883 | 2.6 | 230 | 11.7037 | 1227.6 | 1418.4 | 277.7 | 0 | 1 | 17
4882 | 7/23 | 09:00:00 | 291.15 | 98892 | 2.1 | 230 | 10.9627 | 1746 | 1713.6 | 278.434 | 0 | 1 | 18
4883 | 7/23 | 10:00:00 | 291.15 | 98892 | 2.6 | 200 | 11.7026 | 2318.4 | 2451.6 | 278.384 | 0 | 1 | 18
4884 | 7/23 | 11:00:00 | 292.15 | 98900 | 3.1 | 240 | 11.7017 | 2671.2 | 2685.6 | 279.34 | 0 | 1 | 19
4885 | 7/23 | 12:00:00 | 294.15 | 98916 | 3.1 | 180 | 12.484 | 2700 | 2224.8 | 281.751 | 0 | 1 | 21
4886 | 7/23 | 13:00:00 | 295.15 | 98924 | 3.6 | 180 | 13.3141 | 2732.4 | 2322 | 282.932 | 0 | 1 | 22
4887 | 7/23 | 14:00:00 | 295.15 | 98924 | 3.1 | 240 | 12.483 | 2613.6 | 2282.4 | 282.709 | 0 | 1 | 22
4888 | 7/23 | 15:00:00 | 296.15 | 98932 | 2.6 | 220 | 13.313 | 2336.4 | 2214 | 283.89 | 0 | 1 | 23
4889 | 7/23 | 16:00:00 | 297.15 | 98940 | 2.6 | 45 | 13.3119 | 2059.2 | 2480.4 | 284.57 | 0 | 1 | 24
4890 | 7/23 | 17:00:00 | 296.15 | 98932 | 3.1 | 210 | 13.313 | 1540.8 | 2109.6 | 283.613 | 0 | 1 | 23
4891 | 7/23 | 18:00:00 | 295.15 | 98924 | 2.6 | 230 | 13.3141 | 921.6 | 1108.8 | 282.932 | 0 | 1 | 22
4892 | 7/23 | 19:00:00 | 293.15 | 98908 | 5.7 | 290 | 13.3163 | 460.8 | 640.8 | 280.74 | 0 | 1 | 20
4893 | 7/23 | 20:00:00 | 292.15 | 98900 | 4.1 | 300 | 12.4861 | 61.2 | 0 | 280.331 | 0 | 1 | 19
4894 | 7/23 | 21:00:00 | 291.15 | 98892 | 5.7 | 280 | 12.4871 | 0 | 0 | 279.484 | 0 | 1 | 18
4895 | 7/23 | 22:00:00 | 290.15 | 98883 | 4.1 | 270 | 11.7037 | 0 | 0 | 278.304 | 0 | 1 | 17
4896 | 7/23 | 23:00:00 | 290.15 | 98883 | 4.1 | 270 | 11.7037 | 0 | 0 | 278.304 | 0 | 1 | 17
4897 | 7/23 | 24:00:00 | 289.15 | 98875 | 1.5 | 234 | 11.7047 | 0 | 0 | 276.743 | 0 | 1 | 16
4898 | 7/24 | 01:00:00 | 289.15 | 98875 | 1.5 | 300 | 11.7047 | 0 | 0 | 276.743 | 0 | 1 | 16
4899 | 7/24 | 02:00:00 | 289.15 | 98875 | 2.1 | 260 | 11.7047 | 0 | 0 | 276.743 | 0 | 1 | 16
4900 | 7/24 | 03:00:00 | 288.15 | 98867 | 3.6 | 280 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4901 | 7/24 | 04:00:00 | 287.15 | 98858 | 3.6 | 290 | 10.2686 | 0 | 0 | 274.389 | 0 | 1 | 14
4902 | 7/24 | 05:00:00 | 287.15 | 98858 | 3.1 | 280 | 10.2686 | 36 | 0 | 274.389 | 0 | 1 | 14
4903 | 7/24 | 06:00:00 | 287.15 | 98858 | 3.6 | 290 | 10.2686 | 259.2 | 194.4 | 274.389 | 0 | 1 | 14
4904 | 7/24 | 07:00:00 | 288.15 | 98867 | 2.1 | 260 | 10.2677 | 694.8 | 802.8 | 275.344 | 0 | 1 | 15
4905 | 7/24 | 08:00:00 | 289.15 | 98875 | 2.1 | 300 | 10.9646 | 1296 | 1548 | 276.251 | 0 | 1 | 16
4906 | 7/24 | 09:00:00 | 290.15 | 98883 | 1.5 | 275 | 10.9637 | 1843.2 | 2282.4 | 277.207 | 0 | 1 | 17
4907 | 7/24 | 10:00:00 | 292.15 | 98900 | 3.1 | 280 | 10.9618 | 2181.6 | 1782 | 279.391 | 0 | 1 | 19
4908 | 7/24 | 11:00:00 | 292.15 | 98900 | 2.1 | 260 | 11.7017 | 1393.2 | 352.8 | 280.109 | 0 | 1 | 19
4909 | 7/24 | 12:00:00 | 292.15 | 98900 | 1.5 | 127 | 11.7017 | 1497.6 | 360 | 280.109 | 0 | 1 | 19
4910 | 7/24 | 13:00:00 | 293.15 | 98908 | 3.6 | 290 | 12.485 | 2728.8 | 1936.8 | 280.793 | 0 | 1 | 20
4911 | 7/24 | 14:00:00 | 293.15 | 98908 | 3.6 | 260 | 11.7007 | 2610 | 2059.2 | 280.571 | 0 | 1 | 20
4912 | 7/24 | 15:00:00 | 295.15 | 98924 | 3.6 | 250 | 12.483 | 2476.8 | 2512.8 | 282.433 | 0 | 1 | 22
4913 | 7/24 | 16:00:00 | 294.15 | 98916 | 3.1 | 240 | 11.6997 | 1936.8 | 1832.4 | 281.528 | 0 | 1 | 21
4914 | 7/24 | 17:00:00 | 294.15 | 98916 | 2.6 | 270 | 12.484 | 1443.6 | 1558.8 | 281.751 | 0 | 1 | 21
4915 | 7/24 | 18:00:00 | 294.15 | 98916 | 2.6 | 280 | 12.484 | 777.6 | 576 | 282.009 | 0 | 1 | 21
4916 | 7/24 | 19:00:00 | 293.15 | 98908 | 2.6 | 300 | 11.7007 | 363.6 | 198 | 280.828 | 0 | 1 | 20
4917 | 7/24 | 20:00:00 | 292.15 | 98900 | 2.6 | 310 | 11.7017 | 68.4 | 0 | 279.991 | 0 | 1 | 19
4918 | 7/24 | 21:00:00 | 290.15 | 98883 | 4.1 | 310 | 10.9637 | 0 | 0 | 277.969 | 0 | 1 | 17
4919 | 7/24 | 22:00:00 | 289.15 | 98875 | 4.6 | 300 | 10.9646 | 0 | 0 | 276.251 | 0 | 1 | 16
4920 | 7/24 | 23:00:00 | 289.15 | 98875 | 3.6 | 290 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
4921 | 7/24 | 24:00:00 | 289.15 | 98875 | 3.1 | 290 | 10.2668 | 0 | 0 | 276.029 | 0 | 1 | 16
4922 | 7/25 | 01:00:00 | 288.15 | 98867 | 2.1 | 290 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
4923 | 7/25 | 02:00:00 | 288.15 | 98867 | 3.1 | 290 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
4924 | 7/25 | 03:00:00 | 287.15 | 98858 | 2.1 | 270 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
4925 | 7/25 | 04:00:00 | 286.15 | 98850 | 2.1 | 280 | 9.6116 | 0 | 0 | 272.945 | 0 | 1 | 13
4926 | 7/25 | 05:00:00 | 286.15 | 98850 | 1.5 | 260 | 8.9918 | 32.4 | 0 | 272.99 | 0 | 1 | 13
4927 | 7/25 | 06:00:00 | 288.15 | 98867 | 2.1 | 260 | 9.6099 | 252 | 198 | 275.122 | 0 | 1 | 15
4928 | 7/25 | 07:00:00 | 288.15 | 98867 | 3.1 | 260 | 10.2677 | 687.6 | 795.6 | 275.344 | 0 | 1 | 15
4929 | 7/25 | 08:00:00 | 290.15 | 98883 | 1 | 237 | 10.9637 | 1213.2 | 1270.8 | 277.478 | 0 | 1 | 17
4930 | 7/25 | 09:00:00 | 291.15 | 98892 | 2.1 | 220 | 10.9627 | 1832.4 | 2102.4 | 278.162 | 0 | 1 | 18
4931 | 7/25 | 10:00:00 | 292.15 | 98900 | 2.1 | 220 | 11.7017 | 2170.8 | 2019.6 | 279.614 | 0 | 1 | 19
4932 | 7/25 | 11:00:00 | 292.15 | 98900 | 3.1 | 170 | 11.7017 | 2502 | 1782 | 279.614 | 0 | 1 | 19
4933 | 7/25 | 12:00:00 | 293.15 | 98908 | 3.1 | 210 | 12.485 | 2685.6 | 2289.6 | 280.793 | 0 | 1 | 20
4934 | 7/25 | 13:00:00 | 292.15 | 98900 | 4.1 | 260 | 12.4861 | 2721.6 | 2296.8 | 279.836 | 0 | 1 | 19
4935 | 7/25 | 14:00:00 | 293.15 | 98908 | 4.1 | 200 | 12.485 | 2599.2 | 2282.4 | 280.793 | 0 | 1 | 20
4936 | 7/25 | 15:00:00 | 292.15 | 98900 | 3.1 | 210 | 11.7017 | 2329.2 | 1807.2 | 279.614 | 0 | 1 | 19
4937 | 7/25 | 16:00:00 | 292.15 | 98900 | 2.6 | 200 | 12.4861 | 1069.2 | 288 | 280.331 | 0 | 1 | 19
4938 | 7/25 | 17:00:00 | 292.15 | 98900 | 3.6 | 220 | 11.7017 | 799.2 | 72 | 280.109 | 0 | 1 | 19
4939 | 7/25 | 18:00:00 | 291.15 | 98892 | 1.5 | 220 | 12.4871 | 504 | 68.4 | 279.371 | 0 | 1 | 18
4940 | 7/25 | 19:00:00 | 291.15 | 98892 | 4.6 | 220 | 12.4871 | 421.2 | 486 | 278.878 | 0 | 1 | 18
4941 | 7/25 | 20:00:00 | 291.15 | 98892 | 3.1 | 200 | 12.4871 | 86.4 | 0 | 278.878 | 0 | 1 | 18
4942 | 7/25 | 21:00:00 | 290.15 | 98883 | 2.6 | 230 | 12.4883 | 0 | 0 | 277.92 | 0 | 1 | 17
4943 | 7/25 | 22:00:00 | 289.15 | 98875 | 4.1 | 260 | 10.2668 | 0 | 0 | 276.029 | 0 | 1 | 16
4944 | 7/25 | 23:00:00 | 288.15 | 98867 | 2.6 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
4945 | 7/25 | 24:00:00 | 288.15 | 98867 | 4.6 | 250 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
4946 | 7/26 | 01:00:00 | 288.15 | 98867 | 4.6 | 260 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
4947 | 7/26 | 02:00:00 | 287.15 | 98858 | 5.1 | 260 | 10.2686 | 0 | 0 | 274.12 | 0 | 1 | 14
4948 | 7/26 | 03:00:00 | 287.15 | 98858 | 4.1 | 260 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
4949 | 7/26 | 04:00:00 | 286.15 | 98850 | 3.6 | 260 | 9.6116 | 0 | 0 | 272.945 | 0 | 1 | 13
4950 | 7/26 | 05:00:00 | 286.15 | 98850 | 3.1 | 270 | 8.9918 | 32.4 | 0 | 272.723 | 0 | 1 | 13
4951 | 7/26 | 06:00:00 | 286.15 | 98850 | 5.1 | 270 | 8.9918 | 259.2 | 262.8 | 272.723 | 0 | 1 | 13
4952 | 7/26 | 07:00:00 | 287.15 | 98858 | 5.1 | 260 | 8.991 | 720 | 957.6 | 273.676 | 0 | 1 | 14
4953 | 7/26 | 08:00:00 | 288.15 | 98867 | 6.7 | 260 | 9.6099 | 1206 | 1422 | 275.122 | 0 | 1 | 15
4954 | 7/26 | 09:00:00 | 288.15 | 98867 | 6.2 | 260 | 8.9902 | 1728 | 1814.4 | 274.898 | 0 | 1 | 15
4955 | 7/26 | 10:00:00 | 289.15 | 98875 | 6.2 | 260 | 8.9895 | 2174.4 | 2055.6 | 275.852 | 0 | 1 | 16
4956 | 7/26 | 11:00:00 | 290.15 | 98883 | 6.7 | 260 | 8.9887 | 2509.2 | 1814.4 | 276.806 | 0 | 1 | 17
4957 | 7/26 | 12:00:00 | 288.15 | 98867 | 5.1 | 250 | 9.6099 | 2696.4 | 2239.2 | 275.122 | 0 | 1 | 15
4958 | 7/26 | 13:00:00 | 288.15 | 98867 | 6.7 | 260 | 8.9902 | 2732.4 | 2250 | 274.898 | 0 | 1 | 15
4959 | 7/26 | 14:00:00 | 288.15 | 98867 | 5.7 | 260 | 8.9902 | 2610 | 2228.4 | 274.898 | 0 | 1 | 15
4960 | 7/26 | 15:00:00 | 290.15 | 98883 | 6.2 | 260 | 9.6084 | 2332.8 | 2008.8 | 277.031 | 0 | 1 | 17
4961 | 7/26 | 16:00:00 | 290.15 | 98883 | 5.1 | 250 | 8.9887 | 1933.2 | 1958.4 | 276.806 | 0 | 1 | 17
4962 | 7/26 | 17:00:00 | 289.15 | 98875 | 6.2 | 260 | 8.9895 | 1440 | 1609.2 | 275.852 | 0 | 1 | 16
4963 | 7/26 | 18:00:00 | 290.15 | 98883 | 6.2 | 260 | 8.9887 | 903.6 | 1018.8 | 276.806 | 0 | 1 | 17
4964 | 7/26 | 19:00:00 | 288.15 | 98867 | 5.1 | 260 | 8.9902 | 414 | 439.2 | 274.898 | 0 | 1 | 15
4965 | 7/26 | 20:00:00 | 288.15 | 98867 | 6.2 | 260 | 8.9902 | 82.8 | 0 | 274.898 | 0 | 1 | 15
4966 | 7/26 | 21:00:00 | 287.15 | 98858 | 4.1 | 250 | 8.991 | 0 | 0 | 273.676 | 0 | 1 | 14
4967 | 7/26 | 22:00:00 | 286.15 | 98850 | 2.1 | 250 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
4968 | 7/26 | 23:00:00 | 286.15 | 98850 | 1 | 202 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
4969 | 7/26 | 24:00:00 | 285.15 | 98841 | 3.6 | 260 | 8.9926 | 0 | 0 | 272.627 | 0 | 1 | 12
4970 | 7/27 | 01:00:00 | 285.15 | 98841 | 3.1 | 230 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
4971 | 7/27 | 02:00:00 | 285.15 | 98841 | 2.6 | 240 | 8.9926 | 0 | 0 | 271.77 | 0 | 1 | 12
4972 | 7/27 | 03:00:00 | 286.15 | 98850 | 3.1 | 250 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
4973 | 7/27 | 04:00:00 | 285.15 | 98841 | 3.1 | 260 | 8.9926 | 0 | 0 | 271.77 | 0 | 1 | 12
4974 | 7/27 | 05:00:00 | 286.15 | 98850 | 3.6 | 260 | 9.6116 | 28.8 | 0 | 272.945 | 0 | 1 | 13
4975 | 7/27 | 06:00:00 | 286.15 | 98850 | 1.5 | 250 | 9.6116 | 237.6 | 176.4 | 273.212 | 0 | 1 | 13
4976 | 7/27 | 07:00:00 | 287.15 | 98858 | 2.1 | 220 | 9.6108 | 370.8 | 3.6 | 274.652 | 0 | 1 | 14
4977 | 7/27 | 08:00:00 | 289.15 | 98875 | 5.1 | 260 | 9.6091 | 1195.2 | 1116 | 276.076 | 0 | 1 | 16
4978 | 7/27 | 09:00:00 | 289.15 | 98875 | 6.2 | 250 | 9.6091 | 1717.2 | 1796.4 | 276.076 | 0 | 1 | 16
4979 | 7/27 | 10:00:00 | 291.15 | 98892 | 6.7 | 260 | 10.265 | 2160 | 2034 | 278.211 | 0 | 1 | 18
4980 | 7/27 | 11:00:00 | 291.15 | 98892 | 6.2 | 260 | 9.6075 | 2494.8 | 1807.2 | 277.986 | 0 | 1 | 18
4981 | 7/27 | 12:00:00 | 290.15 | 98883 | 5.1 | 230 | 9.6084 | 2685.6 | 2242.8 | 277.031 | 0 | 1 | 17
4982 | 7/27 | 13:00:00 | 291.15 | 98892 | 3.1 | 260 | 10.265 | 2718 | 2246.4 | 278.211 | 0 | 1 | 18
4983 | 7/27 | 14:00:00 | 291.15 | 98892 | 5.1 | 230 | 10.265 | 2595.6 | 2221.2 | 278.211 | 0 | 1 | 18
4984 | 7/27 | 15:00:00 | 290.15 | 98883 | 4.6 | 230 | 10.266 | 2322 | 2001.6 | 277.255 | 0 | 1 | 17
4985 | 7/27 | 16:00:00 | 291.15 | 98892 | 4.1 | 260 | 10.265 | 1918.8 | 1936.8 | 278.211 | 0 | 1 | 18
4986 | 7/27 | 17:00:00 | 291.15 | 98892 | 3.6 | 250 | 10.265 | 1425.6 | 1591.2 | 278.211 | 0 | 1 | 18
4987 | 7/27 | 18:00:00 | 290.15 | 98883 | 4.1 | 250 | 10.266 | 892.8 | 1116 | 277.255 | 0 | 1 | 17
4988 | 7/27 | 19:00:00 | 290.15 | 98883 | 4.1 | 220 | 10.266 | 432 | 543.6 | 276.984 | 0 | 1 | 17
4989 | 7/27 | 20:00:00 | 289.15 | 98875 | 4.1 | 230 | 10.2668 | 82.8 | 0 | 276.029 | 0 | 1 | 16
4990 | 7/27 | 21:00:00 | 289.15 | 98875 | 3.6 | 210 | 10.2668 | 0 | 0 | 276.029 | 0 | 1 | 16
4991 | 7/27 | 22:00:00 | 289.15 | 98875 | 3.1 | 200 | 10.2668 | 0 | 0 | 276.3 | 0 | 1 | 16
4992 | 7/27 | 23:00:00 | 289.15 | 98875 | 3.1 | 190 | 10.2668 | 0 | 0 | 276.789 | 0 | 1 | 16
4993 | 7/27 | 24:00:00 | 288.15 | 98867 | 3.6 | 200 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4994 | 7/28 | 01:00:00 | 288.15 | 98867 | 4.1 | 200 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4995 | 7/28 | 02:00:00 | 288.15 | 98867 | 5.1 | 210 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4996 | 7/28 | 03:00:00 | 289.15 | 98875 | 6.2 | 220 | 10.2668 | 0 | 0 | 276.789 | 0 | 1 | 16
4997 | 7/28 | 04:00:00 | 288.15 | 98867 | 5.1 | 230 | 10.9655 | 0 | 0 | 276.053 | 0 | 1 | 15
4998 | 7/28 | 05:00:00 | 288.15 | 98867 | 4.1 | 260 | 10.9655 | 14.4 | 0 | 276.053 | 0 | 1 | 15
4999 | 7/28 | 06:00:00 | 288.15 | 98867 | 4.6 | 280 | 10.9655 | 126 | 0 | 276.053 | 0 | 1 | 15
5000 | 7/28 | 07:00:00 | 288.15 | 98867 | 7.2 | 290 | 10.2677 | 658.8 | 921.6 | 275.344 | 0 | 1 | 15
5001 | 7/28 | 08:00:00 | 289.15 | 98875 | 4.6 | 300 | 10.9646 | 1180.8 | 1393.2 | 276.522 | 0 | 1 | 16
5002 | 7/28 | 09:00:00 | 289.15 | 98875 | 5.1 | 310 | 10.2668 | 1702.8 | 1774.8 | 276.3 | 0 | 1 | 16
5003 | 7/28 | 10:00:00 | 290.15 | 98883 | 4.1 | 320 | 10.266 | 2149.2 | 2034 | 277.255 | 0 | 1 | 17
5004 | 7/28 | 11:00:00 | 290.15 | 98883 | 3.6 | 300 | 10.266 | 2484 | 1796.4 | 277.255 | 0 | 1 | 17
5005 | 7/28 | 12:00:00 | 291.15 | 98892 | 4.6 | 300 | 10.265 | 2674.8 | 2239.2 | 278.211 | 0 | 1 | 18
5006 | 7/28 | 13:00:00 | 291.15 | 98892 | 5.7 | 280 | 10.265 | 2710.8 | 2246.4 | 278.211 | 0 | 1 | 18
5007 | 7/28 | 14:00:00 | 292.15 | 98900 | 5.7 | 280 | 9.6067 | 2588.4 | 2224.8 | 278.941 | 0 | 1 | 19
5008 | 7/28 | 15:00:00 | 292.15 | 98900 | 6.2 | 270 | 9.6067 | 2314.8 | 2008.8 | 278.941 | 0 | 1 | 19
5009 | 7/28 | 16:00:00 | 292.15 | 98900 | 6.7 | 270 | 9.6067 | 1911.6 | 1872 | 278.941 | 0 | 1 | 19
5010 | 7/28 | 17:00:00 | 291.15 | 98892 | 7.7 | 280 | 9.6075 | 1504.8 | 1972.8 | 277.714 | 0 | 1 | 18
5011 | 7/28 | 18:00:00 | 290.15 | 98883 | 7.7 | 290 | 8.9887 | 939.6 | 1220.4 | 276.535 | 0 | 1 | 17
5012 | 7/28 | 19:00:00 | 288.15 | 98867 | 5.7 | 270 | 8.9902 | 424.8 | 532.8 | 274.629 | 0 | 1 | 15
5013 | 7/28 | 20:00:00 | 287.15 | 98858 | 6.2 | 290 | 8.991 | 79.2 | 0 | 273.676 | 0 | 1 | 14
5014 | 7/28 | 21:00:00 | 286.15 | 98850 | 5.1 | 270 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
5015 | 7/28 | 22:00:00 | 285.15 | 98841 | 5.1 | 280 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
5016 | 7/28 | 23:00:00 | 285.15 | 98841 | 5.1 | 280 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
5017 | 7/28 | 24:00:00 | 285.15 | 98841 | 4.6 | 290 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
5018 | 7/29 | 01:00:00 | 285.15 | 98841 | 5.7 | 280 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
5019 | 7/29 | 02:00:00 | 284.15 | 98833 | 5.1 | 280 | 8.4095 | 0 | 0 | 271.449 | 0 | 1 | 11
5020 | 7/29 | 03:00:00 | 283.15 | 98824 | 3.1 | 280 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5021 | 7/29 | 04:00:00 | 283.15 | 98824 | 3.1 | 280 | 7.8605 | 0 | 0 | 269.42 | 0 | 1 | 10
5022 | 7/29 | 05:00:00 | 284.15 | 98833 | 3.1 | 250 | 8.4095 | 21.6 | 0 | 270.595 | 0 | 1 | 11
5023 | 7/29 | 06:00:00 | 285.15 | 98841 | 2.6 | 270 | 8.9926 | 237.6 | 223.2 | 271.77 | 0 | 1 | 12
5024 | 7/29 | 07:00:00 | 286.15 | 98850 | 2.6 | 250 | 8.9918 | 691.2 | 925.2 | 272.723 | 0 | 1 | 13
5025 | 7/29 | 08:00:00 | 287.15 | 98858 | 2.1 | 220 | 8.991 | 1249.2 | 1710 | 273.676 | 0 | 1 | 14
5026 | 7/29 | 09:00:00 | 288.15 | 98867 | 3.1 | 210 | 8.4065 | 1803.6 | 2242.8 | 274.404 | 0 | 1 | 15
5027 | 7/29 | 10:00:00 | 288.15 | 98867 | 2.1 | 180 | 8.9902 | 2149.2 | 1803.6 | 274.898 | 0 | 1 | 15
5028 | 7/29 | 11:00:00 | 289.15 | 98875 | 3.6 | 200 | 8.9895 | 1378.8 | 104.4 | 276.34 | 0 | 1 | 16
5029 | 7/29 | 12:00:00 | 287.15 | 98858 | 3.6 | 200 | 10.2686 | 1479.6 | 154.8 | 274.874 | 0 | 1 | 14
5030 | 7/29 | 13:00:00 | 287.15 | 98858 | 3.6 | 190 | 9.6108 | 1501.2 | 154.8 | 274.652 | 0 | 1 | 14
5031 | 7/29 | 14:00:00 | 287.15 | 98858 | 3.6 | 150 | 10.2686 | 1429.2 | 151.2 | 274.874 | 0 | 1 | 14
5032 | 7/29 | 15:00:00 | 287.15 | 98858 | 3.6 | 150 | 10.2686 | 1278 | 104.4 | 274.874 | 0 | 1 | 14
5033 | 7/29 | 16:00:00 | 286.15 | 98850 | 3.6 | 150 | 9.6116 | 1054.8 | 93.6 | 273.695 | 0 | 1 | 13
5034 | 7/29 | 17:00:00 | 286.15 | 98850 | 3.6 | 160 | 9.6116 | 781.2 | 93.6 | 273.695 | 0 | 1 | 13
5035 | 7/29 | 18:00:00 | 287.15 | 98858 | 3.1 | 160 | 10.2686 | 874.8 | 867.6 | 274.389 | 0 | 1 | 14
5036 | 7/29 | 19:00:00 | 288.15 | 98867 | 1.5 | 34 | 10.9655 | 388.8 | 399.6 | 275.565 | 0 | 1 | 15
5037 | 7/29 | 20:00:00 | 288.15 | 98867 | 1.5 | 97 | 10.9655 | 39.6 | 0 | 276.053 | 0 | 1 | 15
5038 | 7/29 | 21:00:00 | 288.15 | 98867 | 3.6 | 260 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
5039 | 7/29 | 22:00:00 | 288.15 | 98867 | 3.6 | 270 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
5040 | 7/29 | 23:00:00 | 288.15 | 98867 | 2.1 | 240 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
5041 | 7/29 | 24:00:00 | 288.15 | 98867 | 3.6 | 240 | 10.9655 | 0 | 0 | 275.296 | 0 | 1 | 15
5042 | 7/30 | 01:00:00 | 288.15 | 98867 | 1.5 | 224 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
5043 | 7/30 | 02:00:00 | 288.15 | 98867 | 2.6 | 240 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
5044 | 7/30 | 03:00:00 | 288.15 | 98867 | 2.6 | 240 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
5045 | 7/30 | 04:00:00 | 288.15 | 98867 | 3.1 | 230 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
5046 | 7/30 | 05:00:00 | 288.15 | 98867 | 1.5 | 177 | 10.9655 | 18 | 0 | 275.565 | 0 | 1 | 15
5047 | 7/30 | 06:00:00 | 288.15 | 98867 | 2.6 | 230 | 10.9655 | 118.8 | 0 | 276.053 | 0 | 1 | 15
5048 | 7/30 | 07:00:00 | 288.15 | 98867 | 2.6 | 260 | 10.9655 | 356.4 | 0 | 276.053 | 0 | 1 | 15
5049 | 7/30 | 08:00:00 | 288.15 | 98867 | 3.1 | 270 | 10.9655 | 1162.8 | 1087.2 | 275.565 | 0 | 1 | 15
5050 | 7/30 | 09:00:00 | 289.15 | 98875 | 4.1 | 290 | 10.9646 | 1681.2 | 1749.6 | 276.522 | 0 | 1 | 16
5051 | 7/30 | 10:00:00 | 289.15 | 98875 | 3.1 | 280 | 10.9646 | 2127.6 | 2019.6 | 276.522 | 0 | 1 | 16
5052 | 7/30 | 11:00:00 | 290.15 | 98883 | 4.1 | 290 | 11.7037 | 2458.8 | 1828.8 | 277.7 | 0 | 1 | 17
5053 | 7/30 | 12:00:00 | 291.15 | 98892 | 3.6 | 330 | 11.7026 | 1468.8 | 277.2 | 279.15 | 0 | 1 | 18
5054 | 7/30 | 13:00:00 | 288.15 | 98867 | 3.1 | 20 | 10.9655 | 2689.2 | 1522.8 | 275.565 | 0 | 1 | 15
5055 | 7/30 | 14:00:00 | 288.15 | 98867 | 2.6 | 40 | 10.9655 | 1422 | 356.4 | 276.053 | 0 | 1 | 15
5056 | 7/30 | 15:00:00 | 289.15 | 98875 | 1 | 208 | 10.9646 | 1270.8 | 115.2 | 277.011 | 0 | 1 | 16
5057 | 7/30 | 16:00:00 | 289.15 | 98875 | 1 | 142 | 10.9646 | 1886.4 | 1681.2 | 276.522 | 0 | 1 | 16
5058 | 7/30 | 17:00:00 | 290.15 | 98883 | 1.5 | 89 | 10.9637 | 1393.2 | 1562.4 | 277.478 | 0 | 1 | 17
5059 | 7/30 | 18:00:00 | 290.15 | 98883 | 3.1 | 220 | 10.9637 | 860.4 | 968.4 | 277.478 | 0 | 1 | 17
5060 | 7/30 | 19:00:00 | 289.15 | 98875 | 2.6 | 190 | 11.7047 | 381.6 | 381.6 | 276.743 | 0 | 1 | 16
5061 | 7/30 | 20:00:00 | 289.15 | 98875 | 2.6 | 290 | 10.2668 | 68.4 | 0 | 276.3 | 0 | 1 | 16
5062 | 7/30 | 21:00:00 | 287.15 | 98858 | 2.6 | 30 | 9.6108 | 0 | 0 | 274.167 | 0 | 1 | 14
5063 | 7/30 | 22:00:00 | 286.15 | 98850 | 1 | 55 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
5064 | 7/30 | 23:00:00 | 286.15 | 98850 | 1 | 152 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
5065 | 7/30 | 24:00:00 | 286.15 | 98850 | 1 | 330 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
5066 | 7/31 | 01:00:00 | 285.15 | 98841 | 0.5 | 152 | 8.9926 | 0 | 0 | 272.036 | 0 | 1 | 12
5067 | 7/31 | 02:00:00 | 284.15 | 98833 | 1.5 | 290 | 8.4095 | 0 | 0 | 270.595 | 0 | 1 | 11
5068 | 7/31 | 03:00:00 | 286.15 | 98850 | 3.6 | 280 | 8.6955 | 0 | 0 | 272.878 | 0 | 1 | 13
5069 | 7/31 | 04:00:00 | 285.15 | 98841 | 3.1 | 280 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
5070 | 7/31 | 05:00:00 | 285.15 | 98841 | 4.1 | 280 | 8.9926 | 7.2 | 0 | 272.517 | 0 | 1 | 12
5071 | 7/31 | 06:00:00 | 285.15 | 98841 | 3.6 | 290 | 8.9926 | 208.8 | 129.6 | 272.036 | 0 | 1 | 12
5072 | 7/31 | 07:00:00 | 285.15 | 98841 | 3.6 | 290 | 8.4088 | 633.6 | 745.2 | 271.813 | 0 | 1 | 12
5073 | 7/31 | 08:00:00 | 286.15 | 98850 | 5.1 | 280 | 8.408 | 1231.2 | 1522.8 | 272.499 | 0 | 1 | 13
5074 | 7/31 | 09:00:00 | 288.15 | 98867 | 6.2 | 290 | 7.857 | 1785.6 | 2232 | 274.177 | 0 | 1 | 15
5075 | 7/31 | 10:00:00 | 289.15 | 98875 | 7.2 | 280 | 8.4059 | 2131.2 | 2055.6 | 275.626 | 0 | 1 | 16
5076 | 7/31 | 11:00:00 | 290.15 | 98883 | 6.7 | 280 | 8.4052 | 2469.6 | 2055.6 | 276.579 | 0 | 1 | 17
5077 | 7/31 | 12:00:00 | 289.15 | 98875 | 5.7 | 290 | 8.4059 | 2660.4 | 2246.4 | 275.626 | 0 | 1 | 16
5078 | 7/31 | 13:00:00 | 289.15 | 98875 | 6.2 | 290 | 8.4059 | 2696.4 | 2253.6 | 275.626 | 0 | 1 | 16
5079 | 7/31 | 14:00:00 | 290.15 | 98883 | 6.7 | 280 | 7.8557 | 2574 | 1850.4 | 276.351 | 0 | 1 | 17
5080 | 7/31 | 15:00:00 | 289.15 | 98875 | 6.7 | 280 | 7.8564 | 1274.4 | 180 | 275.885 | 0 | 1 | 16
5081 | 7/31 | 16:00:00 | 288.15 | 98867 | 6.2 | 270 | 7.857 | 1051.2 | 68.4 | 274.931 | 0 | 1 | 15
5082 | 7/31 | 17:00:00 | 288.15 | 98867 | 4.6 | 270 | 7.857 | 1393.2 | 1263.6 | 274.446 | 0 | 1 | 15
5083 | 7/31 | 18:00:00 | 288.15 | 98867 | 5.7 | 270 | 8.4065 | 856.8 | 982.8 | 274.672 | 0 | 1 | 15
5084 | 7/31 | 19:00:00 | 286.35 | 98852 | 5.9 | 275 | 8.1289 | 374.4 | 320.4 | 272.844 | 0 | 1 | 13.2
5085 | 7/31 | 20:00:00 | 285.95 | 98848 | 5.7 | 272 | 8.2956 | 64.8 | 0 | 272.53 | 0 | 1 | 12.8
5086 | 7/31 | 21:00:00 | 285.35 | 98843 | 5.5 | 270 | 8.296 | 0 | 0 | 271.959 | 0 | 1 | 12.2
5087 | 7/31 | 22:00:00 | 285.15 | 98841 | 4.5 | 265 | 8.1298 | 0 | 0 | 272.292 | 0 | 1 | 12
5088 | 7/31 | 23:00:00 | 285.15 | 98841 | 2.9 | 205 | 7.8591 | 0 | 0 | 272.179 | 0 | 1 | 12
5089 | 7/31 | 24:00:00 | 285.15 | 98841 | 2 | 145 | 7.5965 | 0 | 0 | 272.066 | 0 | 1 | 12
5090 | 8/1 | 01:00:00 | 285.15 | 98841 | 0.6 | 88 | 7.4428 | 0 | 0 | 271.888 | 0 | 1 | 12
5091 | 8/1 | 02:00:00 | 285.15 | 98841 | 0.6 | 34 | 7.5965 | 0 | 0 | 272.066 | 0 | 1 | 12
5092 | 8/1 | 03:00:00 | 284.95 | 98839 | 0.9 | 69 | 7.7533 | 0 | 0 | 271.943 | 0 | 1 | 11.8
5093 | 8/1 | 04:00:00 | 284.65 | 98837 | 0.9 | 76 | 7.8594 | 0 | 0 | 271.592 | 0 | 1 | 11.5
5094 | 8/1 | 05:00:00 | 284.65 | 98837 | 0.9 | 82 | 7.8594 | 3.6 | 0 | 271.702 | 0 | 1 | 11.5
5095 | 8/1 | 06:00:00 | 284.65 | 98837 | 0.8 | 95 | 7.8594 | 64.8 | 0 | 271.702 | 0 | 1 | 11.5
5096 | 8/1 | 07:00:00 | 284.15 | 98833 | 1 | 45 | 7.8598 | 208.8 | 0 | 271.225 | 0 | 1 | 11
5097 | 8/1 | 08:00:00 | 285.15 | 98841 | 0.5 | 66 | 7.8591 | 385.2 | 0 | 272.179 | 0 | 1 | 12
5098 | 8/1 | 09:00:00 | 285.15 | 98841 | 0.5 | 99 | 7.8591 | 921.6 | 122.4 | 272.069 | 0 | 1 | 12
5099 | 8/1 | 10:00:00 | 286.15 | 98850 | 0.5 | 204 | 8.408 | 1173.6 | 100.8 | 273.248 | 0 | 1 | 13
5100 | 8/1 | 11:00:00 | 287.15 | 98858 | 1 | 31 | 8.4073 | 1357.2 | 108 | 274.203 | 0 | 1 | 14
5101 | 8/1 | 12:00:00 | 288.15 | 98867 | 0.5 | 257 | 8.9902 | 1461.6 | 154.8 | 275.384 | 0 | 1 | 15
5102 | 8/1 | 13:00:00 | 289.15 | 98875 | 0.5 | 259 | 8.9895 | 1483.2 | 158.4 | 276.34 | 0 | 1 | 16
5103 | 8/1 | 14:00:00 | 289.15 | 98875 | 1.5 | 97 | 8.4059 | 1414.8 | 154.8 | 276.113 | 0 | 1 | 16
5104 | 8/1 | 15:00:00 | 289.15 | 98875 | 3.1 | 180 | 8.9895 | 1260 | 104.4 | 276.34 | 0 | 1 | 16
5105 | 8/1 | 16:00:00 | 289.15 | 98875 | 2.6 | 190 | 8.9895 | 1033.2 | 93.6 | 276.34 | 0 | 1 | 16
5106 | 8/1 | 17:00:00 | 289.15 | 98875 | 2.6 | 170 | 8.9895 | 759.6 | 68.4 | 276.34 | 0 | 1 | 16
5107 | 8/1 | 18:00:00 | 289.15 | 98875 | 1.5 | 305 | 8.9895 | 460.8 | 21.6 | 276.34 | 0 | 1 | 16
5108 | 8/1 | 19:00:00 | 289.15 | 98875 | 0.5 | 39 | 8.9895 | 198 | 0 | 276.34 | 0 | 1 | 16
5109 | 8/1 | 20:00:00 | 288.15 | 98867 | 1.5 | 24 | 8.4065 | 32.4 | 0 | 275.158 | 0 | 1 | 15
5110 | 8/1 | 21:00:00 | 287.15 | 98858 | 1 | 280 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
5111 | 8/1 | 22:00:00 | 287.15 | 98858 | 1 | 280 | 8.991 | 0 | 0 | 273.944 | 0 | 1 | 14
5112 | 8/1 | 23:00:00 | 286.15 | 98850 | 2.1 | 280 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
5113 | 8/1 | 24:00:00 | 285.15 | 98841 | 1.5 | 250 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5114 | 8/2 | 01:00:00 | 285.15 | 98841 | 1 | 250 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
5115 | 8/2 | 02:00:00 | 285.15 | 98841 | 1 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5116 | 8/2 | 03:00:00 | 285.15 | 98841 | 2.1 | 250 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5117 | 8/2 | 04:00:00 | 284.15 | 98833 | 2.1 | 280 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
5118 | 8/2 | 05:00:00 | 284.15 | 98833 | 3.1 | 270 | 7.3425 | 3.6 | 0 | 270.147 | 0 | 1 | 11
5119 | 8/2 | 06:00:00 | 285.15 | 98841 | 1.5 | 270 | 7.8591 | 198 | 79.2 | 271.323 | 0 | 1 | 12
5120 | 8/2 | 07:00:00 | 286.15 | 98850 | 3.1 | 260 | 7.8584 | 464.4 | 154.8 | 272.909 | 0 | 1 | 13
5121 | 8/2 | 08:00:00 | 287.15 | 98858 | 4.1 | 280 | 7.8578 | 975.6 | 716.4 | 273.743 | 0 | 1 | 14
5122 | 8/2 | 09:00:00 | 289.15 | 98875 | 4.1 | 240 | 7.8564 | 1623.6 | 1501.2 | 275.398 | 0 | 1 | 16
5123 | 8/2 | 10:00:00 | 290.15 | 98883 | 4.1 | 250 | 7.8557 | 2232 | 2379.6 | 276.08 | 0 | 1 | 17
5124 | 8/2 | 11:00:00 | 291.15 | 98892 | 4.6 | 260 | 7.855 | 2592 | 2703.6 | 277.032 | 0 | 1 | 18
5125 | 8/2 | 12:00:00 | 292.15 | 98900 | 4.1 | 240 | 8.4037 | 2793.6 | 2775.6 | 278.213 | 0 | 1 | 19
5126 | 8/2 | 13:00:00 | 293.15 | 98908 | 4.6 | 240 | 8.403 | 2829.6 | 2790 | 279.165 | 0 | 1 | 20
5127 | 8/2 | 14:00:00 | 293.15 | 98908 | 5.1 | 240 | 7.8537 | 2700 | 2674.8 | 278.935 | 0 | 1 | 20
5128 | 8/2 | 15:00:00 | 294.15 | 98916 | 5.1 | 220 | 8.4023 | 2264.4 | 1994.4 | 280.392 | 0 | 1 | 21
5129 | 8/2 | 16:00:00 | 294.15 | 98916 | 6.2 | 250 | 7.8531 | 1857.6 | 2008.8 | 280.16 | 0 | 1 | 21
5130 | 8/2 | 17:00:00 | 293.15 | 98908 | 6.2 | 280 | 8.9864 | 1436.4 | 1911.6 | 279.394 | 0 | 1 | 20
5131 | 8/2 | 18:00:00 | 292.15 | 98900 | 6.2 | 270 | 8.9872 | 871.2 | 1155.6 | 278.441 | 0 | 1 | 19
5132 | 8/2 | 19:00:00 | 291.15 | 98892 | 6.7 | 260 | 8.4044 | 367.2 | 442.8 | 277.261 | 0 | 1 | 18
5133 | 8/2 | 20:00:00 | 289.15 | 98875 | 5.1 | 250 | 8.4059 | 61.2 | 0 | 275.356 | 0 | 1 | 16
5134 | 8/2 | 21:00:00 | 288.15 | 98867 | 6.2 | 240 | 8.9902 | 0 | 0 | 274.629 | 0 | 1 | 15
5135 | 8/2 | 22:00:00 | 287.15 | 98858 | 5.1 | 230 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
5136 | 8/2 | 23:00:00 | 287.15 | 98858 | 3.1 | 230 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
5137 | 8/2 | 24:00:00 | 287.15 | 98858 | 4.1 | 250 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
5138 | 8/3 | 01:00:00 | 286.15 | 98850 | 5.7 | 270 | 9.6116 | 0 | 0 | 272.945 | 0 | 1 | 13
5139 | 8/3 | 02:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
5140 | 8/3 | 03:00:00 | 285.15 | 98841 | 3.6 | 270 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
5141 | 8/3 | 04:00:00 | 283.15 | 98824 | 3.1 | 270 | 7.8605 | 0 | 0 | 269.42 | 0 | 1 | 10
5142 | 8/3 | 05:00:00 | 284.15 | 98833 | 3.6 | 240 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
5143 | 8/3 | 06:00:00 | 286.15 | 98850 | 5.7 | 250 | 8.408 | 190.8 | 136.8 | 272.499 | 0 | 1 | 13
5144 | 8/3 | 07:00:00 | 287.15 | 98858 | 6.7 | 260 | 8.991 | 594 | 691.2 | 273.944 | 0 | 1 | 14
5145 | 8/3 | 08:00:00 | 287.15 | 98858 | 9.3 | 270 | 8.991 | 1116 | 1357.2 | 273.944 | 0 | 1 | 14
5146 | 8/3 | 09:00:00 | 288.15 | 98867 | 10.3 | 270 | 8.9902 | 1638 | 1767.6 | 274.898 | 0 | 1 | 15
5147 | 8/3 | 10:00:00 | 289.15 | 98875 | 9.3 | 280 | 7.8564 | 2095.2 | 1980 | 275.398 | 0 | 1 | 16
5148 | 8/3 | 11:00:00 | 290.15 | 98883 | 8.7 | 260 | 7.8557 | 2433.6 | 2210.4 | 276.351 | 0 | 1 | 17
5149 | 8/3 | 12:00:00 | 289.15 | 98875 | 7.7 | 280 | 7.8564 | 2624.4 | 2246.4 | 275.398 | 0 | 1 | 16
5150 | 8/3 | 13:00:00 | 289.15 | 98875 | 9.8 | 270 | 7.8564 | 2660.4 | 2253.6 | 275.398 | 0 | 1 | 16
5151 | 8/3 | 14:00:00 | 290.15 | 98883 | 9.3 | 270 | 7.8557 | 2534.4 | 2228.4 | 276.351 | 0 | 1 | 17
5152 | 8/3 | 15:00:00 | 290.15 | 98883 | 9.3 | 270 | 7.8557 | 2253.6 | 2026.8 | 276.351 | 0 | 1 | 17
5153 | 8/3 | 16:00:00 | 290.15 | 98883 | 10.3 | 270 | 7.8557 | 1846.8 | 1864.8 | 276.351 | 0 | 1 | 17
5154 | 8/3 | 17:00:00 | 290.15 | 98883 | 10.3 | 270 | 7.8557 | 1346.4 | 1465.2 | 276.351 | 0 | 1 | 17
5155 | 8/3 | 18:00:00 | 289.15 | 98875 | 10.8 | 280 | 7.8564 | 813.6 | 982.8 | 275.398 | 0 | 1 | 16
5156 | 8/3 | 19:00:00 | 288.15 | 98867 | 6.7 | 270 | 7.857 | 356.4 | 356.4 | 274.177 | 0 | 1 | 15
5157 | 8/3 | 20:00:00 | 287.15 | 98858 | 7.7 | 260 | 8.4073 | 57.6 | 0 | 273.451 | 0 | 1 | 14
5158 | 8/3 | 21:00:00 | 287.15 | 98858 | 7.2 | 270 | 8.4073 | 0 | 0 | 273.451 | 0 | 1 | 14
5159 | 8/3 | 22:00:00 | 286.15 | 98850 | 6.2 | 260 | 8.408 | 0 | 0 | 272.499 | 0 | 1 | 13
5160 | 8/3 | 23:00:00 | 286.15 | 98850 | 5.7 | 260 | 8.408 | 0 | 0 | 272.499 | 0 | 1 | 13
5161 | 8/3 | 24:00:00 | 286.15 | 98850 | 6.7 | 270 | 7.8584 | 0 | 0 | 272.274 | 0 | 1 | 13
5162 | 8/4 | 01:00:00 | 286.15 | 98850 | 6.7 | 270 | 7.8584 | 0 | 0 | 272.274 | 0 | 1 | 13
5163 | 8/4 | 02:00:00 | 285.15 | 98841 | 7.2 | 270 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
5164 | 8/4 | 03:00:00 | 285.15 | 98841 | 5.1 | 260 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
5165 | 8/4 | 04:00:00 | 285.15 | 98841 | 8.2 | 270 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
5166 | 8/4 | 05:00:00 | 285.15 | 98841 | 6.7 | 270 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
5167 | 8/4 | 06:00:00 | 286.15 | 98850 | 6.2 | 270 | 8.408 | 172.8 | 25.2 | 272.766 | 0 | 1 | 13
5168 | 8/4 | 07:00:00 | 287.15 | 98858 | 8.2 | 260 | 8.991 | 583.2 | 680.4 | 273.944 | 0 | 1 | 14
5169 | 8/4 | 08:00:00 | 287.15 | 98858 | 7.2 | 260 | 8.4073 | 1105.2 | 1357.2 | 273.719 | 0 | 1 | 14
5170 | 8/4 | 09:00:00 | 288.15 | 98867 | 7.2 | 260 | 8.4065 | 1627.2 | 1774.8 | 274.672 | 0 | 1 | 15
5171 | 8/4 | 10:00:00 | 288.15 | 98867 | 8.2 | 270 | 8.4065 | 2080.8 | 2044.8 | 274.672 | 0 | 1 | 15
5172 | 8/4 | 11:00:00 | 288.15 | 98867 | 7.7 | 270 | 8.4065 | 2419.2 | 2052 | 274.672 | 0 | 1 | 15
5173 | 8/4 | 12:00:00 | 289.15 | 98875 | 6.7 | 260 | 8.4059 | 2613.6 | 2242.8 | 275.626 | 0 | 1 | 16
5174 | 8/4 | 13:00:00 | 289.15 | 98875 | 5.7 | 260 | 8.4059 | 2646 | 2250 | 275.626 | 0 | 1 | 16
5175 | 8/4 | 14:00:00 | 289.15 | 98875 | 6.7 | 270 | 8.4059 | 2520 | 2224.8 | 275.626 | 0 | 1 | 16
5176 | 8/4 | 15:00:00 | 289.15 | 98875 | 6.2 | 270 | 8.4059 | 2239.2 | 2019.6 | 275.626 | 0 | 1 | 16
5177 | 8/4 | 16:00:00 | 289.15 | 98875 | 6.7 | 260 | 7.8564 | 1836 | 1861.2 | 275.398 | 0 | 1 | 16
5178 | 8/4 | 17:00:00 | 289.15 | 98875 | 6.7 | 260 | 7.8564 | 1335.6 | 1519.2 | 275.398 | 0 | 1 | 16
5179 | 8/4 | 18:00:00 | 288.15 | 98867 | 5.1 | 260 | 8.4065 | 846 | 1130.4 | 274.404 | 0 | 1 | 15
5180 | 8/4 | 19:00:00 | 288.15 | 98867 | 3.6 | 250 | 8.9902 | 324 | 309.6 | 274.898 | 0 | 1 | 15
5181 | 8/4 | 20:00:00 | 288.15 | 98867 | 4.1 | 260 | 8.4065 | 50.4 | 0 | 274.672 | 0 | 1 | 15
5182 | 8/4 | 21:00:00 | 286.15 | 98850 | 4.1 | 250 | 8.9918 | 0 | 0 | 272.99 | 0 | 1 | 13
5183 | 8/4 | 22:00:00 | 286.15 | 98850 | 4.6 | 270 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
5184 | 8/4 | 23:00:00 | 285.15 | 98841 | 3.1 | 220 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
5185 | 8/4 | 24:00:00 | 285.15 | 98841 | 3.6 | 210 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
5186 | 8/5 | 01:00:00 | 285.15 | 98841 | 1.5 | 230 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
5187 | 8/5 | 02:00:00 | 285.15 | 98841 | 1.5 | 205 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
5188 | 8/5 | 03:00:00 | 285.15 | 98841 | 2.1 | 220 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
5189 | 8/5 | 04:00:00 | 285.15 | 98841 | 1.5 | 240 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
5190 | 8/5 | 05:00:00 | 285.15 | 98841 | 1.5 | 263 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
5191 | 8/5 | 06:00:00 | 285.15 | 98841 | 3.1 | 280 | 8.9926 | 90 | 0 | 272.517 | 0 | 1 | 12
5192 | 8/5 | 07:00:00 | 286.15 | 98850 | 3.6 | 300 | 8.9918 | 572.4 | 806.4 | 272.99 | 0 | 1 | 13
5193 | 8/5 | 08:00:00 | 287.15 | 98858 | 4.1 | 310 | 8.4073 | 1094.4 | 1346.4 | 273.719 | 0 | 1 | 14
5194 | 8/5 | 09:00:00 | 288.15 | 98867 | 7.2 | 310 | 8.9902 | 1612.8 | 1382.4 | 274.898 | 0 | 1 | 15
5195 | 8/5 | 10:00:00 | 288.15 | 98867 | 7.7 | 300 | 7.857 | 1148.4 | 172.8 | 274.931 | 0 | 1 | 15
5196 | 8/5 | 11:00:00 | 289.15 | 98875 | 6.2 | 310 | 7.3393 | 2415.6 | 1900.8 | 275.169 | 0 | 1 | 16
5197 | 8/5 | 12:00:00 | 290.15 | 98883 | 8.2 | 280 | 6.8523 | 2613.6 | 2257.2 | 275.89 | 0 | 1 | 17
5198 | 8/5 | 13:00:00 | 290.15 | 98883 | 9.3 | 280 | 7.3387 | 2642.4 | 2257.2 | 276.121 | 0 | 1 | 17
5199 | 8/5 | 14:00:00 | 290.15 | 98883 | 8.2 | 280 | 7.8557 | 2512.8 | 2228.4 | 276.351 | 0 | 1 | 17
5200 | 8/5 | 15:00:00 | 290.15 | 98883 | 9.8 | 290 | 12.4883 | 2206.8 | 2206.8 | 277.92 | 0 | 1 | 17
5201 | 8/5 | 16:00:00 | 290.15 | 98883 | 9.8 | 290 | 12.4883 | 1803.6 | 1951.2 | 277.92 | 0 | 1 | 17
5202 | 8/5 | 17:00:00 | 289.15 | 98875 | 10.3 | 280 | 11.7047 | 1389.6 | 1818 | 276.472 | 0 | 1 | 16
5203 | 8/5 | 18:00:00 | 289.15 | 98875 | 10.3 | 280 | 11.7047 | 828 | 1087.2 | 276.472 | 0 | 1 | 16
5204 | 8/5 | 19:00:00 | 287.15 | 98858 | 8.7 | 290 | 10.2686 | 334.8 | 385.2 | 274.12 | 0 | 1 | 14
5205 | 8/5 | 20:00:00 | 286.15 | 98850 | 6.7 | 270 | 9.6116 | 14.4 | 0 | 273.806 | 0 | 1 | 13
5206 | 8/5 | 21:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.9926 | 0 | 0 | 272.627 | 0 | 1 | 12
5207 | 8/5 | 22:00:00 | 285.15 | 98841 | 7.7 | 270 | 8.9926 | 0 | 0 | 272.627 | 0 | 1 | 12
5208 | 8/5 | 23:00:00 | 284.15 | 98833 | 6.7 | 270 | 8.4095 | 0 | 0 | 271.449 | 0 | 1 | 11
5209 | 8/5 | 24:00:00 | 284.15 | 98833 | 6.7 | 270 | 8.4095 | 0 | 0 | 271.449 | 0 | 1 | 11
5210 | 8/6 | 01:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5211 | 8/6 | 02:00:00 | 283.15 | 98824 | 6.2 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5212 | 8/6 | 03:00:00 | 283.15 | 98824 | 7.7 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5213 | 8/6 | 04:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5214 | 8/6 | 05:00:00 | 283.15 | 98824 | 4.1 | 260 | 7.8605 | 0 | 0 | 269.684 | 0 | 1 | 10
5215 | 8/6 | 06:00:00 | 283.15 | 98824 | 6.2 | 280 | 7.8605 | 169.2 | 68.4 | 269.42 | 0 | 1 | 10
5216 | 8/6 | 07:00:00 | 284.15 | 98833 | 5.1 | 290 | 8.4095 | 597.6 | 806.4 | 270.595 | 0 | 1 | 11
5217 | 8/6 | 08:00:00 | 285.15 | 98841 | 5.1 | 280 | 8.9926 | 1148.4 | 1616.4 | 271.77 | 0 | 1 | 12
5218 | 8/6 | 09:00:00 | 287.15 | 98858 | 7.2 | 280 | 10.2686 | 1695.6 | 2170.8 | 274.12 | 0 | 1 | 14
5219 | 8/6 | 10:00:00 | 288.15 | 98867 | 7.7 | 280 | 10.9655 | 2170.8 | 2476.8 | 275.296 | 0 | 1 | 15
5220 | 8/6 | 11:00:00 | 288.15 | 98867 | 7.7 | 290 | 7.3399 | 2548.8 | 2624.4 | 273.95 | 0 | 1 | 15
5221 | 8/6 | 12:00:00 | 288.15 | 98867 | 7.7 | 270 | 7.3399 | 2599.2 | 2188.8 | 274.218 | 0 | 1 | 15
5222 | 8/6 | 13:00:00 | 289.15 | 98875 | 8.2 | 270 | 7.3393 | 2631.6 | 2257.2 | 275.169 | 0 | 1 | 16
5223 | 8/6 | 14:00:00 | 289.15 | 98875 | 7.7 | 270 | 7.3393 | 2505.6 | 2232 | 275.169 | 0 | 1 | 16
5224 | 8/6 | 15:00:00 | 290.15 | 98883 | 8.2 | 270 | 6.8523 | 2228.4 | 2041.2 | 275.89 | 0 | 1 | 17
5225 | 8/6 | 16:00:00 | 289.15 | 98875 | 8.7 | 270 | 6.8529 | 1814.4 | 1868.4 | 274.939 | 0 | 1 | 16
5226 | 8/6 | 17:00:00 | 289.15 | 98875 | 8.2 | 280 | 7.3393 | 1310.4 | 1512 | 275.169 | 0 | 1 | 16
5227 | 8/6 | 18:00:00 | 288.15 | 98867 | 7.2 | 270 | 6.8534 | 824.4 | 1177.2 | 273.72 | 0 | 1 | 15
5228 | 8/6 | 19:00:00 | 287.15 | 98858 | 6.7 | 260 | 6.854 | 324 | 316.8 | 272.77 | 0 | 1 | 14
5229 | 8/6 | 20:00:00 | 286.15 | 98850 | 5.1 | 270 | 6.8546 | 46.8 | 0 | 271.821 | 0 | 1 | 13
5230 | 8/6 | 21:00:00 | 285.15 | 98841 | 7.2 | 290 | 6.8552 | 0 | 0 | 270.871 | 0 | 1 | 12
5231 | 8/6 | 22:00:00 | 284.15 | 98833 | 5.1 | 340 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
5232 | 8/6 | 23:00:00 | 284.15 | 98833 | 6.2 | 310 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
5233 | 8/6 | 24:00:00 | 284.15 | 98833 | 4.1 | 310 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
5234 | 8/7 | 01:00:00 | 284.15 | 98833 | 3.6 | 320 | 6.8558 | 0 | 0 | 270.549 | 0 | 1 | 11
5235 | 8/7 | 02:00:00 | 283.15 | 98824 | 2.6 | 320 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
5236 | 8/7 | 03:00:00 | 281.15 | 98806 | 3.1 | 290 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
5237 | 8/7 | 04:00:00 | 281.15 | 98806 | 2.6 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
5238 | 8/7 | 05:00:00 | 281.15 | 98806 | 3.1 | 310 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
5239 | 8/7 | 06:00:00 | 282.15 | 98815 | 3.1 | 290 | 6.8571 | 68.4 | 0 | 268.867 | 0 | 1 | 9
5240 | 8/7 | 07:00:00 | 284.15 | 98833 | 3.6 | 320 | 6.8558 | 424.8 | 201.6 | 270.549 | 0 | 1 | 11
5241 | 8/7 | 08:00:00 | 286.15 | 98850 | 4.1 | 320 | 6.8546 | 1141.2 | 1476 | 271.821 | 0 | 1 | 13
5242 | 8/7 | 09:00:00 | 287.15 | 98858 | 5.7 | 350 | 5.5627 | 1706.4 | 2181.6 | 272.077 | 0 | 1 | 14
5243 | 8/7 | 10:00:00 | 288.15 | 98867 | 6.2 | 350 | 5.5621 | 2066.4 | 2163.6 | 273.292 | 0 | 1 | 15
5244 | 8/7 | 11:00:00 | 289.15 | 98875 | 6.2 | 360 | 5.5617 | 2408.4 | 2242.8 | 274.24 | 0 | 1 | 16
5245 | 8/7 | 12:00:00 | 288.15 | 98867 | 5.1 | 360 | 5.5621 | 2602.8 | 2282.4 | 273.292 | 0 | 1 | 15
5246 | 8/7 | 13:00:00 | 288.15 | 98867 | 5.7 | 360 | 5.5621 | 2635.2 | 2286 | 273.292 | 0 | 1 | 15
5247 | 8/7 | 14:00:00 | 289.15 | 98875 | 4.6 | 360 | 6.3955 | 2498.4 | 2242.8 | 274.708 | 0 | 1 | 16
5248 | 8/7 | 15:00:00 | 289.15 | 98875 | 4.6 | 10 | 6.8529 | 2214 | 2037.6 | 274.939 | 0 | 1 | 16
5249 | 8/7 | 16:00:00 | 289.15 | 98875 | 4.6 | 350 | 6.3955 | 1803.6 | 1868.4 | 274.708 | 0 | 1 | 16
5250 | 8/7 | 17:00:00 | 289.15 | 98875 | 5.1 | 360 | 5.9656 | 1303.2 | 1461.6 | 274.475 | 0 | 1 | 16
5251 | 8/7 | 18:00:00 | 289.15 | 98875 | 4.1 | 360 | 6.3955 | 766.8 | 950.4 | 274.708 | 0 | 1 | 16
5252 | 8/7 | 19:00:00 | 288.15 | 98867 | 3.1 | 340 | 5.9661 | 313.2 | 302.4 | 273.258 | 0 | 1 | 15
5253 | 8/7 | 20:00:00 | 286.15 | 98850 | 2.6 | 300 | 6.3971 | 39.6 | 0 | 271.858 | 0 | 1 | 13
5254 | 8/7 | 21:00:00 | 286.15 | 98850 | 3.1 | 320 | 5.9671 | 0 | 0 | 271.496 | 0 | 1 | 13
5255 | 8/7 | 22:00:00 | 285.15 | 98841 | 2.6 | 360 | 6.8552 | 0 | 0 | 271.384 | 0 | 1 | 12
5256 | 8/7 | 23:00:00 | 283.15 | 98824 | 0.5 | 317 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
5257 | 8/7 | 24:00:00 | 283.15 | 98824 | 1 | 102 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
5258 | 8/8 | 01:00:00 | 282.15 | 98815 | 2.1 | 300 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
5259 | 8/8 | 02:00:00 | 283.15 | 98824 | 2.6 | 350 | 6.3988 | 0 | 0 | 269.37 | 0 | 1 | 10
5260 | 8/8 | 03:00:00 | 282.15 | 98815 | 3.1 | 350 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
5261 | 8/8 | 04:00:00 | 281.15 | 98806 | 2.6 | 310 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
5262 | 8/8 | 05:00:00 | 282.15 | 98815 | 3.6 | 350 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
5263 | 8/8 | 06:00:00 | 282.15 | 98815 | 3.1 | 360 | 6.3994 | 93.6 | 0 | 268.532 | 0 | 1 | 9
5264 | 8/8 | 07:00:00 | 284.15 | 98833 | 2.1 | 330 | 6.8558 | 417.6 | 158.4 | 270.549 | 0 | 1 | 11
5265 | 8/8 | 08:00:00 | 284.15 | 98833 | 1.5 | 128 | 6.8558 | 817.2 | 435.6 | 270.549 | 0 | 1 | 11
5266 | 8/8 | 09:00:00 | 286.15 | 98850 | 1.5 | 224 | 7.3412 | 1375.2 | 961.2 | 272.563 | 0 | 1 | 13
5267 | 8/8 | 10:00:00 | 288.15 | 98867 | 2.6 | 320 | 7.3399 | 2167.2 | 2235.6 | 273.95 | 0 | 1 | 15
5268 | 8/8 | 11:00:00 | 290.15 | 98883 | 2.6 | 300 | 7.3387 | 2527.2 | 2692.8 | 275.851 | 0 | 1 | 17
5269 | 8/8 | 12:00:00 | 291.15 | 98892 | 2.6 | 300 | 7.338 | 2732.4 | 2772 | 276.802 | 0 | 1 | 18
5270 | 8/8 | 13:00:00 | 293.15 | 98908 | 5.1 | 300 | 7.3368 | 2768.4 | 2786.4 | 278.703 | 0 | 1 | 20
5271 | 8/8 | 14:00:00 | 292.15 | 98900 | 6.2 | 290 | 7.8544 | 2628 | 2728.8 | 277.983 | 0 | 1 | 19
5272 | 8/8 | 15:00:00 | 292.15 | 98900 | 5.1 | 280 | 7.8544 | 2329.2 | 2430 | 277.983 | 0 | 1 | 19
5273 | 8/8 | 16:00:00 | 293.15 | 98908 | 4.6 | 290 | 7.8537 | 1785.6 | 1832.4 | 279.208 | 0 | 1 | 20
5274 | 8/8 | 17:00:00 | 292.15 | 98900 | 6.2 | 270 | 7.8544 | 1353.6 | 1699.2 | 277.983 | 0 | 1 | 19
5275 | 8/8 | 18:00:00 | 292.15 | 98900 | 6.2 | 270 | 7.8544 | 792 | 1112.4 | 277.983 | 0 | 1 | 19
5276 | 8/8 | 19:00:00 | 291.15 | 98892 | 5.1 | 280 | 7.855 | 298.8 | 259.2 | 277.17 | 0 | 1 | 18
5277 | 8/8 | 20:00:00 | 289.15 | 98875 | 5.1 | 280 | 7.8564 | 36 | 0 | 275.398 | 0 | 1 | 16
5278 | 8/8 | 21:00:00 | 288.15 | 98867 | 4.6 | 290 | 7.3399 | 0 | 0 | 274.218 | 0 | 1 | 15
5279 | 8/8 | 22:00:00 | 286.15 | 98850 | 5.7 | 290 | 7.3412 | 0 | 0 | 272.563 | 0 | 1 | 13
5280 | 8/8 | 23:00:00 | 286.15 | 98850 | 5.1 | 300 | 7.3412 | 0 | 0 | 272.563 | 0 | 1 | 13
5281 | 8/8 | 24:00:00 | 285.15 | 98841 | 0.5 | 24 | 7.3418 | 0 | 0 | 271.729 | 0 | 1 | 12
5282 | 8/9 | 01:00:00 | 285.15 | 98841 | 3.6 | 320 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5283 | 8/9 | 02:00:00 | 284.15 | 98833 | 1.5 | 290 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
5284 | 8/9 | 03:00:00 | 284.15 | 98833 | 1.5 | 290 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
5285 | 8/9 | 04:00:00 | 284.15 | 98833 | 1 | 360 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
5286 | 8/9 | 05:00:00 | 284.15 | 98833 | 2.1 | 300 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
5287 | 8/9 | 06:00:00 | 285.15 | 98841 | 2.6 | 290 | 8.4088 | 75.6 | 0 | 272.294 | 0 | 1 | 12
5288 | 8/9 | 07:00:00 | 285.15 | 98841 | 2.1 | 280 | 8.4088 | 295.2 | 0 | 272.294 | 0 | 1 | 12
5289 | 8/9 | 08:00:00 | 287.15 | 98858 | 4.1 | 310 | 8.4073 | 806.4 | 439.2 | 274.088 | 0 | 1 | 14
5290 | 8/9 | 09:00:00 | 287.15 | 98858 | 3.1 | 310 | 8.4073 | 1206 | 558 | 274.088 | 0 | 1 | 14
5291 | 8/9 | 10:00:00 | 289.15 | 98875 | 2.1 | 280 | 8.9895 | 1749.6 | 1087.2 | 276.104 | 0 | 1 | 16
5292 | 8/9 | 11:00:00 | 290.15 | 98883 | 1.5 | 320 | 8.4052 | 2322 | 1875.6 | 276.579 | 0 | 1 | 17
5293 | 8/9 | 12:00:00 | 292.15 | 98900 | 1 | 277 | 8.9872 | 2707.2 | 2689.2 | 278.441 | 0 | 1 | 19
5294 | 8/9 | 13:00:00 | 293.15 | 98908 | 2.6 | 217 | 8.9864 | 2743.2 | 2764.8 | 279.394 | 0 | 1 | 20
5295 | 8/9 | 14:00:00 | 293.15 | 98908 | 4.6 | 260 | 8.403 | 2610 | 2718 | 279.165 | 0 | 1 | 20
5296 | 8/9 | 15:00:00 | 294.15 | 98916 | 5.1 | 300 | 7.8531 | 2314.8 | 2113.2 | 279.886 | 0 | 1 | 21
5297 | 8/9 | 16:00:00 | 293.15 | 98908 | 5.1 | 300 | 8.403 | 979.2 | 234 | 279.933 | 0 | 1 | 20
5298 | 8/9 | 17:00:00 | 291.15 | 98892 | 2.6 | 30 | 8.9879 | 702 | 64.8 | 278.251 | 0 | 1 | 18
5299 | 8/9 | 18:00:00 | 290.15 | 98883 | 3.1 | 50 | 8.9887 | 406.8 | 10.8 | 277.295 | 0 | 1 | 17
5300 | 8/9 | 19:00:00 | 289.15 | 98875 | 2.1 | 80 | 8.9895 | 151.2 | 0 | 276.34 | 0 | 1 | 16
5301 | 8/9 | 20:00:00 | 288.15 | 98867 | 1 | 146 | 8.4065 | 18 | 0 | 275.158 | 0 | 1 | 15
5302 | 8/9 | 21:00:00 | 287.15 | 98858 | 1 | 152 | 8.4073 | 0 | 0 | 274.203 | 0 | 1 | 14
5303 | 8/9 | 22:00:00 | 286.15 | 98850 | 3.6 | 260 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
5304 | 8/9 | 23:00:00 | 286.15 | 98850 | 1 | 225 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
5305 | 8/9 | 24:00:00 | 286.15 | 98850 | 0.5 | 250 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
5306 | 8/10 | 01:00:00 | 286.15 | 98850 | 2.1 | 270 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
5307 | 8/10 | 02:00:00 | 286.15 | 98850 | 3.1 | 280 | 9.6116 | 0 | 0 | 272.945 | 0 | 1 | 13
5308 | 8/10 | 03:00:00 | 286.15 | 98850 | 2.1 | 290 | 9.6116 | 0 | 0 | 272.945 | 0 | 1 | 13
5309 | 8/10 | 04:00:00 | 287.15 | 98858 | 2.6 | 300 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
5310 | 8/10 | 05:00:00 | 287.15 | 98858 | 2.1 | 260 | 10.2686 | 0 | 0 | 274.389 | 0 | 1 | 14
5311 | 8/10 | 06:00:00 | 287.15 | 98858 | 2.6 | 290 | 10.2686 | 72 | 0 | 274.874 | 0 | 1 | 14
5312 | 8/10 | 07:00:00 | 287.15 | 98858 | 3.1 | 270 | 10.2686 | 288 | 0 | 274.874 | 0 | 1 | 14
5313 | 8/10 | 08:00:00 | 288.15 | 98867 | 2.6 | 270 | 10.9655 | 572.4 | 39.6 | 276.053 | 0 | 1 | 15
5314 | 8/10 | 09:00:00 | 289.15 | 98875 | 4.6 | 270 | 10.9646 | 860.4 | 79.2 | 277.011 | 0 | 1 | 16
5315 | 8/10 | 10:00:00 | 290.15 | 98883 | 4.1 | 290 | 10.9637 | 1108.8 | 248.4 | 277.969 | 0 | 1 | 17
5316 | 8/10 | 11:00:00 | 290.15 | 98883 | 4.1 | 280 | 10.9637 | 2340 | 1692 | 277.478 | 0 | 1 | 17
5317 | 8/10 | 12:00:00 | 292.15 | 98900 | 5.1 | 280 | 10.9618 | 1404 | 360 | 279.885 | 0 | 1 | 19
5318 | 8/10 | 13:00:00 | 292.15 | 98900 | 4.1 | 290 | 10.9618 | 1422 | 360 | 279.885 | 0 | 1 | 19
5319 | 8/10 | 14:00:00 | 291.15 | 98892 | 5.1 | 270 | 10.9627 | 2433.6 | 1846.8 | 278.434 | 0 | 1 | 18
5320 | 8/10 | 15:00:00 | 293.15 | 98908 | 6.7 | 270 | 11.7007 | 2149.2 | 1789.2 | 280.571 | 0 | 1 | 20
5321 | 8/10 | 16:00:00 | 292.15 | 98900 | 6.7 | 280 | 10.9618 | 968.4 | 226.8 | 279.885 | 0 | 1 | 19
5322 | 8/10 | 17:00:00 | 293.15 | 98908 | 7.7 | 290 | 10.9609 | 691.2 | 61.2 | 280.843 | 0 | 1 | 20
5323 | 8/10 | 18:00:00 | 292.15 | 98900 | 6.7 | 280 | 10.9618 | 396 | 10.8 | 279.885 | 0 | 1 | 19
5324 | 8/10 | 19:00:00 | 291.15 | 98892 | 5.7 | 270 | 10.9627 | 144 | 0 | 278.927 | 0 | 1 | 18
5325 | 8/10 | 20:00:00 | 290.15 | 98883 | 6.7 | 260 | 10.266 | 28.8 | 0 | 277.255 | 0 | 1 | 17
5326 | 8/10 | 21:00:00 | 289.15 | 98875 | 6.7 | 270 | 10.2668 | 0 | 0 | 276.029 | 0 | 1 | 16
5327 | 8/10 | 22:00:00 | 288.15 | 98867 | 6.7 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
5328 | 8/10 | 23:00:00 | 288.15 | 98867 | 7.2 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
5329 | 8/10 | 24:00:00 | 288.15 | 98867 | 6.2 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
5330 | 8/11 | 01:00:00 | 287.15 | 98858 | 5.7 | 280 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
5331 | 8/11 | 02:00:00 | 287.15 | 98858 | 6.7 | 270 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
5332 | 8/11 | 03:00:00 | 287.15 | 98858 | 5.7 | 290 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
5333 | 8/11 | 04:00:00 | 287.15 | 98858 | 5.7 | 290 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
5334 | 8/11 | 05:00:00 | 286.15 | 98850 | 4.1 | 280 | 8.9918 | 0 | 0 | 273.583 | 0 | 1 | 13
5335 | 8/11 | 06:00:00 | 286.15 | 98850 | 2.6 | 280 | 8.9918 | 129.6 | 3.6 | 272.723 | 0 | 1 | 13
5336 | 8/11 | 07:00:00 | 287.15 | 98858 | 3.1 | 310 | 8.991 | 280.8 | 0 | 274.428 | 0 | 1 | 14
5337 | 8/11 | 08:00:00 | 288.15 | 98867 | 1 | 261 | 9.6099 | 565.2 | 39.6 | 275.608 | 0 | 1 | 15
5338 | 8/11 | 09:00:00 | 289.15 | 98875 | 3.1 | 260 | 9.6091 | 856.8 | 79.2 | 276.565 | 0 | 1 | 16
5339 | 8/11 | 10:00:00 | 289.15 | 98875 | 3.6 | 260 | 10.2668 | 1105.2 | 97.2 | 276.789 | 0 | 1 | 16
5340 | 8/11 | 11:00:00 | 290.15 | 98883 | 4.1 | 260 | 10.9637 | 1288.8 | 104.4 | 277.969 | 0 | 1 | 17
5341 | 8/11 | 12:00:00 | 291.15 | 98892 | 6.2 | 270 | 10.265 | 1400.4 | 360 | 278.703 | 0 | 1 | 18
5342 | 8/11 | 13:00:00 | 293.15 | 98908 | 5.1 | 270 | 10.2634 | 2556 | 2019.6 | 280.122 | 0 | 1 | 20
5343 | 8/11 | 14:00:00 | 294.15 | 98916 | 6.7 | 270 | 9.6051 | 2430 | 2048.4 | 280.85 | 0 | 1 | 21
5344 | 8/11 | 15:00:00 | 293.15 | 98908 | 5.7 | 280 | 9.6059 | 2145.6 | 2059.2 | 279.895 | 0 | 1 | 20
5345 | 8/11 | 16:00:00 | 292.15 | 98900 | 5.1 | 310 | 10.2642 | 1731.6 | 1825.2 | 279.166 | 0 | 1 | 19
5346 | 8/11 | 17:00:00 | 293.15 | 98908 | 5.1 | 300 | 10.2634 | 1231.2 | 1461.6 | 280.122 | 0 | 1 | 20
5347 | 8/11 | 18:00:00 | 292.15 | 98900 | 4.6 | 310 | 10.2642 | 745.2 | 1008 | 278.893 | 0 | 1 | 19
5348 | 8/11 | 19:00:00 | 290.15 | 98883 | 5.7 | 320 | 10.3339 | 266.4 | 288 | 277.006 | 0 | 1 | 17
5349 | 8/11 | 20:00:00 | 289.15 | 98875 | 3.6 | 300 | 9.0498 | 25.2 | 0 | 275.604 | 0 | 1 | 16
5350 | 8/11 | 21:00:00 | 288.15 | 98867 | 4.1 | 280 | 8.7525 | 0 | 0 | 274.539 | 0 | 1 | 15
5351 | 8/11 | 22:00:00 | 287.15 | 98858 | 3.1 | 270 | 8.4641 | 0 | 0 | 273.474 | 0 | 1 | 14
5352 | 8/11 | 23:00:00 | 287.15 | 98858 | 4.6 | 280 | 8.8122 | 0 | 0 | 273.609 | 0 | 1 | 14
5353 | 8/11 | 24:00:00 | 286.15 | 98850 | 4.1 | 290 | 8.522 | 0 | 0 | 272.544 | 0 | 1 | 13
5354 | 8/12 | 01:00:00 | 286.15 | 98850 | 4.1 | 280 | 8.522 | 0 | 0 | 272.544 | 0 | 1 | 13
5355 | 8/12 | 02:00:00 | 286.15 | 98850 | 5.1 | 290 | 8.5795 | 0 | 0 | 272.833 | 0 | 1 | 13
5356 | 8/12 | 03:00:00 | 286.15 | 98850 | 4.6 | 290 | 8.5795 | 0 | 0 | 272.833 | 0 | 1 | 13
5357 | 8/12 | 04:00:00 | 286.15 | 98850 | 4.1 | 290 | 8.5795 | 0 | 0 | 273.316 | 0 | 1 | 13
5358 | 8/12 | 05:00:00 | 286.15 | 98850 | 4.1 | 300 | 8.6373 | 0 | 0 | 272.856 | 0 | 1 | 13
5359 | 8/12 | 06:00:00 | 286.15 | 98850 | 2.1 | 320 | 8.3515 | 64.8 | 0 | 273.226 | 0 | 1 | 13
5360 | 8/12 | 07:00:00 | 286.15 | 98850 | 1.5 | 208 | 8.3515 | 277.2 | 0 | 273.226 | 0 | 1 | 13
5361 | 8/12 | 08:00:00 | 286.15 | 98850 | 1 | 96 | 8.9318 | 561.6 | 39.6 | 273.45 | 0 | 1 | 13
5362 | 8/12 | 09:00:00 | 287.15 | 98858 | 2.1 | 10 | 9.2963 | 849.6 | 79.2 | 274.54 | 0 | 1 | 14
5363 | 8/12 | 10:00:00 | 286.15 | 98850 | 1.5 | 54 | 9.6116 | 1101.6 | 248.4 | 273.695 | 0 | 1 | 13
5364 | 8/12 | 11:00:00 | 288.15 | 98867 | 1.5 | 303 | 10.2677 | 2318.4 | 1699.2 | 275.344 | 0 | 1 | 15
5365 | 8/12 | 12:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.2677 | 1393.2 | 280.8 | 275.831 | 0 | 1 | 15
5366 | 8/12 | 13:00:00 | 288.15 | 98867 | 2.1 | 20 | 9.6099 | 2545.2 | 1818 | 275.122 | 0 | 1 | 15
5367 | 8/12 | 14:00:00 | 289.15 | 98875 | 2.1 | 90 | 9.6091 | 2415.6 | 1864.8 | 276.076 | 0 | 1 | 16
5368 | 8/12 | 15:00:00 | 289.15 | 98875 | 0.5 | 30 | 9.6091 | 1184.4 | 259.2 | 276.565 | 0 | 1 | 16
5369 | 8/12 | 16:00:00 | 288.15 | 98867 | 1.5 | 60 | 10.2677 | 954 | 97.2 | 275.831 | 0 | 1 | 15
5370 | 8/12 | 17:00:00 | 288.15 | 98867 | 2.1 | 330 | 10.2677 | 1216.8 | 1144.8 | 275.344 | 0 | 1 | 15
5371 | 8/12 | 18:00:00 | 287.15 | 98858 | 1.5 | 20 | 10.2686 | 691.2 | 986.4 | 274.389 | 0 | 1 | 14
5372 | 8/12 | 19:00:00 | 287.15 | 98858 | 0 | 75 | 10.2686 | 133.2 | 0 | 274.874 | 0 | 1 | 14
5373 | 8/12 | 20:00:00 | 287.15 | 98858 | 3.6 | 260 | 8.4073 | 10.8 | 0 | 274.203 | 0 | 1 | 14
5374 | 8/12 | 21:00:00 | 286.15 | 98850 | 4.1 | 270 | 7.8584 | 0 | 0 | 272.541 | 0 | 1 | 13
5375 | 8/12 | 22:00:00 | 285.15 | 98841 | 3.6 | 270 | 7.3418 | 0 | 0 | 271.363 | 0 | 1 | 12
5376 | 8/12 | 23:00:00 | 285.15 | 98841 | 5.1 | 270 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
5377 | 8/12 | 24:00:00 | 284.15 | 98833 | 4.6 | 270 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
5378 | 8/13 | 01:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
5379 | 8/13 | 02:00:00 | 283.15 | 98824 | 3.6 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5380 | 8/13 | 03:00:00 | 284.15 | 98833 | 2.6 | 260 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
5381 | 8/13 | 04:00:00 | 283.15 | 98824 | 1.5 | 250 | 7.8605 | 0 | 0 | 269.42 | 0 | 1 | 10
5382 | 8/13 | 05:00:00 | 284.15 | 98833 | 3.6 | 220 | 8.4095 | 0 | 0 | 270.859 | 0 | 1 | 11
5383 | 8/13 | 06:00:00 | 284.15 | 98833 | 2.6 | 210 | 7.8598 | 61.2 | 0 | 271.115 | 0 | 1 | 11
5384 | 8/13 | 07:00:00 | 284.15 | 98833 | 2.1 | 200 | 7.8598 | 270 | 0 | 271.115 | 0 | 1 | 11
5385 | 8/13 | 08:00:00 | 284.15 | 98833 | 3.6 | 200 | 8.4095 | 1000.8 | 997.2 | 270.859 | 0 | 1 | 11
5386 | 8/13 | 09:00:00 | 285.15 | 98841 | 3.1 | 200 | 8.9926 | 842.4 | 104.4 | 272.517 | 0 | 1 | 12
5387 | 8/13 | 10:00:00 | 286.15 | 98850 | 4.6 | 210 | 8.9918 | 1094.4 | 97.2 | 273.473 | 0 | 1 | 13
5388 | 8/13 | 11:00:00 | 286.15 | 98850 | 4.1 | 220 | 8.9918 | 1281.6 | 108 | 273.473 | 0 | 1 | 13
5389 | 8/13 | 12:00:00 | 287.15 | 98858 | 3.1 | 220 | 9.6108 | 1386 | 154.8 | 274.652 | 0 | 1 | 14
5390 | 8/13 | 13:00:00 | 288.15 | 98867 | 4.1 | 230 | 9.6099 | 1404 | 154.8 | 275.608 | 0 | 1 | 15
5391 | 8/13 | 14:00:00 | 287.15 | 98858 | 3.6 | 210 | 10.2686 | 1332 | 108 | 274.874 | 0 | 1 | 14
5392 | 8/13 | 15:00:00 | 288.15 | 98867 | 2.6 | 200 | 10.9655 | 1170 | 111.6 | 276.053 | 0 | 1 | 15
5393 | 8/13 | 16:00:00 | 289.15 | 98875 | 3.6 | 240 | 10.9646 | 1699.2 | 1573.2 | 276.522 | 0 | 1 | 16
5394 | 8/13 | 17:00:00 | 290.15 | 98883 | 8.2 | 270 | 9.6084 | 1202.4 | 1447.2 | 277.031 | 0 | 1 | 17
5395 | 8/13 | 18:00:00 | 289.15 | 98875 | 6.7 | 290 | 7.8564 | 680.4 | 676.8 | 275.398 | 0 | 1 | 16
5396 | 8/13 | 19:00:00 | 288.15 | 98867 | 8.2 | 280 | 7.3399 | 244.8 | 190.8 | 273.95 | 0 | 1 | 15
5397 | 8/13 | 20:00:00 | 287.15 | 98858 | 8.7 | 270 | 7.3406 | 14.4 | 0 | 272.999 | 0 | 1 | 14
5398 | 8/13 | 21:00:00 | 286.15 | 98850 | 3.6 | 290 | 7.8584 | 0 | 0 | 272.274 | 0 | 1 | 13
5399 | 8/13 | 22:00:00 | 286.15 | 98850 | 6.7 | 280 | 7.8584 | 0 | 0 | 272.909 | 0 | 1 | 13
5400 | 8/13 | 23:00:00 | 285.15 | 98841 | 6.2 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5401 | 8/13 | 24:00:00 | 285.15 | 98841 | 7.7 | 270 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
5402 | 8/14 | 01:00:00 | 284.15 | 98833 | 6.2 | 290 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
5403 | 8/14 | 02:00:00 | 285.15 | 98841 | 6.2 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5404 | 8/14 | 03:00:00 | 285.15 | 98841 | 7.7 | 290 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5405 | 8/14 | 04:00:00 | 285.15 | 98841 | 6.2 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5406 | 8/14 | 05:00:00 | 285.15 | 98841 | 7.2 | 290 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
5407 | 8/14 | 06:00:00 | 285.15 | 98841 | 6.7 | 300 | 7.8591 | 100.8 | 0 | 271.588 | 0 | 1 | 12
5408 | 8/14 | 07:00:00 | 286.15 | 98850 | 5.7 | 310 | 7.8584 | 266.4 | 0 | 273.023 | 0 | 1 | 13
5409 | 8/14 | 08:00:00 | 286.15 | 98850 | 6.7 | 310 | 8.408 | 986.4 | 993.6 | 272.766 | 0 | 1 | 13
5410 | 8/14 | 09:00:00 | 288.15 | 98867 | 8.2 | 340 | 8.4065 | 1512 | 1339.2 | 274.672 | 0 | 1 | 15
5411 | 8/14 | 10:00:00 | 287.15 | 98858 | 7.2 | 350 | 8.991 | 1087.2 | 252 | 274.428 | 0 | 1 | 14
5412 | 8/14 | 11:00:00 | 289.15 | 98875 | 8.2 | 10 | 8.9895 | 2300.4 | 1857.6 | 275.852 | 0 | 1 | 16
5413 | 8/14 | 12:00:00 | 289.15 | 98875 | 6.7 | 10 | 8.4059 | 2498.4 | 2235.6 | 275.626 | 0 | 1 | 16
5414 | 8/14 | 13:00:00 | 289.15 | 98875 | 8.2 | 360 | 8.4059 | 2527.2 | 2242.8 | 275.626 | 0 | 1 | 16
5415 | 8/14 | 14:00:00 | 289.15 | 98875 | 6.2 | 360 | 8.4059 | 2397.6 | 2062.8 | 275.626 | 0 | 1 | 16
5416 | 8/14 | 15:00:00 | 289.15 | 98875 | 5.7 | 360 | 8.4059 | 2109.6 | 1818 | 275.626 | 0 | 1 | 16
5417 | 8/14 | 16:00:00 | 289.15 | 98875 | 5.7 | 360 | 7.8564 | 943.2 | 262.8 | 275.885 | 0 | 1 | 16
5418 | 8/14 | 17:00:00 | 289.15 | 98875 | 4.1 | 360 | 8.4059 | 1191.6 | 1144.8 | 275.626 | 0 | 1 | 16
5419 | 8/14 | 18:00:00 | 289.15 | 98875 | 3.6 | 20 | 8.4059 | 367.2 | 3.6 | 276.113 | 0 | 1 | 16
5420 | 8/14 | 19:00:00 | 289.15 | 98875 | 3.1 | 20 | 8.4059 | 219.6 | 158.4 | 275.626 | 0 | 1 | 16
5421 | 8/14 | 20:00:00 | 287.15 | 98858 | 1.5 | 30 | 8.4073 | 10.8 | 0 | 273.719 | 0 | 1 | 14
5422 | 8/14 | 21:00:00 | 287.15 | 98858 | 0.5 | 10 | 7.8578 | 0 | 0 | 273.743 | 0 | 1 | 14
5423 | 8/14 | 22:00:00 | 286.15 | 98850 | 0.5 | 23 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
5424 | 8/14 | 23:00:00 | 286.15 | 98850 | 0 | 44 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
5425 | 8/14 | 24:00:00 | 285.15 | 98841 | 0.5 | 40 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
5426 | 8/15 | 01:00:00 | 285.15 | 98841 | 0.5 | 40 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5427 | 8/15 | 02:00:00 | 284.15 | 98833 | 0.5 | 320 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5428 | 8/15 | 03:00:00 | 284.15 | 98833 | 2.1 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
5429 | 8/15 | 04:00:00 | 284.15 | 98833 | 2.1 | 260 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
5430 | 8/15 | 05:00:00 | 284.15 | 98833 | 2.1 | 260 | 8.4095 | 0 | 0 | 270.595 | 0 | 1 | 11
5431 | 8/15 | 06:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.9926 | 97.2 | 0 | 272.036 | 0 | 1 | 12
5432 | 8/15 | 07:00:00 | 286.15 | 98850 | 6.2 | 270 | 8.9918 | 493.2 | 666 | 272.723 | 0 | 1 | 13
5433 | 8/15 | 08:00:00 | 287.15 | 98858 | 7.7 | 270 | 8.991 | 1033.2 | 1350 | 273.676 | 0 | 1 | 14
5434 | 8/15 | 09:00:00 | 288.15 | 98867 | 8.2 | 270 | 8.4065 | 1587.6 | 2116.8 | 274.404 | 0 | 1 | 15
5435 | 8/15 | 10:00:00 | 289.15 | 98875 | 6.2 | 270 | 8.4059 | 1951.2 | 1933.2 | 275.626 | 0 | 1 | 16
5436 | 8/15 | 11:00:00 | 289.15 | 98875 | 7.2 | 260 | 8.4059 | 2293.2 | 2044.8 | 275.626 | 0 | 1 | 16
5437 | 8/15 | 12:00:00 | 289.15 | 98875 | 7.2 | 270 | 8.4059 | 2484 | 2232 | 275.626 | 0 | 1 | 16
5438 | 8/15 | 13:00:00 | 289.15 | 98875 | 6.7 | 270 | 8.4059 | 2516.4 | 2185.2 | 275.626 | 0 | 1 | 16
5439 | 8/15 | 14:00:00 | 290.15 | 98883 | 7.2 | 270 | 8.4052 | 2527.2 | 2523.6 | 276.308 | 0 | 1 | 17
5440 | 8/15 | 15:00:00 | 291.15 | 98892 | 7.2 | 260 | 8.4044 | 2127.6 | 2163.6 | 277.532 | 0 | 1 | 18
5441 | 8/15 | 16:00:00 | 291.15 | 98892 | 7.2 | 270 | 8.9879 | 1778.4 | 2257.2 | 277.488 | 0 | 1 | 18
5442 | 8/15 | 17:00:00 | 290.15 | 98883 | 9.3 | 270 | 8.9887 | 1245.6 | 1555.2 | 276.535 | 0 | 1 | 17
5443 | 8/15 | 18:00:00 | 289.15 | 98875 | 9.8 | 280 | 8.9895 | 648 | 774 | 275.852 | 0 | 1 | 16
5444 | 8/15 | 19:00:00 | 288.15 | 98867 | 7.7 | 270 | 8.9902 | 208.8 | 136.8 | 274.898 | 0 | 1 | 15
5445 | 8/15 | 20:00:00 | 288.15 | 98867 | 5.7 | 270 | 8.9902 | 7.2 | 0 | 274.898 | 0 | 1 | 15
5446 | 8/15 | 21:00:00 | 287.15 | 98858 | 6.7 | 280 | 9.6108 | 0 | 0 | 274.167 | 0 | 1 | 14
5447 | 8/15 | 22:00:00 | 287.15 | 98858 | 5.1 | 270 | 9.6108 | 0 | 0 | 274.167 | 0 | 1 | 14
5448 | 8/15 | 23:00:00 | 287.15 | 98858 | 4.6 | 270 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
5449 | 8/15 | 24:00:00 | 287.15 | 98858 | 6.7 | 280 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
5450 | 8/16 | 01:00:00 | 287.15 | 98858 | 5.7 | 280 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
5451 | 8/16 | 02:00:00 | 288.15 | 98867 | 3.1 | 290 | 10.2677 | 0 | 0 | 275.831 | 0 | 1 | 15
5452 | 8/16 | 03:00:00 | 288.15 | 98867 | 3.1 | 250 | 10.2677 | 0 | 0 | 275.831 | 0 | 1 | 15
5453 | 8/16 | 04:00:00 | 288.15 | 98867 | 3.6 | 260 | 10.2677 | 0 | 0 | 275.831 | 0 | 1 | 15
5454 | 8/16 | 05:00:00 | 288.15 | 98867 | 3.1 | 260 | 10.9655 | 0 | 0 | 275.296 | 0 | 1 | 15
5455 | 8/16 | 06:00:00 | 288.15 | 98867 | 2.6 | 270 | 10.9655 | 50.4 | 0 | 276.053 | 0 | 1 | 15
5456 | 8/16 | 07:00:00 | 288.15 | 98867 | 3.6 | 280 | 10.9655 | 453.6 | 612 | 275.565 | 0 | 1 | 15
5457 | 8/16 | 08:00:00 | 289.15 | 98875 | 3.1 | 280 | 10.9646 | 957.6 | 1083.6 | 276.522 | 0 | 1 | 16
5458 | 8/16 | 09:00:00 | 289.15 | 98875 | 3.1 | 270 | 10.9646 | 1476 | 1299.6 | 276.522 | 0 | 1 | 16
5459 | 8/16 | 10:00:00 | 290.15 | 98883 | 3.1 | 260 | 11.7037 | 1069.2 | 241.2 | 278.191 | 0 | 1 | 17
5460 | 8/16 | 11:00:00 | 291.15 | 98892 | 2.1 | 230 | 11.7026 | 2260.8 | 1818 | 278.657 | 0 | 1 | 18
5461 | 8/16 | 12:00:00 | 292.15 | 98900 | 0.5 | 138 | 10.9618 | 2455.2 | 2037.6 | 279.391 | 0 | 1 | 19
5462 | 8/16 | 13:00:00 | 293.15 | 98908 | 1.5 | 81 | 11.7007 | 2484 | 1854 | 280.571 | 0 | 1 | 20
5463 | 8/16 | 14:00:00 | 293.15 | 98908 | 1.5 | 301 | 10.9609 | 1306.8 | 270 | 280.843 | 0 | 1 | 20
5464 | 8/16 | 15:00:00 | 293.15 | 98908 | 2.1 | 250 | 10.9609 | 1148.4 | 100.8 | 280.843 | 0 | 1 | 20
5465 | 8/16 | 16:00:00 | 293.15 | 98908 | 1.5 | 35 | 10.9609 | 918 | 86.4 | 280.843 | 0 | 1 | 20
5466 | 8/16 | 17:00:00 | 293.15 | 98908 | 0.5 | 80 | 10.9609 | 637.2 | 54 | 280.843 | 0 | 1 | 20
5467 | 8/16 | 18:00:00 | 293.15 | 98908 | 1 | 106 | 10.9609 | 349.2 | 0 | 280.843 | 0 | 1 | 20
5468 | 8/16 | 19:00:00 | 292.15 | 98900 | 1.5 | 130 | 10.9618 | 169.2 | 0 | 279.646 | 0 | 1 | 19
5469 | 8/16 | 20:00:00 | 292.15 | 98900 | 1.5 | 120 | 10.9618 | 0 | 0 | 279.885 | 0 | 1 | 19
5470 | 8/16 | 21:00:00 | 291.15 | 98892 | 2.1 | 100 | 10.9627 | 0 | 0 | 278.927 | 0 | 1 | 18
5471 | 8/16 | 22:00:00 | 290.15 | 98883 | 3.6 | 140 | 10.9637 | 0 | 0 | 277.969 | 0 | 1 | 17
5472 | 8/16 | 23:00:00 | 289.15 | 98875 | 3.1 | 150 | 10.9646 | 0 | 0 | 277.123 | 0 | 1 | 16
5473 | 8/16 | 24:00:00 | 289.15 | 98875 | 3.1 | 150 | 10.2668 | 0 | 0 | 276.789 | 0 | 1 | 16
5474 | 8/17 | 01:00:00 | 288.15 | 98867 | 3.6 | 150 | 10.2677 | 0 | 0 | 275.943 | 0 | 1 | 15
5475 | 8/17 | 02:00:00 | 289.15 | 98875 | 2.6 | 150 | 10.2668 | 0 | 0 | 276.3 | 0 | 1 | 16
5476 | 8/17 | 03:00:00 | 288.15 | 98867 | 2.6 | 160 | 10.2677 | 0 | 0 | 275.344 | 0 | 1 | 15
5477 | 8/17 | 04:00:00 | 287.15 | 98858 | 2.1 | 170 | 9.6108 | 0 | 0 | 274.167 | 0 | 1 | 14
5478 | 8/17 | 05:00:00 | 286.15 | 98850 | 1 | 222 | 8.9918 | 0 | 0 | 272.99 | 0 | 1 | 13
5479 | 8/17 | 06:00:00 | 287.15 | 98858 | 0.5 | 269 | 9.6108 | 36 | 0 | 274.763 | 0 | 1 | 14
5480 | 8/17 | 07:00:00 | 288.15 | 98867 | 0.5 | 277 | 10.2677 | 183.6 | 0 | 275.943 | 0 | 1 | 15
5481 | 8/17 | 08:00:00 | 290.15 | 98883 | 1 | 169 | 10.266 | 727.2 | 381.6 | 277.629 | 0 | 1 | 17
5482 | 8/17 | 09:00:00 | 292.15 | 98900 | 2.1 | 200 | 10.9618 | 1551.6 | 1832.4 | 279.117 | 0 | 1 | 19
5483 | 8/17 | 10:00:00 | 293.15 | 98908 | 2.1 | 200 | 10.9609 | 1915.2 | 1886.4 | 280.347 | 0 | 1 | 20
5484 | 8/17 | 11:00:00 | 294.15 | 98916 | 4.1 | 220 | 10.2625 | 2257.2 | 2016 | 281.078 | 0 | 1 | 21
5485 | 8/17 | 12:00:00 | 295.15 | 98924 | 4.1 | 230 | 9.6043 | 2451.6 | 2134.8 | 281.805 | 0 | 1 | 22
5486 | 8/17 | 13:00:00 | 295.15 | 98924 | 2.6 | 230 | 9.6043 | 2631.6 | 2674.8 | 281.529 | 0 | 1 | 22
5487 | 8/17 | 14:00:00 | 296.15 | 98932 | 3.1 | 14 | 8.9842 | 2494.8 | 2674.8 | 282.253 | 0 | 1 | 23
5488 | 8/17 | 15:00:00 | 297.15 | 98940 | 4.6 | 220 | 8.9835 | 2188.8 | 2527.2 | 283.206 | 0 | 1 | 24
5489 | 8/17 | 16:00:00 | 296.15 | 98932 | 3.1 | 230 | 8.4009 | 1767.6 | 2314.8 | 281.877 | 0 | 1 | 23
5490 | 8/17 | 17:00:00 | 296.15 | 98932 | 4.1 | 220 | 8.9842 | 1220.4 | 1742.4 | 282.108 | 0 | 1 | 23
5491 | 8/17 | 18:00:00 | 296.15 | 98932 | 2.6 | 220 | 8.9842 | 658.8 | 925.2 | 282.108 | 0 | 1 | 23
5492 | 8/17 | 19:00:00 | 294.15 | 98916 | 3.1 | 170 | 9.6051 | 198 | 158.4 | 280.576 | 0 | 1 | 21
5493 | 8/17 | 20:00:00 | 293.15 | 98908 | 2.1 | 170 | 9.6059 | 0 | 0 | 279.622 | 0 | 1 | 20
5494 | 8/17 | 21:00:00 | 292.15 | 98900 | 2.1 | 170 | 9.6067 | 0 | 0 | 278.941 | 0 | 1 | 19
5495 | 8/17 | 22:00:00 | 290.15 | 98883 | 1 | 230 | 9.6084 | 0 | 0 | 277.285 | 0 | 1 | 17
5496 | 8/17 | 23:00:00 | 288.15 | 98867 | 2.6 | 90 | 9.6099 | 0 | 0 | 275.608 | 0 | 1 | 15
5497 | 8/17 | 24:00:00 | 289.15 | 98875 | 0.5 | 240 | 9.6091 | 0 | 0 | 276.449 | 0 | 1 | 16
5498 | 8/18 | 01:00:00 | 287.15 | 98858 | 3.6 | 140 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14
5499 | 8/18 | 02:00:00 | 287.15 | 98858 | 3.1 | 140 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14
5500 | 8/18 | 03:00:00 | 286.15 | 98850 | 1.5 | 157 | 9.6116 | 0 | 0 | 273.806 | 0 | 1 | 13
5501 | 8/18 | 04:00:00 | 286.15 | 98850 | 0.5 | 72 | 8.9918 | 0 | 0 | 272.287 | 0 | 1 | 13
5502 | 8/18 | 05:00:00 | 286.15 | 98850 | 0 | 67 | 9.6116 | 0 | 0 | 272.509 | 0 | 1 | 13
5503 | 8/18 | 06:00:00 | 286.15 | 98850 | 0 | 217 | 8.9918 | 82.8 | 0 | 272.723 | 0 | 1 | 13
5504 | 8/18 | 07:00:00 | 288.15 | 98867 | 1 | 245 | 9.6099 | 457.2 | 612 | 274.852 | 0 | 1 | 15
5505 | 8/18 | 08:00:00 | 290.15 | 98883 | 1.5 | 55 | 9.6084 | 993.6 | 1310.4 | 276.76 | 0 | 1 | 17
5506 | 8/18 | 09:00:00 | 291.15 | 98892 | 2.6 | 240 | 10.265 | 1540.8 | 2044.8 | 277.939 | 0 | 1 | 18
5507 | 8/18 | 10:00:00 | 293.15 | 98908 | 3.1 | 250 | 10.2634 | 2023.2 | 2412 | 279.848 | 0 | 1 | 20
5508 | 8/18 | 11:00:00 | 294.15 | 98916 | 3.1 | 240 | 9.6051 | 2246.4 | 2098.8 | 280.85 | 0 | 1 | 21
5509 | 8/18 | 12:00:00 | 295.15 | 98924 | 3.6 | 220 | 9.6043 | 2437.2 | 2134.8 | 281.805 | 0 | 1 | 22
5510 | 8/18 | 13:00:00 | 295.15 | 98924 | 3.1 | 260 | 9.6043 | 2617.2 | 2671.2 | 281.529 | 0 | 1 | 22
5511 | 8/18 | 14:00:00 | 296.15 | 98932 | 3.6 | 260 | 9.6035 | 2473.2 | 2664 | 282.483 | 0 | 1 | 23
5512 | 8/18 | 15:00:00 | 295.15 | 98924 | 3.1 | 250 | 9.6043 | 2167.2 | 2412 | 281.529 | 0 | 1 | 22
5513 | 8/18 | 16:00:00 | 293.15 | 98908 | 6.2 | 300 | 10.2634 | 1623.6 | 1764 | 280.122 | 0 | 1 | 20
5514 | 8/18 | 17:00:00 | 293.15 | 98908 | 6.2 | 300 | 10.2634 | 1123.2 | 1378.8 | 280.122 | 0 | 1 | 20
5515 | 8/18 | 18:00:00 | 292.15 | 98900 | 6.2 | 300 | 10.2642 | 601.2 | 716.4 | 279.166 | 0 | 1 | 19
5516 | 8/18 | 19:00:00 | 291.15 | 98892 | 6.2 | 290 | 9.6075 | 176.4 | 75.6 | 277.986 | 0 | 1 | 18
5517 | 8/18 | 20:00:00 | 289.15 | 98875 | 5.7 | 290 | 9.6091 | 0 | 0 | 276.449 | 0 | 1 | 16
5518 | 8/18 | 21:00:00 | 289.15 | 98875 | 3.6 | 300 | 10.2668 | 0 | 0 | 276.789 | 0 | 1 | 16
5519 | 8/18 | 22:00:00 | 289.15 | 98875 | 3.6 | 290 | 10.2668 | 0 | 0 | 276.789 | 0 | 1 | 16
5520 | 8/18 | 23:00:00 | 289.15 | 98875 | 3.6 | 310 | 9.6091 | 0 | 0 | 276.449 | 0 | 1 | 16
5521 | 8/18 | 24:00:00 | 288.15 | 98867 | 2.6 | 330 | 10.2677 | 0 | 0 | 275.943 | 0 | 1 | 15
5522 | 8/19 | 01:00:00 | 288.15 | 98867 | 4.6 | 290 | 10.2677 | 0 | 0 | 275.943 | 0 | 1 | 15
5523 | 8/19 | 02:00:00 | 287.15 | 98858 | 3.6 | 300 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
5524 | 8/19 | 03:00:00 | 287.15 | 98858 | 3.6 | 300 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
5525 | 8/19 | 04:00:00 | 286.15 | 98850 | 3.1 | 300 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
5526 | 8/19 | 05:00:00 | 286.15 | 98850 | 2.6 | 300 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
5527 | 8/19 | 06:00:00 | 286.15 | 98850 | 3.1 | 300 | 9.6116 | 75.6 | 0 | 273.212 | 0 | 1 | 13
5528 | 8/19 | 07:00:00 | 286.15 | 98850 | 4.1 | 310 | 8.9918 | 446.4 | 601.2 | 272.723 | 0 | 1 | 13
5529 | 8/19 | 08:00:00 | 286.15 | 98850 | 3.6 | 300 | 8.408 | 982.8 | 1310.4 | 272.499 | 0 | 1 | 13
5530 | 8/19 | 09:00:00 | 288.15 | 98867 | 5.7 | 300 | 8.9902 | 1533.6 | 2059.2 | 274.629 | 0 | 1 | 15
5531 | 8/19 | 10:00:00 | 289.15 | 98875 | 4.1 | 310 | 8.4059 | 1900.8 | 1915.2 | 275.626 | 0 | 1 | 16
5532 | 8/19 | 11:00:00 | 290.15 | 98883 | 3.6 | 320 | 8.4052 | 2239.2 | 2041.2 | 276.579 | 0 | 1 | 17
5533 | 8/19 | 12:00:00 | 291.15 | 98892 | 5.7 | 300 | 7.338 | 2437.2 | 2239.2 | 277.073 | 0 | 1 | 18
5534 | 8/19 | 13:00:00 | 291.15 | 98892 | 5.7 | 290 | 7.855 | 2462.4 | 2242.8 | 277.303 | 0 | 1 | 18
5535 | 8/19 | 14:00:00 | 291.15 | 98892 | 5.1 | 290 | 7.855 | 2329.2 | 2217.6 | 277.303 | 0 | 1 | 18
5536 | 8/19 | 15:00:00 | 291.15 | 98892 | 4.1 | 330 | 6.8517 | 2044.8 | 2005.2 | 276.841 | 0 | 1 | 18
5537 | 8/19 | 16:00:00 | 290.15 | 98883 | 5.1 | 300 | 7.8557 | 1616.4 | 1756.8 | 276.351 | 0 | 1 | 17
5538 | 8/19 | 17:00:00 | 290.15 | 98883 | 6.2 | 280 | 8.4052 | 1108.8 | 1386 | 276.579 | 0 | 1 | 17
5539 | 8/19 | 18:00:00 | 290.15 | 98883 | 6.7 | 280 | 8.4052 | 622.8 | 864 | 276.308 | 0 | 1 | 17
5540 | 8/19 | 19:00:00 | 289.15 | 98875 | 6.7 | 280 | 8.4059 | 165.6 | 50.4 | 275.626 | 0 | 1 | 16
5541 | 8/19 | 20:00:00 | 288.15 | 98867 | 5.7 | 290 | 8.9902 | 0 | 0 | 274.898 | 0 | 1 | 15
5542 | 8/19 | 21:00:00 | 287.15 | 98858 | 4.1 | 300 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
5543 | 8/19 | 22:00:00 | 286.15 | 98850 | 5.7 | 300 | 8.408 | 0 | 0 | 272.766 | 0 | 1 | 13
5544 | 8/19 | 23:00:00 | 286.15 | 98850 | 6.2 | 300 | 8.408 | 0 | 0 | 272.766 | 0 | 1 | 13
5545 | 8/19 | 24:00:00 | 285.15 | 98841 | 5.1 | 300 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
5546 | 8/20 | 01:00:00 | 285.15 | 98841 | 5.1 | 310 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
5547 | 8/20 | 02:00:00 | 285.15 | 98841 | 5.1 | 320 | 7.3418 | 0 | 0 | 271.729 | 0 | 1 | 12
5548 | 8/20 | 03:00:00 | 284.15 | 98833 | 4.6 | 320 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5549 | 8/20 | 04:00:00 | 285.15 | 98841 | 3.1 | 340 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5550 | 8/20 | 05:00:00 | 285.15 | 98841 | 4.1 | 350 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5551 | 8/20 | 06:00:00 | 285.15 | 98841 | 4.6 | 310 | 7.3418 | 39.6 | 0 | 271.843 | 0 | 1 | 12
5552 | 8/20 | 07:00:00 | 285.15 | 98841 | 4.6 | 320 | 7.3418 | 230.4 | 0 | 271.843 | 0 | 1 | 12
5553 | 8/20 | 08:00:00 | 286.15 | 98850 | 5.1 | 350 | 7.3412 | 507.6 | 14.4 | 272.796 | 0 | 1 | 13
5554 | 8/20 | 09:00:00 | 287.15 | 98858 | 6.2 | 350 | 7.3406 | 799.2 | 57.6 | 273.75 | 0 | 1 | 14
5555 | 8/20 | 10:00:00 | 287.15 | 98858 | 5.7 | 340 | 7.3406 | 1051.2 | 165.6 | 273.75 | 0 | 1 | 14
5556 | 8/20 | 11:00:00 | 289.15 | 98875 | 5.1 | 340 | 7.3393 | 2232 | 1890 | 275.169 | 0 | 1 | 16
5557 | 8/20 | 12:00:00 | 289.15 | 98875 | 5.1 | 320 | 7.3393 | 2426.4 | 2239.2 | 275.169 | 0 | 1 | 16
5558 | 8/20 | 13:00:00 | 290.15 | 98883 | 3.6 | 340 | 7.3387 | 2451.6 | 2246.4 | 276.121 | 0 | 1 | 17
5559 | 8/20 | 14:00:00 | 291.15 | 98892 | 4.1 | 350 | 7.338 | 2314.8 | 2228.4 | 277.073 | 0 | 1 | 18
5560 | 8/20 | 15:00:00 | 291.15 | 98892 | 5.1 | 360 | 6.8517 | 2026.8 | 2001.6 | 276.841 | 0 | 1 | 18
5561 | 8/20 | 16:00:00 | 293.15 | 98908 | 5.1 | 350 | 6.3933 | 1609.2 | 1778.4 | 278.508 | 0 | 1 | 20
5562 | 8/20 | 17:00:00 | 292.15 | 98900 | 5.1 | 360 | 6.8511 | 1166.4 | 1584 | 277.52 | 0 | 1 | 19
5563 | 8/20 | 18:00:00 | 292.15 | 98900 | 3.6 | 10 | 6.8511 | 612 | 900 | 277.52 | 0 | 1 | 19
5564 | 8/20 | 19:00:00 | 290.15 | 98883 | 1.5 | 40 | 7.8557 | 158.4 | 72 | 276.351 | 0 | 1 | 17
5565 | 8/20 | 20:00:00 | 289.15 | 98875 | 2.1 | 350 | 7.8564 | 0 | 0 | 275.398 | 0 | 1 | 16
5566 | 8/20 | 21:00:00 | 287.15 | 98858 | 2.1 | 10 | 7.8578 | 0 | 0 | 273.743 | 0 | 1 | 14
5567 | 8/20 | 22:00:00 | 287.15 | 98858 | 2.6 | 350 | 7.8578 | 0 | 0 | 273.743 | 0 | 1 | 14
5568 | 8/20 | 23:00:00 | 286.15 | 98850 | 2.6 | 290 | 7.8584 | 0 | 0 | 272.909 | 0 | 1 | 13
5569 | 8/20 | 24:00:00 | 284.15 | 98833 | 1.5 | 270 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
5570 | 8/21 | 01:00:00 | 284.15 | 98833 | 2.6 | 270 | 8.4095 | 0 | 0 | 271.449 | 0 | 1 | 11
5571 | 8/21 | 02:00:00 | 284.15 | 98833 | 3.6 | 270 | 8.4095 | 0 | 0 | 271.449 | 0 | 1 | 11
5572 | 8/21 | 03:00:00 | 283.15 | 98824 | 3.1 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5573 | 8/21 | 04:00:00 | 283.15 | 98824 | 3.1 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5574 | 8/21 | 05:00:00 | 283.15 | 98824 | 3.6 | 290 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5575 | 8/21 | 06:00:00 | 282.15 | 98815 | 1 | 41 | 7.3438 | 72 | 0 | 268.245 | 0 | 1 | 9
5576 | 8/21 | 07:00:00 | 284.15 | 98833 | 3.1 | 280 | 8.4095 | 424.8 | 568.8 | 270.595 | 0 | 1 | 11
5577 | 8/21 | 08:00:00 | 286.15 | 98850 | 3.6 | 280 | 8.9918 | 954 | 1126.8 | 272.723 | 0 | 1 | 13
5578 | 8/21 | 09:00:00 | 288.15 | 98867 | 2.6 | 250 | 9.6099 | 871.2 | 165.6 | 275.608 | 0 | 1 | 15
5579 | 8/21 | 10:00:00 | 290.15 | 98883 | 4.1 | 260 | 9.6084 | 1616.4 | 1058.4 | 277.285 | 0 | 1 | 17
5580 | 8/21 | 11:00:00 | 291.15 | 98892 | 3.6 | 250 | 8.9879 | 2170.8 | 1857.6 | 277.76 | 0 | 1 | 18
5581 | 8/21 | 12:00:00 | 292.15 | 98900 | 2.1 | 260 | 8.9872 | 2545.2 | 2653.2 | 278.441 | 0 | 1 | 19
5582 | 8/21 | 13:00:00 | 294.15 | 98916 | 3.1 | 260 | 8.9857 | 2574 | 2721.6 | 280.347 | 0 | 1 | 21
5583 | 8/21 | 14:00:00 | 294.15 | 98916 | 4.1 | 270 | 8.9857 | 2430 | 2656.8 | 280.347 | 0 | 1 | 21
5584 | 8/21 | 15:00:00 | 294.15 | 98916 | 4.6 | 260 | 8.4023 | 2124 | 2466 | 280.117 | 0 | 1 | 21
5585 | 8/21 | 16:00:00 | 294.15 | 98916 | 4.1 | 270 | 8.9857 | 1677.6 | 2206.8 | 280.347 | 0 | 1 | 21
5586 | 8/21 | 17:00:00 | 294.15 | 98916 | 3.6 | 260 | 8.9857 | 1134 | 1616.4 | 280.347 | 0 | 1 | 21
5587 | 8/21 | 18:00:00 | 293.15 | 98908 | 3.6 | 270 | 8.403 | 586.8 | 806.4 | 279.165 | 0 | 1 | 20
5588 | 8/21 | 19:00:00 | 292.15 | 98900 | 2.6 | 250 | 8.4037 | 151.2 | 46.8 | 278.351 | 0 | 1 | 19
5589 | 8/21 | 20:00:00 | 291.15 | 98892 | 2.1 | 240 | 8.4044 | 0 | 0 | 277.261 | 0 | 1 | 18
5590 | 8/21 | 21:00:00 | 291.15 | 98892 | 2.6 | 240 | 8.9879 | 0 | 0 | 277.488 | 0 | 1 | 18
5591 | 8/21 | 22:00:00 | 291.15 | 98892 | 2.1 | 220 | 10.265 | 0 | 0 | 278.703 | 0 | 1 | 18
5592 | 8/21 | 23:00:00 | 291.15 | 98892 | 4.1 | 220 | 10.9627 | 0 | 0 | 278.927 | 0 | 1 | 18
5593 | 8/21 | 24:00:00 | 290.15 | 98883 | 3.6 | 210 | 10.9637 | 0 | 0 | 277.969 | 0 | 1 | 17
5594 | 8/22 | 01:00:00 | 290.15 | 98883 | 2.6 | 200 | 11.7037 | 0 | 0 | 278.191 | 0 | 1 | 17
5595 | 8/22 | 02:00:00 | 289.15 | 98875 | 2.6 | 210 | 11.7047 | 0 | 0 | 277.232 | 0 | 1 | 16
5596 | 8/22 | 03:00:00 | 289.15 | 98875 | 3.1 | 240 | 11.7047 | 0 | 0 | 277.232 | 0 | 1 | 16
5597 | 8/22 | 04:00:00 | 289.15 | 98875 | 3.1 | 240 | 11.7047 | 0 | 0 | 277.232 | 0 | 1 | 16
5598 | 8/22 | 05:00:00 | 289.15 | 98875 | 3.6 | 250 | 11.7047 | 0 | 0 | 277.232 | 0 | 1 | 16
5599 | 8/22 | 06:00:00 | 289.15 | 98875 | 4.1 | 270 | 11.7047 | 36 | 0 | 277.232 | 0 | 1 | 16
5600 | 8/22 | 07:00:00 | 289.15 | 98875 | 3.6 | 270 | 10.9646 | 216 | 0 | 277.011 | 0 | 1 | 16
5601 | 8/22 | 08:00:00 | 288.15 | 98867 | 2.1 | 260 | 10.9655 | 489.6 | 28.8 | 276.053 | 0 | 1 | 15
5602 | 8/22 | 09:00:00 | 288.15 | 98867 | 2.1 | 260 | 10.9655 | 777.6 | 72 | 276.053 | 0 | 1 | 15
5603 | 8/22 | 10:00:00 | 288.15 | 98867 | 4.6 | 270 | 10.9655 | 1026 | 93.6 | 276.053 | 0 | 1 | 15
5604 | 8/22 | 11:00:00 | 288.15 | 98867 | 4.1 | 280 | 10.2677 | 1213.2 | 266.4 | 275.831 | 0 | 1 | 15
5605 | 8/22 | 12:00:00 | 288.15 | 98867 | 4.6 | 310 | 10.2677 | 2379.6 | 1868.4 | 275.344 | 0 | 1 | 15
5606 | 8/22 | 13:00:00 | 289.15 | 98875 | 5.1 | 310 | 9.6091 | 2408.4 | 1879.2 | 276.076 | 0 | 1 | 16
5607 | 8/22 | 14:00:00 | 289.15 | 98875 | 4.6 | 340 | 9.6091 | 1260 | 320.4 | 276.565 | 0 | 1 | 16
5608 | 8/22 | 15:00:00 | 287.15 | 98858 | 6.2 | 20 | 9.6108 | 1980 | 1774.8 | 274.167 | 0 | 1 | 14
5609 | 8/22 | 16:00:00 | 289.15 | 98875 | 6.2 | 360 | 8.9895 | 1562.4 | 1738.8 | 275.852 | 0 | 1 | 16
5610 | 8/22 | 17:00:00 | 290.15 | 98883 | 4.6 | 20 | 8.9887 | 1058.4 | 1339.2 | 276.806 | 0 | 1 | 17
5611 | 8/22 | 18:00:00 | 289.15 | 98875 | 3.1 | 20 | 8.4059 | 576 | 802.8 | 275.356 | 0 | 1 | 16
5612 | 8/22 | 19:00:00 | 288.15 | 98867 | 1.5 | 40 | 8.4065 | 136.8 | 0 | 274.672 | 0 | 1 | 15
5613 | 8/22 | 20:00:00 | 288.15 | 98867 | 1 | 10 | 8.4065 | 0 | 0 | 275.158 | 0 | 1 | 15
5614 | 8/22 | 21:00:00 | 287.15 | 98858 | 1 | 350 | 8.4073 | 0 | 0 | 274.203 | 0 | 1 | 14
5615 | 8/22 | 22:00:00 | 287.15 | 98858 | 1.5 | 340 | 8.4073 | 0 | 0 | 274.203 | 0 | 1 | 14
5616 | 8/22 | 23:00:00 | 285.15 | 98841 | 3.1 | 300 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5617 | 8/22 | 24:00:00 | 285.15 | 98841 | 2.6 | 300 | 6.8552 | 0 | 0 | 271.616 | 0 | 1 | 12
5618 | 8/23 | 01:00:00 | 284.15 | 98833 | 3.6 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5619 | 8/23 | 02:00:00 | 283.15 | 98824 | 3.6 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
5620 | 8/23 | 03:00:00 | 282.15 | 98815 | 3.6 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
5621 | 8/23 | 04:00:00 | 282.15 | 98815 | 3.1 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
5622 | 8/23 | 05:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.3988 | 0 | 0 | 269.37 | 0 | 1 | 10
5623 | 8/23 | 06:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 64.8 | 0 | 268.971 | 0 | 1 | 10
5624 | 8/23 | 07:00:00 | 284.15 | 98833 | 3.6 | 260 | 7.8598 | 403.2 | 446.4 | 270.371 | 0 | 1 | 11
5625 | 8/23 | 08:00:00 | 285.15 | 98841 | 2.6 | 240 | 8.4088 | 928.8 | 1407.6 | 271.547 | 0 | 1 | 12
5626 | 8/23 | 09:00:00 | 287.15 | 98858 | 5.1 | 220 | 8.991 | 1393.2 | 1630.8 | 273.944 | 0 | 1 | 14
5627 | 8/23 | 10:00:00 | 288.15 | 98867 | 4.1 | 240 | 8.4065 | 1846.8 | 1965.6 | 274.672 | 0 | 1 | 15
5628 | 8/23 | 11:00:00 | 289.15 | 98875 | 6.2 | 240 | 8.4059 | 2185.2 | 2113.2 | 275.626 | 0 | 1 | 16
5629 | 8/23 | 12:00:00 | 290.15 | 98883 | 7.2 | 250 | 6.8523 | 2530.8 | 2527.2 | 275.62 | 0 | 1 | 17
5630 | 8/23 | 13:00:00 | 291.15 | 98892 | 7.7 | 250 | 7.338 | 2408.4 | 2185.2 | 277.073 | 0 | 1 | 18
5631 | 8/23 | 14:00:00 | 290.15 | 98883 | 7.7 | 250 | 7.3387 | 2268 | 2224.8 | 276.121 | 0 | 1 | 17
5632 | 8/23 | 15:00:00 | 291.15 | 98892 | 7.2 | 240 | 7.855 | 1972.8 | 1969.2 | 277.303 | 0 | 1 | 18
5633 | 8/23 | 16:00:00 | 291.15 | 98892 | 5.1 | 240 | 7.338 | 1551.6 | 1645.2 | 277.073 | 0 | 1 | 18
5634 | 8/23 | 17:00:00 | 290.15 | 98883 | 7.7 | 240 | 7.8557 | 1044 | 1252.8 | 276.351 | 0 | 1 | 17
5635 | 8/23 | 18:00:00 | 289.15 | 98875 | 7.2 | 230 | 8.4059 | 525.6 | 766.8 | 275.626 | 0 | 1 | 16
5636 | 8/23 | 19:00:00 | 289.15 | 98875 | 5.7 | 220 | 8.9895 | 68.4 | 0 | 276.34 | 0 | 1 | 16
5637 | 8/23 | 20:00:00 | 288.15 | 98867 | 6.7 | 230 | 9.6099 | 0 | 0 | 275.608 | 0 | 1 | 15
5638 | 8/23 | 21:00:00 | 289.15 | 98875 | 3.6 | 220 | 9.6091 | 0 | 0 | 276.565 | 0 | 1 | 16
5639 | 8/23 | 22:00:00 | 288.15 | 98867 | 5.7 | 210 | 8.9902 | 0 | 0 | 275.384 | 0 | 1 | 15
5640 | 8/23 | 23:00:00 | 288.15 | 98867 | 9.3 | 220 | 8.9902 | 0 | 0 | 274.898 | 0 | 1 | 15
5641 | 8/23 | 24:00:00 | 288.15 | 98867 | 8.2 | 220 | 8.9902 | 0 | 0 | 274.898 | 0 | 1 | 15
5642 | 8/24 | 01:00:00 | 288.15 | 98867 | 7.2 | 230 | 8.4065 | 0 | 0 | 274.924 | 0 | 1 | 15
5643 | 8/24 | 02:00:00 | 287.15 | 98858 | 6.2 | 220 | 8.4073 | 0 | 0 | 274.088 | 0 | 1 | 14
5644 | 8/24 | 03:00:00 | 287.15 | 98858 | 6.7 | 210 | 8.4073 | 0 | 0 | 274.088 | 0 | 1 | 14
5645 | 8/24 | 04:00:00 | 287.15 | 98858 | 9.3 | 220 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
5646 | 8/24 | 05:00:00 | 288.15 | 98867 | 11.3 | 220 | 9.6099 | 0 | 0 | 275.122 | 0 | 1 | 15
5647 | 8/24 | 06:00:00 | 287.15 | 98858 | 8.7 | 210 | 9.6108 | 57.6 | 0 | 274.167 | 0 | 1 | 14
5648 | 8/24 | 07:00:00 | 287.15 | 98858 | 8.7 | 210 | 8.991 | 205.2 | 0 | 274.428 | 0 | 1 | 14
5649 | 8/24 | 08:00:00 | 287.15 | 98858 | 7.2 | 210 | 9.6108 | 475.2 | 25.2 | 274.652 | 0 | 1 | 14
5650 | 8/24 | 09:00:00 | 287.15 | 98858 | 8.2 | 220 | 9.6108 | 763.2 | 72 | 274.652 | 0 | 1 | 14
5651 | 8/24 | 10:00:00 | 287.15 | 98858 | 7.2 | 210 | 10.2686 | 1011.6 | 93.6 | 274.874 | 0 | 1 | 14
5652 | 8/24 | 11:00:00 | 287.15 | 98858 | 7.2 | 220 | 10.2686 | 1198.8 | 266.4 | 274.874 | 0 | 1 | 14
5653 | 8/24 | 12:00:00 | 286.15 | 98850 | 7.2 | 260 | 8.9918 | 2358 | 1738.8 | 272.99 | 0 | 1 | 13
5654 | 8/24 | 13:00:00 | 287.15 | 98858 | 4.1 | 250 | 9.6108 | 1321.2 | 327.6 | 274.652 | 0 | 1 | 14
5655 | 8/24 | 14:00:00 | 288.15 | 98867 | 7.7 | 270 | 7.3399 | 2253.6 | 1904.4 | 274.218 | 0 | 1 | 15
5656 | 8/24 | 15:00:00 | 289.15 | 98875 | 8.7 | 260 | 6.8529 | 2080.8 | 2455.2 | 274.67 | 0 | 1 | 16
5657 | 8/24 | 16:00:00 | 289.15 | 98875 | 8.7 | 280 | 6.3955 | 1634.4 | 2077.2 | 274.439 | 0 | 1 | 16
5658 | 8/24 | 17:00:00 | 288.15 | 98867 | 8.2 | 270 | 6.396 | 1094.4 | 1472.4 | 273.49 | 0 | 1 | 15
5659 | 8/24 | 18:00:00 | 288.15 | 98867 | 6.7 | 250 | 6.8534 | 511.2 | 518.4 | 273.988 | 0 | 1 | 15
5660 | 8/24 | 19:00:00 | 286.15 | 98850 | 4.6 | 230 | 7.3412 | 115.2 | 0 | 272.314 | 0 | 1 | 13
5661 | 8/24 | 20:00:00 | 285.15 | 98841 | 3.1 | 250 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
5662 | 8/24 | 21:00:00 | 285.15 | 98841 | 3.6 | 250 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
5663 | 8/24 | 22:00:00 | 285.15 | 98841 | 3.6 | 240 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
5664 | 8/24 | 23:00:00 | 283.15 | 98824 | 1.5 | 300 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
5665 | 8/24 | 24:00:00 | 284.15 | 98833 | 3.6 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
5666 | 8/25 | 01:00:00 | 283.15 | 98824 | 4.1 | 260 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
5667 | 8/25 | 02:00:00 | 282.15 | 98815 | 3.1 | 240 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
5668 | 8/25 | 03:00:00 | 283.15 | 98824 | 2.6 | 230 | 7.8605 | 0 | 0 | 269.684 | 0 | 1 | 10
5669 | 8/25 | 04:00:00 | 282.15 | 98815 | 3.6 | 230 | 7.3438 | 0 | 0 | 268.245 | 0 | 1 | 9
5670 | 8/25 | 05:00:00 | 282.15 | 98815 | 3.6 | 250 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
5671 | 8/25 | 06:00:00 | 282.15 | 98815 | 2.1 | 250 | 7.3438 | 54 | 0 | 268.508 | 0 | 1 | 9
5672 | 8/25 | 07:00:00 | 283.15 | 98824 | 3.1 | 250 | 7.8605 | 360 | 324 | 269.684 | 0 | 1 | 10
5673 | 8/25 | 08:00:00 | 283.15 | 98824 | 3.6 | 240 | 7.8605 | 849.6 | 1029.6 | 269.684 | 0 | 1 | 10
5674 | 8/25 | 09:00:00 | 285.15 | 98841 | 4.6 | 250 | 8.4088 | 1368 | 1620 | 271.813 | 0 | 1 | 12
5675 | 8/25 | 10:00:00 | 286.15 | 98850 | 5.7 | 250 | 7.8584 | 1821.6 | 1893.6 | 272.541 | 0 | 1 | 13
5676 | 8/25 | 11:00:00 | 283.15 | 98824 | 3.1 | 240 | 7.8605 | 2160 | 2188.8 | 269.684 | 0 | 1 | 10
5677 | 8/25 | 12:00:00 | 283.15 | 98824 | 6.2 | 290 | 6.8564 | 2354.4 | 2102.4 | 269.234 | 0 | 1 | 10
5678 | 8/25 | 13:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.8598 | 2516.4 | 2538 | 270.371 | 0 | 1 | 11
5679 | 8/25 | 14:00:00 | 286.15 | 98850 | 5.1 | 260 | 7.8584 | 2232 | 2059.2 | 272.541 | 0 | 1 | 13
5680 | 8/25 | 15:00:00 | 286.15 | 98850 | 4.6 | 260 | 8.408 | 1933.2 | 2019.6 | 272.766 | 0 | 1 | 13
5681 | 8/25 | 16:00:00 | 287.15 | 98858 | 8.2 | 270 | 7.3406 | 1609.2 | 2131.2 | 272.999 | 0 | 1 | 14
5682 | 8/25 | 17:00:00 | 287.15 | 98858 | 7.2 | 270 | 6.854 | 1072.8 | 1501.2 | 272.77 | 0 | 1 | 14
5683 | 8/25 | 18:00:00 | 286.15 | 98850 | 7.7 | 260 | 6.8546 | 525.6 | 626.4 | 271.821 | 0 | 1 | 13
5684 | 8/25 | 19:00:00 | 284.15 | 98833 | 4.6 | 250 | 7.8598 | 111.6 | 0 | 270.371 | 0 | 1 | 11
5685 | 8/25 | 20:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
5686 | 8/25 | 21:00:00 | 282.15 | 98815 | 4.1 | 240 | 7.3438 | 0 | 0 | 268.245 | 0 | 1 | 9
5687 | 8/25 | 22:00:00 | 282.15 | 98815 | 4.1 | 270 | 7.3438 | 0 | 0 | 268.245 | 0 | 1 | 9
5688 | 8/25 | 23:00:00 | 282.15 | 98815 | 5.1 | 260 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
5689 | 8/25 | 24:00:00 | 282.15 | 98815 | 5.7 | 270 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
5690 | 8/26 | 01:00:00 | 282.15 | 98815 | 4.1 | 250 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
5691 | 8/26 | 02:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
5692 | 8/26 | 03:00:00 | 282.15 | 98815 | 4.1 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
5693 | 8/26 | 04:00:00 | 282.15 | 98815 | 3.6 | 270 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
5694 | 8/26 | 05:00:00 | 282.15 | 98815 | 4.1 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
5695 | 8/26 | 06:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.8571 | 50.4 | 0 | 268.283 | 0 | 1 | 9
5696 | 8/26 | 07:00:00 | 282.15 | 98815 | 4.1 | 240 | 6.8571 | 349.2 | 316.8 | 268.283 | 0 | 1 | 9
5697 | 8/26 | 08:00:00 | 283.15 | 98824 | 4.1 | 250 | 7.3431 | 838.8 | 1022.4 | 269.46 | 0 | 1 | 10
5698 | 8/26 | 09:00:00 | 285.15 | 98841 | 4.1 | 240 | 7.8591 | 1353.6 | 1519.2 | 271.588 | 0 | 1 | 12
5699 | 8/26 | 10:00:00 | 285.15 | 98841 | 6.2 | 250 | 6.8552 | 1814.4 | 1908 | 271.136 | 0 | 1 | 12
5700 | 8/26 | 11:00:00 | 286.15 | 98850 | 7.7 | 240 | 7.3412 | 2149.2 | 2196 | 272.314 | 0 | 1 | 13
5701 | 8/26 | 12:00:00 | 286.15 | 98850 | 9.3 | 250 | 6.8546 | 2340 | 2257.2 | 272.087 | 0 | 1 | 13
5702 | 8/26 | 13:00:00 | 286.15 | 98850 | 8.7 | 260 | 6.8546 | 2365.2 | 2260.8 | 272.087 | 0 | 1 | 13
5703 | 8/26 | 14:00:00 | 286.15 | 98850 | 6.2 | 240 | 7.8584 | 2217.6 | 2206.8 | 272.541 | 0 | 1 | 13
5704 | 8/26 | 15:00:00 | 285.15 | 98841 | 6.7 | 270 | 8.4088 | 1918.8 | 1771.2 | 271.813 | 0 | 1 | 12
5705 | 8/26 | 16:00:00 | 285.15 | 98841 | 7.2 | 250 | 7.3418 | 831.6 | 241.2 | 271.843 | 0 | 1 | 12
5706 | 8/26 | 17:00:00 | 286.15 | 98850 | 8.7 | 260 | 7.8584 | 990 | 1022.4 | 272.541 | 0 | 1 | 13
5707 | 8/26 | 18:00:00 | 286.15 | 98850 | 7.7 | 250 | 7.8584 | 478.8 | 478.8 | 272.541 | 0 | 1 | 13
5708 | 8/26 | 19:00:00 | 286.15 | 98850 | 6.2 | 250 | 7.8584 | 97.2 | 0 | 272.541 | 0 | 1 | 13
5709 | 8/26 | 20:00:00 | 286.15 | 98850 | 6.7 | 250 | 7.8584 | 0 | 0 | 273.023 | 0 | 1 | 13
5710 | 8/26 | 21:00:00 | 286.15 | 98850 | 8.2 | 250 | 7.8584 | 0 | 0 | 272.541 | 0 | 1 | 13
5711 | 8/26 | 22:00:00 | 285.15 | 98841 | 7.2 | 240 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
5712 | 8/26 | 23:00:00 | 285.15 | 98841 | 7.7 | 250 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
5713 | 8/26 | 24:00:00 | 285.15 | 98841 | 7.2 | 250 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
5714 | 8/27 | 01:00:00 | 285.15 | 98841 | 5.7 | 250 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
5715 | 8/27 | 02:00:00 | 285.15 | 98841 | 4.6 | 250 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
5716 | 8/27 | 03:00:00 | 284.15 | 98833 | 4.6 | 240 | 8.4095 | 0 | 0 | 270.859 | 0 | 1 | 11
5717 | 8/27 | 04:00:00 | 285.15 | 98841 | 6.2 | 250 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
5718 | 8/27 | 05:00:00 | 285.15 | 98841 | 5.7 | 260 | 8.9926 | 0 | 0 | 271.77 | 0 | 1 | 12
5719 | 8/27 | 06:00:00 | 285.15 | 98841 | 5.7 | 250 | 8.9926 | 46.8 | 0 | 271.77 | 0 | 1 | 12
5720 | 8/27 | 07:00:00 | 285.15 | 98841 | 3.6 | 240 | 8.9926 | 356.4 | 464.4 | 271.77 | 0 | 1 | 12
5721 | 8/27 | 08:00:00 | 286.15 | 98850 | 2.6 | 230 | 8.9918 | 871.2 | 1342.8 | 272.723 | 0 | 1 | 13
5722 | 8/27 | 09:00:00 | 286.15 | 98850 | 4.6 | 260 | 8.9918 | 1335.6 | 1602 | 272.99 | 0 | 1 | 13
5723 | 8/27 | 10:00:00 | 287.15 | 98858 | 4.6 | 240 | 8.991 | 1789.2 | 1929.6 | 273.944 | 0 | 1 | 14
5724 | 8/27 | 11:00:00 | 287.15 | 98858 | 5.1 | 250 | 8.4073 | 2127.6 | 2030.4 | 273.719 | 0 | 1 | 14
5725 | 8/27 | 12:00:00 | 288.15 | 98867 | 5.1 | 260 | 8.4065 | 2314.8 | 2077.2 | 274.672 | 0 | 1 | 15
5726 | 8/27 | 13:00:00 | 288.15 | 98867 | 4.6 | 250 | 8.4065 | 2340 | 2080.8 | 274.672 | 0 | 1 | 15
5727 | 8/27 | 14:00:00 | 288.15 | 98867 | 4.1 | 250 | 8.9902 | 2192.4 | 2041.2 | 274.898 | 0 | 1 | 15
5728 | 8/27 | 15:00:00 | 289.15 | 98875 | 5.1 | 270 | 8.4059 | 1900.8 | 2008.8 | 275.626 | 0 | 1 | 16
5729 | 8/27 | 16:00:00 | 289.15 | 98875 | 5.7 | 250 | 8.4059 | 1476 | 1706.4 | 275.626 | 0 | 1 | 16
5730 | 8/27 | 17:00:00 | 289.15 | 98875 | 5.1 | 260 | 8.4059 | 968.4 | 1274.4 | 275.626 | 0 | 1 | 16
5731 | 8/27 | 18:00:00 | 288.15 | 98867 | 4.6 | 260 | 7.857 | 464.4 | 460.8 | 274.446 | 0 | 1 | 15
5732 | 8/27 | 19:00:00 | 288.15 | 98867 | 3.6 | 260 | 7.857 | 93.6 | 0 | 274.177 | 0 | 1 | 15
5733 | 8/27 | 20:00:00 | 287.15 | 98858 | 2.6 | 250 | 8.4073 | 0 | 0 | 274.088 | 0 | 1 | 14
5734 | 8/27 | 21:00:00 | 285.15 | 98841 | 3.6 | 250 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
5735 | 8/27 | 22:00:00 | 285.15 | 98841 | 3.6 | 250 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
5736 | 8/27 | 23:00:00 | 284.15 | 98833 | 4.6 | 250 | 8.4095 | 0 | 0 | 271.449 | 0 | 1 | 11
5737 | 8/27 | 24:00:00 | 284.15 | 98833 | 1.5 | 260 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
5738 | 8/28 | 01:00:00 | 284.15 | 98833 | 2.1 | 210 | 8.4095 | 0 | 0 | 271.449 | 0 | 1 | 11
5739 | 8/28 | 02:00:00 | 285.15 | 98841 | 3.1 | 210 | 8.9926 | 0 | 0 | 272.627 | 0 | 1 | 12
5740 | 8/28 | 03:00:00 | 286.15 | 98850 | 3.1 | 210 | 8.9918 | 0 | 0 | 273.583 | 0 | 1 | 13
5741 | 8/28 | 04:00:00 | 285.15 | 98841 | 3.1 | 240 | 8.4088 | 0 | 0 | 272.404 | 0 | 1 | 12
5742 | 8/28 | 05:00:00 | 286.15 | 98850 | 3.1 | 210 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
5743 | 8/28 | 06:00:00 | 286.15 | 98850 | 2.1 | 210 | 8.408 | 25.2 | 0 | 273.248 | 0 | 1 | 13
5744 | 8/28 | 07:00:00 | 286.15 | 98850 | 3.6 | 210 | 8.9918 | 136.8 | 0 | 273.583 | 0 | 1 | 13
5745 | 8/28 | 08:00:00 | 287.15 | 98858 | 5.7 | 220 | 8.991 | 856.8 | 1051.2 | 273.676 | 0 | 1 | 14
5746 | 8/28 | 09:00:00 | 287.15 | 98858 | 5.7 | 230 | 9.6108 | 1400.4 | 1926 | 273.899 | 0 | 1 | 14
5747 | 8/28 | 10:00:00 | 289.15 | 98875 | 6.7 | 220 | 9.6091 | 1879.2 | 2365.2 | 275.806 | 0 | 1 | 16
5748 | 8/28 | 11:00:00 | 290.15 | 98883 | 7.7 | 230 | 10.266 | 2102.4 | 2073.6 | 277.255 | 0 | 1 | 17
5749 | 8/28 | 12:00:00 | 291.15 | 98892 | 9.8 | 230 | 9.6075 | 2293.2 | 2059.2 | 277.986 | 0 | 1 | 18
5750 | 8/28 | 13:00:00 | 290.15 | 98883 | 7.7 | 240 | 10.266 | 2311.2 | 2052 | 277.255 | 0 | 1 | 17
5751 | 8/28 | 14:00:00 | 292.15 | 98900 | 6.2 | 230 | 10.2642 | 2170.8 | 2019.6 | 279.166 | 0 | 1 | 19
5752 | 8/28 | 15:00:00 | 291.15 | 98892 | 7.7 | 230 | 10.265 | 1872 | 1969.2 | 278.211 | 0 | 1 | 18
5753 | 8/28 | 16:00:00 | 292.15 | 98900 | 8.7 | 230 | 10.2642 | 1450.8 | 1321.2 | 279.166 | 0 | 1 | 19
5754 | 8/28 | 17:00:00 | 292.15 | 98900 | 7.2 | 240 | 10.2642 | 525.6 | 50.4 | 279.66 | 0 | 1 | 19
5755 | 8/28 | 18:00:00 | 292.15 | 98900 | 7.7 | 240 | 10.2642 | 446.4 | 633.6 | 279.166 | 0 | 1 | 19
5756 | 8/28 | 19:00:00 | 290.15 | 98883 | 8.2 | 230 | 10.266 | 43.2 | 0 | 277.746 | 0 | 1 | 17
5757 | 8/28 | 20:00:00 | 290.15 | 98883 | 8.2 | 230 | 10.266 | 0 | 0 | 277.746 | 0 | 1 | 17
5758 | 8/28 | 21:00:00 | 290.15 | 98883 | 8.7 | 230 | 10.266 | 0 | 0 | 277.746 | 0 | 1 | 17
5759 | 8/28 | 22:00:00 | 290.15 | 98883 | 6.7 | 230 | 10.266 | 0 | 0 | 277.746 | 0 | 1 | 17
5760 | 8/28 | 23:00:00 | 289.15 | 98875 | 5.1 | 230 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
5761 | 8/28 | 24:00:00 | 289.15 | 98875 | 6.7 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
5762 | 8/29 | 01:00:00 | 289.15 | 98875 | 7.2 | 230 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
5763 | 8/29 | 02:00:00 | 289.15 | 98875 | 6.7 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
5764 | 8/29 | 03:00:00 | 289.15 | 98875 | 5.7 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
5765 | 8/29 | 04:00:00 | 289.15 | 98875 | 6.7 | 230 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
5766 | 8/29 | 05:00:00 | 289.15 | 98875 | 6.7 | 220 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
5767 | 8/29 | 06:00:00 | 289.15 | 98875 | 6.7 | 230 | 10.9646 | 39.6 | 0 | 276.251 | 0 | 1 | 16
5768 | 8/29 | 07:00:00 | 289.15 | 98875 | 6.7 | 230 | 11.7047 | 334.8 | 504 | 276.472 | 0 | 1 | 16
5769 | 8/29 | 08:00:00 | 290.15 | 98883 | 6.2 | 230 | 11.7037 | 439.2 | 14.4 | 278.191 | 0 | 1 | 17
5770 | 8/29 | 09:00:00 | 290.15 | 98883 | 6.2 | 230 | 12.4883 | 720 | 54 | 278.412 | 0 | 1 | 17
5771 | 8/29 | 10:00:00 | 290.15 | 98883 | 5.7 | 250 | 12.0903 | 968.4 | 230.4 | 278.301 | 0 | 1 | 17
5772 | 8/29 | 11:00:00 | 289.15 | 98875 | 5.7 | 270 | 11.7047 | 2080.8 | 1663.2 | 276.743 | 0 | 1 | 16
5773 | 8/29 | 12:00:00 | 289.15 | 98875 | 6.7 | 280 | 10.2668 | 1260 | 118.8 | 276.789 | 0 | 1 | 16
5774 | 8/29 | 13:00:00 | 289.15 | 98875 | 6.2 | 270 | 8.9895 | 1278 | 108 | 276.34 | 0 | 1 | 16
5775 | 8/29 | 14:00:00 | 290.15 | 98883 | 6.7 | 280 | 8.4052 | 1198.8 | 108 | 277.068 | 0 | 1 | 17
5776 | 8/29 | 15:00:00 | 291.15 | 98892 | 8.7 | 290 | 7.338 | 1036.8 | 194.4 | 277.563 | 0 | 1 | 18
5777 | 8/29 | 16:00:00 | 291.15 | 98892 | 6.2 | 270 | 8.4044 | 799.2 | 104.4 | 278.023 | 0 | 1 | 18
5778 | 8/29 | 17:00:00 | 290.15 | 98883 | 5.7 | 280 | 8.4052 | 990 | 1188 | 276.308 | 0 | 1 | 17
5779 | 8/29 | 18:00:00 | 289.15 | 98875 | 5.1 | 260 | 7.8564 | 457.2 | 536.4 | 275.129 | 0 | 1 | 16
5780 | 8/29 | 19:00:00 | 288.15 | 98867 | 4.6 | 270 | 7.857 | 79.2 | 0 | 274.177 | 0 | 1 | 15
5781 | 8/29 | 20:00:00 | 286.15 | 98850 | 2.1 | 280 | 7.8584 | 0 | 0 | 272.909 | 0 | 1 | 13
5782 | 8/29 | 21:00:00 | 285.15 | 98841 | 1.5 | 191 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5783 | 8/29 | 22:00:00 | 284.15 | 98833 | 3.1 | 260 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
5784 | 8/29 | 23:00:00 | 284.15 | 98833 | 2.6 | 300 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
5785 | 8/29 | 24:00:00 | 283.15 | 98824 | 3.1 | 240 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5786 | 8/30 | 01:00:00 | 283.15 | 98824 | 1.5 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
5787 | 8/30 | 02:00:00 | 282.15 | 98815 | 2.6 | 300 | 7.3438 | 0 | 0 | 269.092 | 0 | 1 | 9
5788 | 8/30 | 03:00:00 | 282.15 | 98815 | 2.1 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
5789 | 8/30 | 04:00:00 | 283.15 | 98824 | 1.5 | 290 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
5790 | 8/30 | 05:00:00 | 283.15 | 98824 | 0 | 277 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
5791 | 8/30 | 06:00:00 | 283.15 | 98824 | 1 | 186 | 7.8605 | 18 | 0 | 270.161 | 0 | 1 | 10
5792 | 8/30 | 07:00:00 | 284.15 | 98833 | 1 | 55 | 8.4095 | 169.2 | 0 | 271.339 | 0 | 1 | 11
5793 | 8/30 | 08:00:00 | 285.15 | 98841 | 1 | 183 | 8.4088 | 435.6 | 21.6 | 272.294 | 0 | 1 | 12
5794 | 8/30 | 09:00:00 | 286.15 | 98850 | 1.5 | 221 | 8.9918 | 720 | 68.4 | 273.473 | 0 | 1 | 13
5795 | 8/30 | 10:00:00 | 287.15 | 98858 | 2.1 | 110 | 8.991 | 968.4 | 93.6 | 274.428 | 0 | 1 | 14
5796 | 8/30 | 11:00:00 | 288.15 | 98867 | 2.6 | 140 | 9.6099 | 1152 | 262.8 | 275.608 | 0 | 1 | 15
5797 | 8/30 | 12:00:00 | 290.15 | 98883 | 3.1 | 140 | 10.266 | 2257.2 | 1864.8 | 277.255 | 0 | 1 | 17
5798 | 8/30 | 13:00:00 | 292.15 | 98900 | 2.6 | 120 | 10.9618 | 2412 | 2563.2 | 279.117 | 0 | 1 | 19
5799 | 8/30 | 14:00:00 | 294.15 | 98916 | 2.6 | 160 | 11.6997 | 2127.6 | 2070 | 281.528 | 0 | 1 | 21
5800 | 8/30 | 15:00:00 | 295.15 | 98924 | 3.1 | 170 | 12.483 | 1828.8 | 2084.4 | 282.709 | 0 | 1 | 22
5801 | 8/30 | 16:00:00 | 294.15 | 98916 | 3.6 | 150 | 12.484 | 1404 | 1821.6 | 281.751 | 0 | 1 | 21
5802 | 8/30 | 17:00:00 | 295.15 | 98924 | 3.1 | 160 | 12.483 | 961.2 | 1555.2 | 282.433 | 0 | 1 | 22
5803 | 8/30 | 18:00:00 | 294.15 | 98916 | 2.1 | 160 | 12.484 | 435.6 | 640.8 | 281.476 | 0 | 1 | 21
5804 | 8/30 | 19:00:00 | 293.15 | 98908 | 3.6 | 90 | 12.485 | 72 | 0 | 280.519 | 0 | 1 | 20
5805 | 8/30 | 20:00:00 | 292.15 | 98900 | 3.1 | 90 | 12.4861 | 0 | 0 | 279.562 | 0 | 1 | 19
5806 | 8/30 | 21:00:00 | 292.15 | 98900 | 3.1 | 110 | 12.4861 | 0 | 0 | 280.331 | 0 | 1 | 19
5807 | 8/30 | 22:00:00 | 291.15 | 98892 | 4.1 | 120 | 12.4871 | 0 | 0 | 279.484 | 0 | 1 | 18
5808 | 8/30 | 23:00:00 | 290.15 | 98883 | 4.6 | 140 | 10.9637 | 0 | 0 | 277.969 | 0 | 1 | 17
5809 | 8/30 | 24:00:00 | 289.15 | 98875 | 4.1 | 140 | 10.9646 | 0 | 0 | 277.123 | 0 | 1 | 16
5810 | 8/31 | 01:00:00 | 289.15 | 98875 | 3.1 | 150 | 10.2668 | 0 | 0 | 276.789 | 0 | 1 | 16
5811 | 8/31 | 02:00:00 | 287.15 | 98858 | 3.6 | 140 | 10.2686 | 0 | 0 | 274.985 | 0 | 1 | 14
5812 | 8/31 | 03:00:00 | 287.15 | 98858 | 2.6 | 130 | 10.2686 | 0 | 0 | 274.985 | 0 | 1 | 14
5813 | 8/31 | 04:00:00 | 286.15 | 98850 | 3.1 | 110 | 9.6116 | 0 | 0 | 273.806 | 0 | 1 | 13
5814 | 8/31 | 05:00:00 | 285.15 | 98841 | 2.6 | 100 | 8.9926 | 0 | 0 | 271.336 | 0 | 1 | 12
5815 | 8/31 | 06:00:00 | 285.15 | 98841 | 3.1 | 100 | 8.9926 | 28.8 | 0 | 272.036 | 0 | 1 | 12
5816 | 8/31 | 07:00:00 | 286.15 | 98850 | 3.1 | 90 | 9.6116 | 295.2 | 352.8 | 273.212 | 0 | 1 | 13
5817 | 8/31 | 08:00:00 | 287.15 | 98858 | 3.1 | 28 | 10.2686 | 259.2 | 0 | 274.985 | 0 | 1 | 14
5818 | 8/31 | 09:00:00 | 288.15 | 98867 | 3.1 | 110 | 10.9655 | 705.6 | 90 | 276.053 | 0 | 1 | 15
5819 | 8/31 | 10:00:00 | 290.15 | 98883 | 2.1 | 110 | 11.7037 | 1825.2 | 1850.4 | 277.428 | 0 | 1 | 17
5820 | 8/31 | 11:00:00 | 292.15 | 98900 | 3.1 | 120 | 12.4861 | 2170.8 | 2592 | 279.562 | 0 | 1 | 19
5821 | 8/31 | 12:00:00 | 293.15 | 98908 | 3.1 | 130 | 13.3163 | 2361.6 | 2707.2 | 280.74 | 0 | 1 | 20
5822 | 8/31 | 13:00:00 | 295.15 | 98924 | 3.1 | 120 | 13.3141 | 2246.4 | 2264.4 | 282.932 | 0 | 1 | 22
5823 | 8/31 | 14:00:00 | 297.15 | 98940 | 3.6 | 130 | 14.1924 | 2098.8 | 2160 | 285.072 | 0 | 1 | 24
5824 | 8/31 | 15:00:00 | 298.15 | 98948 | 4.1 | 140 | 14.1913 | 1803.6 | 2048.4 | 286.031 | 0 | 1 | 25
5825 | 8/31 | 16:00:00 | 298.15 | 98948 | 4.6 | 160 | 13.3108 | 1386 | 1587.6 | 285.808 | 0 | 1 | 25
5826 | 8/31 | 17:00:00 | 294.65 | 98920 | 2.8 | 243 | 12.4835 | 781.2 | 640.8 | 282.488 | 0 | 1 | 21.5
5827 | 8/31 | 18:00:00 | 291.15 | 98892 | 1 | 313 | 10.9627 | 421.2 | 302.4 | 278.162 | 0 | 1 | 18
5828 | 8/31 | 19:00:00 | 290.35 | 98885 | 3 | 148 | 10.4021 | 64.8 | 0 | 277.491 | 0 | 1 | 17.2
5829 | 8/31 | 20:00:00 | 290.35 | 98885 | 2.6 | 154 | 10.4021 | 0 | 0 | 277.491 | 0 | 1 | 17.2
5830 | 8/31 | 21:00:00 | 290.15 | 98883 | 1.7 | 145 | 10.266 | 0 | 0 | 277.255 | 0 | 1 | 17
5831 | 8/31 | 22:00:00 | 288.35 | 98868 | 1.5 | 122 | 9.6098 | 0 | 0 | 275.684 | 0 | 1 | 15.2
5832 | 8/31 | 23:00:00 | 286.65 | 98854 | 1.4 | 89 | 8.8719 | 0 | 0 | 273.791 | 0 | 1 | 13.5
5833 | 8/31 | 24:00:00 | 284.95 | 98839 | 1.4 | 70 | 8.13 | 0 | 0 | 271.991 | 0 | 1 | 11.8
5834 | 9/1 | 01:00:00 | 282.95 | 98822 | 1.4 | 65 | 7.4443 | 0 | 0 | 269.791 | 0 | 1 | 9.8
5835 | 9/1 | 02:00:00 | 282.65 | 98820 | 1.4 | 67 | 7.2437 | 0 | 0 | 269.415 | 0 | 1 | 9.5
5836 | 9/1 | 03:00:00 | 282.35 | 98817 | 1.5 | 77 | 7.2439 | 0 | 0 | 269.129 | 0 | 1 | 9.2
5837 | 9/1 | 04:00:00 | 282.15 | 98815 | 1.4 | 105 | 7.2441 | 0 | 0 | 268.938 | 0 | 1 | 9
5838 | 9/1 | 05:00:00 | 282.65 | 98820 | 1.3 | 91 | 7.2437 | 0 | 0 | 269.415 | 0 | 1 | 9.5
5839 | 9/1 | 06:00:00 | 283.65 | 98828 | 1.4 | 101 | 7.4438 | 25.2 | 0 | 269.98 | 0 | 1 | 10.5
5840 | 9/1 | 07:00:00 | 282.15 | 98815 | 0.5 | 172 | 7.3438 | 158.4 | 0 | 268.983 | 0 | 1 | 9
5841 | 9/1 | 08:00:00 | 284.15 | 98833 | 1 | 3 | 7.3425 | 806.4 | 972 | 270.147 | 0 | 1 | 11
5842 | 9/1 | 09:00:00 | 286.15 | 98850 | 2.1 | 120 | 7.8584 | 975.6 | 572.4 | 272.909 | 0 | 1 | 13
5843 | 9/1 | 10:00:00 | 288.15 | 98867 | 2.1 | 53 | 7.857 | 1825.2 | 2070 | 274.177 | 0 | 1 | 15
5844 | 9/1 | 11:00:00 | 289.15 | 98875 | 2.1 | 192 | 7.3393 | 2059.2 | 2037.6 | 275.169 | 0 | 1 | 16
5845 | 9/1 | 12:00:00 | 288.15 | 98867 | 3.1 | 150 | 6.8534 | 2246.4 | 1929.6 | 273.988 | 0 | 1 | 15
5846 | 9/1 | 13:00:00 | 289.15 | 98875 | 3.1 | 180 | 6.8529 | 1256.4 | 187.2 | 275.426 | 0 | 1 | 16
5847 | 9/1 | 14:00:00 | 289.15 | 98875 | 3.6 | 150 | 6.8529 | 1173.6 | 212.4 | 275.426 | 0 | 1 | 16
5848 | 9/1 | 15:00:00 | 290.15 | 98883 | 4.1 | 180 | 6.8523 | 1008 | 72 | 276.378 | 0 | 1 | 17
5849 | 9/1 | 16:00:00 | 290.15 | 98883 | 4.1 | 150 | 6.8523 | 1386 | 1519.2 | 275.89 | 0 | 1 | 17
5850 | 9/1 | 17:00:00 | 291.15 | 98892 | 3.6 | 150 | 6.8517 | 932.4 | 1371.6 | 276.57 | 0 | 1 | 18
5851 | 9/1 | 18:00:00 | 290.15 | 98883 | 3.6 | 150 | 6.3949 | 406.8 | 478.8 | 275.388 | 0 | 1 | 17
5852 | 9/1 | 19:00:00 | 289.15 | 98875 | 3.1 | 170 | 6.3955 | 61.2 | 0 | 274.439 | 0 | 1 | 16
5853 | 9/1 | 20:00:00 | 288.15 | 98867 | 3.6 | 150 | 6.8534 | 0 | 0 | 273.988 | 0 | 1 | 15
5854 | 9/1 | 21:00:00 | 286.15 | 98850 | 3.6 | 150 | 7.3412 | 0 | 0 | 272.563 | 0 | 1 | 13
5855 | 9/1 | 22:00:00 | 285.15 | 98841 | 4.1 | 140 | 7.3418 | 0 | 0 | 271.729 | 0 | 1 | 12
5856 | 9/1 | 23:00:00 | 284.15 | 98833 | 3.1 | 150 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5857 | 9/1 | 24:00:00 | 284.15 | 98833 | 3.6 | 160 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5858 | 9/2 | 01:00:00 | 284.15 | 98833 | 4.1 | 170 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5859 | 9/2 | 02:00:00 | 284.15 | 98833 | 4.6 | 170 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5860 | 9/2 | 03:00:00 | 284.15 | 98833 | 4.6 | 160 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5861 | 9/2 | 04:00:00 | 284.15 | 98833 | 3.1 | 160 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5862 | 9/2 | 05:00:00 | 284.15 | 98833 | 2.6 | 160 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
5863 | 9/2 | 06:00:00 | 284.15 | 98833 | 3.6 | 160 | 7.3425 | 14.4 | 0 | 270.89 | 0 | 1 | 11
5864 | 9/2 | 07:00:00 | 284.15 | 98833 | 2.1 | 244 | 7.3425 | 176.4 | 0 | 270.89 | 0 | 1 | 11
5865 | 9/2 | 08:00:00 | 285.15 | 98841 | 2.6 | 150 | 7.8591 | 457.2 | 46.8 | 272.069 | 0 | 1 | 12
5866 | 9/2 | 09:00:00 | 285.15 | 98841 | 2.6 | 150 | 7.8591 | 774 | 334.8 | 272.069 | 0 | 1 | 12
5867 | 9/2 | 10:00:00 | 287.15 | 98858 | 2.1 | 210 | 8.4073 | 1807.2 | 1857.6 | 273.451 | 0 | 1 | 14
5868 | 9/2 | 11:00:00 | 290.15 | 98883 | 3.6 | 240 | 8.9887 | 2034 | 2080.8 | 276.806 | 0 | 1 | 17
5869 | 9/2 | 12:00:00 | 292.15 | 98900 | 5.1 | 260 | 8.9872 | 2217.6 | 2138.4 | 278.714 | 0 | 1 | 19
5870 | 9/2 | 13:00:00 | 292.15 | 98900 | 8.2 | 240 | 8.9872 | 2368.8 | 2530.8 | 278.441 | 0 | 1 | 19
5871 | 9/2 | 14:00:00 | 291.15 | 98892 | 7.2 | 230 | 8.9879 | 2088 | 2102.4 | 277.76 | 0 | 1 | 18
5872 | 9/2 | 15:00:00 | 292.15 | 98900 | 4.1 | 250 | 9.6067 | 1782 | 1933.2 | 278.941 | 0 | 1 | 19
5873 | 9/2 | 16:00:00 | 291.15 | 98892 | 7.2 | 260 | 8.4044 | 1360.8 | 1641.6 | 277.532 | 0 | 1 | 18
5874 | 9/2 | 17:00:00 | 291.15 | 98892 | 4.6 | 280 | 9.6075 | 853.2 | 1155.6 | 277.986 | 0 | 1 | 18
5875 | 9/2 | 18:00:00 | 291.15 | 98892 | 4.1 | 260 | 9.6075 | 388.8 | 500.4 | 277.714 | 0 | 1 | 18
5876 | 9/2 | 19:00:00 | 289.15 | 98875 | 2.6 | 260 | 8.9895 | 57.6 | 0 | 275.582 | 0 | 1 | 16
5877 | 9/2 | 20:00:00 | 289.15 | 98875 | 2.6 | 240 | 8.9895 | 0 | 0 | 275.852 | 0 | 1 | 16
5878 | 9/2 | 21:00:00 | 289.15 | 98875 | 3.1 | 220 | 8.4059 | 0 | 0 | 275.356 | 0 | 1 | 16
5879 | 9/2 | 22:00:00 | 289.15 | 98875 | 4.1 | 230 | 7.8564 | 0 | 0 | 275.129 | 0 | 1 | 16
5880 | 9/2 | 23:00:00 | 288.15 | 98867 | 5.7 | 230 | 8.4065 | 0 | 0 | 274.404 | 0 | 1 | 15
5881 | 9/2 | 24:00:00 | 287.15 | 98858 | 4.6 | 230 | 8.4073 | 0 | 0 | 274.088 | 0 | 1 | 14
5882 | 9/3 | 01:00:00 | 287.15 | 98858 | 2.1 | 220 | 8.4073 | 0 | 0 | 274.203 | 0 | 1 | 14
5883 | 9/3 | 02:00:00 | 287.15 | 98858 | 2.1 | 170 | 8.4073 | 0 | 0 | 274.203 | 0 | 1 | 14
5884 | 9/3 | 03:00:00 | 288.15 | 98867 | 2.6 | 210 | 8.9902 | 0 | 0 | 275.384 | 0 | 1 | 15
5885 | 9/3 | 04:00:00 | 289.15 | 98875 | 3.1 | 210 | 8.9895 | 0 | 0 | 276.34 | 0 | 1 | 16
5886 | 9/3 | 05:00:00 | 289.15 | 98875 | 3.1 | 220 | 8.9895 | 0 | 0 | 276.34 | 0 | 1 | 16
5887 | 9/3 | 06:00:00 | 288.15 | 98867 | 2.1 | 200 | 8.9902 | 18 | 0 | 274.898 | 0 | 1 | 15
5888 | 9/3 | 07:00:00 | 288.15 | 98867 | 3.1 | 170 | 8.9902 | 262.8 | 262.8 | 274.898 | 0 | 1 | 15
5889 | 9/3 | 08:00:00 | 289.15 | 98875 | 4.1 | 210 | 9.6091 | 727.2 | 903.6 | 276.076 | 0 | 1 | 16
5890 | 9/3 | 09:00:00 | 289.15 | 98875 | 5.1 | 230 | 8.9895 | 1238.4 | 1540.8 | 275.852 | 0 | 1 | 16
5891 | 9/3 | 10:00:00 | 289.15 | 98875 | 3.6 | 230 | 8.9895 | 1684.8 | 1900.8 | 275.852 | 0 | 1 | 16
5892 | 9/3 | 11:00:00 | 290.15 | 98883 | 3.6 | 220 | 9.6084 | 2012.4 | 1818 | 277.031 | 0 | 1 | 17
5893 | 9/3 | 12:00:00 | 290.15 | 98883 | 3.6 | 230 | 9.6084 | 1216.8 | 118.8 | 277.521 | 0 | 1 | 17
5894 | 9/3 | 13:00:00 | 291.15 | 98892 | 3.6 | 230 | 10.265 | 1227.6 | 108 | 278.703 | 0 | 1 | 18
5895 | 9/3 | 14:00:00 | 291.15 | 98892 | 4.1 | 220 | 9.6075 | 1144.8 | 104.4 | 278.478 | 0 | 1 | 18
5896 | 9/3 | 15:00:00 | 291.15 | 98892 | 5.1 | 220 | 9.6075 | 979.2 | 104.4 | 278.478 | 0 | 1 | 18
5897 | 9/3 | 16:00:00 | 291.15 | 98892 | 3.6 | 240 | 9.6075 | 1335.6 | 1274.4 | 277.986 | 0 | 1 | 18
5898 | 9/3 | 17:00:00 | 290.15 | 98883 | 5.7 | 230 | 10.266 | 831.6 | 1015.2 | 277.255 | 0 | 1 | 17
5899 | 9/3 | 18:00:00 | 290.15 | 98883 | 4.6 | 220 | 10.266 | 349.2 | 388.8 | 277.255 | 0 | 1 | 17
5900 | 9/3 | 19:00:00 | 289.15 | 98875 | 3.6 | 220 | 10.2668 | 25.2 | 0 | 276.789 | 0 | 1 | 16
5901 | 9/3 | 20:00:00 | 289.15 | 98875 | 2.1 | 240 | 10.2668 | 0 | 0 | 276.3 | 0 | 1 | 16
5902 | 9/3 | 21:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.2668 | 0 | 0 | 276.3 | 0 | 1 | 16
5903 | 9/3 | 22:00:00 | 289.15 | 98875 | 3.1 | 190 | 10.2668 | 0 | 0 | 276.3 | 0 | 1 | 16
5904 | 9/3 | 23:00:00 | 288.15 | 98867 | 2.6 | 190 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
5905 | 9/3 | 24:00:00 | 288.15 | 98867 | 2.6 | 240 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
5906 | 9/4 | 01:00:00 | 288.15 | 98867 | 3.6 | 250 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
5907 | 9/4 | 02:00:00 | 288.15 | 98867 | 2.1 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
5908 | 9/4 | 03:00:00 | 287.15 | 98858 | 2.1 | 290 | 9.6108 | 0 | 0 | 273.899 | 0 | 1 | 14
5909 | 9/4 | 04:00:00 | 286.15 | 98850 | 2.6 | 310 | 9.6116 | 0 | 0 | 272.945 | 0 | 1 | 13
5910 | 9/4 | 05:00:00 | 285.15 | 98841 | 2.1 | 290 | 8.9926 | 0 | 0 | 272.036 | 0 | 1 | 12
5911 | 9/4 | 06:00:00 | 285.15 | 98841 | 2.6 | 300 | 8.4088 | 7.2 | 0 | 272.294 | 0 | 1 | 12
5912 | 9/4 | 07:00:00 | 285.15 | 98841 | 2.6 | 300 | 8.4088 | 252 | 248.4 | 271.813 | 0 | 1 | 12
5913 | 9/4 | 08:00:00 | 286.15 | 98850 | 2.1 | 290 | 8.9918 | 716.4 | 896.4 | 272.99 | 0 | 1 | 13
5914 | 9/4 | 09:00:00 | 287.15 | 98858 | 1.5 | 327 | 8.4073 | 1224 | 1540.8 | 273.719 | 0 | 1 | 14
5915 | 9/4 | 10:00:00 | 288.15 | 98867 | 1 | 218 | 8.4065 | 1670.4 | 1900.8 | 274.672 | 0 | 1 | 15
5916 | 9/4 | 11:00:00 | 289.15 | 98875 | 1 | 71 | 8.4059 | 2001.6 | 1832.4 | 275.626 | 0 | 1 | 16
5917 | 9/4 | 12:00:00 | 289.15 | 98875 | 1 | 131 | 8.4059 | 1213.2 | 277.2 | 276.113 | 0 | 1 | 16
5918 | 9/4 | 13:00:00 | 289.15 | 98875 | 0.5 | 11 | 8.4059 | 1220.4 | 108 | 276.113 | 0 | 1 | 16
5919 | 9/4 | 14:00:00 | 289.15 | 98875 | 1 | 109 | 8.9895 | 1137.6 | 104.4 | 276.34 | 0 | 1 | 16
5920 | 9/4 | 15:00:00 | 289.15 | 98875 | 3.6 | 270 | 8.4059 | 968.4 | 241.2 | 276.113 | 0 | 1 | 16
5921 | 9/4 | 16:00:00 | 289.15 | 98875 | 3.6 | 260 | 8.4059 | 1400.4 | 1558.8 | 275.356 | 0 | 1 | 16
5922 | 9/4 | 17:00:00 | 289.15 | 98875 | 2.1 | 250 | 7.8564 | 817.2 | 1026 | 275.398 | 0 | 1 | 16
5923 | 9/4 | 18:00:00 | 288.15 | 98867 | 2.6 | 230 | 7.857 | 356.4 | 399.6 | 274.177 | 0 | 1 | 15
5924 | 9/4 | 19:00:00 | 288.15 | 98867 | 1.5 | 177 | 6.8534 | 43.2 | 0 | 273.72 | 0 | 1 | 15
5925 | 9/4 | 20:00:00 | 288.15 | 98867 | 3.1 | 230 | 6.396 | 0 | 0 | 273.49 | 0 | 1 | 15
5926 | 9/4 | 21:00:00 | 287.15 | 98858 | 5.7 | 250 | 5.9666 | 0 | 0 | 272.576 | 0 | 1 | 14
5927 | 9/4 | 22:00:00 | 285.15 | 98841 | 4.1 | 250 | 7.3418 | 0 | 0 | 271.363 | 0 | 1 | 12
5928 | 9/4 | 23:00:00 | 284.15 | 98833 | 3.6 | 240 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
5929 | 9/4 | 24:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
5930 | 9/5 | 01:00:00 | 283.15 | 98824 | 3.1 | 210 | 6.3988 | 0 | 0 | 269.37 | 0 | 1 | 10
5931 | 9/5 | 02:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
5932 | 9/5 | 03:00:00 | 281.15 | 98806 | 1.5 | 190 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
5933 | 9/5 | 04:00:00 | 282.15 | 98815 | 3.1 | 180 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
5934 | 9/5 | 05:00:00 | 282.15 | 98815 | 2.1 | 200 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
5935 | 9/5 | 06:00:00 | 283.15 | 98824 | 4.6 | 210 | 6.8564 | 7.2 | 0 | 269.234 | 0 | 1 | 10
5936 | 9/5 | 07:00:00 | 283.15 | 98824 | 4.6 | 210 | 6.8564 | 259.2 | 241.2 | 268.971 | 0 | 1 | 10
5937 | 9/5 | 08:00:00 | 284.15 | 98833 | 7.7 | 210 | 6.8558 | 705.6 | 946.8 | 270.185 | 0 | 1 | 11
5938 | 9/5 | 09:00:00 | 284.15 | 98833 | 7.7 | 240 | 6.3982 | 1216.8 | 1461.6 | 269.957 | 0 | 1 | 11
5939 | 9/5 | 10:00:00 | 284.15 | 98833 | 6.7 | 250 | 6.8558 | 1663.2 | 1875.6 | 270.185 | 0 | 1 | 11
5940 | 9/5 | 11:00:00 | 284.15 | 98833 | 5.7 | 260 | 7.3425 | 1990.8 | 2167.2 | 270.411 | 0 | 1 | 11
5941 | 9/5 | 12:00:00 | 284.15 | 98833 | 6.2 | 240 | 7.3425 | 2174.4 | 2235.6 | 270.411 | 0 | 1 | 11
5942 | 9/5 | 13:00:00 | 286.15 | 98850 | 9.3 | 250 | 7.3412 | 2188.8 | 2239.2 | 272.314 | 0 | 1 | 13
5943 | 9/5 | 14:00:00 | 286.15 | 98850 | 9.8 | 270 | 6.8546 | 2041.2 | 2199.6 | 272.087 | 0 | 1 | 13
5944 | 9/5 | 15:00:00 | 286.15 | 98850 | 10.8 | 270 | 6.8546 | 1735.2 | 1936.8 | 272.087 | 0 | 1 | 13
5945 | 9/5 | 16:00:00 | 286.15 | 98850 | 9.3 | 260 | 7.3412 | 1303.2 | 1580.4 | 272.314 | 0 | 1 | 13
5946 | 9/5 | 17:00:00 | 287.15 | 98858 | 8.7 | 260 | 7.3406 | 849.6 | 1332 | 272.999 | 0 | 1 | 14
5947 | 9/5 | 18:00:00 | 287.15 | 98858 | 7.7 | 250 | 6.854 | 338.4 | 381.6 | 272.77 | 0 | 1 | 14
5948 | 9/5 | 19:00:00 | 286.15 | 98850 | 6.2 | 250 | 6.8546 | 36 | 0 | 272.087 | 0 | 1 | 13
5949 | 9/5 | 20:00:00 | 285.15 | 98841 | 6.7 | 240 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
5950 | 9/5 | 21:00:00 | 284.15 | 98833 | 5.1 | 220 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
5951 | 9/5 | 22:00:00 | 284.15 | 98833 | 5.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
5952 | 9/5 | 23:00:00 | 284.15 | 98833 | 5.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
5953 | 9/5 | 24:00:00 | 285.15 | 98841 | 4.6 | 220 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
5954 | 9/6 | 01:00:00 | 285.15 | 98841 | 6.7 | 220 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
5955 | 9/6 | 02:00:00 | 286.15 | 98850 | 6.7 | 220 | 8.408 | 0 | 0 | 272.766 | 0 | 1 | 13
5956 | 9/6 | 03:00:00 | 287.15 | 98858 | 9.8 | 220 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
5957 | 9/6 | 04:00:00 | 286.15 | 98850 | 8.2 | 210 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
5958 | 9/6 | 05:00:00 | 286.15 | 98850 | 7.7 | 210 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
5959 | 9/6 | 06:00:00 | 286.15 | 98850 | 7.2 | 220 | 8.9918 | 3.6 | 0 | 273.473 | 0 | 1 | 13
5960 | 9/6 | 07:00:00 | 286.15 | 98850 | 8.7 | 220 | 8.9918 | 129.6 | 0 | 273.473 | 0 | 1 | 13
5961 | 9/6 | 08:00:00 | 287.15 | 98858 | 8.2 | 230 | 9.6108 | 687.6 | 835.2 | 274.167 | 0 | 1 | 14
5962 | 9/6 | 09:00:00 | 288.15 | 98867 | 7.2 | 260 | 9.6099 | 1188 | 1501.2 | 275.122 | 0 | 1 | 15
5963 | 9/6 | 10:00:00 | 285.15 | 98841 | 8.2 | 270 | 8.4088 | 1638 | 1875.6 | 271.813 | 0 | 1 | 12
5964 | 9/6 | 11:00:00 | 285.15 | 98841 | 9.8 | 250 | 7.8591 | 1972.8 | 2149.2 | 271.588 | 0 | 1 | 12
5965 | 9/6 | 12:00:00 | 286.15 | 98850 | 9.8 | 250 | 8.408 | 2149.2 | 2062.8 | 272.766 | 0 | 1 | 13
5966 | 9/6 | 13:00:00 | 288.15 | 98867 | 11.3 | 250 | 7.857 | 2167.2 | 2224.8 | 274.446 | 0 | 1 | 15
5967 | 9/6 | 14:00:00 | 285.15 | 98841 | 8.2 | 250 | 7.8591 | 2016 | 2170.8 | 271.588 | 0 | 1 | 12
5968 | 9/6 | 15:00:00 | 286.15 | 98850 | 9.8 | 250 | 7.3412 | 1713.6 | 1908 | 272.314 | 0 | 1 | 13 |  |  |  |  | 9.3111
5969 | 9/6 | 16:00:00 | 287.15 | 98858 | 11.3 | 250 | 6.854 | 1281.6 | 1508.4 | 273.038 | 0 | 1 | 14
5970 | 9/6 | 17:00:00 | 287.15 | 98858 | 12.9 | 240 | 6.854 | 781.2 | 1072.8 | 273.038 | 0 | 1 | 14
5971 | 9/6 | 18:00:00 | 286.15 | 98850 | 12.3 | 240 | 6.8546 | 324 | 352.8 | 271.821 | 0 | 1 | 13
5972 | 9/6 | 19:00:00 | 285.15 | 98841 | 11.8 | 250 | 6.3977 | 32.4 | 0 | 270.643 | 0 | 1 | 12
5973 | 9/6 | 20:00:00 | 285.15 | 98841 | 10.3 | 250 | 6.8552 | 0 | 0 | 271.136 | 0 | 1 | 12
5974 | 9/6 | 21:00:00 | 285.15 | 98841 | 9.3 | 250 | 7.3418 | 0 | 0 | 271.363 | 0 | 1 | 12
5975 | 9/6 | 22:00:00 | 284.15 | 98833 | 11.8 | 260 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
5976 | 9/6 | 23:00:00 | 284.15 | 98833 | 10.8 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
5977 | 9/6 | 24:00:00 | 284.15 | 98833 | 10.3 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
5978 | 9/7 | 01:00:00 | 284.15 | 98833 | 9.8 | 270 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
5979 | 9/7 | 02:00:00 | 285.15 | 98841 | 9.3 | 270 | 7.3418 | 0 | 0 | 271.363 | 0 | 1 | 12
5980 | 9/7 | 03:00:00 | 284.15 | 98833 | 8.7 | 270 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
5981 | 9/7 | 04:00:00 | 284.15 | 98833 | 7.7 | 270 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
5982 | 9/7 | 05:00:00 | 284.15 | 98833 | 5.7 | 250 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
5983 | 9/7 | 06:00:00 | 284.15 | 98833 | 5.1 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
5984 | 9/7 | 07:00:00 | 285.15 | 98841 | 4.1 | 250 | 7.8591 | 122.4 | 0 | 272.069 | 0 | 1 | 12
5985 | 9/7 | 08:00:00 | 285.15 | 98841 | 4.6 | 250 | 7.8591 | 374.4 | 7.2 | 272.069 | 0 | 1 | 12
5986 | 9/7 | 09:00:00 | 285.15 | 98841 | 6.2 | 260 | 8.4088 | 651.6 | 61.2 | 272.294 | 0 | 1 | 12
5987 | 9/7 | 10:00:00 | 285.15 | 98841 | 6.7 | 270 | 8.4088 | 900 | 122.4 | 272.294 | 0 | 1 | 12
5988 | 9/7 | 11:00:00 | 285.15 | 98841 | 6.7 | 260 | 8.4088 | 1951.2 | 1818 | 271.813 | 0 | 1 | 12
5989 | 9/7 | 12:00:00 | 286.15 | 98850 | 8.7 | 260 | 7.8584 | 2134.8 | 2217.6 | 272.541 | 0 | 1 | 13
5990 | 9/7 | 13:00:00 | 287.15 | 98858 | 6.2 | 250 | 8.4073 | 2145.6 | 2062.8 | 273.719 | 0 | 1 | 14
5991 | 9/7 | 14:00:00 | 287.15 | 98858 | 8.7 | 260 | 7.8578 | 1994.4 | 2167.2 | 273.493 | 0 | 1 | 14
5992 | 9/7 | 15:00:00 | 287.15 | 98858 | 8.2 | 260 | 8.4073 | 1684.8 | 1922.4 | 273.719 | 0 | 1 | 14
5993 | 9/7 | 16:00:00 | 287.15 | 98858 | 9.8 | 260 | 7.8578 | 1260 | 1479.6 | 273.493 | 0 | 1 | 14
5994 | 9/7 | 17:00:00 | 286.15 | 98850 | 8.2 | 260 | 7.8584 | 759.6 | 1008 | 272.541 | 0 | 1 | 13
5995 | 9/7 | 18:00:00 | 285.15 | 98841 | 8.7 | 260 | 7.8591 | 288 | 244.8 | 271.588 | 0 | 1 | 12
5996 | 9/7 | 19:00:00 | 284.15 | 98833 | 6.7 | 250 | 7.3425 | 25.2 | 0 | 270.411 | 0 | 1 | 11
5997 | 9/7 | 20:00:00 | 283.15 | 98824 | 6.7 | 250 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
5998 | 9/7 | 21:00:00 | 283.15 | 98824 | 5.7 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
5999 | 9/7 | 22:00:00 | 283.15 | 98824 | 5.1 | 240 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
6000 | 9/7 | 23:00:00 | 283.15 | 98824 | 5.7 | 250 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
6001 | 9/7 | 24:00:00 | 283.15 | 98824 | 5.7 | 260 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
6002 | 9/8 | 01:00:00 | 283.15 | 98824 | 6.7 | 260 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
6003 | 9/8 | 02:00:00 | 284.15 | 98833 | 5.1 | 250 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6004 | 9/8 | 03:00:00 | 283.15 | 98824 | 5.1 | 260 | 7.8605 | 0 | 0 | 269.684 | 0 | 1 | 10
6005 | 9/8 | 04:00:00 | 284.15 | 98833 | 1.5 | 159 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6006 | 9/8 | 05:00:00 | 284.15 | 98833 | 3.1 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6007 | 9/8 | 06:00:00 | 284.15 | 98833 | 1.5 | 264 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6008 | 9/8 | 07:00:00 | 284.15 | 98833 | 1.5 | 67 | 8.4095 | 118.8 | 0 | 271.339 | 0 | 1 | 11
6009 | 9/8 | 08:00:00 | 284.15 | 98833 | 2.1 | 250 | 8.4095 | 367.2 | 3.6 | 271.339 | 0 | 1 | 11
6010 | 9/8 | 09:00:00 | 285.15 | 98841 | 3.1 | 240 | 8.4088 | 644.4 | 61.2 | 272.294 | 0 | 1 | 12
6011 | 9/8 | 10:00:00 | 285.15 | 98841 | 5.7 | 260 | 8.9926 | 889.2 | 43.2 | 272.517 | 0 | 1 | 12
6012 | 9/8 | 11:00:00 | 286.15 | 98850 | 4.6 | 230 | 8.9918 | 1072.8 | 100.8 | 273.473 | 0 | 1 | 13
6013 | 9/8 | 12:00:00 | 287.15 | 98858 | 5.1 | 250 | 9.6108 | 1170 | 104.4 | 274.652 | 0 | 1 | 14
6014 | 9/8 | 13:00:00 | 287.15 | 98858 | 6.7 | 250 | 9.6108 | 1177.2 | 104.4 | 274.652 | 0 | 1 | 14
6015 | 9/8 | 14:00:00 | 288.15 | 98867 | 6.2 | 260 | 9.6099 | 1090.8 | 115.2 | 275.608 | 0 | 1 | 15
6016 | 9/8 | 15:00:00 | 288.15 | 98867 | 7.7 | 260 | 8.9902 | 1663.2 | 1494 | 274.898 | 0 | 1 | 15
6017 | 9/8 | 16:00:00 | 288.15 | 98867 | 7.2 | 260 | 8.9902 | 1234.8 | 1551.6 | 274.898 | 0 | 1 | 15
6018 | 9/8 | 17:00:00 | 288.15 | 98867 | 6.7 | 260 | 8.9902 | 738 | 932.4 | 274.898 | 0 | 1 | 15
6019 | 9/8 | 18:00:00 | 288.15 | 98867 | 6.2 | 270 | 8.9902 | 270 | 284.4 | 274.898 | 0 | 1 | 15
6020 | 9/8 | 19:00:00 | 287.15 | 98858 | 6.7 | 280 | 8.4073 | 18 | 0 | 273.451 | 0 | 1 | 14
6021 | 9/8 | 20:00:00 | 286.15 | 98850 | 6.2 | 280 | 7.3412 | 0 | 0 | 272.048 | 0 | 1 | 13
6022 | 9/8 | 21:00:00 | 285.15 | 98841 | 4.6 | 270 | 7.3418 | 0 | 0 | 271.097 | 0 | 1 | 12
6023 | 9/8 | 22:00:00 | 285.15 | 98841 | 2.6 | 280 | 7.3418 | 0 | 0 | 271.729 | 0 | 1 | 12
6024 | 9/8 | 23:00:00 | 284.15 | 98833 | 2.6 | 300 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6025 | 9/8 | 24:00:00 | 284.15 | 98833 | 1.5 | 290 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
6026 | 9/9 | 01:00:00 | 284.15 | 98833 | 2.1 | 180 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
6027 | 9/9 | 02:00:00 | 285.15 | 98841 | 1.5 | 63 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
6028 | 9/9 | 03:00:00 | 285.15 | 98841 | 1 | 180 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
6029 | 9/9 | 04:00:00 | 285.15 | 98841 | 1 | 180 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
6030 | 9/9 | 05:00:00 | 285.15 | 98841 | 1.5 | 300 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
6031 | 9/9 | 06:00:00 | 285.15 | 98841 | 2.6 | 170 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
6032 | 9/9 | 07:00:00 | 285.15 | 98841 | 3.1 | 180 | 8.9926 | 111.6 | 0 | 272.517 | 0 | 1 | 12
6033 | 9/9 | 08:00:00 | 286.15 | 98850 | 2.1 | 190 | 8.9918 | 360 | 3.6 | 273.473 | 0 | 1 | 13
6034 | 9/9 | 09:00:00 | 287.15 | 98858 | 3.1 | 220 | 10.2686 | 633.6 | 57.6 | 274.874 | 0 | 1 | 14
6035 | 9/9 | 10:00:00 | 289.15 | 98875 | 4.1 | 240 | 10.9646 | 878.4 | 43.2 | 277.011 | 0 | 1 | 16
6036 | 9/9 | 11:00:00 | 290.15 | 98883 | 4.1 | 250 | 10.9637 | 1058.4 | 100.8 | 277.969 | 0 | 1 | 17
6037 | 9/9 | 12:00:00 | 290.15 | 98883 | 5.7 | 240 | 10.9637 | 1155.6 | 266.4 | 277.969 | 0 | 1 | 17
6038 | 9/9 | 13:00:00 | 292.15 | 98900 | 5.1 | 250 | 10.9618 | 2095.2 | 1699.2 | 279.391 | 0 | 1 | 19
6039 | 9/9 | 14:00:00 | 291.15 | 98892 | 6.2 | 260 | 9.6075 | 1080 | 259.2 | 278.478 | 0 | 1 | 18
6040 | 9/9 | 15:00:00 | 291.15 | 98892 | 5.1 | 240 | 9.6075 | 1641.6 | 1472.4 | 277.986 | 0 | 1 | 18
6041 | 9/9 | 16:00:00 | 291.15 | 98892 | 5.7 | 240 | 8.9879 | 1213.2 | 1540.8 | 277.76 | 0 | 1 | 18
6042 | 9/9 | 17:00:00 | 292.15 | 98900 | 5.1 | 250 | 8.9872 | 716.4 | 910.8 | 278.714 | 0 | 1 | 19
6043 | 9/9 | 18:00:00 | 291.15 | 98892 | 5.1 | 260 | 9.6075 | 255.6 | 259.2 | 277.986 | 0 | 1 | 18
6044 | 9/9 | 19:00:00 | 290.15 | 98883 | 1.5 | 160 | 9.6084 | 14.4 | 0 | 276.76 | 0 | 1 | 17
6045 | 9/9 | 20:00:00 | 289.15 | 98875 | 2.6 | 220 | 9.6091 | 0 | 0 | 275.806 | 0 | 1 | 16
6046 | 9/9 | 21:00:00 | 288.15 | 98867 | 1.5 | 332 | 9.6099 | 0 | 0 | 274.852 | 0 | 1 | 15
6047 | 9/9 | 22:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.2668 | 0 | 0 | 276.029 | 0 | 1 | 16
6048 | 9/9 | 23:00:00 | 288.15 | 98867 | 1.5 | 180 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
6049 | 9/9 | 24:00:00 | 288.15 | 98867 | 2.1 | 220 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
6050 | 9/10 | 01:00:00 | 288.15 | 98867 | 2.1 | 150 | 10.2677 | 0 | 0 | 275.075 | 0 | 1 | 15
6051 | 9/10 | 02:00:00 | 288.15 | 98867 | 3.6 | 190 | 10.9655 | 0 | 0 | 275.565 | 0 | 1 | 15
6052 | 9/10 | 03:00:00 | 289.15 | 98875 | 2.6 | 140 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
6053 | 9/10 | 04:00:00 | 289.15 | 98875 | 3.1 | 140 | 10.9646 | 0 | 0 | 276.522 | 0 | 1 | 16
6054 | 9/10 | 05:00:00 | 289.15 | 98875 | 5.7 | 150 | 10.9646 | 0 | 0 | 277.011 | 0 | 1 | 16
6055 | 9/10 | 06:00:00 | 289.15 | 98875 | 4.6 | 160 | 11.7047 | 0 | 0 | 277.232 | 0 | 1 | 16
6056 | 9/10 | 07:00:00 | 289.15 | 98875 | 4.1 | 160 | 11.7047 | 64.8 | 0 | 277.345 | 0 | 1 | 16
6057 | 9/10 | 08:00:00 | 289.15 | 98875 | 4.6 | 170 | 11.7047 | 349.2 | 0 | 277.232 | 0 | 1 | 16
6058 | 9/10 | 09:00:00 | 290.15 | 98883 | 4.1 | 160 | 12.4883 | 622.8 | 43.2 | 278.412 | 0 | 1 | 17
6059 | 9/10 | 10:00:00 | 291.15 | 98892 | 4.6 | 160 | 12.4871 | 864 | 194.4 | 279.371 | 0 | 1 | 18
6060 | 9/10 | 11:00:00 | 292.15 | 98900 | 3.6 | 160 | 13.3174 | 1879.2 | 1864.8 | 280.056 | 0 | 1 | 19
6061 | 9/10 | 12:00:00 | 294.15 | 98916 | 6.2 | 200 | 10.96 | 1144.8 | 115.2 | 281.801 | 0 | 1 | 21
6062 | 9/10 | 13:00:00 | 293.15 | 98908 | 5.1 | 210 | 10.2634 | 1152 | 266.4 | 280.618 | 0 | 1 | 20
6063 | 9/10 | 14:00:00 | 295.15 | 98924 | 8.7 | 220 | 9.6043 | 1926 | 1800 | 281.805 | 0 | 1 | 22
6064 | 9/10 | 15:00:00 | 294.15 | 98916 | 6.7 | 210 | 10.96 | 1612.8 | 1828.8 | 281.303 | 0 | 1 | 21
6065 | 9/10 | 16:00:00 | 294.15 | 98916 | 5.1 | 240 | 9.6051 | 1191.6 | 1519.2 | 280.85 | 0 | 1 | 21
6066 | 9/10 | 17:00:00 | 293.15 | 98908 | 5.7 | 230 | 8.9864 | 698.4 | 889.2 | 279.668 | 0 | 1 | 20
6067 | 9/10 | 18:00:00 | 291.15 | 98892 | 5.7 | 220 | 9.6075 | 241.2 | 230.4 | 277.986 | 0 | 1 | 18
6068 | 9/10 | 19:00:00 | 290.15 | 98883 | 3.6 | 240 | 9.6084 | 7.2 | 0 | 276.76 | 0 | 1 | 17
6069 | 9/10 | 20:00:00 | 289.15 | 98875 | 4.6 | 220 | 7.8564 | 0 | 0 | 275.129 | 0 | 1 | 16
6070 | 9/10 | 21:00:00 | 288.15 | 98867 | 4.1 | 200 | 7.3399 | 0 | 0 | 273.95 | 0 | 1 | 15
6071 | 9/10 | 22:00:00 | 288.15 | 98867 | 5.7 | 210 | 7.3399 | 0 | 0 | 273.95 | 0 | 1 | 15
6072 | 9/10 | 23:00:00 | 287.15 | 98858 | 5.1 | 230 | 7.8578 | 0 | 0 | 273.226 | 0 | 1 | 14
6073 | 9/10 | 24:00:00 | 286.15 | 98850 | 7.2 | 210 | 7.3412 | 0 | 0 | 272.048 | 0 | 1 | 13
6074 | 9/11 | 01:00:00 | 286.15 | 98850 | 8.2 | 210 | 7.3412 | 0 | 0 | 272.048 | 0 | 1 | 13
6075 | 9/11 | 02:00:00 | 286.15 | 98850 | 7.7 | 210 | 7.8584 | 0 | 0 | 272.274 | 0 | 1 | 13
6076 | 9/11 | 03:00:00 | 286.15 | 98850 | 5.7 | 210 | 7.8584 | 0 | 0 | 272.541 | 0 | 1 | 13
6077 | 9/11 | 04:00:00 | 286.15 | 98850 | 6.2 | 200 | 7.8584 | 0 | 0 | 272.541 | 0 | 1 | 13
6078 | 9/11 | 05:00:00 | 285.15 | 98841 | 4.6 | 220 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
6079 | 9/11 | 06:00:00 | 286.15 | 98850 | 5.7 | 220 | 7.8584 | 0 | 0 | 272.541 | 0 | 1 | 13
6080 | 9/11 | 07:00:00 | 285.15 | 98841 | 5.1 | 230 | 7.3418 | 194.4 | 144 | 271.097 | 0 | 1 | 12
6081 | 9/11 | 08:00:00 | 286.15 | 98850 | 6.2 | 230 | 7.3412 | 658.8 | 1040.4 | 272.048 | 0 | 1 | 13
6082 | 9/11 | 09:00:00 | 287.15 | 98858 | 5.7 | 230 | 7.3406 | 1119.6 | 1339.2 | 273.266 | 0 | 1 | 14
6083 | 9/11 | 10:00:00 | 287.15 | 98858 | 6.2 | 220 | 7.3406 | 867.6 | 259.2 | 273.75 | 0 | 1 | 14
6084 | 9/11 | 11:00:00 | 288.15 | 98867 | 7.2 | 220 | 6.8534 | 1893.6 | 1825.2 | 273.988 | 0 | 1 | 15
6085 | 9/11 | 12:00:00 | 289.15 | 98875 | 7.2 | 240 | 6.8529 | 1148.4 | 248.4 | 275.426 | 0 | 1 | 16
6086 | 9/11 | 13:00:00 | 287.15 | 98858 | 9.3 | 230 | 7.3406 | 2077.2 | 1900.8 | 273.266 | 0 | 1 | 14
6087 | 9/11 | 14:00:00 | 288.15 | 98867 | 9.8 | 230 | 6.396 | 1926 | 2170.8 | 273.758 | 0 | 1 | 15
6088 | 9/11 | 15:00:00 | 289.15 | 98875 | 7.7 | 230 | 5.9656 | 1616.4 | 1872 | 274.475 | 0 | 1 | 16
6089 | 9/11 | 16:00:00 | 289.15 | 98875 | 8.2 | 230 | 6.3955 | 1180.8 | 1508.4 | 274.708 | 0 | 1 | 16
6090 | 9/11 | 17:00:00 | 288.15 | 98867 | 9.3 | 230 | 5.9661 | 723.6 | 1148.4 | 273.258 | 0 | 1 | 15
6091 | 9/11 | 18:00:00 | 288.15 | 98867 | 7.7 | 230 | 6.396 | 226.8 | 262.8 | 273.758 | 0 | 1 | 15
6092 | 9/11 | 19:00:00 | 287.15 | 98858 | 8.2 | 230 | 6.3966 | 0 | 0 | 272.808 | 0 | 1 | 14
6093 | 9/11 | 20:00:00 | 286.15 | 98850 | 7.2 | 230 | 5.9671 | 0 | 0 | 271.361 | 0 | 1 | 13
6094 | 9/11 | 21:00:00 | 286.15 | 98850 | 6.7 | 230 | 6.3971 | 0 | 0 | 271.858 | 0 | 1 | 13
6095 | 9/11 | 22:00:00 | 286.15 | 98850 | 5.1 | 210 | 6.8546 | 0 | 0 | 272.087 | 0 | 1 | 13
6096 | 9/11 | 23:00:00 | 286.15 | 98850 | 5.7 | 220 | 7.3412 | 0 | 0 | 272.314 | 0 | 1 | 13
6097 | 9/11 | 24:00:00 | 286.15 | 98850 | 4.6 | 220 | 7.8584 | 0 | 0 | 272.541 | 0 | 1 | 13
6098 | 9/12 | 01:00:00 | 285.15 | 98841 | 5.7 | 220 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
6099 | 9/12 | 02:00:00 | 284.15 | 98833 | 5.1 | 190 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6100 | 9/12 | 03:00:00 | 284.15 | 98833 | 5.7 | 180 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6101 | 9/12 | 04:00:00 | 285.15 | 98841 | 5.1 | 200 | 8.9926 | 0 | 0 | 272.036 | 0 | 1 | 12
6102 | 9/12 | 05:00:00 | 287.15 | 98858 | 5.1 | 210 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
6103 | 9/12 | 06:00:00 | 288.15 | 98867 | 7.2 | 220 | 10.2677 | 0 | 0 | 275.831 | 0 | 1 | 15
6104 | 9/12 | 07:00:00 | 289.15 | 98875 | 8.7 | 230 | 10.2668 | 172.8 | 100.8 | 276.3 | 0 | 1 | 16
6105 | 9/12 | 08:00:00 | 290.15 | 98883 | 8.7 | 240 | 9.6084 | 604.8 | 788.4 | 277.031 | 0 | 1 | 17
6106 | 9/12 | 09:00:00 | 289.15 | 98875 | 10.3 | 240 | 9.6091 | 1098 | 1440 | 276.076 | 0 | 1 | 16
6107 | 9/12 | 10:00:00 | 289.15 | 98875 | 12.9 | 240 | 7.8564 | 1544.4 | 1767.6 | 275.398 | 0 | 1 | 16
6108 | 9/12 | 11:00:00 | 288.15 | 98867 | 11.8 | 240 | 7.857 | 1868.4 | 2116.8 | 274.446 | 0 | 1 | 15
6109 | 9/12 | 12:00:00 | 290.15 | 98883 | 11.8 | 240 | 7.3387 | 2048.4 | 2214 | 276.121 | 0 | 1 | 17
6110 | 9/12 | 13:00:00 | 290.15 | 98883 | 14.4 | 250 | 6.8523 | 2059.2 | 1908 | 275.89 | 0 | 1 | 17
6111 | 9/12 | 14:00:00 | 289.15 | 98875 | 14.9 | 250 | 6.8529 | 1054.8 | 172.8 | 275.426 | 0 | 1 | 16
6112 | 9/12 | 15:00:00 | 290.15 | 98883 | 14.9 | 250 | 6.3949 | 882 | 129.6 | 276.145 | 0 | 1 | 17
6113 | 9/12 | 16:00:00 | 289.15 | 98875 | 17 | 250 | 6.3955 | 640.8 | 46.8 | 275.194 | 0 | 1 | 16
6114 | 9/12 | 17:00:00 | 289.15 | 98875 | 13.9 | 240 | 6.3955 | 367.2 | 7.2 | 275.194 | 0 | 1 | 16
6115 | 9/12 | 18:00:00 | 288.15 | 98867 | 18.5 | 260 | 6.396 | 118.8 | 0 | 274.242 | 0 | 1 | 15
6116 | 9/12 | 19:00:00 | 287.15 | 98858 | 13.9 | 250 | 6.854 | 0 | 0 | 273.521 | 0 | 1 | 14
6117 | 9/12 | 20:00:00 | 287.15 | 98858 | 12.9 | 250 | 6.854 | 0 | 0 | 273.038 | 0 | 1 | 14
6118 | 9/12 | 21:00:00 | 287.15 | 98858 | 12.9 | 250 | 6.854 | 0 | 0 | 273.038 | 0 | 1 | 14
6119 | 9/12 | 22:00:00 | 286.15 | 98850 | 12.9 | 250 | 6.3971 | 0 | 0 | 271.592 | 0 | 1 | 13
6120 | 9/12 | 23:00:00 | 286.15 | 98850 | 11.3 | 250 | 6.3971 | 0 | 0 | 271.592 | 0 | 1 | 13
6121 | 9/12 | 24:00:00 | 286.15 | 98850 | 11.3 | 250 | 6.3971 | 0 | 0 | 271.592 | 0 | 1 | 13
6122 | 9/13 | 01:00:00 | 285.15 | 98841 | 10.8 | 250 | 6.3977 | 0 | 0 | 270.643 | 0 | 1 | 12
6123 | 9/13 | 02:00:00 | 285.15 | 98841 | 11.3 | 250 | 6.8552 | 0 | 0 | 270.871 | 0 | 1 | 12
6124 | 9/13 | 03:00:00 | 285.15 | 98841 | 10.8 | 250 | 6.3977 | 0 | 0 | 270.643 | 0 | 1 | 12
6125 | 9/13 | 04:00:00 | 285.15 | 98841 | 11.8 | 250 | 6.8552 | 0 | 0 | 271.136 | 0 | 1 | 12
6126 | 9/13 | 05:00:00 | 284.15 | 98833 | 10.8 | 250 | 6.8558 | 0 | 0 | 269.921 | 0 | 1 | 11
6127 | 9/13 | 06:00:00 | 283.15 | 98824 | 10.8 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
6128 | 9/13 | 07:00:00 | 283.15 | 98824 | 11.8 | 250 | 6.8564 | 176.4 | 111.6 | 268.971 | 0 | 1 | 10
6129 | 9/13 | 08:00:00 | 284.15 | 98833 | 11.8 | 250 | 6.3982 | 630 | 1011.6 | 269.693 | 0 | 1 | 11
6130 | 9/13 | 09:00:00 | 285.15 | 98841 | 12.3 | 250 | 6.3977 | 1155.6 | 1666.8 | 270.643 | 0 | 1 | 12
6131 | 9/13 | 10:00:00 | 287.15 | 98858 | 13.4 | 250 | 5.9666 | 1537.2 | 1566 | 272.576 | 0 | 1 | 14
6132 | 9/13 | 11:00:00 | 287.15 | 98858 | 11.8 | 250 | 5.5627 | 1864.8 | 2163.6 | 272.343 | 0 | 1 | 14
6133 | 9/13 | 12:00:00 | 288.15 | 98867 | 11.3 | 250 | 5.5621 | 2041.2 | 2250 | 273.292 | 0 | 1 | 15
6134 | 9/13 | 13:00:00 | 286.15 | 98850 | 11.3 | 260 | 6.3971 | 2041.2 | 2232 | 271.858 | 0 | 1 | 13
6135 | 9/13 | 14:00:00 | 286.15 | 98850 | 10.3 | 250 | 6.8546 | 1879.2 | 2145.6 | 272.087 | 0 | 1 | 13
6136 | 9/13 | 15:00:00 | 287.15 | 98858 | 10.3 | 260 | 5.9666 | 1573.2 | 1836 | 272.576 | 0 | 1 | 14
6137 | 9/13 | 16:00:00 | 286.15 | 98850 | 8.7 | 250 | 6.3971 | 1137.6 | 1418.4 | 271.858 | 0 | 1 | 13
6138 | 9/13 | 17:00:00 | 285.15 | 98841 | 9.3 | 260 | 5.9676 | 644.4 | 892.8 | 270.678 | 0 | 1 | 12
6139 | 9/13 | 18:00:00 | 284.15 | 98833 | 9.8 | 260 | 6.3982 | 198 | 118.8 | 269.957 | 0 | 1 | 11
6140 | 9/13 | 19:00:00 | 283.15 | 98824 | 8.7 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
6141 | 9/13 | 20:00:00 | 283.15 | 98824 | 8.2 | 260 | 5.5646 | 0 | 0 | 268.287 | 0 | 1 | 10
6142 | 9/13 | 21:00:00 | 283.15 | 98824 | 9.8 | 260 | 6.3988 | 0 | 0 | 268.744 | 0 | 1 | 10
6143 | 9/13 | 22:00:00 | 283.15 | 98824 | 9.8 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
6144 | 9/13 | 23:00:00 | 283.15 | 98824 | 12.3 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
6145 | 9/13 | 24:00:00 | 283.15 | 98824 | 11.8 | 270 | 6.3988 | 0 | 0 | 268.744 | 0 | 1 | 10
6146 | 9/14 | 01:00:00 | 283.15 | 98824 | 8.7 | 260 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
6147 | 9/14 | 02:00:00 | 284.15 | 98833 | 8.2 | 260 | 6.8558 | 0 | 0 | 270.663 | 0 | 1 | 11
6148 | 9/14 | 03:00:00 | 284.15 | 98833 | 8.2 | 260 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6149 | 9/14 | 04:00:00 | 284.15 | 98833 | 7.7 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
6150 | 9/14 | 05:00:00 | 284.15 | 98833 | 6.7 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6151 | 9/14 | 06:00:00 | 284.15 | 98833 | 5.1 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6152 | 9/14 | 07:00:00 | 284.15 | 98833 | 4.6 | 270 | 7.8598 | 86.4 | 0 | 271.115 | 0 | 1 | 11
6153 | 9/14 | 08:00:00 | 285.15 | 98841 | 5.1 | 270 | 7.8591 | 320.4 | 0 | 272.069 | 0 | 1 | 12
6154 | 9/14 | 09:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.4088 | 594 | 72 | 272.294 | 0 | 1 | 12
6155 | 9/14 | 10:00:00 | 286.15 | 98850 | 5.7 | 280 | 8.408 | 1504.8 | 1400.4 | 272.766 | 0 | 1 | 13
6156 | 9/14 | 11:00:00 | 286.15 | 98850 | 6.7 | 280 | 7.8584 | 1832.4 | 2102.4 | 272.541 | 0 | 1 | 13
6157 | 9/14 | 12:00:00 | 287.15 | 98858 | 7.2 | 270 | 7.8578 | 2005.2 | 2192.4 | 273.493 | 0 | 1 | 14
6158 | 9/14 | 13:00:00 | 287.15 | 98858 | 5.7 | 290 | 7.8578 | 2012.4 | 2196 | 273.493 | 0 | 1 | 14
6159 | 9/14 | 14:00:00 | 288.15 | 98867 | 9.8 | 260 | 7.3399 | 1857.6 | 2127.6 | 274.218 | 0 | 1 | 15
6160 | 9/14 | 15:00:00 | 288.15 | 98867 | 10.3 | 270 | 7.3399 | 1544.4 | 1551.6 | 274.218 | 0 | 1 | 15
6161 | 9/14 | 16:00:00 | 288.15 | 98867 | 11.8 | 270 | 7.3399 | 1177.2 | 1677.6 | 273.95 | 0 | 1 | 15
6162 | 9/14 | 17:00:00 | 285.15 | 98841 | 12.3 | 270 | 7.8591 | 658.8 | 1044 | 271.323 | 0 | 1 | 12
6163 | 9/14 | 18:00:00 | 285.15 | 98841 | 9.8 | 270 | 7.8591 | 194.4 | 147.6 | 271.323 | 0 | 1 | 12
6164 | 9/14 | 19:00:00 | 284.15 | 98833 | 7.2 | 270 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6165 | 9/14 | 20:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6166 | 9/14 | 21:00:00 | 284.15 | 98833 | 6.7 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6167 | 9/14 | 22:00:00 | 283.15 | 98824 | 4.6 | 270 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
6168 | 9/14 | 23:00:00 | 282.15 | 98815 | 4.1 | 310 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
6169 | 9/14 | 24:00:00 | 281.15 | 98806 | 4.1 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
6170 | 9/15 | 01:00:00 | 281.15 | 98806 | 3.6 | 260 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
6171 | 9/15 | 02:00:00 | 280.15 | 98798 | 3.6 | 270 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
6172 | 9/15 | 03:00:00 | 279.15 | 98789 | 3.1 | 290 | 5.9708 | 0 | 0 | 265.559 | 0 | 1 | 6
6173 | 9/15 | 04:00:00 | 279.15 | 98789 | 1.5 | 270 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
6174 | 9/15 | 05:00:00 | 279.15 | 98789 | 2.1 | 260 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
6175 | 9/15 | 06:00:00 | 278.15 | 98780 | 2.1 | 270 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
6176 | 9/15 | 07:00:00 | 279.15 | 98789 | 2.6 | 300 | 5.187 | 93.6 | 0 | 264.996 | 0 | 1 | 6
6177 | 9/15 | 08:00:00 | 280.15 | 98798 | 2.1 | 300 | 5.9703 | 259.2 | 0 | 266.51 | 0 | 1 | 7
6178 | 9/15 | 09:00:00 | 283.15 | 98824 | 2.1 | 30 | 5.9687 | 936 | 882 | 269.025 | 0 | 1 | 10
6179 | 9/15 | 10:00:00 | 284.15 | 98833 | 1.5 | 39 | 5.9681 | 1425.6 | 1389.6 | 269.854 | 0 | 1 | 11
6180 | 9/15 | 11:00:00 | 285.15 | 98841 | 1 | 208 | 6.3977 | 1933.2 | 2325.6 | 270.643 | 0 | 1 | 12
6181 | 9/15 | 12:00:00 | 286.15 | 98850 | 1.5 | 86 | 5.9671 | 2120.4 | 2631.6 | 271.361 | 0 | 1 | 13
6182 | 9/15 | 13:00:00 | 287.15 | 98858 | 2.1 | 60 | 5.9666 | 2127.6 | 2635.2 | 272.31 | 0 | 1 | 14
6183 | 9/15 | 14:00:00 | 288.15 | 98867 | 2.1 | 50 | 5.9661 | 1954.8 | 2530.8 | 273.258 | 0 | 1 | 15
6184 | 9/15 | 15:00:00 | 288.15 | 98867 | 2.1 | 110 | 5.9661 | 1620 | 2239.2 | 273.258 | 0 | 1 | 15
6185 | 9/15 | 16:00:00 | 288.15 | 98867 | 3.1 | 110 | 5.5621 | 1162.8 | 1692 | 273.025 | 0 | 1 | 15
6186 | 9/15 | 17:00:00 | 288.15 | 98867 | 3.1 | 120 | 5.5621 | 640.8 | 1040.4 | 273.025 | 0 | 1 | 15
6187 | 9/15 | 18:00:00 | 287.15 | 98858 | 2.6 | 120 | 5.9666 | 180 | 183.6 | 272.445 | 0 | 1 | 14
6188 | 9/15 | 19:00:00 | 285.15 | 98841 | 4.1 | 100 | 6.8552 | 0 | 0 | 271.384 | 0 | 1 | 12
6189 | 9/15 | 20:00:00 | 283.15 | 98824 | 3.1 | 110 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
6190 | 9/15 | 21:00:00 | 282.15 | 98815 | 3.6 | 100 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6191 | 9/15 | 22:00:00 | 283.15 | 98824 | 3.1 | 90 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
6192 | 9/15 | 23:00:00 | 283.15 | 98824 | 3.1 | 90 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
6193 | 9/15 | 24:00:00 | 283.15 | 98824 | 2.6 | 90 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
6194 | 9/16 | 01:00:00 | 283.15 | 98824 | 3.1 | 80 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
6195 | 9/16 | 02:00:00 | 283.15 | 98824 | 2.6 | 80 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
6196 | 9/16 | 03:00:00 | 283.15 | 98824 | 2.6 | 70 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
6197 | 9/16 | 04:00:00 | 284.15 | 98833 | 2.6 | 90 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6198 | 9/16 | 05:00:00 | 284.15 | 98833 | 3.6 | 120 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6199 | 9/16 | 06:00:00 | 285.15 | 98841 | 4.6 | 130 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
6200 | 9/16 | 07:00:00 | 285.15 | 98841 | 6.2 | 130 | 8.4088 | 75.6 | 0 | 272.294 | 0 | 1 | 12
6201 | 9/16 | 08:00:00 | 285.15 | 98841 | 5.1 | 130 | 8.4088 | 306 | 0 | 272.294 | 0 | 1 | 12
6202 | 9/16 | 09:00:00 | 285.15 | 98841 | 5.1 | 140 | 8.4088 | 576 | 50.4 | 272.294 | 0 | 1 | 12
6203 | 9/16 | 10:00:00 | 285.15 | 98841 | 5.1 | 150 | 8.4088 | 817.2 | 82.8 | 272.294 | 0 | 1 | 12
6204 | 9/16 | 11:00:00 | 286.15 | 98850 | 6.2 | 150 | 8.9918 | 993.6 | 248.4 | 273.473 | 0 | 1 | 13
6205 | 9/16 | 12:00:00 | 286.15 | 98850 | 6.2 | 150 | 8.408 | 1965.6 | 1846.8 | 272.766 | 0 | 1 | 13
6206 | 9/16 | 13:00:00 | 287.15 | 98858 | 6.2 | 140 | 8.991 | 1965.6 | 1839.6 | 273.944 | 0 | 1 | 14
6207 | 9/16 | 14:00:00 | 287.15 | 98858 | 4.6 | 150 | 8.991 | 1000.8 | 252 | 274.428 | 0 | 1 | 14
6208 | 9/16 | 15:00:00 | 288.15 | 98867 | 5.1 | 150 | 7.857 | 831.6 | 61.2 | 274.931 | 0 | 1 | 15
6209 | 9/16 | 16:00:00 | 288.15 | 98867 | 6.2 | 140 | 8.4065 | 590.4 | 54 | 275.158 | 0 | 1 | 15
6210 | 9/16 | 17:00:00 | 288.15 | 98867 | 6.2 | 140 | 7.857 | 320.4 | 0 | 274.931 | 0 | 1 | 15
6211 | 9/16 | 18:00:00 | 286.15 | 98850 | 4.1 | 230 | 9.6116 | 154.8 | 68.4 | 273.212 | 0 | 1 | 13
6212 | 9/16 | 19:00:00 | 286.15 | 98850 | 2.6 | 200 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
6213 | 9/16 | 20:00:00 | 285.15 | 98841 | 2.1 | 250 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
6214 | 9/16 | 21:00:00 | 285.15 | 98841 | 3.1 | 230 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
6215 | 9/16 | 22:00:00 | 284.15 | 98833 | 2.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6216 | 9/16 | 23:00:00 | 285.15 | 98841 | 4.1 | 220 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
6217 | 9/16 | 24:00:00 | 284.15 | 98833 | 3.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6218 | 9/17 | 01:00:00 | 284.15 | 98833 | 4.1 | 220 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6219 | 9/17 | 02:00:00 | 284.15 | 98833 | 3.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6220 | 9/17 | 03:00:00 | 284.15 | 98833 | 2.1 | 180 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6221 | 9/17 | 04:00:00 | 284.15 | 98833 | 3.6 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6222 | 9/17 | 05:00:00 | 284.15 | 98833 | 4.6 | 230 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6223 | 9/17 | 06:00:00 | 284.15 | 98833 | 2.6 | 200 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6224 | 9/17 | 07:00:00 | 284.15 | 98833 | 2.6 | 210 | 7.8598 | 129.6 | 3.6 | 270.636 | 0 | 1 | 11
6225 | 9/17 | 08:00:00 | 284.15 | 98833 | 4.6 | 220 | 7.8598 | 540 | 601.2 | 270.636 | 0 | 1 | 11
6226 | 9/17 | 09:00:00 | 284.15 | 98833 | 5.7 | 230 | 7.8598 | 1022.4 | 1314 | 270.636 | 0 | 1 | 11
6227 | 9/17 | 10:00:00 | 284.15 | 98833 | 6.7 | 230 | 7.3425 | 1461.6 | 1735.2 | 270.411 | 0 | 1 | 11
6228 | 9/17 | 11:00:00 | 284.15 | 98833 | 5.7 | 250 | 7.8598 | 1778.4 | 2077.2 | 270.636 | 0 | 1 | 11
6229 | 9/17 | 12:00:00 | 286.15 | 98850 | 6.7 | 260 | 7.3412 | 1951.2 | 2188.8 | 272.314 | 0 | 1 | 13
6230 | 9/17 | 13:00:00 | 284.15 | 98833 | 7.2 | 250 | 6.8558 | 1958.4 | 2203.2 | 270.185 | 0 | 1 | 11
6231 | 9/17 | 14:00:00 | 284.15 | 98833 | 4.6 | 260 | 7.3425 | 1792.8 | 2098.8 | 270.411 | 0 | 1 | 11
6232 | 9/17 | 15:00:00 | 284.15 | 98833 | 5.1 | 240 | 7.3425 | 1479.6 | 1519.2 | 270.411 | 0 | 1 | 11
6233 | 9/17 | 16:00:00 | 286.15 | 98850 | 7.2 | 260 | 7.3412 | 1108.8 | 1623.6 | 272.048 | 0 | 1 | 13
6234 | 9/17 | 17:00:00 | 285.15 | 98841 | 6.7 | 260 | 6.8552 | 561.6 | 633.6 | 271.136 | 0 | 1 | 12
6235 | 9/17 | 18:00:00 | 284.15 | 98833 | 3.6 | 270 | 7.3425 | 151.2 | 75.6 | 270.147 | 0 | 1 | 11
6236 | 9/17 | 19:00:00 | 283.15 | 98824 | 3.6 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
6237 | 9/17 | 20:00:00 | 282.15 | 98815 | 2.6 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6238 | 9/17 | 21:00:00 | 282.15 | 98815 | 3.1 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6239 | 9/17 | 22:00:00 | 282.15 | 98815 | 2.6 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6240 | 9/17 | 23:00:00 | 282.15 | 98815 | 2.6 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6241 | 9/17 | 24:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
6242 | 9/18 | 01:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
6243 | 9/18 | 02:00:00 | 281.15 | 98806 | 1.5 | 260 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
6244 | 9/18 | 03:00:00 | 281.15 | 98806 | 3.6 | 270 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
6245 | 9/18 | 04:00:00 | 280.15 | 98798 | 2.6 | 250 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
6246 | 9/18 | 05:00:00 | 280.15 | 98798 | 3.1 | 260 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
6247 | 9/18 | 06:00:00 | 280.15 | 98798 | 3.1 | 260 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
6248 | 9/18 | 07:00:00 | 282.15 | 98815 | 2.6 | 320 | 6.8571 | 118.8 | 0 | 268.283 | 0 | 1 | 9
6249 | 9/18 | 08:00:00 | 282.15 | 98815 | 2.1 | 310 | 7.3438 | 558 | 903.6 | 268.245 | 0 | 1 | 9
6250 | 9/18 | 09:00:00 | 283.15 | 98824 | 2.1 | 270 | 7.3431 | 1008 | 1310.4 | 269.46 | 0 | 1 | 10
6251 | 9/18 | 10:00:00 | 285.15 | 98841 | 3.1 | 310 | 7.8591 | 1440 | 1720.8 | 271.588 | 0 | 1 | 12
6252 | 9/18 | 11:00:00 | 285.15 | 98841 | 2.1 | 300 | 7.8591 | 1760.4 | 2066.4 | 271.588 | 0 | 1 | 12
6253 | 9/18 | 12:00:00 | 286.15 | 98850 | 1.5 | 182 | 7.3412 | 1933.2 | 1872 | 272.314 | 0 | 1 | 13
6254 | 9/18 | 13:00:00 | 286.15 | 98850 | 1.5 | 250 | 7.3412 | 1072.8 | 176.4 | 272.796 | 0 | 1 | 13
6255 | 9/18 | 14:00:00 | 288.15 | 98867 | 2.6 | 290 | 7.3399 | 982.8 | 72 | 274.703 | 0 | 1 | 15
6256 | 9/18 | 15:00:00 | 284.15 | 98833 | 1.5 | 248 | 7.8598 | 1454.4 | 1404 | 270.636 | 0 | 1 | 11
6257 | 9/18 | 16:00:00 | 285.15 | 98841 | 4.6 | 340 | 7.3418 | 1026 | 1328.4 | 271.363 | 0 | 1 | 12
6258 | 9/18 | 17:00:00 | 285.15 | 98841 | 4.1 | 360 | 7.3418 | 543.6 | 608.4 | 271.363 | 0 | 1 | 12
6259 | 9/18 | 18:00:00 | 285.15 | 98841 | 2.1 | 320 | 7.3418 | 129.6 | 10.8 | 271.363 | 0 | 1 | 12
6260 | 9/18 | 19:00:00 | 284.15 | 98833 | 3.1 | 360 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6261 | 9/18 | 20:00:00 | 284.15 | 98833 | 2.6 | 320 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6262 | 9/18 | 21:00:00 | 284.15 | 98833 | 5.7 | 300 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6263 | 9/18 | 22:00:00 | 284.15 | 98833 | 5.7 | 300 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6264 | 9/18 | 23:00:00 | 284.15 | 98833 | 6.2 | 300 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6265 | 9/18 | 24:00:00 | 284.15 | 98833 | 5.7 | 310 | 6.8558 | 0 | 0 | 269.921 | 0 | 1 | 11
6266 | 9/19 | 01:00:00 | 283.15 | 98824 | 4.1 | 310 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
6267 | 9/19 | 02:00:00 | 282.15 | 98815 | 4.1 | 300 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6268 | 9/19 | 03:00:00 | 281.15 | 98806 | 3.1 | 280 | 6.8577 | 0 | 0 | 267.071 | 0 | 1 | 8
6269 | 9/19 | 04:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6270 | 9/19 | 05:00:00 | 283.15 | 98824 | 4.6 | 270 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
6271 | 9/19 | 06:00:00 | 282.15 | 98815 | 3.1 | 290 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
6272 | 9/19 | 07:00:00 | 282.15 | 98815 | 3.6 | 290 | 7.3438 | 111.6 | 0 | 268.508 | 0 | 1 | 9
6273 | 9/19 | 08:00:00 | 284.15 | 98833 | 3.6 | 270 | 7.7013 | 511.2 | 572.4 | 270.569 | 0 | 1 | 11
6274 | 9/19 | 09:00:00 | 285.15 | 98841 | 5.7 | 260 | 7.8591 | 1051.2 | 1562.4 | 271.323 | 0 | 1 | 12
6275 | 9/19 | 10:00:00 | 286.15 | 98850 | 7.7 | 270 | 7.3412 | 1425.6 | 1494 | 272.314 | 0 | 1 | 13
6276 | 9/19 | 11:00:00 | 287.15 | 98858 | 5.1 | 260 | 7.3406 | 1742.4 | 1609.2 | 273.266 | 0 | 1 | 14
6277 | 9/19 | 12:00:00 | 286.15 | 98850 | 5.1 | 230 | 7.3412 | 1062 | 75.6 | 272.796 | 0 | 1 | 13
6278 | 9/19 | 13:00:00 | 287.15 | 98858 | 6.2 | 240 | 7.3406 | 1062 | 205.2 | 273.75 | 0 | 1 | 14
6279 | 9/19 | 14:00:00 | 287.15 | 98858 | 7.7 | 240 | 7.8578 | 968.4 | 136.8 | 273.977 | 0 | 1 | 14
6280 | 9/19 | 15:00:00 | 286.15 | 98850 | 8.2 | 230 | 8.408 | 1429.2 | 1382.4 | 272.766 | 0 | 1 | 13
6281 | 9/19 | 16:00:00 | 287.15 | 98858 | 7.2 | 230 | 8.991 | 997.2 | 1087.2 | 273.944 | 0 | 1 | 14
6282 | 9/19 | 17:00:00 | 287.15 | 98858 | 6.2 | 230 | 8.991 | 288 | 0 | 274.428 | 0 | 1 | 14
6283 | 9/19 | 18:00:00 | 287.15 | 98858 | 4.6 | 230 | 8.991 | 118.8 | 0 | 273.944 | 0 | 1 | 14
6284 | 9/19 | 19:00:00 | 287.15 | 98858 | 4.6 | 220 | 8.991 | 0 | 0 | 273.944 | 0 | 1 | 14
6285 | 9/19 | 20:00:00 | 287.15 | 98858 | 4.1 | 220 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
6286 | 9/19 | 21:00:00 | 287.15 | 98858 | 3.1 | 220 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
6287 | 9/19 | 22:00:00 | 287.15 | 98858 | 5.1 | 230 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
6288 | 9/19 | 23:00:00 | 287.15 | 98858 | 5.7 | 230 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
6289 | 9/19 | 24:00:00 | 287.15 | 98858 | 6.7 | 220 | 8.991 | 0 | 0 | 273.944 | 0 | 1 | 14
6290 | 9/20 | 01:00:00 | 287.15 | 98858 | 7.7 | 230 | 8.991 | 0 | 0 | 273.944 | 0 | 1 | 14
6291 | 9/20 | 02:00:00 | 287.15 | 98858 | 6.7 | 230 | 9.6108 | 0 | 0 | 274.167 | 0 | 1 | 14
6292 | 9/20 | 03:00:00 | 287.15 | 98858 | 5.7 | 230 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
6293 | 9/20 | 04:00:00 | 286.15 | 98850 | 7.2 | 270 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
6294 | 9/20 | 05:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
6295 | 9/20 | 06:00:00 | 284.15 | 98833 | 2.1 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6296 | 9/20 | 07:00:00 | 284.15 | 98833 | 3.1 | 240 | 7.8598 | 57.6 | 0 | 271.115 | 0 | 1 | 11
6297 | 9/20 | 08:00:00 | 285.15 | 98841 | 1 | 74 | 7.3418 | 277.2 | 0 | 271.843 | 0 | 1 | 12
6298 | 9/20 | 09:00:00 | 285.15 | 98841 | 2.1 | 230 | 7.8591 | 540 | 32.4 | 272.069 | 0 | 1 | 12
6299 | 9/20 | 10:00:00 | 285.15 | 98841 | 3.6 | 250 | 8.4088 | 777.6 | 79.2 | 272.294 | 0 | 1 | 12
6300 | 9/20 | 11:00:00 | 285.15 | 98841 | 3.1 | 250 | 7.8591 | 954 | 140.4 | 272.069 | 0 | 1 | 12
6301 | 9/20 | 12:00:00 | 285.15 | 98841 | 2.6 | 270 | 8.4088 | 1047.6 | 262.8 | 272.294 | 0 | 1 | 12
6302 | 9/20 | 13:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.4088 | 1886.4 | 1688.4 | 271.813 | 0 | 1 | 12
6303 | 9/20 | 14:00:00 | 286.15 | 98850 | 4.6 | 260 | 7.8584 | 957.6 | 288 | 273.023 | 0 | 1 | 13
6304 | 9/20 | 15:00:00 | 286.15 | 98850 | 5.1 | 260 | 7.8584 | 1411.2 | 1386 | 272.541 | 0 | 1 | 13
6305 | 9/20 | 16:00:00 | 286.15 | 98850 | 5.1 | 250 | 7.3412 | 982.8 | 1296 | 272.314 | 0 | 1 | 13
6306 | 9/20 | 17:00:00 | 285.15 | 98841 | 4.6 | 250 | 6.3977 | 504 | 576 | 270.907 | 0 | 1 | 12
6307 | 9/20 | 18:00:00 | 285.15 | 98841 | 4.1 | 260 | 6.8552 | 108 | 0 | 271.136 | 0 | 1 | 12
6308 | 9/20 | 19:00:00 | 284.15 | 98833 | 2.6 | 240 | 6.8558 | 0 | 0 | 269.921 | 0 | 1 | 11
6309 | 9/20 | 20:00:00 | 284.15 | 98833 | 2.6 | 240 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6310 | 9/20 | 21:00:00 | 284.15 | 98833 | 4.1 | 240 | 6.8558 | 0 | 0 | 269.921 | 0 | 1 | 11
6311 | 9/20 | 22:00:00 | 284.15 | 98833 | 3.1 | 220 | 6.8558 | 0 | 0 | 269.921 | 0 | 1 | 11
6312 | 9/20 | 23:00:00 | 283.15 | 98824 | 3.1 | 220 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
6313 | 9/20 | 24:00:00 | 283.15 | 98824 | 3.6 | 220 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
6314 | 9/21 | 01:00:00 | 282.15 | 98815 | 3.6 | 220 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
6315 | 9/21 | 02:00:00 | 282.15 | 98815 | 2.6 | 190 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
6316 | 9/21 | 03:00:00 | 282.15 | 98815 | 1.5 | 90 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
6317 | 9/21 | 04:00:00 | 282.15 | 98815 | 1.5 | 49 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
6318 | 9/21 | 05:00:00 | 282.15 | 98815 | 2.1 | 230 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
6319 | 9/21 | 06:00:00 | 282.15 | 98815 | 2.6 | 220 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
6320 | 9/21 | 07:00:00 | 282.15 | 98815 | 4.1 | 210 | 6.8571 | 100.8 | 0 | 268.021 | 0 | 1 | 9
6321 | 9/21 | 08:00:00 | 283.15 | 98824 | 4.1 | 220 | 6.8564 | 514.8 | 849.6 | 268.971 | 0 | 1 | 10
6322 | 9/21 | 09:00:00 | 283.15 | 98824 | 5.1 | 220 | 6.8564 | 1018.8 | 1551.6 | 268.971 | 0 | 1 | 10
6323 | 9/21 | 10:00:00 | 285.15 | 98841 | 6.7 | 220 | 6.8552 | 1476 | 2120.4 | 270.871 | 0 | 1 | 12
6324 | 9/21 | 11:00:00 | 285.15 | 98841 | 6.7 | 220 | 6.3977 | 1710 | 1728 | 270.907 | 0 | 1 | 12
6325 | 9/21 | 12:00:00 | 286.15 | 98850 | 8.7 | 220 | 6.8546 | 1875.6 | 2178 | 272.087 | 0 | 1 | 13
6326 | 9/21 | 13:00:00 | 287.15 | 98858 | 11.8 | 230 | 6.3966 | 1879.2 | 2041.2 | 272.808 | 0 | 1 | 14
6327 | 9/21 | 14:00:00 | 288.15 | 98867 | 10.8 | 230 | 6.396 | 1814.4 | 2286 | 273.49 | 0 | 1 | 15
6328 | 9/21 | 15:00:00 | 287.15 | 98858 | 9.3 | 230 | 6.3966 | 1393.2 | 1396.8 | 272.808 | 0 | 1 | 14
6329 | 9/21 | 16:00:00 | 287.15 | 98858 | 10.8 | 230 | 6.854 | 532.8 | 136.8 | 273.521 | 0 | 1 | 14
6330 | 9/21 | 17:00:00 | 286.15 | 98850 | 8.7 | 230 | 7.3412 | 270 | 0 | 272.796 | 0 | 1 | 13
6331 | 9/21 | 18:00:00 | 285.15 | 98841 | 6.7 | 250 | 8.4088 | 93.6 | 0 | 271.813 | 0 | 1 | 12
6332 | 9/21 | 19:00:00 | 284.15 | 98833 | 6.2 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6333 | 9/21 | 20:00:00 | 285.15 | 98841 | 6.7 | 240 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
6334 | 9/21 | 21:00:00 | 284.15 | 98833 | 5.1 | 250 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6335 | 9/21 | 22:00:00 | 284.15 | 98833 | 6.7 | 250 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6336 | 9/21 | 23:00:00 | 284.15 | 98833 | 5.7 | 260 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6337 | 9/21 | 24:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
6338 | 9/22 | 01:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
6339 | 9/22 | 02:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
6340 | 9/22 | 03:00:00 | 282.15 | 98815 | 5.1 | 250 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
6341 | 9/22 | 04:00:00 | 281.15 | 98806 | 3.1 | 250 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
6342 | 9/22 | 05:00:00 | 281.15 | 98806 | 3.6 | 260 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
6343 | 9/22 | 06:00:00 | 282.15 | 98815 | 4.6 | 260 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
6344 | 9/22 | 07:00:00 | 282.15 | 98815 | 3.6 | 250 | 6.3994 | 93.6 | 0 | 267.795 | 0 | 1 | 9
6345 | 9/22 | 08:00:00 | 283.15 | 98824 | 5.7 | 250 | 6.3988 | 471.6 | 540 | 269.007 | 0 | 1 | 10
6346 | 9/22 | 09:00:00 | 284.15 | 98833 | 7.2 | 250 | 6.3982 | 1004.4 | 1490.4 | 269.693 | 0 | 1 | 11
6347 | 9/22 | 10:00:00 | 284.15 | 98833 | 7.7 | 260 | 5.9681 | 1461.6 | 2127.6 | 269.465 | 0 | 1 | 11
6348 | 9/22 | 11:00:00 | 284.15 | 98833 | 6.2 | 270 | 6.3982 | 1692 | 1976.4 | 269.957 | 0 | 1 | 11
6349 | 9/22 | 12:00:00 | 285.15 | 98841 | 8.7 | 260 | 5.5636 | 1864.8 | 2203.2 | 270.447 | 0 | 1 | 12
6350 | 9/22 | 13:00:00 | 286.15 | 98850 | 10.3 | 270 | 5.5631 | 1861.2 | 2052 | 271.395 | 0 | 1 | 13
6351 | 9/22 | 14:00:00 | 285.15 | 98841 | 10.3 | 260 | 5.1842 | 1800 | 2404.8 | 269.95 | 0 | 1 | 12
6352 | 9/22 | 15:00:00 | 286.15 | 98850 | 7.7 | 260 | 5.1837 | 1461.6 | 2145.6 | 270.896 | 0 | 1 | 13
6353 | 9/22 | 16:00:00 | 285.15 | 98841 | 6.7 | 260 | 5.1842 | 1000.8 | 1558.8 | 269.95 | 0 | 1 | 12
6354 | 9/22 | 17:00:00 | 285.15 | 98841 | 7.7 | 270 | 5.9676 | 496.8 | 828 | 270.413 | 0 | 1 | 12
6355 | 9/22 | 18:00:00 | 285.15 | 98841 | 6.2 | 260 | 5.9676 | 90 | 0 | 270.413 | 0 | 1 | 12
6356 | 9/22 | 19:00:00 | 284.15 | 98833 | 3.6 | 240 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
6357 | 9/22 | 20:00:00 | 284.15 | 98833 | 3.1 | 240 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6358 | 9/22 | 21:00:00 | 284.15 | 98833 | 2.6 | 240 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6359 | 9/22 | 22:00:00 | 284.15 | 98833 | 2.6 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6360 | 9/22 | 23:00:00 | 284.15 | 98833 | 3.1 | 210 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6361 | 9/22 | 24:00:00 | 285.15 | 98841 | 4.1 | 230 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
6362 | 9/23 | 01:00:00 | 284.15 | 98833 | 2.1 | 200 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6363 | 9/23 | 02:00:00 | 284.15 | 98833 | 2.1 | 210 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6364 | 9/23 | 03:00:00 | 284.15 | 98833 | 3.6 | 230 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
6365 | 9/23 | 04:00:00 | 283.15 | 98824 | 3.1 | 230 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
6366 | 9/23 | 05:00:00 | 283.15 | 98824 | 2.6 | 210 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
6367 | 9/23 | 06:00:00 | 283.15 | 98824 | 3.6 | 230 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
6368 | 9/23 | 07:00:00 | 283.15 | 98824 | 2.1 | 230 | 7.3431 | 82.8 | 0 | 269.46 | 0 | 1 | 10
6369 | 9/23 | 08:00:00 | 283.15 | 98824 | 2.1 | 180 | 7.3431 | 457.2 | 518.4 | 269.46 | 0 | 1 | 10
6370 | 9/23 | 09:00:00 | 284.15 | 98833 | 3.6 | 230 | 7.3425 | 925.2 | 1058.4 | 270.411 | 0 | 1 | 11
6371 | 9/23 | 10:00:00 | 285.15 | 98841 | 4.6 | 220 | 7.3418 | 752.4 | 111.6 | 271.843 | 0 | 1 | 12
6372 | 9/23 | 11:00:00 | 285.15 | 98841 | 4.6 | 220 | 7.3418 | 925.2 | 136.8 | 271.843 | 0 | 1 | 12
6373 | 9/23 | 12:00:00 | 286.15 | 98850 | 3.6 | 230 | 7.8584 | 1015.2 | 172.8 | 273.023 | 0 | 1 | 13
6374 | 9/23 | 13:00:00 | 287.15 | 98858 | 4.6 | 230 | 7.8578 | 1828.8 | 1828.8 | 273.493 | 0 | 1 | 14
6375 | 9/23 | 14:00:00 | 288.15 | 98867 | 4.1 | 230 | 7.857 | 1659.6 | 1674 | 274.446 | 0 | 1 | 15
6376 | 9/23 | 15:00:00 | 288.15 | 98867 | 3.1 | 220 | 7.857 | 1342.8 | 1674 | 274.446 | 0 | 1 | 15
6377 | 9/23 | 16:00:00 | 288.15 | 98867 | 4.6 | 230 | 7.3399 | 914.4 | 1238.4 | 274.218 | 0 | 1 | 15
6378 | 9/23 | 17:00:00 | 288.15 | 98867 | 3.1 | 220 | 7.3399 | 446.4 | 504 | 274.218 | 0 | 1 | 15
6379 | 9/23 | 18:00:00 | 287.15 | 98858 | 3.6 | 220 | 7.3406 | 79.2 | 0 | 273.266 | 0 | 1 | 14
6380 | 9/23 | 19:00:00 | 286.15 | 98850 | 2.1 | 210 | 7.3412 | 0 | 0 | 272.314 | 0 | 1 | 13
6381 | 9/23 | 20:00:00 | 286.15 | 98850 | 2.1 | 180 | 7.3412 | 0 | 0 | 272.314 | 0 | 1 | 13
6382 | 9/23 | 21:00:00 | 285.15 | 98841 | 2.6 | 210 | 7.3418 | 0 | 0 | 271.097 | 0 | 1 | 12
6383 | 9/23 | 22:00:00 | 285.15 | 98841 | 3.6 | 230 | 7.3418 | 0 | 0 | 271.097 | 0 | 1 | 12
6384 | 9/23 | 23:00:00 | 285.15 | 98841 | 5.1 | 220 | 7.3418 | 0 | 0 | 271.729 | 0 | 1 | 12
6385 | 9/23 | 24:00:00 | 285.15 | 98841 | 3.6 | 200 | 6.8552 | 0 | 0 | 271.384 | 0 | 1 | 12
6386 | 9/24 | 01:00:00 | 283.15 | 98824 | 3.1 | 210 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
6387 | 9/24 | 02:00:00 | 283.15 | 98824 | 3.1 | 210 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
6388 | 9/24 | 03:00:00 | 283.15 | 98824 | 2.1 | 200 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
6389 | 9/24 | 04:00:00 | 284.15 | 98833 | 2.1 | 210 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6390 | 9/24 | 05:00:00 | 284.15 | 98833 | 5.1 | 220 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6391 | 9/24 | 06:00:00 | 283.15 | 98824 | 3.6 | 220 | 7.3431 | 0 | 0 | 269.196 | 0 | 1 | 10
6392 | 9/24 | 07:00:00 | 284.15 | 98833 | 2.1 | 220 | 7.3425 | 79.2 | 0 | 270.411 | 0 | 1 | 11
6393 | 9/24 | 08:00:00 | 284.15 | 98833 | 5.1 | 220 | 7.3425 | 442.8 | 507.6 | 270.411 | 0 | 1 | 11
6394 | 9/24 | 09:00:00 | 286.15 | 98850 | 4.1 | 200 | 7.8584 | 910.8 | 1044 | 272.541 | 0 | 1 | 13
6395 | 9/24 | 10:00:00 | 286.15 | 98850 | 5.7 | 220 | 7.8584 | 741.6 | 230.4 | 273.023 | 0 | 1 | 13
6396 | 9/24 | 11:00:00 | 286.15 | 98850 | 4.1 | 200 | 7.8584 | 1645.2 | 619.2 | 272.541 | 0 | 1 | 13
6397 | 9/24 | 12:00:00 | 287.15 | 98858 | 4.6 | 200 | 8.4073 | 1000.8 | 115.2 | 274.203 | 0 | 1 | 14
6398 | 9/24 | 13:00:00 | 287.15 | 98858 | 3.1 | 210 | 8.4073 | 1000.8 | 115.2 | 274.203 | 0 | 1 | 14
6399 | 9/24 | 14:00:00 | 287.15 | 98858 | 3.6 | 220 | 7.8578 | 1638 | 1551.6 | 273.493 | 0 | 1 | 14
6400 | 9/24 | 15:00:00 | 288.15 | 98867 | 2.6 | 240 | 8.4065 | 1317.6 | 1699.2 | 274.672 | 0 | 1 | 15
6401 | 9/24 | 16:00:00 | 288.15 | 98867 | 3.6 | 210 | 8.9902 | 889.2 | 1018.8 | 274.898 | 0 | 1 | 15
6402 | 9/24 | 17:00:00 | 288.15 | 98867 | 3.1 | 230 | 8.4065 | 237.6 | 0 | 275.158 | 0 | 1 | 15
6403 | 9/24 | 18:00:00 | 287.15 | 98858 | 3.1 | 220 | 8.4073 | 39.6 | 0 | 274.203 | 0 | 1 | 14
6404 | 9/24 | 19:00:00 | 287.15 | 98858 | 2.1 | 230 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
6405 | 9/24 | 20:00:00 | 286.15 | 98850 | 2.1 | 170 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
6406 | 9/24 | 21:00:00 | 286.15 | 98850 | 2.1 | 190 | 8.9918 | 0 | 0 | 272.99 | 0 | 1 | 13
6407 | 9/24 | 22:00:00 | 286.15 | 98850 | 0.5 | 162 | 8.9918 | 0 | 0 | 272.99 | 0 | 1 | 13
6408 | 9/24 | 23:00:00 | 286.15 | 98850 | 1.5 | 248 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6409 | 9/24 | 24:00:00 | 286.15 | 98850 | 1 | 327 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6410 | 9/25 | 01:00:00 | 286.15 | 98850 | 1 | 160 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6411 | 9/25 | 02:00:00 | 285.15 | 98841 | 2.1 | 190 | 8.4088 | 0 | 0 | 271.813 | 0 | 1 | 12
6412 | 9/25 | 03:00:00 | 285.15 | 98841 | 2.1 | 200 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
6413 | 9/25 | 04:00:00 | 285.15 | 98841 | 2.1 | 200 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
6414 | 9/25 | 05:00:00 | 285.15 | 98841 | 3.1 | 170 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
6415 | 9/25 | 06:00:00 | 285.15 | 98841 | 2.6 | 180 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
6416 | 9/25 | 07:00:00 | 285.15 | 98841 | 2.6 | 170 | 8.4088 | 43.2 | 0 | 272.294 | 0 | 1 | 12
6417 | 9/25 | 08:00:00 | 285.15 | 98841 | 3.6 | 180 | 8.4088 | 237.6 | 0 | 272.294 | 0 | 1 | 12
6418 | 9/25 | 09:00:00 | 285.15 | 98841 | 2.6 | 190 | 8.9926 | 493.2 | 39.6 | 272.517 | 0 | 1 | 12
6419 | 9/25 | 10:00:00 | 287.15 | 98858 | 3.1 | 180 | 9.6108 | 727.2 | 75.6 | 274.652 | 0 | 1 | 14
6420 | 9/25 | 11:00:00 | 287.15 | 98858 | 3.6 | 210 | 9.6108 | 900 | 46.8 | 274.652 | 0 | 1 | 14
6421 | 9/25 | 12:00:00 | 287.15 | 98858 | 4.1 | 220 | 10.2686 | 986.4 | 252 | 274.874 | 0 | 1 | 14
6422 | 9/25 | 13:00:00 | 288.15 | 98867 | 4.1 | 230 | 9.6099 | 1778.4 | 1771.2 | 275.122 | 0 | 1 | 15
6423 | 9/25 | 14:00:00 | 288.15 | 98867 | 5.1 | 220 | 8.4065 | 1612.8 | 1879.2 | 274.672 | 0 | 1 | 15
6424 | 9/25 | 15:00:00 | 290.15 | 98883 | 4.6 | 230 | 8.4052 | 1375.2 | 2052 | 276.308 | 0 | 1 | 17
6425 | 9/25 | 16:00:00 | 290.15 | 98883 | 4.6 | 220 | 8.4052 | 871.2 | 1274.4 | 276.579 | 0 | 1 | 17
6426 | 9/25 | 17:00:00 | 290.15 | 98883 | 4.6 | 230 | 8.4052 | 435.6 | 651.6 | 276.308 | 0 | 1 | 17
6427 | 9/25 | 18:00:00 | 288.15 | 98867 | 5.7 | 230 | 7.3399 | 72 | 0 | 273.95 | 0 | 1 | 15
6428 | 9/25 | 19:00:00 | 288.15 | 98867 | 5.7 | 230 | 7.3399 | 0 | 0 | 273.95 | 0 | 1 | 15
6429 | 9/25 | 20:00:00 | 288.15 | 98867 | 5.1 | 230 | 7.3399 | 0 | 0 | 273.95 | 0 | 1 | 15
6430 | 9/25 | 21:00:00 | 288.15 | 98867 | 6.2 | 200 | 7.3399 | 0 | 0 | 273.95 | 0 | 1 | 15
6431 | 9/25 | 22:00:00 | 287.15 | 98858 | 4.1 | 200 | 7.8578 | 0 | 0 | 273.493 | 0 | 1 | 14
6432 | 9/25 | 23:00:00 | 287.15 | 98858 | 3.6 | 190 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
6433 | 9/25 | 24:00:00 | 287.15 | 98858 | 3.6 | 210 | 8.4073 | 0 | 0 | 273.719 | 0 | 1 | 14
6434 | 9/26 | 01:00:00 | 287.15 | 98858 | 4.1 | 220 | 7.8578 | 0 | 0 | 273.493 | 0 | 1 | 14
6435 | 9/26 | 02:00:00 | 287.15 | 98858 | 5.7 | 250 | 7.8578 | 0 | 0 | 273.493 | 0 | 1 | 14
6436 | 9/26 | 03:00:00 | 284.15 | 98833 | 6.2 | 250 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6437 | 9/26 | 04:00:00 | 284.15 | 98833 | 4.1 | 230 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6438 | 9/26 | 05:00:00 | 284.15 | 98833 | 4.6 | 250 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6439 | 9/26 | 06:00:00 | 284.15 | 98833 | 4.1 | 240 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
6440 | 9/26 | 07:00:00 | 283.15 | 98824 | 2.1 | 270 | 7.3431 | 75.6 | 0 | 269.196 | 0 | 1 | 10
6441 | 9/26 | 08:00:00 | 283.15 | 98824 | 3.6 | 280 | 7.3431 | 442.8 | 594 | 269.196 | 0 | 1 | 10
6442 | 9/26 | 09:00:00 | 285.15 | 98841 | 4.6 | 270 | 7.8591 | 928.8 | 1461.6 | 271.323 | 0 | 1 | 12
6443 | 9/26 | 10:00:00 | 286.15 | 98850 | 5.7 | 260 | 7.3412 | 1299.6 | 1443.6 | 272.314 | 0 | 1 | 13
6444 | 9/26 | 11:00:00 | 287.15 | 98858 | 7.2 | 260 | 6.3966 | 1616.4 | 1854 | 272.808 | 0 | 1 | 14
6445 | 9/26 | 12:00:00 | 288.15 | 98867 | 6.7 | 270 | 5.5621 | 1890 | 2480.4 | 273.025 | 0 | 1 | 15
6446 | 9/26 | 13:00:00 | 288.15 | 98867 | 4.6 | 250 | 5.5621 | 1886.4 | 2548.8 | 273.025 | 0 | 1 | 15
6447 | 9/26 | 14:00:00 | 289.15 | 98875 | 5.7 | 260 | 5.9656 | 1702.8 | 2361.6 | 274.206 | 0 | 1 | 16
6448 | 9/26 | 15:00:00 | 288.15 | 98867 | 4.6 | 260 | 5.1829 | 1368 | 2059.2 | 272.79 | 0 | 1 | 15
6449 | 9/26 | 16:00:00 | 288.15 | 98867 | 3.6 | 260 | 5.5621 | 907.2 | 1476 | 273.025 | 0 | 1 | 15
6450 | 9/26 | 17:00:00 | 287.15 | 98858 | 2.1 | 230 | 5.9666 | 417.6 | 561.6 | 272.31 | 0 | 1 | 14
6451 | 9/26 | 18:00:00 | 286.15 | 98850 | 1.5 | 42 | 6.3971 | 64.8 | 0 | 271.592 | 0 | 1 | 13
6452 | 9/26 | 19:00:00 | 285.15 | 98841 | 0.5 | 355 | 6.3977 | 0 | 0 | 271.033 | 0 | 1 | 12
6453 | 9/26 | 20:00:00 | 285.15 | 98841 | 1 | 150 | 5.5636 | 0 | 0 | 270.316 | 0 | 1 | 12
6454 | 9/26 | 21:00:00 | 285.15 | 98841 | 1 | 193 | 5.5636 | 0 | 0 | 270.316 | 0 | 1 | 12
6455 | 9/26 | 22:00:00 | 284.15 | 98833 | 2.1 | 140 | 5.9681 | 0 | 0 | 269.854 | 0 | 1 | 11
6456 | 9/26 | 23:00:00 | 283.15 | 98824 | 2.6 | 200 | 5.9687 | 0 | 0 | 269.025 | 0 | 1 | 10
6457 | 9/26 | 24:00:00 | 283.15 | 98824 | 2.6 | 180 | 5.9687 | 0 | 0 | 269.025 | 0 | 1 | 10
6458 | 9/27 | 01:00:00 | 283.15 | 98824 | 2.1 | 210 | 5.9687 | 0 | 0 | 269.025 | 0 | 1 | 10
6459 | 9/27 | 02:00:00 | 282.15 | 98815 | 2.6 | 200 | 5.9692 | 0 | 0 | 268.191 | 0 | 1 | 9
6460 | 9/27 | 03:00:00 | 283.15 | 98824 | 2.6 | 220 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
6461 | 9/27 | 04:00:00 | 284.15 | 98833 | 3.6 | 210 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
6462 | 9/27 | 05:00:00 | 283.15 | 98824 | 2.1 | 220 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
6463 | 9/27 | 06:00:00 | 284.15 | 98833 | 3.1 | 210 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
6464 | 9/27 | 07:00:00 | 284.15 | 98833 | 2.6 | 230 | 8.4095 | 68.4 | 0 | 270.595 | 0 | 1 | 11
6465 | 9/27 | 08:00:00 | 286.15 | 98850 | 3.1 | 240 | 8.408 | 428.4 | 691.2 | 272.499 | 0 | 1 | 13
6466 | 9/27 | 09:00:00 | 287.15 | 98858 | 2.6 | 210 | 8.991 | 910.8 | 1533.6 | 273.676 | 0 | 1 | 14
6467 | 9/27 | 10:00:00 | 288.15 | 98867 | 3.1 | 220 | 8.9902 | 1353.6 | 2034 | 274.629 | 0 | 1 | 15
6468 | 9/27 | 11:00:00 | 290.15 | 98883 | 3.1 | 230 | 8.4052 | 1684.8 | 2358 | 276.308 | 0 | 1 | 17
6469 | 9/27 | 12:00:00 | 292.15 | 98900 | 3.6 | 220 | 8.4037 | 1850.4 | 2494.8 | 278.213 | 0 | 1 | 19
6470 | 9/27 | 13:00:00 | 293.15 | 98908 | 3.1 | 240 | 7.8537 | 1854 | 2516.4 | 278.935 | 0 | 1 | 20
6471 | 9/27 | 14:00:00 | 294.15 | 98916 | 2.6 | 230 | 7.8531 | 1681.2 | 2408.4 | 279.742 | 0 | 1 | 21
6472 | 9/27 | 15:00:00 | 293.15 | 98908 | 3.1 | 240 | 8.403 | 1321.2 | 1969.2 | 279.165 | 0 | 1 | 20
6473 | 9/27 | 16:00:00 | 294.15 | 98916 | 2.6 | 210 | 8.4023 | 882 | 1555.2 | 280.117 | 0 | 1 | 21
6474 | 9/27 | 17:00:00 | 293.15 | 98908 | 3.1 | 230 | 8.403 | 392.4 | 619.2 | 279.165 | 0 | 1 | 20
6475 | 9/27 | 18:00:00 | 291.15 | 98892 | 2.6 | 220 | 8.4044 | 54 | 0 | 277.532 | 0 | 1 | 18
6476 | 9/27 | 19:00:00 | 290.15 | 98883 | 1 | 38 | 8.4052 | 0 | 0 | 276.579 | 0 | 1 | 17
6477 | 9/27 | 20:00:00 | 289.15 | 98875 | 1.5 | 160 | 8.4059 | 0 | 0 | 275.754 | 0 | 1 | 16
6478 | 9/27 | 21:00:00 | 288.15 | 98867 | 2.6 | 180 | 8.4065 | 0 | 0 | 274.924 | 0 | 1 | 15
6479 | 9/27 | 22:00:00 | 287.15 | 98858 | 2.1 | 200 | 8.4073 | 0 | 0 | 274.088 | 0 | 1 | 14
6480 | 9/27 | 23:00:00 | 288.15 | 98867 | 1 | 250 | 8.4065 | 0 | 0 | 274.924 | 0 | 1 | 15
6481 | 9/27 | 24:00:00 | 287.15 | 98858 | 1 | 250 | 8.4073 | 0 | 0 | 274.088 | 0 | 1 | 14
6482 | 9/28 | 01:00:00 | 286.15 | 98850 | 2.1 | 190 | 8.9918 | 0 | 0 | 273.583 | 0 | 1 | 13
6483 | 9/28 | 02:00:00 | 286.15 | 98850 | 2.1 | 190 | 8.9918 | 0 | 0 | 273.583 | 0 | 1 | 13
6484 | 9/28 | 03:00:00 | 286.15 | 98850 | 2.6 | 170 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6485 | 9/28 | 04:00:00 | 285.15 | 98841 | 3.1 | 170 | 8.9926 | 0 | 0 | 271.336 | 0 | 1 | 12
6486 | 9/28 | 05:00:00 | 285.15 | 98841 | 3.6 | 160 | 8.9926 | 0 | 0 | 271.336 | 0 | 1 | 12
6487 | 9/28 | 06:00:00 | 284.15 | 98833 | 2.1 | 150 | 8.4095 | 0 | 0 | 270.162 | 0 | 1 | 11
6488 | 9/28 | 07:00:00 | 285.15 | 98841 | 3.6 | 140 | 8.9926 | 64.8 | 0 | 271.336 | 0 | 1 | 12
6489 | 9/28 | 08:00:00 | 285.15 | 98841 | 1.5 | 53 | 8.9926 | 417.6 | 694.8 | 271.336 | 0 | 1 | 12
6490 | 9/28 | 09:00:00 | 287.15 | 98858 | 3.6 | 150 | 10.2686 | 900 | 1609.2 | 273.683 | 0 | 1 | 14
6491 | 9/28 | 10:00:00 | 290.15 | 98883 | 2.6 | 160 | 10.9637 | 1346.4 | 2077.2 | 276.764 | 0 | 1 | 17
6492 | 9/28 | 11:00:00 | 292.15 | 98900 | 2.6 | 140 | 10.9618 | 1674 | 2444.4 | 278.672 | 0 | 1 | 19
6493 | 9/28 | 12:00:00 | 294.15 | 98916 | 1.5 | 325 | 11.6997 | 1814.4 | 2484 | 281.253 | 0 | 1 | 21
6494 | 9/28 | 13:00:00 | 297.15 | 98940 | 5.1 | 190 | 10.9573 | 1810.8 | 2469.6 | 283.894 | 0 | 1 | 24
6495 | 9/28 | 14:00:00 | 297.15 | 98940 | 3.6 | 190 | 10.9573 | 1630.8 | 2347.2 | 283.894 | 0 | 1 | 24
6496 | 9/28 | 15:00:00 | 297.15 | 98940 | 3.6 | 170 | 10.6035 | 1296 | 1947.6 | 283.781 | 0 | 1 | 24
6497 | 9/28 | 16:00:00 | 297.15 | 98940 | 4.6 | 170 | 10.26 | 849.6 | 1306.8 | 283.666 | 0 | 1 | 24
6498 | 9/28 | 17:00:00 | 295.15 | 98924 | 5.1 | 170 | 9.6043 | 374.4 | 572.4 | 281.67 | 0 | 1 | 22
6499 | 9/28 | 18:00:00 | 294.15 | 98916 | 2.6 | 160 | 9.6051 | 50.4 | 0 | 280.715 | 0 | 1 | 21
6500 | 9/28 | 19:00:00 | 293.15 | 98908 | 3.6 | 170 | 8.9864 | 0 | 0 | 279.533 | 0 | 1 | 20
6501 | 9/28 | 20:00:00 | 292.15 | 98900 | 4.1 | 160 | 9.6067 | 0 | 0 | 278.941 | 0 | 1 | 19
6502 | 9/28 | 21:00:00 | 291.15 | 98892 | 3.1 | 150 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18
6503 | 9/28 | 22:00:00 | 291.15 | 98892 | 1 | 140 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18
6504 | 9/28 | 23:00:00 | 290.15 | 98883 | 1 | 4 | 9.6084 | 0 | 0 | 277.285 | 0 | 1 | 17
6505 | 9/28 | 24:00:00 | 288.15 | 98867 | 3.6 | 130 | 8.9902 | 0 | 0 | 275.269 | 0 | 1 | 15
6506 | 9/29 | 01:00:00 | 288.15 | 98867 | 3.6 | 150 | 9.6099 | 0 | 0 | 275.608 | 0 | 1 | 15
6507 | 9/29 | 02:00:00 | 288.15 | 98867 | 3.1 | 170 | 9.6099 | 0 | 0 | 275.608 | 0 | 1 | 15 | 2.8111
6508 | 9/29 | 03:00:00 | 287.15 | 98858 | 3.6 | 160 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14
6509 | 9/29 | 04:00:00 | 287.15 | 98858 | 0 | 130 | 9.6108 | 0 | 0 | 274.763 | 0 | 1 | 14
6510 | 9/29 | 05:00:00 | 285.15 | 98841 | 3.6 | 140 | 8.9926 | 0 | 0 | 272.627 | 0 | 1 | 12
6511 | 9/29 | 06:00:00 | 285.15 | 98841 | 2.6 | 140 | 8.9926 | 0 | 0 | 271.77 | 0 | 1 | 12
6512 | 9/29 | 07:00:00 | 285.15 | 98841 | 4.1 | 130 | 8.9926 | 61.2 | 0 | 271.336 | 0 | 1 | 12
6513 | 9/29 | 08:00:00 | 286.15 | 98850 | 2.1 | 335 | 9.6116 | 403.2 | 669.6 | 272.509 | 0 | 1 | 13
6514 | 9/29 | 09:00:00 | 289.15 | 98875 | 0.5 | 95 | 10.2668 | 882 | 1591.2 | 275.589 | 0 | 1 | 16
6515 | 9/29 | 10:00:00 | 291.15 | 98892 | 2.6 | 140 | 10.9627 | 1324.8 | 2055.6 | 277.718 | 0 | 1 | 18
6516 | 9/29 | 11:00:00 | 293.15 | 98908 | 3.6 | 140 | 10.9609 | 1652.4 | 2448 | 279.626 | 0 | 1 | 20
6517 | 9/29 | 12:00:00 | 295.15 | 98924 | 2.1 | 150 | 11.6988 | 1818 | 2570.4 | 281.758 | 0 | 1 | 22
6518 | 9/29 | 13:00:00 | 297.15 | 98940 | 2.6 | 160 | 11.6968 | 1807.2 | 2566.8 | 283.667 | 0 | 1 | 24
6519 | 9/29 | 14:00:00 | 298.15 | 98948 | 4.1 | 220 | 9.602 | 1630.8 | 2397.6 | 284.245 | 0 | 1 | 25
6520 | 9/29 | 15:00:00 | 298.15 | 98948 | 4.1 | 200 | 9.602 | 1288.8 | 2016 | 284.245 | 0 | 1 | 25
6521 | 9/29 | 16:00:00 | 298.15 | 98948 | 3.6 | 210 | 9.602 | 838.8 | 1332 | 284.245 | 0 | 1 | 25
6522 | 9/29 | 17:00:00 | 297.15 | 98940 | 3.6 | 180 | 10.26 | 356.4 | 558 | 283.666 | 0 | 1 | 24
6523 | 9/29 | 18:00:00 | 295.15 | 98924 | 2.6 | 170 | 10.2617 | 43.2 | 0 | 281.897 | 0 | 1 | 22
6524 | 9/29 | 19:00:00 | 294.15 | 98916 | 2.6 | 160 | 10.2625 | 0 | 0 | 281.078 | 0 | 1 | 21
6525 | 9/29 | 20:00:00 | 294.15 | 98916 | 2.6 | 190 | 9.6051 | 0 | 0 | 280.715 | 0 | 1 | 21
6526 | 9/29 | 21:00:00 | 292.15 | 98900 | 2.1 | 200 | 9.6067 | 0 | 0 | 278.941 | 0 | 1 | 19
6527 | 9/29 | 22:00:00 | 291.15 | 98892 | 1.5 | 200 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18
6528 | 9/29 | 23:00:00 | 291.15 | 98892 | 1 | 210 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18
6529 | 9/29 | 24:00:00 | 291.15 | 98892 | 1.5 | 180 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18
6530 | 9/30 | 01:00:00 | 291.15 | 98892 | 1 | 170 | 9.6075 | 0 | 0 | 278.115 | 0 | 1 | 18
6531 | 9/30 | 02:00:00 | 288.15 | 98867 | 1 | 170 | 8.9902 | 0 | 0 | 275.269 | 0 | 1 | 15
6532 | 9/30 | 03:00:00 | 287.15 | 98858 | 0 | 263 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
6533 | 9/30 | 04:00:00 | 287.15 | 98858 | 1.5 | 216 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
6534 | 9/30 | 05:00:00 | 287.15 | 98858 | 3.6 | 160 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
6535 | 9/30 | 06:00:00 | 287.15 | 98858 | 3.6 | 160 | 8.991 | 0 | 0 | 274.428 | 0 | 1 | 14
6536 | 9/30 | 07:00:00 | 288.15 | 98867 | 4.1 | 150 | 8.9902 | 39.6 | 0 | 275.269 | 0 | 1 | 15
6537 | 9/30 | 08:00:00 | 287.15 | 98858 | 3.6 | 140 | 8.991 | 223.2 | 0 | 274.428 | 0 | 1 | 14
6538 | 9/30 | 09:00:00 | 289.15 | 98875 | 2.1 | 110 | 9.6091 | 867.6 | 1342.8 | 275.366 | 0 | 1 | 16
6539 | 9/30 | 10:00:00 | 291.15 | 98892 | 4.1 | 140 | 9.6075 | 1130.4 | 1263.6 | 278.115 | 0 | 1 | 18
6540 | 9/30 | 11:00:00 | 293.15 | 98908 | 3.6 | 130 | 10.2634 | 1494 | 1738.8 | 280.122 | 0 | 1 | 20
6541 | 9/30 | 12:00:00 | 295.15 | 98924 | 3.6 | 140 | 10.9591 | 1699.2 | 2098.8 | 282.26 | 0 | 1 | 22
6542 | 9/30 | 13:00:00 | 297.15 | 98940 | 4.6 | 140 | 10.9573 | 1749.6 | 2394 | 284.036 | 0 | 1 | 24
6543 | 9/30 | 14:00:00 | 299.15 | 98956 | 6.7 | 170 | 9.6012 | 1609.2 | 2390.4 | 285.198 | 0 | 1 | 26
6544 | 9/30 | 15:00:00 | 299.15 | 98956 | 4.6 | 170 | 8.982 | 1270.8 | 2026.8 | 284.814 | 0 | 1 | 26
6545 | 9/30 | 16:00:00 | 298.15 | 98948 | 4.1 | 180 | 9.602 | 817.2 | 1314 | 284.245 | 0 | 1 | 25
6546 | 9/30 | 17:00:00 | 297.15 | 98940 | 3.1 | 180 | 8.9835 | 345.6 | 558 | 283.061 | 0 | 1 | 24
6547 | 9/30 | 18:00:00 | 296.15 | 98932 | 2.6 | 160 | 8.9842 | 39.6 | 0 | 282.108 | 0 | 1 | 23
6548 | 9/30 | 19:00:00 | 292.95 | 98906 | 2.2 | 114 | 9.1076 | 0 | 0 | 279.249 | 0 | 1 | 19.8
6549 | 9/30 | 20:00:00 | 292.35 | 98902 | 1.9 | 122 | 9.108 | 0 | 0 | 278.95 | 0 | 1 | 19.2
6550 | 9/30 | 21:00:00 | 292.65 | 98904 | 2 | 137 | 9.1078 | 0 | 0 | 279.236 | 0 | 1 | 19.5
6551 | 9/30 | 22:00:00 | 290.35 | 98885 | 3.1 | 201 | 8.6924 | 0 | 0 | 276.883 | 0 | 1 | 17.2
6552 | 9/30 | 23:00:00 | 288.15 | 98866 | 3.8 | 262 | 8.1277 | 0 | 0 | 274.559 | 0 | 1 | 15
6553 | 9/30 | 24:00:00 | 285.35 | 98843 | 4.1 | 285 | 7.3417 | 0 | 0 | 271.423 | 0 | 1 | 12.2
6554 | 10/1 | 01:00:00 | 282.35 | 98817 | 4.8 | 305 | 6.6246 | 0 | 0 | 268.361 | 0 | 1 | 9.2
6555 | 10/1 | 02:00:00 | 281.65 | 98811 | 4.5 | 310 | 6.1812 | 0 | 0 | 267.469 | 0 | 1 | 8.5
6556 | 10/1 | 03:00:00 | 281.15 | 98806 | 4.6 | 312 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
6557 | 10/1 | 04:00:00 | 280.95 | 98804 | 4.5 | 317 | 5.9699 | 0 | 0 | 266.43 | 0 | 1 | 7.8
6558 | 10/1 | 05:00:00 | 281.15 | 98806 | 4.1 | 325 | 5.8869 | 0 | 0 | 266.835 | 0 | 1 | 8
6559 | 10/1 | 06:00:00 | 281.35 | 98809 | 3.7 | 327 | 5.8867 | 0 | 0 | 267.025 | 0 | 1 | 8.2
6560 | 10/1 | 07:00:00 | 280.15 | 98798 | 3.6 | 320 | 5.9703 | 46.8 | 0 | 265.931 | 0 | 1 | 7
6561 | 10/1 | 08:00:00 | 282.15 | 98815 | 3.6 | 340 | 5.5651 | 374.4 | 514.8 | 267.339 | 0 | 1 | 9
6562 | 10/1 | 09:00:00 | 282.15 | 98815 | 3.1 | 330 | 5.9692 | 849.6 | 1422 | 267.568 | 0 | 1 | 9
6563 | 10/1 | 10:00:00 | 283.15 | 98824 | 3.1 | 10 | 5.9687 | 1288.8 | 1980 | 268.516 | 0 | 1 | 10
6564 | 10/1 | 11:00:00 | 284.15 | 98833 | 4.1 | 360 | 6.3982 | 1515.6 | 1623.6 | 269.957 | 0 | 1 | 11
6565 | 10/1 | 12:00:00 | 284.15 | 98833 | 2.6 | 360 | 6.8558 | 1670.4 | 1998 | 270.185 | 0 | 1 | 11
6566 | 10/1 | 13:00:00 | 286.15 | 98850 | 4.1 | 310 | 7.3412 | 1760.4 | 2430 | 272.048 | 0 | 1 | 13
6567 | 10/1 | 14:00:00 | 285.15 | 98841 | 4.6 | 300 | 7.3418 | 1576.8 | 2289.6 | 271.097 | 0 | 1 | 12
6568 | 10/1 | 15:00:00 | 286.15 | 98850 | 4.1 | 280 | 7.3412 | 1238.4 | 1825.2 | 272.048 | 0 | 1 | 13
6569 | 10/1 | 16:00:00 | 285.15 | 98841 | 4.6 | 310 | 7.3418 | 792 | 1328.4 | 271.097 | 0 | 1 | 12
6570 | 10/1 | 17:00:00 | 284.15 | 98833 | 5.1 | 290 | 7.3425 | 324 | 421.2 | 270.147 | 0 | 1 | 11
6571 | 10/1 | 18:00:00 | 283.15 | 98824 | 4.6 | 270 | 6.8564 | 32.4 | 0 | 268.971 | 0 | 1 | 10
6572 | 10/1 | 19:00:00 | 282.15 | 98815 | 3.6 | 290 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
6573 | 10/1 | 20:00:00 | 281.15 | 98806 | 4.1 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
6574 | 10/1 | 21:00:00 | 280.15 | 98798 | 3.6 | 280 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
6575 | 10/1 | 22:00:00 | 281.15 | 98806 | 3.6 | 260 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
6576 | 10/1 | 23:00:00 | 280.15 | 98798 | 2.6 | 240 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
6577 | 10/1 | 24:00:00 | 282.15 | 98815 | 3.1 | 300 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
6578 | 10/2 | 01:00:00 | 282.15 | 98815 | 4.6 | 290 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
6579 | 10/2 | 02:00:00 | 281.15 | 98806 | 4.1 | 290 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
6580 | 10/2 | 03:00:00 | 281.15 | 98806 | 3.1 | 300 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
6581 | 10/2 | 04:00:00 | 282.15 | 98815 | 4.1 | 290 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
6582 | 10/2 | 05:00:00 | 282.15 | 98815 | 3.6 | 290 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
6583 | 10/2 | 06:00:00 | 282.15 | 98815 | 5.7 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
6584 | 10/2 | 07:00:00 | 282.15 | 98815 | 3.1 | 270 | 6.3994 | 25.2 | 0 | 268.532 | 0 | 1 | 9
6585 | 10/2 | 08:00:00 | 282.15 | 98815 | 3.6 | 260 | 6.8571 | 187.2 | 0 | 268.758 | 0 | 1 | 9
6586 | 10/2 | 09:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.8571 | 781.2 | 918 | 268.283 | 0 | 1 | 9
6587 | 10/2 | 10:00:00 | 283.15 | 98824 | 5.1 | 260 | 7.3431 | 1191.6 | 1299.6 | 269.46 | 0 | 1 | 10
6588 | 10/2 | 11:00:00 | 284.15 | 98833 | 4.1 | 240 | 7.8598 | 828 | 126 | 271.115 | 0 | 1 | 11
6589 | 10/2 | 12:00:00 | 284.15 | 98833 | 6.7 | 260 | 8.4095 | 910.8 | 133.2 | 271.339 | 0 | 1 | 11
6590 | 10/2 | 13:00:00 | 285.15 | 98841 | 6.7 | 260 | 8.4088 | 1630.8 | 1569.6 | 271.813 | 0 | 1 | 12
6591 | 10/2 | 14:00:00 | 285.15 | 98841 | 7.7 | 270 | 8.4088 | 1458 | 1447.2 | 271.813 | 0 | 1 | 12
6592 | 10/2 | 15:00:00 | 286.15 | 98850 | 8.2 | 270 | 8.9918 | 630 | 86.4 | 273.473 | 0 | 1 | 13
6593 | 10/2 | 16:00:00 | 286.15 | 98850 | 9.3 | 280 | 8.408 | 399.6 | 14.4 | 273.248 | 0 | 1 | 13
6594 | 10/2 | 17:00:00 | 286.15 | 98850 | 8.7 | 270 | 8.408 | 288 | 356.4 | 272.766 | 0 | 1 | 13
6595 | 10/2 | 18:00:00 | 285.15 | 98841 | 6.7 | 270 | 8.4088 | 21.6 | 0 | 271.813 | 0 | 1 | 12
6596 | 10/2 | 19:00:00 | 286.15 | 98850 | 8.2 | 260 | 8.9918 | 0 | 0 | 272.99 | 0 | 1 | 13
6597 | 10/2 | 20:00:00 | 286.15 | 98850 | 8.2 | 260 | 8.9918 | 0 | 0 | 272.99 | 0 | 1 | 13
6598 | 10/2 | 21:00:00 | 286.15 | 98850 | 9.3 | 260 | 8.9918 | 0 | 0 | 272.99 | 0 | 1 | 13
6599 | 10/2 | 22:00:00 | 286.15 | 98850 | 10.8 | 270 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6600 | 10/2 | 23:00:00 | 286.15 | 98850 | 11.3 | 260 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6601 | 10/2 | 24:00:00 | 286.15 | 98850 | 8.7 | 250 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6602 | 10/3 | 01:00:00 | 286.15 | 98850 | 8.2 | 240 | 8.408 | 0 | 0 | 272.766 | 0 | 1 | 13
6603 | 10/3 | 02:00:00 | 286.15 | 98850 | 7.2 | 240 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6604 | 10/3 | 03:00:00 | 286.15 | 98850 | 7.7 | 240 | 8.408 | 0 | 0 | 273.248 | 0 | 1 | 13
6605 | 10/3 | 04:00:00 | 286.15 | 98850 | 9.8 | 250 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
6606 | 10/3 | 05:00:00 | 285.15 | 98841 | 10.8 | 250 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
6607 | 10/3 | 06:00:00 | 285.15 | 98841 | 12.3 | 250 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
6608 | 10/3 | 07:00:00 | 285.15 | 98841 | 10.8 | 250 | 8.4088 | 21.6 | 0 | 272.294 | 0 | 1 | 12
6609 | 10/3 | 08:00:00 | 285.15 | 98841 | 13.9 | 250 | 8.4088 | 324 | 432 | 271.813 | 0 | 1 | 12
6610 | 10/3 | 09:00:00 | 285.15 | 98841 | 17.5 | 250 | 8.4088 | 759.6 | 1213.2 | 271.813 | 0 | 1 | 12
6611 | 10/3 | 10:00:00 | 286.15 | 98850 | 16.5 | 260 | 8.9918 | 1166.4 | 1267.2 | 272.99 | 0 | 1 | 13
6612 | 10/3 | 11:00:00 | 285.15 | 98841 | 18 | 260 | 8.9926 | 813.6 | 118.8 | 272.517 | 0 | 1 | 12
6613 | 10/3 | 12:00:00 | 285.15 | 98841 | 17.5 | 260 | 8.9926 | 1616.4 | 1555.2 | 272.036 | 0 | 1 | 12
6614 | 10/3 | 13:00:00 | 284.15 | 98833 | 17 | 270 | 8.4095 | 1609.2 | 1915.2 | 270.859 | 0 | 1 | 11
6615 | 10/3 | 14:00:00 | 285.15 | 98841 | 16.5 | 270 | 8.4088 | 1522.8 | 2250 | 271.547 | 0 | 1 | 12
6616 | 10/3 | 15:00:00 | 286.15 | 98850 | 15.4 | 270 | 9.6116 | 1180.8 | 1875.6 | 272.945 | 0 | 1 | 13
6617 | 10/3 | 16:00:00 | 285.15 | 98841 | 12.9 | 270 | 8.9926 | 741.6 | 1198.8 | 271.77 | 0 | 1 | 12
6618 | 10/3 | 17:00:00 | 285.15 | 98841 | 12.9 | 270 | 5.5636 | 273.6 | 273.6 | 270.447 | 0 | 1 | 12
6619 | 10/3 | 18:00:00 | 283.15 | 98824 | 10.3 | 270 | 5.9687 | 18 | 0 | 268.516 | 0 | 1 | 10
6620 | 10/3 | 19:00:00 | 283.15 | 98824 | 9.8 | 280 | 5.5646 | 0 | 0 | 268.287 | 0 | 1 | 10
6621 | 10/3 | 20:00:00 | 282.15 | 98815 | 8.7 | 280 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
6622 | 10/3 | 21:00:00 | 283.15 | 98824 | 9.8 | 280 | 5.5646 | 0 | 0 | 268.287 | 0 | 1 | 10
6623 | 10/3 | 22:00:00 | 282.15 | 98815 | 9.3 | 280 | 5.1856 | 0 | 0 | 267.11 | 0 | 1 | 9
6624 | 10/3 | 23:00:00 | 282.15 | 98815 | 10.3 | 280 | 5.1856 | 0 | 0 | 267.11 | 0 | 1 | 9
6625 | 10/3 | 24:00:00 | 281.15 | 98806 | 6.2 | 290 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
6626 | 10/4 | 01:00:00 | 282.15 | 98815 | 7.2 | 270 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
6627 | 10/4 | 02:00:00 | 281.15 | 98806 | 9.3 | 290 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
6628 | 10/4 | 03:00:00 | 280.15 | 98798 | 7.2 | 280 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
6629 | 10/4 | 04:00:00 | 280.15 | 98798 | 3.1 | 10 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
6630 | 10/4 | 05:00:00 | 280.15 | 98798 | 3.6 | 290 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
6631 | 10/4 | 06:00:00 | 280.15 | 98798 | 5.7 | 270 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
6632 | 10/4 | 07:00:00 | 280.15 | 98798 | 5.1 | 260 | 5.5661 | 36 | 0 | 265.444 | 0 | 1 | 7
6633 | 10/4 | 08:00:00 | 281.15 | 98806 | 4.6 | 250 | 5.5656 | 334.8 | 388.8 | 266.392 | 0 | 1 | 8
6634 | 10/4 | 09:00:00 | 282.15 | 98815 | 7.2 | 280 | 5.5651 | 662.4 | 486 | 267.846 | 0 | 1 | 9
6635 | 10/4 | 10:00:00 | 283.15 | 98824 | 7.2 | 280 | 5.5646 | 1101.6 | 1267.2 | 268.675 | 0 | 1 | 10
6636 | 10/4 | 11:00:00 | 284.15 | 98833 | 7.2 | 280 | 5.5641 | 1461.6 | 1850.4 | 269.498 | 0 | 1 | 11
6637 | 10/4 | 12:00:00 | 284.15 | 98833 | 5.7 | 270 | 5.1847 | 1616.4 | 2008.8 | 269.266 | 0 | 1 | 11
6638 | 10/4 | 13:00:00 | 283.15 | 98824 | 6.2 | 310 | 5.9687 | 1695.6 | 2401.2 | 268.516 | 0 | 1 | 10
6639 | 10/4 | 14:00:00 | 285.15 | 98841 | 5.7 | 280 | 5.5636 | 1512 | 2257.2 | 270.182 | 0 | 1 | 12
6640 | 10/4 | 15:00:00 | 285.15 | 98841 | 6.7 | 280 | 5.1842 | 1177.2 | 1818 | 269.95 | 0 | 1 | 12
6641 | 10/4 | 16:00:00 | 285.15 | 98841 | 5.7 | 270 | 5.1842 | 730.8 | 1285.2 | 269.95 | 0 | 1 | 12
6642 | 10/4 | 17:00:00 | 283.15 | 98824 | 4.6 | 280 | 5.5646 | 273.6 | 331.2 | 268.287 | 0 | 1 | 10
6643 | 10/4 | 18:00:00 | 283.15 | 98824 | 4.1 | 260 | 5.5646 | 10.8 | 0 | 268.287 | 0 | 1 | 10
6644 | 10/4 | 19:00:00 | 282.15 | 98815 | 3.1 | 280 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
6645 | 10/4 | 20:00:00 | 280.15 | 98798 | 0.5 | 55 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
6646 | 10/4 | 21:00:00 | 280.15 | 98798 | 2.6 | 310 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
6647 | 10/4 | 22:00:00 | 280.15 | 98798 | 2.6 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
6648 | 10/4 | 23:00:00 | 279.15 | 98789 | 2.1 | 270 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
6649 | 10/4 | 24:00:00 | 279.15 | 98789 | 2.1 | 250 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
6650 | 10/5 | 01:00:00 | 278.15 | 98780 | 2.6 | 220 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6651 | 10/5 | 02:00:00 | 278.15 | 98780 | 2.1 | 240 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
6652 | 10/5 | 03:00:00 | 278.15 | 98780 | 1.5 | 256 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
6653 | 10/5 | 04:00:00 | 278.15 | 98780 | 2.1 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6654 | 10/5 | 05:00:00 | 278.15 | 98780 | 1.5 | 220 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
6655 | 10/5 | 06:00:00 | 279.15 | 98789 | 2.6 | 230 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
6656 | 10/5 | 07:00:00 | 278.15 | 98780 | 2.6 | 260 | 5.1875 | 14.4 | 0 | 264.154 | 0 | 1 | 5
6657 | 10/5 | 08:00:00 | 279.15 | 98789 | 2.1 | 240 | 5.5666 | 320.4 | 417.6 | 264.497 | 0 | 1 | 6
6658 | 10/5 | 09:00:00 | 280.15 | 98798 | 1 | 239 | 5.9703 | 777.6 | 1346.4 | 265.671 | 0 | 1 | 7
6659 | 10/5 | 10:00:00 | 283.15 | 98824 | 2.1 | 130 | 5.9687 | 1209.6 | 1843.2 | 268.516 | 0 | 1 | 10
6660 | 10/5 | 11:00:00 | 283.15 | 98824 | 2.6 | 150 | 5.9687 | 1526.4 | 2268 | 268.516 | 0 | 1 | 10
6661 | 10/5 | 12:00:00 | 284.15 | 98833 | 2.1 | 150 | 5.9681 | 1688.4 | 2440.8 | 269.465 | 0 | 1 | 11
6662 | 10/5 | 13:00:00 | 285.15 | 98841 | 2.1 | 110 | 5.9676 | 1674 | 2430 | 270.413 | 0 | 1 | 12
6663 | 10/5 | 14:00:00 | 285.15 | 98841 | 2.6 | 130 | 5.5636 | 1490.4 | 2239.2 | 270.182 | 0 | 1 | 12
6664 | 10/5 | 15:00:00 | 286.15 | 98850 | 1 | 50 | 5.5631 | 1148.4 | 1792.8 | 271.13 | 0 | 1 | 13
6665 | 10/5 | 16:00:00 | 286.15 | 98850 | 2.1 | 150 | 5.5631 | 705.6 | 1249.2 | 271.13 | 0 | 1 | 13
6666 | 10/5 | 17:00:00 | 285.15 | 98841 | 2.1 | 140 | 5.5636 | 255.6 | 306 | 270.182 | 0 | 1 | 12
6667 | 10/5 | 18:00:00 | 283.15 | 98824 | 1.5 | 140 | 5.1851 | 3.6 | 0 | 268.319 | 0 | 1 | 10
6668 | 10/5 | 19:00:00 | 282.15 | 98815 | 2.1 | 160 | 5.5651 | 0 | 0 | 267.601 | 0 | 1 | 9
6669 | 10/5 | 20:00:00 | 283.15 | 98824 | 2.1 | 150 | 5.5646 | 0 | 0 | 268.55 | 0 | 1 | 10
6670 | 10/5 | 21:00:00 | 282.15 | 98815 | 2.1 | 140 | 5.5651 | 0 | 0 | 267.601 | 0 | 1 | 9
6671 | 10/5 | 22:00:00 | 281.15 | 98806 | 2.1 | 140 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
6672 | 10/5 | 23:00:00 | 281.15 | 98806 | 2.6 | 150 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
6673 | 10/5 | 24:00:00 | 280.15 | 98798 | 2.6 | 160 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
6674 | 10/6 | 01:00:00 | 280.15 | 98798 | 3.1 | 160 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
6675 | 10/6 | 02:00:00 | 280.15 | 98798 | 2.1 | 170 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
6676 | 10/6 | 03:00:00 | 279.15 | 98789 | 3.6 | 150 | 5.5666 | 0 | 0 | 264.497 | 0 | 1 | 6
6677 | 10/6 | 04:00:00 | 280.15 | 98798 | 4.1 | 160 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
6678 | 10/6 | 05:00:00 | 282.15 | 98815 | 3.1 | 140 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
6679 | 10/6 | 06:00:00 | 281.15 | 98806 | 3.1 | 130 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
6680 | 10/6 | 07:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 14.4 | 0 | 267.805 | 0 | 1 | 8
6681 | 10/6 | 08:00:00 | 283.15 | 98824 | 3.1 | 140 | 7.8605 | 158.4 | 0 | 270.161 | 0 | 1 | 10
6682 | 10/6 | 09:00:00 | 284.15 | 98833 | 3.6 | 130 | 8.4095 | 396 | 21.6 | 271.339 | 0 | 1 | 11
6683 | 10/6 | 10:00:00 | 285.15 | 98841 | 2.6 | 140 | 8.9926 | 615.6 | 64.8 | 272.517 | 0 | 1 | 12
6684 | 10/6 | 11:00:00 | 287.15 | 98858 | 4.1 | 200 | 10.2686 | 777.6 | 43.2 | 274.874 | 0 | 1 | 14
6685 | 10/6 | 12:00:00 | 289.15 | 98875 | 4.6 | 220 | 10.9646 | 856.8 | 46.8 | 277.011 | 0 | 1 | 16
6686 | 10/6 | 13:00:00 | 290.15 | 98883 | 5.7 | 220 | 10.9637 | 849.6 | 46.8 | 277.969 | 0 | 1 | 17
6687 | 10/6 | 14:00:00 | 289.15 | 98875 | 3.6 | 220 | 11.7047 | 752.4 | 104.4 | 277.232 | 0 | 1 | 16
6688 | 10/6 | 15:00:00 | 288.15 | 98867 | 5.7 | 230 | 10.2677 | 1047.6 | 1184.4 | 275.344 | 0 | 1 | 15
6689 | 10/6 | 16:00:00 | 289.15 | 98875 | 2.6 | 270 | 10.9646 | 633.6 | 907.2 | 276.522 | 0 | 1 | 16
6690 | 10/6 | 17:00:00 | 288.15 | 98867 | 5.1 | 290 | 10.2677 | 223.2 | 259.2 | 275.344 | 0 | 1 | 15
6691 | 10/6 | 18:00:00 | 287.15 | 98858 | 4.1 | 280 | 10.2686 | 0 | 0 | 274.874 | 0 | 1 | 14
6692 | 10/6 | 19:00:00 | 286.15 | 98850 | 4.6 | 310 | 9.6116 | 0 | 0 | 273.695 | 0 | 1 | 13
6693 | 10/6 | 20:00:00 | 285.15 | 98841 | 3.6 | 360 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
6694 | 10/6 | 21:00:00 | 284.15 | 98833 | 2.6 | 300 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6695 | 10/6 | 22:00:00 | 283.15 | 98824 | 3.1 | 310 | 7.8605 | 0 | 0 | 269.684 | 0 | 1 | 10
6696 | 10/6 | 23:00:00 | 283.15 | 98824 | 1.5 | 318 | 5.9687 | 0 | 0 | 268.779 | 0 | 1 | 10
6697 | 10/6 | 24:00:00 | 282.15 | 98815 | 1.5 | 310 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
6698 | 10/7 | 01:00:00 | 281.15 | 98806 | 2.1 | 310 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
6699 | 10/7 | 02:00:00 | 280.15 | 98798 | 3.6 | 330 | 4.496 | 0 | 0 | 264.755 | 0 | 1 | 7
6700 | 10/7 | 03:00:00 | 278.15 | 98780 | 3.6 | 310 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
6701 | 10/7 | 04:00:00 | 277.15 | 98771 | 3.6 | 290 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
6702 | 10/7 | 05:00:00 | 277.15 | 98771 | 4.1 | 280 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
6703 | 10/7 | 06:00:00 | 276.15 | 98762 | 4.1 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
6704 | 10/7 | 07:00:00 | 276.15 | 98762 | 3.6 | 270 | 4.1841 | 10.8 | 0 | 261.463 | 0 | 1 | 3
6705 | 10/7 | 08:00:00 | 277.15 | 98771 | 4.1 | 300 | 4.1838 | 219.6 | 50.4 | 262.3 | 0 | 1 | 4
6706 | 10/7 | 09:00:00 | 278.15 | 98780 | 3.6 | 260 | 4.8311 | 453.6 | 93.6 | 263.818 | 0 | 1 | 5
6707 | 10/7 | 10:00:00 | 280.15 | 98798 | 3.1 | 250 | 4.8303 | 975.6 | 968.4 | 265.488 | 0 | 1 | 7
6708 | 10/7 | 11:00:00 | 282.15 | 98815 | 2.1 | 300 | 5.1856 | 1335.6 | 1490.4 | 267.495 | 0 | 1 | 9
6709 | 10/7 | 12:00:00 | 284.15 | 98833 | 1.5 | 58 | 5.1847 | 1598.4 | 2095.2 | 269.137 | 0 | 1 | 11
6710 | 10/7 | 13:00:00 | 283.15 | 98824 | 5.1 | 310 | 5.1851 | 1540.8 | 1954.8 | 268.319 | 0 | 1 | 10
6711 | 10/7 | 14:00:00 | 284.15 | 98833 | 4.6 | 310 | 5.1847 | 1443.6 | 2214 | 269.003 | 0 | 1 | 11
6712 | 10/7 | 15:00:00 | 284.15 | 98833 | 3.1 | 300 | 5.5641 | 1105.2 | 1756.8 | 269.234 | 0 | 1 | 11
6713 | 10/7 | 16:00:00 | 283.15 | 98824 | 3.6 | 300 | 5.5646 | 662.4 | 1195.2 | 268.287 | 0 | 1 | 10
6714 | 10/7 | 17:00:00 | 282.15 | 98815 | 4.1 | 300 | 5.1856 | 223.2 | 255.6 | 267.11 | 0 | 1 | 9
6715 | 10/7 | 18:00:00 | 282.15 | 98815 | 3.6 | 300 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
6716 | 10/7 | 19:00:00 | 281.15 | 98806 | 3.6 | 300 | 5.5656 | 0 | 0 | 267.013 | 0 | 1 | 8
6717 | 10/7 | 20:00:00 | 280.15 | 98798 | 4.1 | 310 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
6718 | 10/7 | 21:00:00 | 279.15 | 98789 | 3.6 | 300 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
6719 | 10/7 | 22:00:00 | 279.15 | 98789 | 3.6 | 300 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
6720 | 10/7 | 23:00:00 | 278.15 | 98780 | 3.1 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6721 | 10/7 | 24:00:00 | 278.15 | 98780 | 3.6 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6722 | 10/8 | 01:00:00 | 277.15 | 98771 | 4.1 | 270 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
6723 | 10/8 | 02:00:00 | 277.15 | 98771 | 3.6 | 270 | 5.1879 | 0 | 0 | 262.633 | 0 | 1 | 4
6724 | 10/8 | 03:00:00 | 279.15 | 98789 | 2.6 | 270 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
6725 | 10/8 | 04:00:00 | 280.15 | 98798 | 3.1 | 260 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
6726 | 10/8 | 05:00:00 | 279.15 | 98789 | 1.5 | 260 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
6727 | 10/8 | 06:00:00 | 278.15 | 98780 | 1.5 | 260 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
6728 | 10/8 | 07:00:00 | 277.15 | 98771 | 1 | 32 | 5.1879 | 3.6 | 0 | 263.204 | 0 | 1 | 4
6729 | 10/8 | 08:00:00 | 279.15 | 98789 | 1 | 167 | 5.5666 | 118.8 | 0 | 265.332 | 0 | 1 | 6
6730 | 10/8 | 09:00:00 | 281.15 | 98806 | 0 | 206 | 5.9698 | 439.2 | 115.2 | 267.353 | 0 | 1 | 8
6731 | 10/8 | 10:00:00 | 282.15 | 98815 | 3.1 | 310 | 5.5651 | 1152 | 1530 | 267.339 | 0 | 1 | 9
6732 | 10/8 | 11:00:00 | 283.15 | 98824 | 4.1 | 300 | 5.5646 | 1465.2 | 2235.6 | 268.287 | 0 | 1 | 10
6733 | 10/8 | 12:00:00 | 284.15 | 98833 | 4.1 | 300 | 5.5641 | 1530 | 1940.4 | 269.498 | 0 | 1 | 11
6734 | 10/8 | 13:00:00 | 285.15 | 98841 | 4.6 | 330 | 4.8281 | 1519.2 | 1695.6 | 269.98 | 0 | 1 | 12
6735 | 10/8 | 14:00:00 | 285.15 | 98841 | 4.6 | 310 | 6.3977 | 1332 | 1533.6 | 270.907 | 0 | 1 | 12
6736 | 10/8 | 15:00:00 | 285.15 | 98841 | 3.1 | 300 | 6.8552 | 1076.4 | 1782 | 270.871 | 0 | 1 | 12
6737 | 10/8 | 16:00:00 | 284.15 | 98833 | 3.1 | 300 | 6.3982 | 640.8 | 1155.6 | 269.693 | 0 | 1 | 11
6738 | 10/8 | 17:00:00 | 284.15 | 98833 | 2.6 | 310 | 5.9681 | 194.4 | 262.8 | 269.728 | 0 | 1 | 11
6739 | 10/8 | 18:00:00 | 283.15 | 98824 | 2.1 | 360 | 5.5646 | 0 | 0 | 268.287 | 0 | 1 | 10
6740 | 10/8 | 19:00:00 | 282.15 | 98815 | 2.1 | 350 | 5.1856 | 0 | 0 | 267.495 | 0 | 1 | 9
6741 | 10/8 | 20:00:00 | 281.15 | 98806 | 2.6 | 360 | 5.1861 | 0 | 0 | 266.667 | 0 | 1 | 8
6742 | 10/8 | 21:00:00 | 279.15 | 98789 | 2.1 | 70 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
6743 | 10/8 | 22:00:00 | 278.15 | 98780 | 2.1 | 100 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6744 | 10/8 | 23:00:00 | 278.15 | 98780 | 1.5 | 120 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6745 | 10/8 | 24:00:00 | 278.15 | 98780 | 1.5 | 70 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
6746 | 10/9 | 01:00:00 | 278.15 | 98780 | 1.5 | 80 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
6747 | 10/9 | 02:00:00 | 278.15 | 98780 | 1.5 | 110 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6748 | 10/9 | 03:00:00 | 277.15 | 98771 | 1.5 | 60 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
6749 | 10/9 | 04:00:00 | 277.15 | 98771 | 1.5 | 90 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
6750 | 10/9 | 05:00:00 | 276.15 | 98762 | 2.1 | 90 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
6751 | 10/9 | 06:00:00 | 277.15 | 98771 | 2.6 | 80 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
6752 | 10/9 | 07:00:00 | 277.15 | 98771 | 3.1 | 90 | 4.8316 | 7.2 | 0 | 262.149 | 0 | 1 | 4
6753 | 10/9 | 08:00:00 | 277.15 | 98771 | 2.6 | 100 | 5.1879 | 266.4 | 338.4 | 262.376 | 0 | 1 | 4
6754 | 10/9 | 09:00:00 | 278.15 | 98780 | 3.1 | 110 | 5.1875 | 709.2 | 1281.6 | 263.323 | 0 | 1 | 5
6755 | 10/9 | 10:00:00 | 279.15 | 98789 | 2.6 | 140 | 5.5666 | 1130.4 | 1792.8 | 264.497 | 0 | 1 | 6
6756 | 10/9 | 11:00:00 | 281.15 | 98806 | 4.6 | 150 | 5.5656 | 1443.6 | 2217.6 | 266.392 | 0 | 1 | 8
6757 | 10/9 | 12:00:00 | 282.15 | 98815 | 5.1 | 150 | 5.5651 | 1508.4 | 1926 | 267.601 | 0 | 1 | 9
6758 | 10/9 | 13:00:00 | 282.15 | 98815 | 4.6 | 140 | 5.9692 | 1490.4 | 1537.2 | 267.83 | 0 | 1 | 9
6759 | 10/9 | 14:00:00 | 284.15 | 98833 | 4.6 | 150 | 6.3982 | 727.2 | 244.8 | 270.435 | 0 | 1 | 11
6760 | 10/9 | 15:00:00 | 284.15 | 98833 | 6.2 | 170 | 6.3982 | 550.8 | 79.2 | 270.435 | 0 | 1 | 11
6761 | 10/9 | 16:00:00 | 284.15 | 98833 | 5.7 | 130 | 6.3982 | 583.2 | 738 | 269.957 | 0 | 1 | 11
6762 | 10/9 | 17:00:00 | 284.15 | 98833 | 5.1 | 130 | 6.3982 | 100.8 | 0 | 270.435 | 0 | 1 | 11
6763 | 10/9 | 18:00:00 | 283.15 | 98824 | 5.7 | 140 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
6764 | 10/9 | 19:00:00 | 282.15 | 98815 | 6.7 | 140 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
6765 | 10/9 | 20:00:00 | 282.15 | 98815 | 6.2 | 140 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
6766 | 10/9 | 21:00:00 | 282.15 | 98815 | 5.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
6767 | 10/9 | 22:00:00 | 282.15 | 98815 | 5.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
6768 | 10/9 | 23:00:00 | 281.15 | 98806 | 4.1 | 150 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
6769 | 10/9 | 24:00:00 | 282.15 | 98815 | 2.6 | 170 | 7.3438 | 0 | 0 | 269.092 | 0 | 1 | 9
6770 | 10/10 | 01:00:00 | 282.15 | 98815 | 1.5 | 180 | 7.3438 | 0 | 0 | 269.092 | 0 | 1 | 9
6771 | 10/10 | 02:00:00 | 282.15 | 98815 | 0.5 | 216 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
6772 | 10/10 | 03:00:00 | 282.15 | 98815 | 0.5 | 252 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
6773 | 10/10 | 04:00:00 | 282.15 | 98815 | 1.5 | 280 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
6774 | 10/10 | 05:00:00 | 282.15 | 98815 | 3.1 | 280 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
6775 | 10/10 | 06:00:00 | 283.15 | 98824 | 5.1 | 290 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
6776 | 10/10 | 07:00:00 | 282.15 | 98815 | 4.1 | 310 | 7.3438 | 3.6 | 0 | 268.245 | 0 | 1 | 9
6777 | 10/10 | 08:00:00 | 282.15 | 98815 | 3.6 | 290 | 7.3438 | 241.2 | 237.6 | 268.508 | 0 | 1 | 9
6778 | 10/10 | 09:00:00 | 284.15 | 98833 | 4.6 | 270 | 7.3425 | 687.6 | 1234.8 | 270.147 | 0 | 1 | 11
6779 | 10/10 | 10:00:00 | 284.15 | 98833 | 5.7 | 280 | 7.3425 | 1044 | 1512 | 270.411 | 0 | 1 | 11
6780 | 10/10 | 11:00:00 | 285.15 | 98841 | 5.7 | 280 | 7.3418 | 1332 | 1760.4 | 271.363 | 0 | 1 | 12
6781 | 10/10 | 12:00:00 | 286.15 | 98850 | 4.6 | 280 | 7.8584 | 1476 | 1854 | 272.541 | 0 | 1 | 13
6782 | 10/10 | 13:00:00 | 287.15 | 98858 | 5.7 | 280 | 7.8578 | 1548 | 2322 | 273.226 | 0 | 1 | 14
6783 | 10/10 | 14:00:00 | 287.15 | 98858 | 6.2 | 270 | 7.8578 | 1360.8 | 2091.6 | 273.226 | 0 | 1 | 14
6784 | 10/10 | 15:00:00 | 287.15 | 98858 | 6.2 | 270 | 8.4073 | 1022.4 | 1764 | 273.451 | 0 | 1 | 14
6785 | 10/10 | 16:00:00 | 286.15 | 98850 | 5.1 | 280 | 8.408 | 594 | 1029.6 | 272.499 | 0 | 1 | 13
6786 | 10/10 | 17:00:00 | 286.15 | 98850 | 5.1 | 280 | 8.408 | 165.6 | 136.8 | 272.766 | 0 | 1 | 13
6787 | 10/10 | 18:00:00 | 285.15 | 98841 | 5.1 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1 | 12
6788 | 10/10 | 19:00:00 | 285.15 | 98841 | 3.6 | 260 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
6789 | 10/10 | 20:00:00 | 284.15 | 98833 | 3.6 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6790 | 10/10 | 21:00:00 | 284.15 | 98833 | 3.1 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6791 | 10/10 | 22:00:00 | 284.15 | 98833 | 0.5 | 196 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6792 | 10/10 | 23:00:00 | 284.15 | 98833 | 1.5 | 187 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6793 | 10/10 | 24:00:00 | 284.15 | 98833 | 2.6 | 230 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6794 | 10/11 | 01:00:00 | 284.15 | 98833 | 2.6 | 240 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6795 | 10/11 | 02:00:00 | 284.15 | 98833 | 2.1 | 240 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6796 | 10/11 | 03:00:00 | 284.15 | 98833 | 3.1 | 240 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6797 | 10/11 | 04:00:00 | 284.15 | 98833 | 6.2 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
6798 | 10/11 | 05:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6799 | 10/11 | 06:00:00 | 284.15 | 98833 | 6.2 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
6800 | 10/11 | 07:00:00 | 283.15 | 98824 | 8.7 | 260 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
6801 | 10/11 | 08:00:00 | 284.15 | 98833 | 4.6 | 250 | 7.3425 | 241.2 | 291.6 | 270.147 | 0 | 1 | 11
6802 | 10/11 | 09:00:00 | 285.15 | 98841 | 6.7 | 260 | 7.8591 | 630 | 1026 | 271.588 | 0 | 1 | 12
6803 | 10/11 | 10:00:00 | 284.15 | 98833 | 5.1 | 260 | 7.8598 | 1022.4 | 1432.8 | 270.636 | 0 | 1 | 11
6804 | 10/11 | 11:00:00 | 285.15 | 98841 | 7.2 | 270 | 7.8591 | 1310.4 | 1738.8 | 271.588 | 0 | 1 | 12
6805 | 10/11 | 12:00:00 | 287.15 | 98858 | 9.8 | 280 | 7.3406 | 1458 | 1609.2 | 273.266 | 0 | 1 | 14
6806 | 10/11 | 13:00:00 | 287.15 | 98858 | 8.7 | 290 | 9.6108 | 1429.2 | 1796.4 | 274.167 | 0 | 1 | 14
6807 | 10/11 | 14:00:00 | 285.15 | 98841 | 10.8 | 310 | 8.9926 | 1256.4 | 1728 | 272.036 | 0 | 1 | 12
6808 | 10/11 | 15:00:00 | 286.15 | 98850 | 9.8 | 290 | 9.6116 | 939.6 | 1429.2 | 273.212 | 0 | 1 | 13
6809 | 10/11 | 16:00:00 | 285.15 | 98841 | 10.3 | 300 | 8.9926 | 572.4 | 993.6 | 271.77 | 0 | 1 | 12
6810 | 10/11 | 17:00:00 | 285.15 | 98841 | 8.7 | 300 | 8.4088 | 162 | 183.6 | 271.547 | 0 | 1 | 12
6811 | 10/11 | 18:00:00 | 284.15 | 98833 | 9.3 | 300 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
6812 | 10/11 | 19:00:00 | 282.15 | 98815 | 6.7 | 310 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
6813 | 10/11 | 20:00:00 | 282.15 | 98815 | 7.2 | 300 | 5.5651 | 0 | 0 | 267.846 | 0 | 1 | 9
6814 | 10/11 | 21:00:00 | 282.15 | 98815 | 7.2 | 300 | 5.5651 | 0 | 0 | 267.846 | 0 | 1 | 9
6815 | 10/11 | 22:00:00 | 281.15 | 98806 | 6.2 | 300 | 5.5656 | 0 | 0 | 267.013 | 0 | 1 | 8
6816 | 10/11 | 23:00:00 | 282.15 | 98815 | 6.7 | 330 | 5.5651 | 0 | 0 | 267.846 | 0 | 1 | 9
6817 | 10/11 | 24:00:00 | 282.15 | 98815 | 6.7 | 340 | 5.1856 | 0 | 0 | 267.495 | 0 | 1 | 9
6818 | 10/12 | 01:00:00 | 280.15 | 98798 | 5.7 | 290 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
6819 | 10/12 | 02:00:00 | 280.15 | 98798 | 5.7 | 330 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
6820 | 10/12 | 03:00:00 | 281.15 | 98806 | 7.2 | 350 | 4.8299 | 0 | 0 | 266.316 | 0 | 1 | 8
6821 | 10/12 | 04:00:00 | 281.15 | 98806 | 5.7 | 340 | 4.8299 | 0 | 0 | 266.316 | 0 | 1 | 8
6822 | 10/12 | 05:00:00 | 280.15 | 98798 | 4.6 | 310 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
6823 | 10/12 | 06:00:00 | 278.15 | 98780 | 4.1 | 310 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
6824 | 10/12 | 07:00:00 | 279.15 | 98789 | 4.6 | 280 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
6825 | 10/12 | 08:00:00 | 279.15 | 98789 | 4.1 | 300 | 4.8307 | 172.8 | 10.8 | 264.656 | 0 | 1 | 6
6826 | 10/12 | 09:00:00 | 280.15 | 98798 | 3.6 | 270 | 5.1865 | 489.6 | 320.4 | 265.834 | 0 | 1 | 7
6827 | 10/12 | 10:00:00 | 282.15 | 98815 | 3.6 | 310 | 5.1856 | 961.2 | 1195.2 | 267.495 | 0 | 1 | 9
6828 | 10/12 | 11:00:00 | 283.15 | 98824 | 3.6 | 300 | 5.5646 | 1378.8 | 2034 | 268.287 | 0 | 1 | 10
6829 | 10/12 | 12:00:00 | 284.15 | 98833 | 2.1 | 350 | 5.5641 | 1533.6 | 2350.8 | 269.234 | 0 | 1 | 11
6830 | 10/12 | 13:00:00 | 284.15 | 98833 | 3.1 | 330 | 5.5641 | 1512 | 2332.8 | 269.234 | 0 | 1 | 11
6831 | 10/12 | 14:00:00 | 285.15 | 98841 | 3.1 | 320 | 5.5636 | 1324.8 | 2023.2 | 270.182 | 0 | 1 | 12
6832 | 10/12 | 15:00:00 | 285.15 | 98841 | 3.1 | 310 | 5.9676 | 928.8 | 1368 | 270.678 | 0 | 1 | 12
6833 | 10/12 | 16:00:00 | 284.15 | 98833 | 2.6 | 280 | 5.9681 | 525.6 | 853.2 | 269.728 | 0 | 1 | 11
6834 | 10/12 | 17:00:00 | 284.15 | 98833 | 2.1 | 350 | 5.9681 | 140.4 | 64.8 | 269.728 | 0 | 1 | 11
6835 | 10/12 | 18:00:00 | 284.15 | 98833 | 1 | 230 | 5.9681 | 0 | 0 | 269.728 | 0 | 1 | 11
6836 | 10/12 | 19:00:00 | 283.15 | 98824 | 2.1 | 310 | 5.9687 | 0 | 0 | 268.779 | 0 | 1 | 10
6837 | 10/12 | 20:00:00 | 281.15 | 98806 | 3.1 | 300 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
6838 | 10/12 | 21:00:00 | 281.15 | 98806 | 3.1 | 320 | 5.5656 | 0 | 0 | 267.013 | 0 | 1 | 8
6839 | 10/12 | 22:00:00 | 280.15 | 98798 | 2.1 | 290 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
6840 | 10/12 | 23:00:00 | 279.15 | 98789 | 2.6 | 290 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
6841 | 10/12 | 24:00:00 | 279.15 | 98789 | 2.6 | 290 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
6842 | 10/13 | 01:00:00 | 278.15 | 98780 | 2.1 | 290 | 5.5671 | 0 | 0 | 264.381 | 0 | 1 | 5
6843 | 10/13 | 02:00:00 | 278.15 | 98780 | 2.1 | 280 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6844 | 10/13 | 03:00:00 | 277.15 | 98771 | 3.1 | 260 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
6845 | 10/13 | 04:00:00 | 277.15 | 98771 | 3.6 | 270 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
6846 | 10/13 | 05:00:00 | 277.15 | 98771 | 3.1 | 280 | 5.1879 | 0 | 0 | 263.204 | 0 | 1 | 4
6847 | 10/13 | 06:00:00 | 278.15 | 98780 | 3.6 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6848 | 10/13 | 07:00:00 | 278.15 | 98780 | 2.6 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1 | 5
6849 | 10/13 | 08:00:00 | 278.15 | 98780 | 3.1 | 280 | 5.1875 | 93.6 | 0 | 264.154 | 0 | 1 | 5
6850 | 10/13 | 09:00:00 | 281.15 | 98806 | 3.6 | 270 | 5.9698 | 388.8 | 72 | 267.353 | 0 | 1 | 8
6851 | 10/13 | 10:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.3994 | 637.2 | 234 | 268.532 | 0 | 1 | 9
6852 | 10/13 | 11:00:00 | 285.15 | 98841 | 3.1 | 260 | 6.8552 | 1123.2 | 1054.8 | 271.384 | 0 | 1 | 12
6853 | 10/13 | 12:00:00 | 285.15 | 98841 | 3.6 | 290 | 6.8552 | 1501.2 | 2167.2 | 270.871 | 0 | 1 | 12
6854 | 10/13 | 13:00:00 | 286.15 | 98850 | 5.1 | 290 | 7.3412 | 1479.6 | 2278.8 | 272.048 | 0 | 1 | 13
6855 | 10/13 | 14:00:00 | 286.15 | 98850 | 4.1 | 320 | 7.3412 | 1292.4 | 2034 | 272.048 | 0 | 1 | 13
6856 | 10/13 | 15:00:00 | 286.15 | 98850 | 3.1 | 300 | 7.3412 | 957.6 | 1602 | 272.048 | 0 | 1 | 13
6857 | 10/13 | 16:00:00 | 286.15 | 98850 | 4.1 | 270 | 7.8584 | 536.4 | 993.6 | 272.274 | 0 | 1 | 13
6858 | 10/13 | 17:00:00 | 285.15 | 98841 | 3.6 | 280 | 7.3418 | 136.8 | 133.2 | 271.097 | 0 | 1 | 12
6859 | 10/13 | 18:00:00 | 285.15 | 98841 | 3.6 | 270 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
6860 | 10/13 | 19:00:00 | 284.15 | 98833 | 3.1 | 270 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6861 | 10/13 | 20:00:00 | 284.15 | 98833 | 2.6 | 280 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6862 | 10/13 | 21:00:00 | 284.15 | 98833 | 3.1 | 280 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
6863 | 10/13 | 22:00:00 | 284.15 | 98833 | 4.1 | 290 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
6864 | 10/13 | 23:00:00 | 284.15 | 98833 | 4.1 | 280 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
6865 | 10/13 | 24:00:00 | 284.15 | 98833 | 3.1 | 300 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
6866 | 10/14 | 01:00:00 | 284.15 | 98833 | 3.6 | 290 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
6867 | 10/14 | 02:00:00 | 284.15 | 98833 | 3.1 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6868 | 10/14 | 03:00:00 | 284.15 | 98833 | 2.6 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6869 | 10/14 | 04:00:00 | 284.15 | 98833 | 3.1 | 270 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6870 | 10/14 | 05:00:00 | 284.15 | 98833 | 2.6 | 270 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6871 | 10/14 | 06:00:00 | 284.15 | 98833 | 3.1 | 280 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6872 | 10/14 | 07:00:00 | 284.15 | 98833 | 3.1 | 270 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6873 | 10/14 | 08:00:00 | 284.15 | 98833 | 3.1 | 280 | 8.4095 | 190.8 | 219.6 | 270.859 | 0 | 1 | 11
6874 | 10/14 | 09:00:00 | 284.15 | 98833 | 3.1 | 300 | 8.4095 | 583.2 | 889.2 | 270.859 | 0 | 1 | 11
6875 | 10/14 | 10:00:00 | 286.15 | 98850 | 2.1 | 290 | 8.9918 | 964.8 | 1476 | 272.99 | 0 | 1 | 13
6876 | 10/14 | 11:00:00 | 286.15 | 98850 | 1 | 230 | 8.9918 | 1245.6 | 1371.6 | 272.99 | 0 | 1 | 13
6877 | 10/14 | 12:00:00 | 287.15 | 98858 | 1 | 200 | 8.991 | 770.4 | 115.2 | 274.428 | 0 | 1 | 14
6878 | 10/14 | 13:00:00 | 287.15 | 98858 | 1.5 | 135 | 8.4073 | 759.6 | 43.2 | 274.203 | 0 | 1 | 14
6879 | 10/14 | 14:00:00 | 287.15 | 98858 | 2.6 | 240 | 8.4073 | 662.4 | 97.2 | 274.203 | 0 | 1 | 14
6880 | 10/14 | 15:00:00 | 287.15 | 98858 | 2.6 | 230 | 8.991 | 878.4 | 1209.6 | 273.944 | 0 | 1 | 14
6881 | 10/14 | 16:00:00 | 287.15 | 98858 | 2.6 | 260 | 8.4073 | 486 | 914.4 | 273.719 | 0 | 1 | 14
6882 | 10/14 | 17:00:00 | 287.15 | 98858 | 2.1 | 250 | 8.991 | 64.8 | 0 | 274.428 | 0 | 1 | 14
6883 | 10/14 | 18:00:00 | 286.15 | 98850 | 1.5 | 3 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
6884 | 10/14 | 19:00:00 | 286.15 | 98850 | 3.1 | 270 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
6885 | 10/14 | 20:00:00 | 286.15 | 98850 | 2.6 | 270 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
6886 | 10/14 | 21:00:00 | 285.15 | 98841 | 2.1 | 280 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6887 | 10/14 | 22:00:00 | 285.15 | 98841 | 2.6 | 300 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6888 | 10/14 | 23:00:00 | 285.15 | 98841 | 2.6 | 290 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6889 | 10/14 | 24:00:00 | 285.15 | 98841 | 2.1 | 290 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6890 | 10/15 | 01:00:00 | 285.15 | 98841 | 2.6 | 290 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6891 | 10/15 | 02:00:00 | 285.15 | 98841 | 1.5 | 290 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6892 | 10/15 | 03:00:00 | 285.15 | 98841 | 2.6 | 300 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6893 | 10/15 | 04:00:00 | 285.15 | 98841 | 2.1 | 310 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6894 | 10/15 | 05:00:00 | 285.15 | 98841 | 3.6 | 320 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6895 | 10/15 | 06:00:00 | 285.15 | 98841 | 3.1 | 310 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6896 | 10/15 | 07:00:00 | 285.15 | 98841 | 3.1 | 320 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
6897 | 10/15 | 08:00:00 | 285.15 | 98841 | 1.5 | 252 | 8.9926 | 61.2 | 0 | 272.627 | 0 | 1 | 12
6898 | 10/15 | 09:00:00 | 285.15 | 98841 | 0 | 218 | 8.9926 | 313.2 | 0 | 272.517 | 0 | 1 | 12
6899 | 10/15 | 10:00:00 | 286.15 | 98850 | 2.6 | 360 | 9.6116 | 522 | 50.4 | 273.695 | 0 | 1 | 13
6900 | 10/15 | 11:00:00 | 286.15 | 98850 | 2.1 | 10 | 9.6116 | 680.4 | 39.6 | 273.695 | 0 | 1 | 13
6901 | 10/15 | 12:00:00 | 287.15 | 98858 | 2.6 | 10 | 9.6108 | 756 | 43.2 | 274.652 | 0 | 1 | 14
6902 | 10/15 | 13:00:00 | 287.15 | 98858 | 1.5 | 121 | 9.6108 | 745.2 | 43.2 | 274.652 | 0 | 1 | 14
6903 | 10/15 | 14:00:00 | 286.15 | 98850 | 1.5 | 240 | 9.6116 | 648 | 93.6 | 273.695 | 0 | 1 | 13
6904 | 10/15 | 15:00:00 | 287.15 | 98858 | 1.5 | 189 | 9.6108 | 856.8 | 1184.4 | 274.167 | 0 | 1 | 14
6905 | 10/15 | 16:00:00 | 287.15 | 98858 | 1 | 106 | 9.6108 | 259.2 | 0 | 274.652 | 0 | 1 | 14
6906 | 10/15 | 17:00:00 | 287.15 | 98858 | 0.5 | 57 | 9.6108 | 57.6 | 0 | 274.652 | 0 | 1 | 14
6907 | 10/15 | 18:00:00 | 286.15 | 98850 | 0 | 69 | 9.6116 | 0 | 0 | 273.695 | 0 | 1 | 13
6908 | 10/15 | 19:00:00 | 286.15 | 98850 | 2.1 | 280 | 9.6116 | 0 | 0 | 273.695 | 0 | 1 | 13
6909 | 10/15 | 20:00:00 | 286.15 | 98850 | 2.1 | 310 | 9.6116 | 0 | 0 | 273.212 | 0 | 1 | 13
6910 | 10/15 | 21:00:00 | 286.15 | 98850 | 2.6 | 340 | 9.6116 | 0 | 0 | 273.695 | 0 | 1 | 13
6911 | 10/15 | 22:00:00 | 286.15 | 98850 | 4.6 | 350 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
6912 | 10/15 | 23:00:00 | 284.15 | 98833 | 6.2 | 20 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
6913 | 10/15 | 24:00:00 | 284.15 | 98833 | 4.6 | 10 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6914 | 10/16 | 01:00:00 | 284.15 | 98833 | 8.2 | 20 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6915 | 10/16 | 02:00:00 | 284.15 | 98833 | 6.7 | 20 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
6916 | 10/16 | 03:00:00 | 283.15 | 98824 | 7.7 | 30 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
6917 | 10/16 | 04:00:00 | 283.15 | 98824 | 6.2 | 20 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
6918 | 10/16 | 05:00:00 | 282.15 | 98815 | 7.2 | 10 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
6919 | 10/16 | 06:00:00 | 282.15 | 98815 | 6.2 | 10 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
6920 | 10/16 | 07:00:00 | 282.15 | 98815 | 3.1 | 340 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
6921 | 10/16 | 08:00:00 | 282.15 | 98815 | 4.1 | 360 | 6.3994 | 169.2 | 129.6 | 268.057 | 0 | 1 | 9
6922 | 10/16 | 09:00:00 | 282.15 | 98815 | 5.1 | 360 | 5.9692 | 554.4 | 918 | 267.83 | 0 | 1 | 9
6923 | 10/16 | 10:00:00 | 282.15 | 98815 | 6.2 | 20 | 5.9692 | 936 | 1393.2 | 267.83 | 0 | 1 | 9
6924 | 10/16 | 11:00:00 | 283.15 | 98824 | 7.2 | 10 | 5.5646 | 1220.4 | 1659.6 | 268.55 | 0 | 1 | 10
6925 | 10/16 | 12:00:00 | 283.15 | 98824 | 7.2 | 10 | 5.5646 | 1443.6 | 2113.2 | 268.287 | 0 | 1 | 10
6926 | 10/16 | 13:00:00 | 284.15 | 98833 | 6.2 | 10 | 5.1847 | 1342.8 | 1832.4 | 269.266 | 0 | 1 | 11
6927 | 10/16 | 14:00:00 | 284.15 | 98833 | 5.1 | 10 | 5.1847 | 1162.8 | 1688.4 | 269.266 | 0 | 1 | 11
6928 | 10/16 | 15:00:00 | 284.15 | 98833 | 5.7 | 360 | 5.5641 | 846 | 1360.8 | 269.498 | 0 | 1 | 11
6929 | 10/16 | 16:00:00 | 284.15 | 98833 | 4.6 | 10 | 5.1847 | 453.6 | 507.6 | 269.266 | 0 | 1 | 11
6930 | 10/16 | 17:00:00 | 283.15 | 98824 | 4.1 | 360 | 5.1851 | 100.8 | 3.6 | 268.056 | 0 | 1 | 10
6931 | 10/16 | 18:00:00 | 282.15 | 98815 | 3.1 | 330 | 4.8294 | 0 | 0 | 267.139 | 0 | 1 | 9
6932 | 10/16 | 19:00:00 | 280.15 | 98798 | 4.6 | 320 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
6933 | 10/16 | 20:00:00 | 280.15 | 98798 | 5.1 | 320 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
6934 | 10/16 | 21:00:00 | 280.15 | 98798 | 5.1 | 340 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
6935 | 10/16 | 22:00:00 | 280.15 | 98798 | 4.6 | 320 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
6936 | 10/16 | 23:00:00 | 280.15 | 98798 | 5.1 | 360 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
6937 | 10/16 | 24:00:00 | 280.15 | 98798 | 5.1 | 360 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
6938 | 10/17 | 01:00:00 | 280.15 | 98798 | 4.1 | 310 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
6939 | 10/17 | 02:00:00 | 280.15 | 98798 | 3.6 | 340 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
6940 | 10/17 | 03:00:00 | 280.15 | 98798 | 2.1 | 330 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
6941 | 10/17 | 04:00:00 | 279.15 | 98789 | 3.1 | 300 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
6942 | 10/17 | 05:00:00 | 279.15 | 98789 | 3.6 | 310 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
6943 | 10/17 | 06:00:00 | 280.15 | 98798 | 3.6 | 320 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
6944 | 10/17 | 07:00:00 | 280.15 | 98798 | 3.1 | 330 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
6945 | 10/17 | 08:00:00 | 280.15 | 98798 | 3.1 | 350 | 5.9703 | 90 | 0 | 266.402 | 0 | 1 | 7
6946 | 10/17 | 09:00:00 | 281.15 | 98806 | 3.1 | 310 | 5.9698 | 298.8 | 0 | 267.353 | 0 | 1 | 8
6947 | 10/17 | 10:00:00 | 281.15 | 98806 | 3.1 | 340 | 5.9698 | 918 | 1166.4 | 266.881 | 0 | 1 | 8
6948 | 10/17 | 11:00:00 | 282.15 | 98815 | 2.1 | 30 | 5.9692 | 1198.8 | 1710 | 267.83 | 0 | 1 | 9
6949 | 10/17 | 12:00:00 | 282.15 | 98815 | 3.6 | 360 | 5.1856 | 1339.2 | 1598.4 | 267.371 | 0 | 1 | 9
6950 | 10/17 | 13:00:00 | 283.15 | 98824 | 2.6 | 10 | 5.1851 | 1321.2 | 1584 | 268.319 | 0 | 1 | 10
6951 | 10/17 | 14:00:00 | 284.15 | 98833 | 3.1 | 20 | 5.1847 | 1141.2 | 1357.2 | 269.266 | 0 | 1 | 11
6952 | 10/17 | 15:00:00 | 283.15 | 98824 | 3.1 | 10 | 4.829 | 460.8 | 64.8 | 268.561 | 0 | 1 | 10
6953 | 10/17 | 16:00:00 | 283.15 | 98824 | 3.1 | 350 | 5.1851 | 241.2 | 0 | 268.793 | 0 | 1 | 10
6954 | 10/17 | 17:00:00 | 283.15 | 98824 | 1.5 | 10 | 5.1851 | 28.8 | 0 | 268.902 | 0 | 1 | 10
6955 | 10/17 | 18:00:00 | 282.15 | 98815 | 1 | 340 | 5.1856 | 0 | 0 | 267.844 | 0 | 1 | 9
6956 | 10/17 | 19:00:00 | 282.15 | 98815 | 0.5 | 330 | 5.5651 | 0 | 0 | 268.183 | 0 | 1 | 9
6957 | 10/17 | 20:00:00 | 281.15 | 98806 | 0.5 | 6 | 5.5656 | 0 | 0 | 267.233 | 0 | 1 | 8
6958 | 10/17 | 21:00:00 | 281.15 | 98806 | 0 | 355 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
6959 | 10/17 | 22:00:00 | 281.15 | 98806 | 1 | 140 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
6960 | 10/17 | 23:00:00 | 279.15 | 98789 | 1.5 | 180 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
6961 | 10/17 | 24:00:00 | 280.15 | 98798 | 1 | 103 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
6962 | 10/18 | 01:00:00 | 279.15 | 98789 | 1.5 | 250 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
6963 | 10/18 | 02:00:00 | 278.15 | 98780 | 2.1 | 260 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
6964 | 10/18 | 03:00:00 | 277.15 | 98771 | 2.1 | 250 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
6965 | 10/18 | 04:00:00 | 277.15 | 98771 | 2.6 | 260 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
6966 | 10/18 | 05:00:00 | 278.15 | 98780 | 2.6 | 260 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
6967 | 10/18 | 06:00:00 | 278.15 | 98780 | 2.1 | 230 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
6968 | 10/18 | 07:00:00 | 278.15 | 98780 | 2.1 | 210 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
6969 | 10/18 | 08:00:00 | 278.15 | 98780 | 2.1 | 220 | 5.1875 | 82.8 | 0 | 264.047 | 0 | 1 | 5
6970 | 10/18 | 09:00:00 | 279.15 | 98789 | 1.5 | 139 | 5.187 | 291.6 | 0 | 264.996 | 0 | 1 | 6
6971 | 10/18 | 10:00:00 | 280.15 | 98798 | 3.1 | 240 | 5.1865 | 500.4 | 36 | 265.946 | 0 | 1 | 7
6972 | 10/18 | 11:00:00 | 281.15 | 98806 | 3.6 | 220 | 5.1861 | 655.2 | 111.6 | 266.895 | 0 | 1 | 8
6973 | 10/18 | 12:00:00 | 282.15 | 98815 | 4.1 | 240 | 5.5651 | 730.8 | 126 | 268.075 | 0 | 1 | 9
6974 | 10/18 | 13:00:00 | 282.15 | 98815 | 7.7 | 260 | 5.1856 | 720 | 255.6 | 267.844 | 0 | 1 | 9
6975 | 10/18 | 14:00:00 | 282.15 | 98815 | 6.7 | 260 | 5.5651 | 1184.4 | 1609.2 | 267.339 | 0 | 1 | 9
6976 | 10/18 | 15:00:00 | 282.15 | 98815 | 7.7 | 260 | 5.9692 | 853.2 | 1580.4 | 267.568 | 0 | 1 | 9
6977 | 10/18 | 16:00:00 | 282.15 | 98815 | 6.7 | 250 | 6.3994 | 442.8 | 853.2 | 267.795 | 0 | 1 | 9
6978 | 10/18 | 17:00:00 | 282.15 | 98815 | 5.7 | 260 | 6.3994 | 90 | 0 | 267.795 | 0 | 1 | 9
6979 | 10/18 | 18:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
6980 | 10/18 | 19:00:00 | 282.15 | 98815 | 2.6 | 240 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
6981 | 10/18 | 20:00:00 | 282.15 | 98815 | 3.6 | 240 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
6982 | 10/18 | 21:00:00 | 282.15 | 98815 | 3.6 | 240 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
6983 | 10/18 | 22:00:00 | 282.15 | 98815 | 5.1 | 240 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
6984 | 10/18 | 23:00:00 | 282.15 | 98815 | 5.7 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6985 | 10/18 | 24:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
6986 | 10/19 | 01:00:00 | 282.15 | 98815 | 4.1 | 230 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
6987 | 10/19 | 02:00:00 | 281.15 | 98806 | 4.6 | 230 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
6988 | 10/19 | 03:00:00 | 281.15 | 98806 | 3.6 | 240 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
6989 | 10/19 | 04:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
6990 | 10/19 | 05:00:00 | 281.15 | 98806 | 2.6 | 230 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
6991 | 10/19 | 06:00:00 | 281.15 | 98806 | 2.1 | 210 | 6.8577 | 0 | 0 | 267.071 | 0 | 1 | 8
6992 | 10/19 | 07:00:00 | 281.15 | 98806 | 2.6 | 230 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
6993 | 10/19 | 08:00:00 | 281.15 | 98806 | 3.6 | 200 | 6.8577 | 140.4 | 68.4 | 267.332 | 0 | 1 | 8
6994 | 10/19 | 09:00:00 | 281.15 | 98806 | 4.1 | 220 | 6.8577 | 504 | 842.4 | 267.332 | 0 | 1 | 8
6995 | 10/19 | 10:00:00 | 283.15 | 98824 | 4.6 | 220 | 6.8564 | 874.8 | 1389.6 | 269.234 | 0 | 1 | 10
6996 | 10/19 | 11:00:00 | 283.15 | 98824 | 4.1 | 210 | 6.8564 | 1152 | 1666.8 | 269.234 | 0 | 1 | 10
6997 | 10/19 | 12:00:00 | 284.15 | 98833 | 4.6 | 210 | 7.3425 | 1288.8 | 1537.2 | 270.411 | 0 | 1 | 11
6998 | 10/19 | 13:00:00 | 284.15 | 98833 | 6.7 | 200 | 6.8558 | 1267.2 | 1530 | 270.185 | 0 | 1 | 11
6999 | 10/19 | 14:00:00 | 284.15 | 98833 | 3.1 | 210 | 6.8558 | 1090.8 | 1306.8 | 270.185 | 0 | 1 | 11
7000 | 10/19 | 15:00:00 | 285.15 | 98841 | 2.6 | 200 | 6.3977 | 435.6 | 54 | 271.387 | 0 | 1 | 12
7001 | 10/19 | 16:00:00 | 285.15 | 98841 | 3.1 | 180 | 5.9676 | 399.6 | 658.8 | 270.678 | 0 | 1 | 12
7002 | 10/19 | 17:00:00 | 283.15 | 98824 | 3.6 | 200 | 5.5646 | 75.6 | 0 | 268.55 | 0 | 1 | 10
7003 | 10/19 | 18:00:00 | 282.15 | 98815 | 2.6 | 180 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
7004 | 10/19 | 19:00:00 | 281.15 | 98806 | 2.6 | 170 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
7005 | 10/19 | 20:00:00 | 282.15 | 98815 | 3.6 | 170 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
7006 | 10/19 | 21:00:00 | 282.15 | 98815 | 4.1 | 170 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
7007 | 10/19 | 22:00:00 | 281.15 | 98806 | 4.1 | 160 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
7008 | 10/19 | 23:00:00 | 281.15 | 98806 | 5.1 | 160 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
7009 | 10/19 | 24:00:00 | 281.15 | 98806 | 6.7 | 160 | 5.5656 | 0 | 0 | 267.013 | 0 | 1 | 8
7010 | 10/20 | 01:00:00 | 280.15 | 98798 | 5.7 | 170 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
7011 | 10/20 | 02:00:00 | 280.15 | 98798 | 6.2 | 140 | 4.8303 | 0 | 0 | 265.246 | 0 | 1 | 7
7012 | 10/20 | 03:00:00 | 279.15 | 98789 | 6.2 | 150 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
7013 | 10/20 | 04:00:00 | 279.15 | 98789 | 6.2 | 140 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
7014 | 10/20 | 05:00:00 | 278.15 | 98780 | 6.2 | 150 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7015 | 10/20 | 06:00:00 | 278.15 | 98780 | 7.7 | 130 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7016 | 10/20 | 07:00:00 | 278.15 | 98780 | 5.7 | 130 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7017 | 10/20 | 08:00:00 | 278.15 | 98780 | 6.7 | 120 | 4.8311 | 82.8 | 0 | 263.818 | 0 | 1 | 5
7018 | 10/20 | 09:00:00 | 279.15 | 98789 | 8.2 | 130 | 5.187 | 493.2 | 676.8 | 264.528 | 0 | 1 | 6
7019 | 10/20 | 10:00:00 | 280.15 | 98798 | 7.2 | 130 | 5.5661 | 864 | 1400.4 | 265.704 | 0 | 1 | 7
7020 | 10/20 | 11:00:00 | 280.15 | 98798 | 8.2 | 140 | 5.5661 | 1141.2 | 1684.8 | 265.704 | 0 | 1 | 7
7021 | 10/20 | 12:00:00 | 281.15 | 98806 | 8.2 | 130 | 5.5656 | 1278 | 1562.4 | 266.653 | 0 | 1 | 8
7022 | 10/20 | 13:00:00 | 281.15 | 98806 | 6.7 | 130 | 5.5656 | 1252.8 | 1443.6 | 266.653 | 0 | 1 | 8
7023 | 10/20 | 14:00:00 | 281.15 | 98806 | 5.1 | 130 | 5.9698 | 594 | 201.6 | 267.353 | 0 | 1 | 8
7024 | 10/20 | 15:00:00 | 280.15 | 98798 | 6.7 | 140 | 6.4005 | 424.8 | 21.6 | 266.628 | 0 | 1 | 7
7025 | 10/20 | 16:00:00 | 281.15 | 98806 | 5.7 | 130 | 6.4 | 212.4 | 0 | 267.58 | 0 | 1 | 8
7026 | 10/20 | 17:00:00 | 281.15 | 98806 | 5.7 | 140 | 6.8577 | 39.6 | 0 | 267.805 | 0 | 1 | 8
7027 | 10/20 | 18:00:00 | 281.15 | 98806 | 6.7 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7028 | 10/20 | 19:00:00 | 281.15 | 98806 | 4.6 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7029 | 10/20 | 20:00:00 | 281.15 | 98806 | 6.2 | 130 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7030 | 10/20 | 21:00:00 | 281.15 | 98806 | 5.7 | 120 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7031 | 10/20 | 22:00:00 | 281.15 | 98806 | 5.7 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7032 | 10/20 | 23:00:00 | 281.15 | 98806 | 4.1 | 130 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
7033 | 10/20 | 24:00:00 | 281.15 | 98806 | 3.6 | 100 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
7034 | 10/21 | 01:00:00 | 281.15 | 98806 | 4.1 | 110 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
7035 | 10/21 | 02:00:00 | 282.15 | 98815 | 4.1 | 110 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
7036 | 10/21 | 03:00:00 | 282.15 | 98815 | 3.6 | 110 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
7037 | 10/21 | 04:00:00 | 282.15 | 98815 | 3.6 | 120 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7038 | 10/21 | 05:00:00 | 282.15 | 98815 | 4.1 | 150 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7039 | 10/21 | 06:00:00 | 282.15 | 98815 | 3.1 | 160 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7040 | 10/21 | 07:00:00 | 282.15 | 98815 | 3.1 | 160 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7041 | 10/21 | 08:00:00 | 283.15 | 98824 | 3.6 | 180 | 7.8605 | 64.8 | 0 | 270.161 | 0 | 1 | 10
7042 | 10/21 | 09:00:00 | 283.15 | 98824 | 3.1 | 160 | 7.8605 | 262.8 | 0 | 270.161 | 0 | 1 | 10
7043 | 10/21 | 10:00:00 | 283.15 | 98824 | 4.1 | 150 | 7.8605 | 464.4 | 28.8 | 270.161 | 0 | 1 | 10
7044 | 10/21 | 11:00:00 | 283.15 | 98824 | 4.1 | 150 | 7.8605 | 615.6 | 100.8 | 270.161 | 0 | 1 | 10
7045 | 10/21 | 12:00:00 | 284.15 | 98833 | 3.6 | 130 | 7.8598 | 691.2 | 115.2 | 271.115 | 0 | 1 | 11
7046 | 10/21 | 13:00:00 | 284.15 | 98833 | 4.1 | 140 | 7.8598 | 676.8 | 115.2 | 271.115 | 0 | 1 | 11
7047 | 10/21 | 14:00:00 | 284.15 | 98833 | 2.1 | 160 | 8.4095 | 579.6 | 32.4 | 271.339 | 0 | 1 | 11
7048 | 10/21 | 15:00:00 | 284.15 | 98833 | 4.1 | 140 | 8.4095 | 410.4 | 21.6 | 271.339 | 0 | 1 | 11
7049 | 10/21 | 16:00:00 | 284.15 | 98833 | 4.1 | 140 | 8.4095 | 201.6 | 0 | 271.339 | 0 | 1 | 11
7050 | 10/21 | 17:00:00 | 284.15 | 98833 | 4.6 | 130 | 8.4095 | 64.8 | 0 | 270.859 | 0 | 1 | 11
7051 | 10/21 | 18:00:00 | 284.15 | 98833 | 5.1 | 130 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7052 | 10/21 | 19:00:00 | 283.15 | 98824 | 5.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7053 | 10/21 | 20:00:00 | 283.15 | 98824 | 4.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7054 | 10/21 | 21:00:00 | 283.15 | 98824 | 4.6 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7055 | 10/21 | 22:00:00 | 283.15 | 98824 | 4.1 | 130 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7056 | 10/21 | 23:00:00 | 283.15 | 98824 | 4.6 | 130 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7057 | 10/21 | 24:00:00 | 283.15 | 98824 | 5.1 | 120 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7058 | 10/22 | 01:00:00 | 282.15 | 98815 | 4.6 | 120 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7059 | 10/22 | 02:00:00 | 282.15 | 98815 | 4.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7060 | 10/22 | 03:00:00 | 283.15 | 98824 | 4.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7061 | 10/22 | 04:00:00 | 282.15 | 98815 | 4.1 | 120 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7062 | 10/22 | 05:00:00 | 282.15 | 98815 | 4.6 | 130 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7063 | 10/22 | 06:00:00 | 283.15 | 98824 | 4.6 | 130 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7064 | 10/22 | 07:00:00 | 282.15 | 98815 | 3.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7065 | 10/22 | 08:00:00 | 282.15 | 98815 | 4.1 | 110 | 7.3438 | 61.2 | 0 | 268.983 | 0 | 1 | 9
7066 | 10/22 | 09:00:00 | 282.15 | 98815 | 4.1 | 110 | 7.3438 | 255.6 | 0 | 268.983 | 0 | 1 | 9
7067 | 10/22 | 10:00:00 | 283.15 | 98824 | 3.6 | 130 | 7.3431 | 457.2 | 28.8 | 269.936 | 0 | 1 | 10
7068 | 10/22 | 11:00:00 | 283.15 | 98824 | 5.1 | 130 | 7.8605 | 604.8 | 97.2 | 270.161 | 0 | 1 | 10
7069 | 10/22 | 12:00:00 | 283.15 | 98824 | 5.7 | 140 | 7.3431 | 680.4 | 115.2 | 269.936 | 0 | 1 | 10
7070 | 10/22 | 13:00:00 | 283.15 | 98824 | 3.6 | 160 | 7.3431 | 666 | 111.6 | 269.936 | 0 | 1 | 10
7071 | 10/22 | 14:00:00 | 284.15 | 98833 | 3.6 | 160 | 7.3425 | 568.8 | 90 | 270.89 | 0 | 1 | 11
7072 | 10/22 | 15:00:00 | 284.15 | 98833 | 2.6 | 130 | 7.8598 | 399.6 | 18 | 271.115 | 0 | 1 | 11
7073 | 10/22 | 16:00:00 | 284.15 | 98833 | 3.6 | 120 | 7.8598 | 194.4 | 0 | 271.115 | 0 | 1 | 11
7074 | 10/22 | 17:00:00 | 284.15 | 98833 | 2.6 | 130 | 7.8598 | 32.4 | 0 | 271.115 | 0 | 1 | 11
7075 | 10/22 | 18:00:00 | 284.15 | 98833 | 4.6 | 110 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
7076 | 10/22 | 19:00:00 | 284.15 | 98833 | 3.1 | 150 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
7077 | 10/22 | 20:00:00 | 284.15 | 98833 | 3.6 | 140 | 8.4095 | 0 | 0 | 270.859 | 0 | 1 | 11
7078 | 10/22 | 21:00:00 | 284.15 | 98833 | 4.1 | 140 | 8.4095 | 0 | 0 | 270.859 | 0 | 1 | 11
7079 | 10/22 | 22:00:00 | 284.15 | 98833 | 4.6 | 160 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
7080 | 10/22 | 23:00:00 | 283.15 | 98824 | 4.1 | 160 | 7.8605 | 0 | 0 | 269.42 | 0 | 1 | 10
7081 | 10/22 | 24:00:00 | 283.15 | 98824 | 4.6 | 160 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7082 | 10/23 | 01:00:00 | 283.15 | 98824 | 3.6 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7083 | 10/23 | 02:00:00 | 283.15 | 98824 | 3.6 | 150 | 7.8605 | 0 | 0 | 269.684 | 0 | 1 | 10
7084 | 10/23 | 03:00:00 | 283.15 | 98824 | 4.1 | 150 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
7085 | 10/23 | 04:00:00 | 283.15 | 98824 | 4.6 | 150 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
7086 | 10/23 | 05:00:00 | 282.15 | 98815 | 3.6 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7087 | 10/23 | 06:00:00 | 282.15 | 98815 | 3.1 | 150 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7088 | 10/23 | 07:00:00 | 282.15 | 98815 | 3.6 | 150 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7089 | 10/23 | 08:00:00 | 282.15 | 98815 | 3.6 | 150 | 7.3438 | 57.6 | 0 | 268.983 | 0 | 1 | 9
7090 | 10/23 | 09:00:00 | 283.15 | 98824 | 3.6 | 170 | 7.8605 | 244.8 | 0 | 270.161 | 0 | 1 | 10
7091 | 10/23 | 10:00:00 | 283.15 | 98824 | 3.6 | 170 | 7.8605 | 802.8 | 1018.8 | 269.684 | 0 | 1 | 10
7092 | 10/23 | 11:00:00 | 284.15 | 98833 | 3.1 | 180 | 7.8598 | 1072.8 | 1602 | 270.636 | 0 | 1 | 11
7093 | 10/23 | 12:00:00 | 285.15 | 98841 | 3.1 | 200 | 7.8591 | 1206 | 1494 | 271.588 | 0 | 1 | 12
7094 | 10/23 | 13:00:00 | 286.15 | 98850 | 2.1 | 220 | 7.8584 | 1180.8 | 1476 | 272.541 | 0 | 1 | 13
7095 | 10/23 | 14:00:00 | 286.15 | 98850 | 2.1 | 230 | 7.8584 | 1004.4 | 1537.2 | 272.541 | 0 | 1 | 13
7096 | 10/23 | 15:00:00 | 286.15 | 98850 | 2.1 | 230 | 7.8584 | 702 | 1188 | 272.541 | 0 | 1 | 13
7097 | 10/23 | 16:00:00 | 286.15 | 98850 | 2.1 | 220 | 7.8584 | 352.8 | 709.2 | 272.274 | 0 | 1 | 13
7098 | 10/23 | 17:00:00 | 285.15 | 98841 | 2.1 | 220 | 7.3418 | 54 | 0 | 271.097 | 0 | 1 | 12
7099 | 10/23 | 18:00:00 | 284.15 | 98833 | 1.5 | 220 | 7.3425 | 0 | 0 | 270.147 | 0 | 1 | 11
7100 | 10/23 | 19:00:00 | 284.15 | 98833 | 2.6 | 180 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
7101 | 10/23 | 20:00:00 | 284.15 | 98833 | 2.6 | 180 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
7102 | 10/23 | 21:00:00 | 283.15 | 98824 | 3.1 | 180 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
7103 | 10/23 | 22:00:00 | 283.15 | 98824 | 2.6 | 160 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
7104 | 10/23 | 23:00:00 | 283.15 | 98824 | 2.1 | 160 | 7.3431 | 0 | 0 | 270.046 | 0 | 1 | 10
7105 | 10/23 | 24:00:00 | 283.15 | 98824 | 2.6 | 150 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
7106 | 10/24 | 01:00:00 | 283.15 | 98824 | 3.1 | 140 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
7107 | 10/24 | 02:00:00 | 283.15 | 98824 | 3.1 | 130 | 7.8605 | 0 | 0 | 269.42 | 0 | 1 | 10
7108 | 10/24 | 03:00:00 | 283.15 | 98824 | 2.6 | 120 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7109 | 10/24 | 04:00:00 | 283.15 | 98824 | 3.1 | 130 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7110 | 10/24 | 05:00:00 | 283.15 | 98824 | 4.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7111 | 10/24 | 06:00:00 | 283.15 | 98824 | 5.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7112 | 10/24 | 07:00:00 | 283.15 | 98824 | 5.7 | 150 | 7.8605 | 0 | 0 | 270.27 | 0 | 1 | 10
7113 | 10/24 | 08:00:00 | 283.15 | 98824 | 6.2 | 150 | 7.8605 | 32.4 | 0 | 270.27 | 0 | 1 | 10
7114 | 10/24 | 09:00:00 | 284.15 | 98833 | 6.7 | 150 | 8.4095 | 144 | 0 | 271.449 | 0 | 1 | 11
7115 | 10/24 | 10:00:00 | 284.15 | 98833 | 6.7 | 150 | 8.4095 | 266.4 | 0 | 271.449 | 0 | 1 | 11
7116 | 10/24 | 11:00:00 | 285.15 | 98841 | 6.7 | 150 | 8.9926 | 356.4 | 0 | 272.627 | 0 | 1 | 12
7117 | 10/24 | 12:00:00 | 285.15 | 98841 | 5.7 | 160 | 8.9926 | 399.6 | 0 | 272.627 | 0 | 1 | 12
7118 | 10/24 | 13:00:00 | 286.15 | 98850 | 5.7 | 160 | 9.6116 | 392.4 | 0 | 273.806 | 0 | 1 | 13
7119 | 10/24 | 14:00:00 | 287.15 | 98858 | 5.1 | 170 | 10.2686 | 979.2 | 1206 | 274.389 | 0 | 1 | 14
7120 | 10/24 | 15:00:00 | 289.15 | 98875 | 6.2 | 210 | 9.6091 | 720 | 1465.2 | 275.806 | 0 | 1 | 16
7121 | 10/24 | 16:00:00 | 288.15 | 98867 | 5.1 | 210 | 8.4065 | 316.8 | 532.8 | 274.672 | 0 | 1 | 15
7122 | 10/24 | 17:00:00 | 286.15 | 98850 | 7.2 | 230 | 7.8584 | 46.8 | 0 | 272.541 | 0 | 1 | 13
7123 | 10/24 | 18:00:00 | 286.15 | 98850 | 9.3 | 220 | 7.8584 | 0 | 0 | 273.023 | 0 | 1 | 13
7124 | 10/24 | 19:00:00 | 285.15 | 98841 | 9.3 | 240 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
7125 | 10/24 | 20:00:00 | 285.15 | 98841 | 11.8 | 240 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
7126 | 10/24 | 21:00:00 | 285.15 | 98841 | 10.3 | 240 | 7.3418 | 0 | 0 | 271.363 | 0 | 1 | 12
7127 | 10/24 | 22:00:00 | 285.15 | 98841 | 10.8 | 250 | 6.8552 | 0 | 0 | 270.871 | 0 | 1 | 12
7128 | 10/24 | 23:00:00 | 285.15 | 98841 | 9.3 | 240 | 6.3977 | 0 | 0 | 270.643 | 0 | 1 | 12
7129 | 10/24 | 24:00:00 | 284.15 | 98833 | 10.8 | 250 | 6.3982 | 0 | 0 | 270.204 | 0 | 1 | 11
7130 | 10/25 | 01:00:00 | 283.15 | 98824 | 6.7 | 230 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
7131 | 10/25 | 02:00:00 | 283.15 | 98824 | 8.2 | 230 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
7132 | 10/25 | 03:00:00 | 284.15 | 98833 | 7.7 | 230 | 6.3982 | 0 | 0 | 269.693 | 0 | 1 | 11
7133 | 10/25 | 04:00:00 | 284.15 | 98833 | 7.2 | 240 | 6.8558 | 0 | 0 | 269.921 | 0 | 1 | 11
7134 | 10/25 | 05:00:00 | 284.15 | 98833 | 8.7 | 250 | 6.8558 | 0 | 0 | 269.921 | 0 | 1 | 11
7135 | 10/25 | 06:00:00 | 284.15 | 98833 | 7.7 | 240 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
7136 | 10/25 | 07:00:00 | 284.15 | 98833 | 7.2 | 240 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
7137 | 10/25 | 08:00:00 | 284.15 | 98833 | 8.2 | 250 | 7.3425 | 50.4 | 0 | 270.89 | 0 | 1 | 11
7138 | 10/25 | 09:00:00 | 284.15 | 98833 | 9.3 | 250 | 7.3425 | 230.4 | 0 | 270.89 | 0 | 1 | 11
7139 | 10/25 | 10:00:00 | 285.15 | 98841 | 8.7 | 250 | 7.3418 | 424.8 | 50.4 | 271.843 | 0 | 1 | 12
7140 | 10/25 | 11:00:00 | 285.15 | 98841 | 9.8 | 240 | 7.3418 | 1033.2 | 1285.2 | 271.363 | 0 | 1 | 12
7141 | 10/25 | 12:00:00 | 285.15 | 98841 | 10.3 | 240 | 7.3418 | 648 | 226.8 | 271.843 | 0 | 1 | 12
7142 | 10/25 | 13:00:00 | 285.15 | 98841 | 9.3 | 240 | 6.8552 | 1144.8 | 1371.6 | 271.136 | 0 | 1 | 12
7143 | 10/25 | 14:00:00 | 285.15 | 98841 | 10.3 | 250 | 7.3418 | 536.4 | 169.2 | 271.843 | 0 | 1 | 12
7144 | 10/25 | 15:00:00 | 284.15 | 98833 | 6.7 | 260 | 7.8598 | 666 | 885.6 | 270.636 | 0 | 1 | 11
7145 | 10/25 | 16:00:00 | 284.15 | 98833 | 6.2 | 240 | 7.8598 | 302.4 | 378 | 270.636 | 0 | 1 | 11
7146 | 10/25 | 17:00:00 | 284.15 | 98833 | 6.7 | 240 | 7.8598 | 39.6 | 0 | 270.636 | 0 | 1 | 11
7147 | 10/25 | 18:00:00 | 284.15 | 98833 | 8.2 | 250 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
7148 | 10/25 | 19:00:00 | 284.15 | 98833 | 8.2 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7149 | 10/25 | 20:00:00 | 284.15 | 98833 | 9.3 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7150 | 10/25 | 21:00:00 | 284.15 | 98833 | 8.7 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7151 | 10/25 | 22:00:00 | 284.15 | 98833 | 8.7 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7152 | 10/25 | 23:00:00 | 284.15 | 98833 | 10.8 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7153 | 10/25 | 24:00:00 | 284.15 | 98833 | 8.2 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7154 | 10/26 | 01:00:00 | 284.15 | 98833 | 7.7 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
7155 | 10/26 | 02:00:00 | 284.15 | 98833 | 7.7 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
7156 | 10/26 | 03:00:00 | 284.15 | 98833 | 8.2 | 280 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7157 | 10/26 | 04:00:00 | 283.15 | 98824 | 8.7 | 280 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7158 | 10/26 | 05:00:00 | 283.15 | 98824 | 7.2 | 280 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7159 | 10/26 | 06:00:00 | 284.15 | 98833 | 6.2 | 280 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7160 | 10/26 | 07:00:00 | 284.15 | 98833 | 6.2 | 290 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
7161 | 10/26 | 08:00:00 | 283.15 | 98824 | 5.1 | 300 | 7.3431 | 46.8 | 0 | 269.936 | 0 | 1 | 10
7162 | 10/26 | 09:00:00 | 283.15 | 98824 | 3.6 | 280 | 7.3431 | 223.2 | 0 | 269.936 | 0 | 1 | 10
7163 | 10/26 | 10:00:00 | 284.15 | 98833 | 4.6 | 310 | 7.8598 | 414 | 21.6 | 271.115 | 0 | 1 | 11
7164 | 10/26 | 11:00:00 | 284.15 | 98833 | 3.1 | 320 | 7.8598 | 561.6 | 90 | 271.115 | 0 | 1 | 11
7165 | 10/26 | 12:00:00 | 285.15 | 98841 | 1.5 | 109 | 7.3418 | 637.2 | 108 | 271.843 | 0 | 1 | 12
7166 | 10/26 | 13:00:00 | 285.15 | 98841 | 3.6 | 280 | 7.3418 | 622.8 | 104.4 | 271.843 | 0 | 1 | 12
7167 | 10/26 | 14:00:00 | 284.15 | 98833 | 3.6 | 270 | 7.8598 | 943.2 | 1209.6 | 270.636 | 0 | 1 | 11
7168 | 10/26 | 15:00:00 | 285.15 | 98841 | 1.5 | 71 | 7.3418 | 648 | 874.8 | 271.363 | 0 | 1 | 12
7169 | 10/26 | 16:00:00 | 285.15 | 98841 | 1.5 | 260 | 7.8591 | 158.4 | 0 | 272.069 | 0 | 1 | 12
7170 | 10/26 | 17:00:00 | 284.15 | 98833 | 1 | 237 | 7.8598 | 18 | 0 | 271.115 | 0 | 1 | 11
7171 | 10/26 | 18:00:00 | 284.15 | 98833 | 1 | 120 | 7.3425 | 0 | 0 | 270.411 | 0 | 1 | 11
7172 | 10/26 | 19:00:00 | 283.15 | 98824 | 1 | 50 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
7173 | 10/26 | 20:00:00 | 283.15 | 98824 | 1 | 172 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
7174 | 10/26 | 21:00:00 | 283.15 | 98824 | 2.1 | 100 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
7175 | 10/26 | 22:00:00 | 282.15 | 98815 | 3.1 | 110 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
7176 | 10/26 | 23:00:00 | 283.15 | 98824 | 3.1 | 130 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7177 | 10/26 | 24:00:00 | 282.15 | 98815 | 3.1 | 130 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
7178 | 10/27 | 01:00:00 | 283.15 | 98824 | 3.6 | 130 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7179 | 10/27 | 02:00:00 | 282.15 | 98815 | 4.1 | 130 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
7180 | 10/27 | 03:00:00 | 282.15 | 98815 | 3.6 | 140 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
7181 | 10/27 | 04:00:00 | 282.15 | 98815 | 4.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7182 | 10/27 | 05:00:00 | 282.15 | 98815 | 4.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7183 | 10/27 | 06:00:00 | 282.15 | 98815 | 2.6 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7184 | 10/27 | 07:00:00 | 282.15 | 98815 | 4.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7185 | 10/27 | 08:00:00 | 282.15 | 98815 | 3.6 | 130 | 7.3438 | 43.2 | 0 | 268.983 | 0 | 1 | 9
7186 | 10/27 | 09:00:00 | 282.15 | 98815 | 2.1 | 150 | 7.3438 | 212.4 | 0 | 268.983 | 0 | 1 | 9
7187 | 10/27 | 10:00:00 | 283.15 | 98824 | 2.6 | 150 | 7.8605 | 406.8 | 21.6 | 270.161 | 0 | 1 | 10
7188 | 10/27 | 11:00:00 | 283.15 | 98824 | 2.1 | 150 | 7.8605 | 550.8 | 86.4 | 270.161 | 0 | 1 | 10
7189 | 10/27 | 12:00:00 | 284.15 | 98833 | 2.6 | 140 | 8.4095 | 622.8 | 36 | 271.339 | 0 | 1 | 11
7190 | 10/27 | 13:00:00 | 284.15 | 98833 | 1.5 | 130 | 8.4095 | 608.4 | 36 | 271.339 | 0 | 1 | 11
7191 | 10/27 | 14:00:00 | 285.15 | 98841 | 3.1 | 140 | 8.9926 | 511.2 | 54 | 272.517 | 0 | 1 | 12
7192 | 10/27 | 15:00:00 | 285.15 | 98841 | 3.1 | 150 | 8.9926 | 349.2 | 10.8 | 272.517 | 0 | 1 | 12
7193 | 10/27 | 16:00:00 | 286.15 | 98850 | 2.1 | 140 | 9.6116 | 151.2 | 0 | 273.695 | 0 | 1 | 13
7194 | 10/27 | 17:00:00 | 286.15 | 98850 | 3.1 | 160 | 9.6116 | 14.4 | 0 | 273.695 | 0 | 1 | 13
7195 | 10/27 | 18:00:00 | 287.15 | 98858 | 3.6 | 170 | 9.6108 | 0 | 0 | 274.652 | 0 | 1 | 14
7196 | 10/27 | 19:00:00 | 287.15 | 98858 | 2.1 | 160 | 9.6108 | 0 | 0 | 274.167 | 0 | 1 | 14
7197 | 10/27 | 20:00:00 | 286.15 | 98850 | 3.6 | 160 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
7198 | 10/27 | 21:00:00 | 286.15 | 98850 | 4.1 | 170 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
7199 | 10/27 | 22:00:00 | 285.15 | 98841 | 4.1 | 170 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
7200 | 10/27 | 23:00:00 | 285.15 | 98841 | 3.6 | 190 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
7201 | 10/27 | 24:00:00 | 285.15 | 98841 | 2.6 | 220 | 7.3418 | 0 | 0 | 271.097 | 0 | 1 | 12
7202 | 10/28 | 01:00:00 | 285.15 | 98841 | 3.1 | 220 | 7.3418 | 0 | 0 | 271.097 | 0 | 1 | 12
7203 | 10/28 | 02:00:00 | 284.15 | 98833 | 4.1 | 220 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
7204 | 10/28 | 03:00:00 | 285.15 | 98841 | 3.1 | 190 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
7205 | 10/28 | 04:00:00 | 285.15 | 98841 | 2.6 | 260 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
7206 | 10/28 | 05:00:00 | 284.15 | 98833 | 3.1 | 230 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7207 | 10/28 | 06:00:00 | 284.15 | 98833 | 1.5 | 277 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
7208 | 10/28 | 07:00:00 | 285.15 | 98841 | 2.6 | 240 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
7209 | 10/28 | 08:00:00 | 285.15 | 98841 | 3.6 | 250 | 8.4088 | 75.6 | 0 | 271.813 | 0 | 1 | 12
7210 | 10/28 | 09:00:00 | 285.15 | 98841 | 4.6 | 250 | 8.4088 | 370.8 | 615.6 | 271.813 | 0 | 1 | 12
7211 | 10/28 | 10:00:00 | 286.15 | 98850 | 5.1 | 250 | 8.9918 | 756 | 1548 | 272.723 | 0 | 1 | 13
7212 | 10/28 | 11:00:00 | 287.15 | 98858 | 6.2 | 240 | 8.4073 | 1033.2 | 1882.8 | 273.451 | 0 | 1 | 14
7213 | 10/28 | 12:00:00 | 288.15 | 98867 | 4.6 | 240 | 8.4065 | 1101.6 | 1641.6 | 274.672 | 0 | 1 | 15
7214 | 10/28 | 13:00:00 | 288.15 | 98867 | 6.2 | 260 | 8.4065 | 1080 | 1620 | 274.672 | 0 | 1 | 15
7215 | 10/28 | 14:00:00 | 288.15 | 98867 | 6.2 | 260 | 8.4065 | 903.6 | 1465.2 | 274.672 | 0 | 1 | 15
7216 | 10/28 | 15:00:00 | 288.15 | 98867 | 5.7 | 250 | 8.4065 | 608.4 | 1134 | 274.672 | 0 | 1 | 15
7217 | 10/28 | 16:00:00 | 287.15 | 98858 | 4.6 | 260 | 8.4073 | 259.2 | 421.2 | 273.719 | 0 | 1 | 14
7218 | 10/28 | 17:00:00 | 287.15 | 98858 | 5.1 | 270 | 7.8578 | 21.6 | 0 | 273.493 | 0 | 1 | 14
7219 | 10/28 | 18:00:00 | 286.15 | 98850 | 3.1 | 260 | 7.8584 | 0 | 0 | 272.274 | 0 | 1 | 13
7220 | 10/28 | 19:00:00 | 284.15 | 98833 | 2.6 | 310 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
7221 | 10/28 | 20:00:00 | 284.15 | 98833 | 1.5 | 310 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
7222 | 10/28 | 21:00:00 | 285.15 | 98841 | 1.5 | 240 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
7223 | 10/28 | 22:00:00 | 285.15 | 98841 | 1.5 | 280 | 8.4088 | 0 | 0 | 272.294 | 0 | 1 | 12
7224 | 10/28 | 23:00:00 | 284.15 | 98833 | 2.1 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7225 | 10/28 | 24:00:00 | 284.15 | 98833 | 2.1 | 300 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7226 | 10/29 | 01:00:00 | 284.15 | 98833 | 2.1 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7227 | 10/29 | 02:00:00 | 284.15 | 98833 | 1 | 300 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
7228 | 10/29 | 03:00:00 | 282.15 | 98815 | 1.5 | 280 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
7229 | 10/29 | 04:00:00 | 282.15 | 98815 | 1.5 | 270 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
7230 | 10/29 | 05:00:00 | 283.15 | 98824 | 0 | 220 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
7231 | 10/29 | 06:00:00 | 282.15 | 98815 | 1.5 | 140 | 7.3438 | 0 | 0 | 268.508 | 0 | 1 | 9
7232 | 10/29 | 07:00:00 | 282.15 | 98815 | 2.1 | 170 | 7.3438 | 0 | 0 | 268.245 | 0 | 1 | 9
7233 | 10/29 | 08:00:00 | 282.15 | 98815 | 2.6 | 160 | 7.3438 | 72 | 0 | 268.245 | 0 | 1 | 9
7234 | 10/29 | 09:00:00 | 283.15 | 98824 | 2.6 | 180 | 7.3431 | 378 | 615.6 | 269.196 | 0 | 1 | 10
7235 | 10/29 | 10:00:00 | 285.15 | 98841 | 2.6 | 180 | 7.8591 | 428.4 | 75.6 | 272.069 | 0 | 1 | 12
7236 | 10/29 | 11:00:00 | 285.15 | 98841 | 2.1 | 170 | 7.8591 | 590.4 | 320.4 | 272.069 | 0 | 1 | 12
7237 | 10/29 | 12:00:00 | 286.15 | 98850 | 2.6 | 180 | 8.408 | 1162.8 | 1652.4 | 272.064 | 0 | 1 | 13
7238 | 10/29 | 13:00:00 | 287.15 | 98858 | 3.1 | 160 | 8.4073 | 1137.6 | 1854 | 273.015 | 0 | 1 | 14
7239 | 10/29 | 14:00:00 | 288.15 | 98867 | 4.1 | 180 | 8.4065 | 766.8 | 820.8 | 274.924 | 0 | 1 | 15
7240 | 10/29 | 15:00:00 | 288.15 | 98867 | 3.6 | 190 | 8.4065 | 594 | 1112.4 | 274.672 | 0 | 1 | 15
7241 | 10/29 | 16:00:00 | 287.15 | 98858 | 2.6 | 170 | 8.991 | 259.2 | 324 | 273.676 | 0 | 1 | 14
7242 | 10/29 | 17:00:00 | 286.15 | 98850 | 3.1 | 160 | 8.408 | 18 | 0 | 272.499 | 0 | 1 | 13
7243 | 10/29 | 18:00:00 | 286.15 | 98850 | 3.1 | 170 | 8.9918 | 0 | 0 | 272.723 | 0 | 1 | 13
7244 | 10/29 | 19:00:00 | 286.15 | 98850 | 2.1 | 160 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
7245 | 10/29 | 20:00:00 | 286.15 | 98850 | 3.6 | 170 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
7246 | 10/29 | 21:00:00 | 286.15 | 98850 | 3.6 | 150 | 8.9918 | 0 | 0 | 273.473 | 0 | 1 | 13
7247 | 10/29 | 22:00:00 | 285.15 | 98841 | 3.1 | 160 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
7248 | 10/29 | 23:00:00 | 285.15 | 98841 | 4.1 | 160 | 8.4088 | 0 | 0 | 271.547 | 0 | 1 | 12
7249 | 10/29 | 24:00:00 | 284.15 | 98833 | 4.6 | 150 | 8.4095 | 0 | 0 | 270.595 | 0 | 1 | 11
7250 | 10/30 | 01:00:00 | 284.15 | 98833 | 3.1 | 160 | 8.4095 | 0 | 0 | 270.595 | 0 | 1 | 11
7251 | 10/30 | 02:00:00 | 284.15 | 98833 | 3.6 | 150 | 8.4095 | 0 | 0 | 270.595 | 0 | 1 | 11
7252 | 10/30 | 03:00:00 | 283.15 | 98824 | 4.1 | 150 | 7.8605 | 0 | 0 | 269.42 | 0 | 1 | 10
7253 | 10/30 | 04:00:00 | 283.15 | 98824 | 4.6 | 160 | 7.8605 | 0 | 0 | 269.42 | 0 | 1 | 10
7254 | 10/30 | 05:00:00 | 283.15 | 98824 | 5.1 | 150 | 7.8605 | 0 | 0 | 269.42 | 0 | 1 | 10
7255 | 10/30 | 06:00:00 | 282.15 | 98815 | 2.6 | 140 | 7.3438 | 0 | 0 | 268.245 | 0 | 1 | 9
7256 | 10/30 | 07:00:00 | 282.15 | 98815 | 4.1 | 160 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7257 | 10/30 | 08:00:00 | 282.15 | 98815 | 6.2 | 160 | 7.3438 | 36 | 0 | 268.983 | 0 | 1 | 9
7258 | 10/30 | 09:00:00 | 282.15 | 98815 | 5.7 | 160 | 7.3438 | 190.8 | 0 | 268.983 | 0 | 1 | 9
7259 | 10/30 | 10:00:00 | 282.15 | 98815 | 5.7 | 170 | 7.3438 | 378 | 14.4 | 268.983 | 0 | 1 | 9
7260 | 10/30 | 11:00:00 | 283.15 | 98824 | 6.2 | 160 | 7.8605 | 522 | 79.2 | 270.161 | 0 | 1 | 10
7261 | 10/30 | 12:00:00 | 284.15 | 98833 | 6.2 | 160 | 8.4095 | 590.4 | 93.6 | 271.339 | 0 | 1 | 11
7262 | 10/30 | 13:00:00 | 285.15 | 98841 | 5.1 | 150 | 8.4088 | 1101.6 | 1555.2 | 271.547 | 0 | 1 | 12
7263 | 10/30 | 14:00:00 | 286.15 | 98850 | 6.2 | 150 | 7.8584 | 921.6 | 1688.4 | 272.274 | 0 | 1 | 13
7264 | 10/30 | 15:00:00 | 286.15 | 98850 | 6.7 | 170 | 7.3412 | 612 | 1263.6 | 272.048 | 0 | 1 | 13
7265 | 10/30 | 16:00:00 | 285.15 | 98841 | 6.7 | 160 | 7.3418 | 248.4 | 360 | 271.097 | 0 | 1 | 12
7266 | 10/30 | 17:00:00 | 285.15 | 98841 | 7.2 | 160 | 7.8591 | 10.8 | 0 | 271.323 | 0 | 1 | 12
7267 | 10/30 | 18:00:00 | 285.15 | 98841 | 6.7 | 170 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
7268 | 10/30 | 19:00:00 | 285.15 | 98841 | 6.7 | 170 | 7.8591 | 0 | 0 | 271.323 | 0 | 1 | 12
7269 | 10/30 | 20:00:00 | 284.15 | 98833 | 6.2 | 160 | 7.8598 | 0 | 0 | 269.94 | 0 | 1 | 11
7270 | 10/30 | 21:00:00 | 284.15 | 98833 | 5.7 | 150 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
7271 | 10/30 | 22:00:00 | 284.15 | 98833 | 5.7 | 160 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
7272 | 10/30 | 23:00:00 | 284.15 | 98833 | 5.7 | 150 | 7.8598 | 0 | 0 | 270.371 | 0 | 1 | 11
7273 | 10/30 | 24:00:00 | 284.15 | 98833 | 5.1 | 150 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
7274 | 10/31 | 01:00:00 | 284.15 | 98833 | 4.1 | 170 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7275 | 10/31 | 02:00:00 | 283.15 | 98824 | 4.6 | 160 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7276 | 10/31 | 03:00:00 | 283.15 | 98824 | 5.1 | 170 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7277 | 10/31 | 04:00:00 | 284.15 | 98833 | 2.6 | 160 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
7278 | 10/31 | 05:00:00 | 283.15 | 98824 | 1 | 189 | 7.8605 | 0 | 0 | 270.161 | 0 | 1 | 10
7279 | 10/31 | 06:00:00 | 284.15 | 98833 | 1.5 | 130 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
7280 | 10/31 | 07:00:00 | 285.15 | 98841 | 1.5 | 336 | 8.9926 | 0 | 0 | 272.517 | 0 | 1 | 12
7281 | 10/31 | 08:00:00 | 285.15 | 98841 | 2.6 | 240 | 8.9926 | 32.4 | 0 | 272.517 | 0 | 1 | 12
7282 | 10/31 | 09:00:00 | 285.15 | 98841 | 1.5 | 260 | 8.9926 | 327.6 | 374.4 | 272.036 | 0 | 1 | 12
7283 | 10/31 | 10:00:00 | 285.15 | 98841 | 3.1 | 250 | 8.4088 | 662.4 | 1234.8 | 271.813 | 0 | 1 | 12
7284 | 10/31 | 11:00:00 | 286.15 | 98850 | 4.6 | 260 | 8.408 | 918 | 1526.4 | 272.766 | 0 | 1 | 13
7285 | 10/31 | 12:00:00 | 287.15 | 98858 | 4.1 | 260 | 8.4073 | 1047.6 | 1609.2 | 273.719 | 0 | 1 | 14
7286 | 10/31 | 13:00:00 | 287.15 | 98858 | 4.1 | 250 | 8.4073 | 1022.4 | 1584 | 273.719 | 0 | 1 | 14
7287 | 10/31 | 14:00:00 | 287.15 | 98858 | 4.1 | 260 | 8.4073 | 900 | 1710 | 273.451 | 0 | 1 | 14
7288 | 10/31 | 15:00:00 | 287.15 | 98858 | 4.1 | 250 | 8.4073 | 594 | 1303.2 | 273.451 | 0 | 1 | 14
7289 | 10/31 | 16:00:00 | 287.15 | 98858 | 2.6 | 250 | 8.4073 | 234 | 450 | 273.451 | 0 | 1 | 14
7290 | 10/31 | 17:00:00 | 286.15 | 98850 | 2.6 | 220 | 7.8584 | 3.6 | 0 | 272.541 | 0 | 1 | 13
7291 | 10/31 | 18:00:00 | 285.15 | 98841 | 2.1 | 180 | 7.8591 | 0 | 0 | 271.588 | 0 | 1 | 12
7292 | 10/31 | 19:00:00 | 283.95 | 98831 | 2.2 | 220 | 7.4436 | 0 | 0 | 270.266 | 0 | 1 | 10.8
7293 | 10/31 | 20:00:00 | 283.65 | 98829 | 2.1 | 225 | 7.3427 | 0 | 0 | 269.671 | 0 | 1 | 10.5
7294 | 10/31 | 21:00:00 | 283.65 | 98829 | 1.9 | 227 | 7.3427 | 0 | 0 | 270.413 | 0 | 1 | 10.5
7295 | 10/31 | 22:00:00 | 281.35 | 98808 | 3 | 245 | 6.3998 | 0 | 0 | 267.77 | 0 | 1 | 8.2
7296 | 10/31 | 23:00:00 | 279.35 | 98790 | 4 | 275 | 5.6453 | 0 | 0 | 265.567 | 0 | 1 | 6.2
7297 | 10/31 | 24:00:00 | 277.35 | 98772 | 5.2 | 307 | 4.901 | 0 | 0 | 263.212 | 0 | 1 | 4.2
7298 | 11/1 | 01:00:00 | 275.15 | 98752 | 5.9 | 342 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
7299 | 11/1 | 02:00:00 | 275.15 | 98752 | 5.9 | 347 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7300 | 11/1 | 03:00:00 | 275.15 | 98752 | 6.1 | 347 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7301 | 11/1 | 04:00:00 | 275.15 | 98752 | 5.9 | 352 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7302 | 11/1 | 05:00:00 | 275.35 | 98755 | 6.1 | 350 | 4.1845 | 0 | 0 | 259.99 | 0 | 1 | 2.2
7303 | 11/1 | 06:00:00 | 275.65 | 98757 | 5.8 | 350 | 4.1844 | 0 | 0 | 260.274 | 0 | 1 | 2.5
7304 | 11/1 | 07:00:00 | 275.15 | 98752 | 5.7 | 360 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
7305 | 11/1 | 08:00:00 | 276.15 | 98762 | 5.7 | 350 | 4.1841 | 57.6 | 0 | 261.001 | 0 | 1 | 3
7306 | 11/1 | 09:00:00 | 276.15 | 98762 | 5.1 | 350 | 4.1841 | 334.8 | 450 | 261.001 | 0 | 1 | 3
7307 | 11/1 | 10:00:00 | 277.15 | 98771 | 5.7 | 330 | 4.4973 | 374.4 | 39.6 | 262.64 | 0 | 1 | 4
7308 | 11/1 | 11:00:00 | 278.15 | 98780 | 5.7 | 330 | 4.4968 | 990 | 1515.6 | 262.865 | 0 | 1 | 5
7309 | 11/1 | 12:00:00 | 279.15 | 98789 | 6.2 | 330 | 4.4964 | 1062 | 1468.8 | 264.069 | 0 | 1 | 6
7310 | 11/1 | 13:00:00 | 279.15 | 98789 | 6.2 | 360 | 4.4964 | 1036.8 | 1447.2 | 264.069 | 0 | 1 | 6
7311 | 11/1 | 14:00:00 | 279.15 | 98789 | 5.1 | 350 | 4.4964 | 914.4 | 1742.4 | 263.81 | 0 | 1 | 6
7312 | 11/1 | 15:00:00 | 279.15 | 98789 | 6.7 | 350 | 4.183 | 604.8 | 1054.8 | 263.578 | 0 | 1 | 6
7313 | 11/1 | 16:00:00 | 278.15 | 98780 | 5.7 | 340 | 4.1834 | 237.6 | 266.4 | 262.634 | 0 | 1 | 5
7314 | 11/1 | 17:00:00 | 277.15 | 98771 | 4.1 | 350 | 4.1838 | 3.6 | 0 | 261.69 | 0 | 1 | 4
7315 | 11/1 | 18:00:00 | 277.15 | 98771 | 4.6 | 350 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
7316 | 11/1 | 19:00:00 | 276.15 | 98762 | 4.6 | 10 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
7317 | 11/1 | 20:00:00 | 275.15 | 98752 | 3.6 | 350 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7318 | 11/1 | 21:00:00 | 276.15 | 98762 | 3.6 | 20 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
7319 | 11/1 | 22:00:00 | 275.15 | 98752 | 4.1 | 10 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7320 | 11/1 | 23:00:00 | 276.15 | 98762 | 4.1 | 20 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
7321 | 11/1 | 24:00:00 | 275.15 | 98752 | 3.1 | 30 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7322 | 11/2 | 01:00:00 | 276.15 | 98762 | 3.6 | 20 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
7323 | 11/2 | 02:00:00 | 275.15 | 98752 | 4.1 | 20 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7324 | 11/2 | 03:00:00 | 275.15 | 98752 | 4.1 | 20 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7325 | 11/2 | 04:00:00 | 275.15 | 98752 | 4.1 | 10 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
7326 | 11/2 | 05:00:00 | 276.15 | 98762 | 4.6 | 10 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
7327 | 11/2 | 06:00:00 | 276.15 | 98762 | 4.6 | 20 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
7328 | 11/2 | 07:00:00 | 276.15 | 98762 | 4.1 | 10 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
7329 | 11/2 | 08:00:00 | 276.15 | 98762 | 4.6 | 10 | 4.4977 | 54 | 0 | 261.231 | 0 | 1 | 3
7330 | 11/2 | 09:00:00 | 277.15 | 98771 | 4.1 | 20 | 4.8316 | 338.4 | 730.8 | 262.149 | 0 | 1 | 4
7331 | 11/2 | 10:00:00 | 278.15 | 98780 | 5.1 | 10 | 5.1875 | 694.8 | 1440 | 263.323 | 0 | 1 | 5
7332 | 11/2 | 11:00:00 | 279.15 | 98789 | 4.6 | 20 | 5.187 | 910.8 | 1288.8 | 264.528 | 0 | 1 | 6
7333 | 11/2 | 12:00:00 | 279.15 | 98789 | 4.1 | 20 | 5.187 | 1040.4 | 1659.6 | 264.528 | 0 | 1 | 6
7334 | 11/2 | 13:00:00 | 281.15 | 98806 | 5.1 | 50 | 4.8299 | 1076.4 | 1969.2 | 265.932 | 0 | 1 | 8
7335 | 11/2 | 14:00:00 | 282.15 | 98815 | 6.2 | 50 | 4.8294 | 892.8 | 1717.2 | 266.878 | 0 | 1 | 9
7336 | 11/2 | 15:00:00 | 281.15 | 98806 | 6.2 | 50 | 4.8299 | 583.2 | 1216.8 | 265.932 | 0 | 1 | 8
7337 | 11/2 | 16:00:00 | 280.15 | 98798 | 5.7 | 40 | 4.8303 | 223.2 | 327.6 | 264.986 | 0 | 1 | 7
7338 | 11/2 | 17:00:00 | 279.15 | 98789 | 4.6 | 30 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
7339 | 11/2 | 18:00:00 | 279.15 | 98789 | 5.7 | 30 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
7340 | 11/2 | 19:00:00 | 278.15 | 98780 | 5.1 | 20 | 5.1875 | 0 | 0 | 263.323 | 0 | 1 | 5
7341 | 11/2 | 20:00:00 | 278.15 | 98780 | 5.7 | 20 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
7342 | 11/2 | 21:00:00 | 278.15 | 98780 | 7.2 | 10 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7343 | 11/2 | 22:00:00 | 278.15 | 98780 | 6.7 | 10 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
7344 | 11/2 | 23:00:00 | 278.15 | 98780 | 8.2 | 20 | 4.4968 | 0 | 0 | 263.588 | 0 | 1 | 5
7345 | 11/2 | 24:00:00 | 278.15 | 98780 | 7.2 | 20 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
7346 | 11/3 | 01:00:00 | 278.15 | 98780 | 8.2 | 20 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
7347 | 11/3 | 02:00:00 | 279.15 | 98789 | 8.2 | 20 | 4.4964 | 0 | 0 | 264.536 | 0 | 1 | 6
7348 | 11/3 | 03:00:00 | 279.15 | 98789 | 8.2 | 20 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
7349 | 11/3 | 04:00:00 | 278.15 | 98780 | 7.7 | 10 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7350 | 11/3 | 05:00:00 | 278.15 | 98780 | 8.7 | 10 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7351 | 11/3 | 06:00:00 | 279.15 | 98789 | 8.7 | 10 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
7352 | 11/3 | 07:00:00 | 278.15 | 98780 | 8.7 | 10 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7353 | 11/3 | 08:00:00 | 279.15 | 98789 | 8.2 | 10 | 4.8307 | 46.8 | 0 | 264.299 | 0 | 1 | 6
7354 | 11/3 | 09:00:00 | 279.15 | 98789 | 8.2 | 20 | 4.8307 | 324 | 669.6 | 264.041 | 0 | 1 | 6
7355 | 11/3 | 10:00:00 | 279.15 | 98789 | 8.7 | 20 | 5.187 | 637.2 | 1173.6 | 264.528 | 0 | 1 | 6
7356 | 11/3 | 11:00:00 | 279.15 | 98789 | 7.7 | 20 | 5.187 | 892.8 | 1486.8 | 264.528 | 0 | 1 | 6
7357 | 11/3 | 12:00:00 | 280.15 | 98798 | 8.7 | 10 | 5.1865 | 1018.8 | 1335.6 | 265.476 | 0 | 1 | 7
7358 | 11/3 | 13:00:00 | 280.15 | 98798 | 8.2 | 10 | 5.5661 | 550.8 | 194.4 | 266.174 | 0 | 1 | 7
7359 | 11/3 | 14:00:00 | 280.15 | 98798 | 8.7 | 20 | 6.4005 | 453.6 | 28.8 | 266.628 | 0 | 1 | 7
7360 | 11/3 | 15:00:00 | 280.15 | 98798 | 7.2 | 20 | 5.9703 | 295.2 | 0 | 266.402 | 0 | 1 | 7
7361 | 11/3 | 16:00:00 | 280.15 | 98798 | 6.7 | 10 | 5.9703 | 111.6 | 0 | 266.402 | 0 | 1 | 7
7362 | 11/3 | 17:00:00 | 280.15 | 98798 | 7.2 | 10 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
7363 | 11/3 | 18:00:00 | 279.15 | 98789 | 6.7 | 360 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
7364 | 11/3 | 19:00:00 | 279.15 | 98789 | 7.2 | 360 | 5.9708 | 0 | 0 | 265.451 | 0 | 1 | 6
7365 | 11/3 | 20:00:00 | 280.15 | 98798 | 7.2 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7366 | 11/3 | 21:00:00 | 280.15 | 98798 | 4.6 | 20 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7367 | 11/3 | 22:00:00 | 280.15 | 98798 | 2.6 | 40 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7368 | 11/3 | 23:00:00 | 281.15 | 98806 | 3.1 | 40 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7369 | 11/3 | 24:00:00 | 281.15 | 98806 | 3.6 | 40 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7370 | 11/4 | 01:00:00 | 281.15 | 98806 | 3.6 | 40 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7371 | 11/4 | 02:00:00 | 280.15 | 98798 | 3.1 | 40 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7372 | 11/4 | 03:00:00 | 280.15 | 98798 | 3.1 | 40 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7373 | 11/4 | 04:00:00 | 280.15 | 98798 | 2.1 | 40 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7374 | 11/4 | 05:00:00 | 280.15 | 98798 | 3.1 | 20 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7375 | 11/4 | 06:00:00 | 279.15 | 98789 | 2.1 | 30 | 5.9708 | 0 | 0 | 264.723 | 0 | 1 | 6
7376 | 11/4 | 07:00:00 | 279.15 | 98789 | 3.1 | 30 | 5.9708 | 0 | 0 | 264.723 | 0 | 1 | 6
7377 | 11/4 | 08:00:00 | 279.15 | 98789 | 3.1 | 20 | 5.5666 | 18 | 0 | 265.332 | 0 | 1 | 6
7378 | 11/4 | 09:00:00 | 279.15 | 98789 | 3.1 | 20 | 5.9708 | 97.2 | 0 | 265.559 | 0 | 1 | 6
7379 | 11/4 | 10:00:00 | 279.15 | 98789 | 3.1 | 30 | 5.9708 | 619.2 | 885.6 | 264.982 | 0 | 1 | 6
7380 | 11/4 | 11:00:00 | 281.15 | 98806 | 3.1 | 30 | 6.4 | 871.2 | 1144.8 | 267.107 | 0 | 1 | 8
7381 | 11/4 | 12:00:00 | 281.15 | 98806 | 3.1 | 40 | 6.4 | 554.4 | 93.6 | 267.58 | 0 | 1 | 8
7382 | 11/4 | 13:00:00 | 282.15 | 98815 | 3.6 | 40 | 6.3994 | 540 | 90 | 268.532 | 0 | 1 | 9
7383 | 11/4 | 14:00:00 | 282.15 | 98815 | 3.6 | 40 | 6.3994 | 802.8 | 1080 | 268.057 | 0 | 1 | 9
7384 | 11/4 | 15:00:00 | 282.15 | 98815 | 3.6 | 30 | 6.3994 | 514.8 | 752.4 | 268.057 | 0 | 1 | 9
7385 | 11/4 | 16:00:00 | 282.15 | 98815 | 4.6 | 30 | 5.9692 | 104.4 | 0 | 268.304 | 0 | 1 | 9
7386 | 11/4 | 17:00:00 | 281.15 | 98806 | 4.6 | 20 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
7387 | 11/4 | 18:00:00 | 281.15 | 98806 | 3.6 | 40 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
7388 | 11/4 | 19:00:00 | 281.15 | 98806 | 4.1 | 50 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
7389 | 11/4 | 20:00:00 | 281.15 | 98806 | 3.1 | 50 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
7390 | 11/4 | 21:00:00 | 280.15 | 98798 | 4.1 | 50 | 5.5661 | 0 | 0 | 266.282 | 0 | 1 | 7
7391 | 11/4 | 22:00:00 | 280.15 | 98798 | 3.1 | 40 | 5.5661 | 0 | 0 | 266.282 | 0 | 1 | 7
7392 | 11/4 | 23:00:00 | 280.15 | 98798 | 4.1 | 30 | 5.5661 | 0 | 0 | 266.282 | 0 | 1 | 7
7393 | 11/4 | 24:00:00 | 280.15 | 98798 | 3.6 | 40 | 5.5661 | 0 | 0 | 266.282 | 0 | 1 | 7
7394 | 11/5 | 01:00:00 | 280.15 | 98798 | 4.6 | 30 | 5.5661 | 0 | 0 | 266.282 | 0 | 1 | 7
7395 | 11/5 | 02:00:00 | 280.15 | 98798 | 4.1 | 30 | 5.5661 | 0 | 0 | 266.282 | 0 | 1 | 7
7396 | 11/5 | 03:00:00 | 280.15 | 98798 | 4.6 | 20 | 5.5661 | 0 | 0 | 266.282 | 0 | 1 | 7
7397 | 11/5 | 04:00:00 | 280.15 | 98798 | 4.1 | 30 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
7398 | 11/5 | 05:00:00 | 280.15 | 98798 | 4.6 | 30 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
7399 | 11/5 | 06:00:00 | 280.15 | 98798 | 5.1 | 30 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
7400 | 11/5 | 07:00:00 | 280.15 | 98798 | 5.1 | 30 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
7401 | 11/5 | 08:00:00 | 280.15 | 98798 | 5.1 | 30 | 6.4005 | 21.6 | 0 | 266.628 | 0 | 1 | 7
7402 | 11/5 | 09:00:00 | 280.15 | 98798 | 5.1 | 30 | 6.4005 | 154.8 | 0 | 266.628 | 0 | 1 | 7
7403 | 11/5 | 10:00:00 | 280.15 | 98798 | 5.1 | 30 | 6.4005 | 205.2 | 0 | 266.736 | 0 | 1 | 7
7404 | 11/5 | 11:00:00 | 280.15 | 98798 | 5.1 | 20 | 6.4005 | 288 | 0 | 266.736 | 0 | 1 | 7
7405 | 11/5 | 12:00:00 | 280.15 | 98798 | 4.1 | 30 | 6.4005 | 543.6 | 90 | 266.628 | 0 | 1 | 7
7406 | 11/5 | 13:00:00 | 281.15 | 98806 | 3.6 | 30 | 6.4 | 529.2 | 90 | 267.58 | 0 | 1 | 8
7407 | 11/5 | 14:00:00 | 281.15 | 98806 | 3.6 | 10 | 6.8577 | 435.6 | 28.8 | 267.805 | 0 | 1 | 8
7408 | 11/5 | 15:00:00 | 281.15 | 98806 | 4.6 | 20 | 6.8577 | 277.2 | 0 | 267.805 | 0 | 1 | 8
7409 | 11/5 | 16:00:00 | 281.15 | 98806 | 4.1 | 20 | 6.8577 | 97.2 | 0 | 267.805 | 0 | 1 | 8
7410 | 11/5 | 17:00:00 | 281.15 | 98806 | 3.6 | 20 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7411 | 11/5 | 18:00:00 | 281.15 | 98806 | 4.6 | 20 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
7412 | 11/5 | 19:00:00 | 281.15 | 98806 | 3.6 | 20 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
7413 | 11/5 | 20:00:00 | 281.15 | 98806 | 3.6 | 30 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7414 | 11/5 | 21:00:00 | 281.15 | 98806 | 3.6 | 30 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7415 | 11/5 | 22:00:00 | 281.15 | 98806 | 3.6 | 30 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7416 | 11/5 | 23:00:00 | 281.15 | 98806 | 3.6 | 20 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7417 | 11/5 | 24:00:00 | 281.15 | 98806 | 4 | 223 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
7418 | 11/6 | 01:00:00 | 281.15 | 98806 | 4.5 | 228 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
7419 | 11/6 | 02:00:00 | 281.15 | 98806 | 4.9 | 350 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
7420 | 11/6 | 03:00:00 | 281.15 | 98806 | 5.3 | 340 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
7421 | 11/6 | 04:00:00 | 281.15 | 98806 | 5.8 | 140 | 6.8577 | 0 | 0 | 267.914 | 0 | 1 | 8
7422 | 11/6 | 05:00:00 | 281.15 | 98806 | 6.2 | 10 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7423 | 11/6 | 06:00:00 | 280.15 | 98798 | 4.6 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7424 | 11/6 | 07:00:00 | 280.15 | 98798 | 4.6 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7425 | 11/6 | 08:00:00 | 280.15 | 98798 | 3.6 | 360 | 6.4005 | 18 | 0 | 266.628 | 0 | 1 | 7
7426 | 11/6 | 09:00:00 | 280.15 | 98798 | 4.1 | 20 | 6.4005 | 147.6 | 0 | 266.628 | 0 | 1 | 7
7427 | 11/6 | 10:00:00 | 280.15 | 98798 | 5.1 | 20 | 6.4005 | 324 | 7.2 | 266.628 | 0 | 1 | 7
7428 | 11/6 | 11:00:00 | 280.15 | 98798 | 4.6 | 20 | 5.9703 | 464.4 | 50.4 | 266.402 | 0 | 1 | 7
7429 | 11/6 | 12:00:00 | 280.15 | 98798 | 4.6 | 10 | 6.4005 | 532.8 | 90 | 266.628 | 0 | 1 | 7
7430 | 11/6 | 13:00:00 | 280.15 | 98798 | 3.6 | 10 | 6.4005 | 518.4 | 86.4 | 266.628 | 0 | 1 | 7
7431 | 11/6 | 14:00:00 | 280.15 | 98798 | 4.6 | 10 | 6.4005 | 424.8 | 25.2 | 266.628 | 0 | 1 | 7
7432 | 11/6 | 15:00:00 | 280.15 | 98798 | 4.1 | 10 | 5.9703 | 270 | 0 | 266.402 | 0 | 1 | 7
7433 | 11/6 | 16:00:00 | 280.15 | 98798 | 3.6 | 10 | 5.9703 | 90 | 0 | 266.402 | 0 | 1 | 7
7434 | 11/6 | 17:00:00 | 280.15 | 98798 | 4.1 | 10 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
7435 | 11/6 | 18:00:00 | 280.15 | 98798 | 3.1 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7436 | 11/6 | 19:00:00 | 280.15 | 98798 | 3.6 | 350 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7437 | 11/6 | 20:00:00 | 280.15 | 98798 | 3.1 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7438 | 11/6 | 21:00:00 | 280.15 | 98798 | 3.6 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7439 | 11/6 | 22:00:00 | 280.15 | 98798 | 3.1 | 20 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
7440 | 11/6 | 23:00:00 | 280.15 | 98798 | 2.6 | 10 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
7441 | 11/6 | 24:00:00 | 280.15 | 98798 | 2.6 | 10 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
7442 | 11/7 | 01:00:00 | 280.15 | 98798 | 2.6 | 20 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
7443 | 11/7 | 02:00:00 | 280.15 | 98798 | 2.6 | 20 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
7444 | 11/7 | 03:00:00 | 280.15 | 98798 | 2.1 | 10 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
7445 | 11/7 | 04:00:00 | 280.15 | 98798 | 3.1 | 350 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
7446 | 11/7 | 05:00:00 | 280.15 | 98798 | 2.6 | 360 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7447 | 11/7 | 06:00:00 | 280.15 | 98798 | 2.6 | 350 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7448 | 11/7 | 07:00:00 | 280.15 | 98798 | 2.6 | 350 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7449 | 11/7 | 08:00:00 | 281.15 | 98806 | 3.1 | 360 | 6.8577 | 14.4 | 0 | 267.805 | 0 | 1 | 8
7450 | 11/7 | 09:00:00 | 281.15 | 98806 | 2.1 | 360 | 6.8577 | 140.4 | 0 | 267.805 | 0 | 1 | 8
7451 | 11/7 | 10:00:00 | 281.15 | 98806 | 3.1 | 350 | 6.4 | 316.8 | 7.2 | 267.58 | 0 | 1 | 8
7452 | 11/7 | 11:00:00 | 281.15 | 98806 | 2.6 | 360 | 6.8577 | 453.6 | 46.8 | 267.805 | 0 | 1 | 8
7453 | 11/7 | 12:00:00 | 281.15 | 98806 | 2.1 | 350 | 6.8577 | 522 | 86.4 | 267.805 | 0 | 1 | 8
7454 | 11/7 | 13:00:00 | 282.15 | 98815 | 2.6 | 20 | 6.8571 | 507.6 | 57.6 | 268.758 | 0 | 1 | 9
7455 | 11/7 | 14:00:00 | 282.15 | 98815 | 1 | 272 | 6.8571 | 417.6 | 25.2 | 268.758 | 0 | 1 | 9
7456 | 11/7 | 15:00:00 | 282.15 | 98815 | 0.5 | 146 | 6.8571 | 259.2 | 0 | 268.758 | 0 | 1 | 9
7457 | 11/7 | 16:00:00 | 281.15 | 98806 | 0.5 | 254 | 6.8577 | 86.4 | 0 | 267.805 | 0 | 1 | 8
7458 | 11/7 | 17:00:00 | 281.15 | 98806 | 1.5 | 160 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7459 | 11/7 | 18:00:00 | 281.15 | 98806 | 2.6 | 160 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7460 | 11/7 | 19:00:00 | 281.15 | 98806 | 2.1 | 150 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7461 | 11/7 | 20:00:00 | 281.15 | 98806 | 2.1 | 150 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7462 | 11/7 | 21:00:00 | 281.15 | 98806 | 2.6 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7463 | 11/7 | 22:00:00 | 281.15 | 98806 | 2.6 | 160 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
7464 | 11/7 | 23:00:00 | 281.15 | 98806 | 3.1 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7465 | 11/7 | 24:00:00 | 281.15 | 98806 | 4.1 | 140 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7466 | 11/8 | 01:00:00 | 280.15 | 98798 | 3.6 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7467 | 11/8 | 02:00:00 | 280.15 | 98798 | 4.6 | 130 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7468 | 11/8 | 03:00:00 | 280.15 | 98798 | 4.6 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7469 | 11/8 | 04:00:00 | 280.15 | 98798 | 4.1 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7470 | 11/8 | 05:00:00 | 280.15 | 98798 | 4.6 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7471 | 11/8 | 06:00:00 | 280.15 | 98798 | 3.6 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
7472 | 11/8 | 07:00:00 | 280.15 | 98798 | 4.6 | 140 | 6.4005 | 0 | 0 | 266.736 | 0 | 1 | 7
7473 | 11/8 | 08:00:00 | 280.15 | 98798 | 5.1 | 130 | 6.4005 | 7.2 | 0 | 266.736 | 0 | 1 | 7
7474 | 11/8 | 09:00:00 | 280.15 | 98798 | 4.6 | 150 | 6.4005 | 82.8 | 0 | 266.736 | 0 | 1 | 7
7475 | 11/8 | 10:00:00 | 281.15 | 98806 | 3.6 | 170 | 6.8577 | 306 | 10.8 | 267.805 | 0 | 1 | 8
7476 | 11/8 | 11:00:00 | 282.15 | 98815 | 4.1 | 200 | 6.8571 | 849.6 | 1310.4 | 268.021 | 0 | 1 | 9
7477 | 11/8 | 12:00:00 | 283.15 | 98824 | 5.1 | 210 | 5.5646 | 928.8 | 1328.4 | 268.55 | 0 | 1 | 10
7478 | 11/8 | 13:00:00 | 282.15 | 98815 | 5.1 | 210 | 5.5651 | 903.6 | 1303.2 | 267.601 | 0 | 1 | 9
7479 | 11/8 | 14:00:00 | 283.15 | 98824 | 4.1 | 210 | 5.9687 | 734.4 | 1310.4 | 268.779 | 0 | 1 | 10
7480 | 11/8 | 15:00:00 | 284.15 | 98833 | 5.1 | 190 | 5.5641 | 457.2 | 896.4 | 269.498 | 0 | 1 | 11
7481 | 11/8 | 16:00:00 | 283.15 | 98824 | 5.7 | 190 | 5.1851 | 154.8 | 176.4 | 268.056 | 0 | 1 | 10
7482 | 11/8 | 17:00:00 | 282.15 | 98815 | 5.7 | 180 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
7483 | 11/8 | 18:00:00 | 280.15 | 98798 | 4.1 | 180 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
7484 | 11/8 | 19:00:00 | 280.15 | 98798 | 4.6 | 190 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
7485 | 11/8 | 20:00:00 | 280.15 | 98798 | 5.1 | 190 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
7486 | 11/8 | 21:00:00 | 279.15 | 98789 | 4.6 | 210 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
7487 | 11/8 | 22:00:00 | 279.15 | 98789 | 4.6 | 180 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
7488 | 11/8 | 23:00:00 | 279.15 | 98789 | 3.1 | 170 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
7489 | 11/8 | 24:00:00 | 279.15 | 98789 | 3.4 | 275 | 4.9352 | 0 | 0 | 264.725 | 0 | 1 | 6
7490 | 11/9 | 01:00:00 | 279.15 | 98789 | 3.8 | 156 | 5.0777 | 0 | 0 | 264.816 | 0 | 1 | 6
7491 | 11/9 | 02:00:00 | 279.15 | 98789 | 4.1 | 262 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
7492 | 11/9 | 03:00:00 | 279.15 | 98789 | 4.4 | 240 | 5.2984 | 0 | 0 | 265.065 | 0 | 1 | 6
7493 | 11/9 | 04:00:00 | 279.15 | 98789 | 4.8 | 351 | 5.4502 | 0 | 0 | 265.156 | 0 | 1 | 6
7494 | 11/9 | 05:00:00 | 279.15 | 98789 | 5.1 | 150 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
7495 | 11/9 | 06:00:00 | 279.15 | 98789 | 6.7 | 150 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
7496 | 11/9 | 07:00:00 | 279.15 | 98789 | 5.1 | 140 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
7497 | 11/9 | 08:00:00 | 279.15 | 98789 | 6.2 | 140 | 5.9708 | 7.2 | 0 | 265.451 | 0 | 1 | 6
7498 | 11/9 | 09:00:00 | 280.15 | 98798 | 5.7 | 150 | 6.4005 | 126 | 0 | 266.628 | 0 | 1 | 7
7499 | 11/9 | 10:00:00 | 281.15 | 98806 | 5.1 | 160 | 6.8577 | 540 | 799.2 | 267.332 | 0 | 1 | 8
7500 | 11/9 | 11:00:00 | 283.15 | 98824 | 6.2 | 170 | 6.8564 | 784.8 | 1368 | 269.234 | 0 | 1 | 10
7501 | 11/9 | 12:00:00 | 284.15 | 98833 | 8.7 | 190 | 7.3425 | 903.6 | 1288.8 | 270.411 | 0 | 1 | 11
7502 | 11/9 | 13:00:00 | 284.15 | 98833 | 7.7 | 200 | 6.3982 | 885.6 | 1278 | 269.957 | 0 | 1 | 11
7503 | 11/9 | 14:00:00 | 284.15 | 98833 | 6.2 | 200 | 6.3982 | 720 | 1288.8 | 269.957 | 0 | 1 | 11
7504 | 11/9 | 15:00:00 | 285.15 | 98841 | 5.7 | 200 | 6.3977 | 442.8 | 835.2 | 270.907 | 0 | 1 | 12
7505 | 11/9 | 16:00:00 | 284.15 | 98833 | 6.2 | 190 | 5.9681 | 133.2 | 97.2 | 269.728 | 0 | 1 | 11
7506 | 11/9 | 17:00:00 | 283.15 | 98824 | 5.1 | 190 | 5.9687 | 0 | 0 | 268.516 | 0 | 1 | 10
7507 | 11/9 | 18:00:00 | 282.15 | 98815 | 5.1 | 170 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
7508 | 11/9 | 19:00:00 | 282.15 | 98815 | 7.2 | 150 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
7509 | 11/9 | 20:00:00 | 283.15 | 98824 | 5.1 | 160 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
7510 | 11/9 | 21:00:00 | 282.15 | 98815 | 7.7 | 160 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
7511 | 11/9 | 22:00:00 | 282.15 | 98815 | 7.2 | 150 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
7512 | 11/9 | 23:00:00 | 280.15 | 98798 | 5.1 | 240 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
7513 | 11/9 | 24:00:00 | 280.15 | 98798 | 6.7 | 250 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
7514 | 11/10 | 01:00:00 | 279.75 | 98794 | 7 | 260 | 5.6451 | 0 | 0 | 265.84 | 0 | 1 | 6.6
7515 | 11/10 | 02:00:00 | 279.35 | 98790 | 7.3 | 4 | 5.3359 | 0 | 0 | 265.278 | 0 | 1 | 6.2
7516 | 11/10 | 03:00:00 | 278.95 | 98787 | 7.6 | 148 | 5.0418 | 0 | 0 | 264.604 | 0 | 1 | 5.8
7517 | 11/10 | 04:00:00 | 278.55 | 98783 | 7.9 | 84 | 4.7624 | 0 | 0 | 264.041 | 0 | 1 | 5.4
7518 | 11/10 | 05:00:00 | 278.15 | 98780 | 8.2 | 240 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
7519 | 11/10 | 06:00:00 | 277.15 | 98771 | 7.7 | 230 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
7520 | 11/10 | 07:00:00 | 277.15 | 98771 | 5.7 | 230 | 3.8896 | 0 | 0 | 261.458 | 0 | 1 | 4
7521 | 11/10 | 08:00:00 | 277.15 | 98771 | 7.7 | 220 | 4.1838 | 7.2 | 0 | 261.69 | 0 | 1 | 4
7522 | 11/10 | 09:00:00 | 277.15 | 98771 | 7.7 | 210 | 4.1838 | 234 | 280.8 | 261.69 | 0 | 1 | 4
7523 | 11/10 | 10:00:00 | 278.15 | 98780 | 8.2 | 210 | 4.1834 | 561.6 | 1105.2 | 262.634 | 0 | 1 | 5
7524 | 11/10 | 11:00:00 | 278.15 | 98780 | 7.2 | 200 | 4.4968 | 774 | 1195.2 | 263.123 | 0 | 1 | 5
7525 | 11/10 | 12:00:00 | 279.15 | 98789 | 7.7 | 210 | 4.4964 | 900 | 1216.8 | 264.069 | 0 | 1 | 6
7526 | 11/10 | 13:00:00 | 279.15 | 98789 | 7.7 | 210 | 4.4964 | 486 | 86.4 | 264.536 | 0 | 1 | 6
7527 | 11/10 | 14:00:00 | 278.15 | 98780 | 3.6 | 200 | 5.1875 | 392.4 | 36 | 264.047 | 0 | 1 | 5
7528 | 11/10 | 15:00:00 | 278.15 | 98780 | 3.1 | 300 | 5.5671 | 432 | 662.4 | 263.807 | 0 | 1 | 5
7529 | 11/10 | 16:00:00 | 280.15 | 98798 | 7.2 | 210 | 5.5661 | 68.4 | 0 | 266.174 | 0 | 1 | 7
7530 | 11/10 | 17:00:00 | 280.15 | 98798 | 8.2 | 210 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
7531 | 11/10 | 18:00:00 | 279.15 | 98789 | 7.2 | 200 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
7532 | 11/10 | 19:00:00 | 278.15 | 98780 | 4.6 | 190 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
7533 | 11/10 | 20:00:00 | 277.15 | 98771 | 3.6 | 170 | 5.1879 | 0 | 0 | 263.098 | 0 | 1 | 4
7534 | 11/10 | 21:00:00 | 278.15 | 98780 | 3.6 | 170 | 5.5671 | 0 | 0 | 264.274 | 0 | 1 | 5
7535 | 11/10 | 22:00:00 | 279.15 | 98789 | 8.7 | 240 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
7536 | 11/10 | 23:00:00 | 279.15 | 98789 | 8.2 | 230 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
7537 | 11/10 | 24:00:00 | 278.85 | 98786 | 8.1 | 44 | 4.9354 | 0 | 0 | 264.44 | 0 | 1 | 5.7
7538 | 11/11 | 01:00:00 | 278.45 | 98783 | 8 | 200 | 4.7284 | 0 | 0 | 263.923 | 0 | 1 | 5.3
7539 | 11/11 | 02:00:00 | 278.15 | 98780 | 7.9 | 4 | 4.4968 | 0 | 0 | 263.478 | 0 | 1 | 5
7540 | 11/11 | 03:00:00 | 277.85 | 98777 | 7.9 | 175 | 4.2754 | 0 | 0 | 262.917 | 0 | 1 | 4.7
7541 | 11/11 | 04:00:00 | 277.45 | 98774 | 7.8 | 243 | 4.0935 | 0 | 0 | 262.4 | 0 | 1 | 4.3
7542 | 11/11 | 05:00:00 | 277.15 | 98771 | 7.7 | 220 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
7543 | 11/11 | 06:00:00 | 277.15 | 98771 | 8.2 | 230 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
7544 | 11/11 | 07:00:00 | 277.15 | 98771 | 8.7 | 230 | 3.8896 | 0 | 0 | 261.458 | 0 | 1 | 4
7545 | 11/11 | 08:00:00 | 277.15 | 98771 | 7.7 | 220 | 4.1838 | 3.6 | 0 | 261.69 | 0 | 1 | 4
7546 | 11/11 | 09:00:00 | 278.15 | 98780 | 6.7 | 220 | 4.1834 | 223.2 | 277.2 | 262.215 | 0 | 1 | 5
7547 | 11/11 | 10:00:00 | 279.15 | 98789 | 6.2 | 210 | 4.4964 | 543.6 | 1242 | 263.81 | 0 | 1 | 6
7548 | 11/11 | 11:00:00 | 279.15 | 98789 | 5.1 | 200 | 4.4964 | 759.6 | 1184.4 | 264.069 | 0 | 1 | 6
7549 | 11/11 | 12:00:00 | 278.15 | 98780 | 6.7 | 220 | 4.8311 | 882 | 1306.8 | 263.352 | 0 | 1 | 5
7550 | 11/11 | 13:00:00 | 278.15 | 98780 | 5.1 | 200 | 4.8311 | 856.8 | 1281.6 | 263.352 | 0 | 1 | 5
7551 | 11/11 | 14:00:00 | 278.15 | 98780 | 5.1 | 210 | 4.8311 | 691.2 | 1011.6 | 263.352 | 0 | 1 | 5
7552 | 11/11 | 15:00:00 | 278.15 | 98780 | 4.6 | 200 | 4.8311 | 234 | 0 | 263.818 | 0 | 1 | 5
7553 | 11/11 | 16:00:00 | 278.15 | 98780 | 4.1 | 210 | 4.8311 | 64.8 | 0 | 263.818 | 0 | 1 | 5
7554 | 11/11 | 17:00:00 | 279.15 | 98789 | 4.1 | 210 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
7555 | 11/11 | 18:00:00 | 279.15 | 98789 | 3.1 | 210 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
7556 | 11/11 | 19:00:00 | 279.15 | 98789 | 6.2 | 220 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
7557 | 11/11 | 20:00:00 | 278.15 | 98780 | 5.1 | 200 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
7558 | 11/11 | 21:00:00 | 278.15 | 98780 | 5.1 | 210 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
7559 | 11/11 | 22:00:00 | 278.15 | 98780 | 4.1 | 210 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
7560 | 11/11 | 23:00:00 | 279.15 | 98789 | 7.2 | 210 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
7561 | 11/11 | 24:00:00 | 279.15 | 98789 | 6.7 | 220 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
7562 | 11/12 | 01:00:00 | 279.15 | 98789 | 6.4 | 45 | 4.9002 | 0 | 0 | 264.702 | 0 | 1 | 6
7563 | 11/12 | 02:00:00 | 279.15 | 98789 | 6.1 | 42 | 4.9705 | 0 | 0 | 264.748 | 0 | 1 | 6
7564 | 11/12 | 03:00:00 | 279.15 | 98789 | 5.7 | 46 | 5.0417 | 0 | 0 | 264.793 | 0 | 1 | 6
7565 | 11/12 | 04:00:00 | 279.15 | 98789 | 5.4 | 195 | 5.1139 | 0 | 0 | 264.839 | 0 | 1 | 6
7566 | 11/12 | 05:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
7567 | 11/12 | 06:00:00 | 280.15 | 98798 | 5.7 | 240 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
7568 | 11/12 | 07:00:00 | 280.15 | 98798 | 6.7 | 250 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
7569 | 11/12 | 08:00:00 | 280.15 | 98798 | 10.3 | 250 | 5.1865 | 0 | 0 | 265.216 | 0 | 1 | 7
7570 | 11/12 | 09:00:00 | 280.15 | 98798 | 10.3 | 260 | 4.8303 | 208.8 | 324 | 264.986 | 0 | 1 | 7
7571 | 11/12 | 10:00:00 | 280.15 | 98798 | 11.3 | 260 | 5.1865 | 529.2 | 1213.2 | 265.216 | 0 | 1 | 7
7572 | 11/12 | 11:00:00 | 281.15 | 98806 | 12.9 | 260 | 4.8299 | 745.2 | 1170 | 266.193 | 0 | 1 | 8
7573 | 11/12 | 12:00:00 | 280.15 | 98798 | 10.3 | 250 | 5.1865 | 864 | 1508.4 | 265.476 | 0 | 1 | 7
7574 | 11/12 | 13:00:00 | 281.15 | 98806 | 11.3 | 250 | 4.8299 | 892.8 | 1404 | 265.932 | 0 | 1 | 8
7575 | 11/12 | 14:00:00 | 281.15 | 98806 | 12.3 | 250 | 5.1861 | 374.4 | 46.8 | 266.895 | 0 | 1 | 8
7576 | 11/12 | 15:00:00 | 280.15 | 98798 | 14.4 | 260 | 5.1865 | 226.8 | 0 | 265.946 | 0 | 1 | 7
7577 | 11/12 | 16:00:00 | 280.15 | 98798 | 12.9 | 260 | 5.5661 | 61.2 | 0 | 266.174 | 0 | 1 | 7
7578 | 11/12 | 17:00:00 | 280.15 | 98798 | 12.9 | 260 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
7579 | 11/12 | 18:00:00 | 280.15 | 98798 | 12.9 | 260 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
7580 | 11/12 | 19:00:00 | 280.15 | 98798 | 11.3 | 260 | 4.8303 | 0 | 0 | 265.246 | 0 | 1 | 7
7581 | 11/12 | 20:00:00 | 280.15 | 98798 | 11.3 | 260 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
7582 | 11/12 | 21:00:00 | 279.15 | 98789 | 9.3 | 260 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
7583 | 11/12 | 22:00:00 | 280.15 | 98798 | 7.7 | 260 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
7584 | 11/12 | 23:00:00 | 280.15 | 98798 | 7.2 | 260 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
7585 | 11/12 | 24:00:00 | 280.15 | 98798 | 6.7 | 270 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
7586 | 11/13 | 01:00:00 | 279.95 | 98796 | 6.6 | 348 | 5.8057 | 0 | 0 | 266.121 | 0 | 1 | 6.8
7587 | 11/13 | 02:00:00 | 279.75 | 98794 | 6.5 | 79 | 5.6451 | 0 | 0 | 265.84 | 0 | 1 | 6.6
7588 | 11/13 | 03:00:00 | 279.55 | 98792 | 6.4 | 215 | 5.4886 | 0 | 0 | 265.559 | 0 | 1 | 6.4
7589 | 11/13 | 04:00:00 | 279.35 | 98790 | 6.3 | 219 | 5.3359 | 0 | 0 | 265.278 | 0 | 1 | 6.2
7590 | 11/13 | 05:00:00 | 279.15 | 98789 | 6.2 | 290 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
7591 | 11/13 | 06:00:00 | 279.15 | 98789 | 5.7 | 300 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
7592 | 11/13 | 07:00:00 | 279.15 | 98789 | 4.6 | 280 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
7593 | 11/13 | 08:00:00 | 279.15 | 98789 | 6.2 | 300 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
7594 | 11/13 | 09:00:00 | 279.15 | 98789 | 5.7 | 290 | 4.8307 | 187.2 | 226.8 | 264.299 | 0 | 1 | 6
7595 | 11/13 | 10:00:00 | 280.15 | 98798 | 4.6 | 290 | 5.1865 | 514.8 | 1148.4 | 265.216 | 0 | 1 | 7
7596 | 11/13 | 11:00:00 | 281.15 | 98806 | 4.1 | 280 | 5.1861 | 770.4 | 1609.2 | 266.163 | 0 | 1 | 8
7597 | 11/13 | 12:00:00 | 281.15 | 98806 | 4.1 | 290 | 5.1861 | 900 | 1537.2 | 266.163 | 0 | 1 | 8
7598 | 11/13 | 13:00:00 | 282.15 | 98815 | 5.1 | 290 | 5.1856 | 874.8 | 1508.4 | 267.11 | 0 | 1 | 9
7599 | 11/13 | 14:00:00 | 282.15 | 98815 | 4.1 | 290 | 5.1856 | 702 | 1530 | 267.11 | 0 | 1 | 9
7600 | 11/13 | 15:00:00 | 281.15 | 98806 | 3.1 | 280 | 5.1861 | 417.6 | 986.4 | 266.163 | 0 | 1 | 8
7601 | 11/13 | 16:00:00 | 281.15 | 98806 | 3.1 | 270 | 5.1861 | 111.6 | 93.6 | 266.163 | 0 | 1 | 8
7602 | 11/13 | 17:00:00 | 279.15 | 98789 | 4.1 | 290 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
7603 | 11/13 | 18:00:00 | 278.15 | 98780 | 3.6 | 270 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7604 | 11/13 | 19:00:00 | 278.15 | 98780 | 2.6 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
7605 | 11/13 | 20:00:00 | 277.15 | 98771 | 2.1 | 300 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
7606 | 11/13 | 21:00:00 | 276.15 | 98762 | 1 | 346 | 4.832 | 0 | 0 | 262.027 | 0 | 1 | 3
7607 | 11/13 | 22:00:00 | 277.15 | 98771 | 1 | 43 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
7608 | 11/13 | 23:00:00 | 277.15 | 98771 | 1 | 193 | 5.1879 | 0 | 0 | 262.376 | 0 | 1 | 4
7609 | 11/13 | 24:00:00 | 277.15 | 98771 | 1.5 | 76 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
7610 | 11/14 | 01:00:00 | 277.55 | 98774 | 2.1 | 25 | 4.9009 | 0 | 0 | 263.295 | 0 | 1 | 4.4
7611 | 11/14 | 02:00:00 | 277.95 | 98778 | 2.7 | 224 | 4.971 | 0 | 0 | 263.72 | 0 | 1 | 4.8
7612 | 11/14 | 03:00:00 | 278.35 | 98781 | 3.4 | 181 | 5.0422 | 0 | 0 | 264.145 | 0 | 1 | 5.2
7613 | 11/14 | 04:00:00 | 278.75 | 98785 | 4 | 78 | 5.1141 | 0 | 0 | 264.571 | 0 | 1 | 5.6
7614 | 11/14 | 05:00:00 | 279.15 | 98789 | 4.6 | 220 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
7615 | 11/14 | 06:00:00 | 279.15 | 98789 | 5.1 | 240 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
7616 | 11/14 | 07:00:00 | 279.15 | 98789 | 6.2 | 230 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
7617 | 11/14 | 08:00:00 | 280.15 | 98798 | 6.7 | 230 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
7618 | 11/14 | 09:00:00 | 280.15 | 98798 | 5.1 | 210 | 5.5661 | 97.2 | 0 | 266.174 | 0 | 1 | 7
7619 | 11/14 | 10:00:00 | 281.15 | 98806 | 4.6 | 230 | 5.9698 | 259.2 | 0 | 267.353 | 0 | 1 | 8
7620 | 11/14 | 11:00:00 | 280.15 | 98798 | 4.1 | 230 | 6.4005 | 392.4 | 36 | 266.628 | 0 | 1 | 7
7621 | 11/14 | 12:00:00 | 281.15 | 98806 | 3.6 | 230 | 6.8577 | 457.2 | 50.4 | 267.805 | 0 | 1 | 8
7622 | 11/14 | 13:00:00 | 281.15 | 98806 | 5.7 | 220 | 6.8577 | 446.4 | 46.8 | 267.805 | 0 | 1 | 8
7623 | 11/14 | 14:00:00 | 282.15 | 98815 | 4.1 | 220 | 6.8571 | 356.4 | 18 | 268.758 | 0 | 1 | 9
7624 | 11/14 | 15:00:00 | 282.15 | 98815 | 4.1 | 210 | 7.3438 | 208.8 | 0 | 268.983 | 0 | 1 | 9
7625 | 11/14 | 16:00:00 | 283.15 | 98824 | 5.7 | 240 | 7.3431 | 57.6 | 0 | 269.936 | 0 | 1 | 10
7626 | 11/14 | 17:00:00 | 283.15 | 98824 | 6.7 | 250 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
7627 | 11/14 | 18:00:00 | 284.15 | 98833 | 8.7 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7628 | 11/14 | 19:00:00 | 284.15 | 98833 | 9.3 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7629 | 11/14 | 20:00:00 | 284.15 | 98833 | 8.2 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7630 | 11/14 | 21:00:00 | 284.15 | 98833 | 11.3 | 260 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
7631 | 11/14 | 22:00:00 | 284.15 | 98833 | 6.7 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7632 | 11/14 | 23:00:00 | 284.15 | 98833 | 8.2 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7633 | 11/14 | 24:00:00 | 284.15 | 98833 | 6.7 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7634 | 11/15 | 01:00:00 | 284.15 | 98833 | 7 | 237 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
7635 | 11/15 | 02:00:00 | 284.15 | 98833 | 7.3 | 243 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
7636 | 11/15 | 03:00:00 | 284.15 | 98833 | 7.6 | 226 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
7637 | 11/15 | 04:00:00 | 284.15 | 98833 | 7.9 | 240 | 7.8598 | 0 | 0 | 271.225 | 0 | 1 | 11
7638 | 11/15 | 05:00:00 | 284.15 | 98833 | 8.2 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7639 | 11/15 | 06:00:00 | 284.15 | 98833 | 5.1 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7640 | 11/15 | 07:00:00 | 284.15 | 98833 | 6.2 | 260 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
7641 | 11/15 | 08:00:00 | 284.15 | 98833 | 5.1 | 260 | 8.4095 | 0 | 0 | 271.339 | 0 | 1 | 11
7642 | 11/15 | 09:00:00 | 284.15 | 98833 | 6.7 | 250 | 8.4095 | 90 | 0 | 271.339 | 0 | 1 | 11
7643 | 11/15 | 10:00:00 | 284.15 | 98833 | 6.2 | 250 | 8.4095 | 252 | 0 | 271.339 | 0 | 1 | 11
7644 | 11/15 | 11:00:00 | 284.15 | 98833 | 5.1 | 260 | 7.8598 | 381.6 | 32.4 | 271.115 | 0 | 1 | 11
7645 | 11/15 | 12:00:00 | 284.15 | 98833 | 9.8 | 260 | 7.8598 | 450 | 46.8 | 271.115 | 0 | 1 | 11
7646 | 11/15 | 13:00:00 | 284.15 | 98833 | 7.7 | 250 | 7.8598 | 435.6 | 43.2 | 271.115 | 0 | 1 | 11
7647 | 11/15 | 14:00:00 | 284.15 | 98833 | 8.7 | 250 | 7.3425 | 349.2 | 14.4 | 270.89 | 0 | 1 | 11
7648 | 11/15 | 15:00:00 | 284.15 | 98833 | 6.2 | 250 | 7.3425 | 205.2 | 0 | 270.89 | 0 | 1 | 11
7649 | 11/15 | 16:00:00 | 284.15 | 98833 | 7.2 | 250 | 6.8558 | 54 | 0 | 270.663 | 0 | 1 | 11
7650 | 11/15 | 17:00:00 | 284.15 | 98833 | 10.8 | 250 | 6.8558 | 0 | 0 | 270.663 | 0 | 1 | 11
7651 | 11/15 | 18:00:00 | 284.15 | 98833 | 10.3 | 250 | 6.8558 | 0 | 0 | 270.185 | 0 | 1 | 11
7652 | 11/15 | 19:00:00 | 284.15 | 98833 | 6.2 | 250 | 6.8558 | 0 | 0 | 270.185 | 0 | 1 | 11
7653 | 11/15 | 20:00:00 | 284.15 | 98833 | 8.7 | 250 | 6.3982 | 0 | 0 | 269.957 | 0 | 1 | 11
7654 | 11/15 | 21:00:00 | 284.15 | 98833 | 9.3 | 250 | 6.3982 | 0 | 0 | 269.957 | 0 | 1 | 11
7655 | 11/15 | 22:00:00 | 283.15 | 98824 | 7.2 | 240 | 6.3988 | 0 | 0 | 268.744 | 0 | 1 | 10
7656 | 11/15 | 23:00:00 | 283.15 | 98824 | 11.8 | 250 | 6.3988 | 0 | 0 | 268.744 | 0 | 1 | 10
7657 | 11/15 | 24:00:00 | 284.15 | 98833 | 13.9 | 260 | 6.3982 | 0 | 0 | 270.204 | 0 | 1 | 11
7658 | 11/16 | 01:00:00 | 284.15 | 98833 | 13.4 | 266 | 6.5325 | 0 | 0 | 270.273 | 0 | 1 | 11
7659 | 11/16 | 02:00:00 | 284.15 | 98833 | 12.9 | 37 | 6.6694 | 0 | 0 | 270.341 | 0 | 1 | 11
7660 | 11/16 | 03:00:00 | 284.15 | 98833 | 12.4 | 345 | 6.8088 | 0 | 0 | 270.527 | 0 | 1 | 11
7661 | 11/16 | 04:00:00 | 284.15 | 98833 | 11.8 | 120 | 6.9031 | 0 | 0 | 270.572 | 0 | 1 | 11
7662 | 11/16 | 05:00:00 | 284.15 | 98833 | 11.3 | 69 | 7.0469 | 0 | 0 | 270.64 | 0 | 1 | 11
7663 | 11/16 | 06:00:00 | 284.15 | 98833 | 7.4 | 229 | 7.1933 | 0 | 0 | 270.708 | 0 | 1 | 11
7664 | 11/16 | 07:00:00 | 284.15 | 98833 | 7.7 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7665 | 11/16 | 08:00:00 | 284.15 | 98833 | 5.1 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
7666 | 11/16 | 09:00:00 | 284.15 | 98833 | 5.7 | 260 | 7.8598 | 86.4 | 0 | 271.115 | 0 | 1 | 11
7667 | 11/16 | 10:00:00 | 283.15 | 98824 | 3.6 | 250 | 6.8564 | 439.2 | 698.4 | 269.234 | 0 | 1 | 10
7668 | 11/16 | 11:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.8564 | 676.8 | 1267.2 | 269.234 | 0 | 1 | 10
7669 | 11/16 | 12:00:00 | 283.15 | 98824 | 4.6 | 250 | 6.8564 | 795.6 | 1224 | 269.234 | 0 | 1 | 10
7670 | 11/16 | 13:00:00 | 283.15 | 98824 | 6.2 | 260 | 5.9687 | 777.6 | 1213.2 | 268.779 | 0 | 1 | 10
7671 | 11/16 | 14:00:00 | 284.15 | 98833 | 7.2 | 260 | 6.3982 | 619.2 | 1188 | 269.957 | 0 | 1 | 11
7672 | 11/16 | 15:00:00 | 283.15 | 98824 | 5.7 | 260 | 5.9687 | 381.6 | 766.8 | 268.516 | 0 | 1 | 10
7673 | 11/16 | 16:00:00 | 282.15 | 98815 | 4.1 | 260 | 5.9692 | 97.2 | 86.4 | 267.568 | 0 | 1 | 9
7674 | 11/16 | 17:00:00 | 281.15 | 98806 | 3.1 | 250 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
7675 | 11/16 | 18:00:00 | 281.15 | 98806 | 4.1 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
7676 | 11/16 | 19:00:00 | 281.15 | 98806 | 5.1 | 260 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
7677 | 11/16 | 20:00:00 | 281.15 | 98806 | 5.7 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
7678 | 11/16 | 21:00:00 | 281.15 | 98806 | 5.1 | 260 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
7679 | 11/16 | 22:00:00 | 280.15 | 98798 | 5.1 | 260 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
7680 | 11/16 | 23:00:00 | 281.15 | 98806 | 6.7 | 260 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
7681 | 11/16 | 24:00:00 | 281.15 | 98806 | 6.6 | 211 | 6.3118 | 0 | 0 | 267.535 | 0 | 1 | 8
7682 | 11/17 | 01:00:00 | 281.15 | 98806 | 6.5 | 192 | 6.2681 | 0 | 0 | 267.512 | 0 | 1 | 8
7683 | 11/17 | 02:00:00 | 281.15 | 98806 | 6.4 | 187 | 6.1815 | 0 | 0 | 267.467 | 0 | 1 | 8
7684 | 11/17 | 03:00:00 | 281.15 | 98806 | 6.4 | 217 | 6.096 | 0 | 0 | 267.421 | 0 | 1 | 8
7685 | 11/17 | 04:00:00 | 281.15 | 98806 | 6.3 | 31 | 6.0537 | 0 | 0 | 267.398 | 0 | 1 | 8
7686 | 11/17 | 05:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
7687 | 11/17 | 06:00:00 | 281.15 | 98806 | 7.7 | 270 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
7688 | 11/17 | 07:00:00 | 281.15 | 98806 | 10.8 | 270 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
7689 | 11/17 | 08:00:00 | 281.15 | 98806 | 6.7 | 280 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
7690 | 11/17 | 09:00:00 | 281.15 | 98806 | 6.2 | 300 | 5.9698 | 151.2 | 194.4 | 266.62 | 0 | 1 | 8
7691 | 11/17 | 10:00:00 | 281.15 | 98806 | 6.7 | 310 | 5.5656 | 453.6 | 1044 | 266.392 | 0 | 1 | 8
7692 | 11/17 | 11:00:00 | 281.15 | 98806 | 5.1 | 310 | 5.5656 | 705.6 | 1522.8 | 266.392 | 0 | 1 | 8
7693 | 11/17 | 12:00:00 | 281.15 | 98806 | 5.1 | 320 | 4.4957 | 835.2 | 1490.4 | 265.7 | 0 | 1 | 8
7694 | 11/17 | 13:00:00 | 281.15 | 98806 | 5.1 | 330 | 4.1823 | 817.2 | 1324.8 | 265.467 | 0 | 1 | 8
7695 | 11/17 | 14:00:00 | 282.15 | 98815 | 3.6 | 340 | 4.1819 | 648 | 1281.6 | 266.411 | 0 | 1 | 9
7696 | 11/17 | 15:00:00 | 281.15 | 98806 | 2.1 | 30 | 4.1823 | 370.8 | 856.8 | 265.467 | 0 | 1 | 8
7697 | 11/17 | 16:00:00 | 280.15 | 98798 | 1 | 151 | 4.1826 | 86.4 | 25.2 | 264.782 | 0 | 1 | 7
7698 | 11/17 | 17:00:00 | 280.15 | 98798 | 2.1 | 20 | 4.1826 | 0 | 0 | 265.25 | 0 | 1 | 7
7699 | 11/17 | 18:00:00 | 279.15 | 98789 | 1.5 | 195 | 4.183 | 0 | 0 | 264.303 | 0 | 1 | 6
7700 | 11/17 | 19:00:00 | 279.15 | 98789 | 1 | 189 | 4.183 | 0 | 0 | 263.837 | 0 | 1 | 6
7701 | 11/17 | 20:00:00 | 278.15 | 98780 | 1.5 | 30 | 4.1834 | 0 | 0 | 262.891 | 0 | 1 | 5
7702 | 11/17 | 21:00:00 | 278.15 | 98780 | 0.5 | 10 | 4.1834 | 0 | 0 | 262.634 | 0 | 1 | 5
7703 | 11/17 | 22:00:00 | 277.15 | 98771 | 0.5 | 60 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
7704 | 11/17 | 23:00:00 | 276.15 | 98762 | 0.5 | 350 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
7705 | 11/17 | 24:00:00 | 277.15 | 98771 | 0.5 | 180 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
7706 | 11/18 | 01:00:00 | 276.75 | 98767 | 0.7 | 80 | 4.1236 | 0 | 0 | 261.875 | 0 | 1 | 3.6
7707 | 11/18 | 02:00:00 | 276.35 | 98763 | 0.9 | 210 | 4.0643 | 0 | 0 | 261.45 | 0 | 1 | 3.2
7708 | 11/18 | 03:00:00 | 275.95 | 98760 | 1.1 | 251 | 4.0056 | 0 | 0 | 261.025 | 0 | 1 | 2.8
7709 | 11/18 | 04:00:00 | 275.55 | 98756 | 1.3 | 34 | 3.9478 | 0 | 0 | 260.601 | 0 | 1 | 2.4
7710 | 11/18 | 05:00:00 | 275.15 | 98752 | 1.5 | 160 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
7711 | 11/18 | 06:00:00 | 276.15 | 98762 | 2.6 | 160 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
7712 | 11/18 | 07:00:00 | 276.15 | 98762 | 3.1 | 150 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
7713 | 11/18 | 08:00:00 | 276.15 | 98762 | 4.1 | 160 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
7714 | 11/18 | 09:00:00 | 277.15 | 98771 | 2.6 | 160 | 4.4973 | 75.6 | 0 | 262.64 | 0 | 1 | 4
7715 | 11/18 | 10:00:00 | 277.15 | 98771 | 3.1 | 180 | 5.1879 | 417.6 | 676.8 | 262.633 | 0 | 1 | 4
7716 | 11/18 | 11:00:00 | 278.15 | 98780 | 3.1 | 170 | 5.1875 | 360 | 32.4 | 264.047 | 0 | 1 | 5
7717 | 11/18 | 12:00:00 | 278.15 | 98780 | 2.6 | 160 | 5.1875 | 428.4 | 46.8 | 264.047 | 0 | 1 | 5
7718 | 11/18 | 13:00:00 | 279.15 | 98789 | 3.6 | 180 | 5.5666 | 417.6 | 43.2 | 265.224 | 0 | 1 | 6
7719 | 11/18 | 14:00:00 | 279.15 | 98789 | 3.1 | 200 | 5.9708 | 327.6 | 10.8 | 265.451 | 0 | 1 | 6
7720 | 11/18 | 15:00:00 | 281.15 | 98806 | 4.6 | 220 | 6.4 | 187.2 | 0 | 267.58 | 0 | 1 | 8
7721 | 11/18 | 16:00:00 | 281.15 | 98806 | 4.1 | 230 | 6.4 | 46.8 | 0 | 267.58 | 0 | 1 | 8
7722 | 11/18 | 17:00:00 | 281.15 | 98806 | 4.1 | 220 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7723 | 11/18 | 18:00:00 | 281.15 | 98806 | 4.1 | 220 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7724 | 11/18 | 19:00:00 | 281.15 | 98806 | 5.1 | 210 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7725 | 11/18 | 20:00:00 | 281.15 | 98806 | 6.2 | 220 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7726 | 11/18 | 21:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7727 | 11/18 | 22:00:00 | 282.15 | 98815 | 3.6 | 220 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
7728 | 11/18 | 23:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7729 | 11/18 | 24:00:00 | 281.35 | 98808 | 3.6 | 114 | 6.8576 | 0 | 0 | 268.105 | 0 | 1 | 8.2
7730 | 11/19 | 01:00:00 | 281.45 | 98809 | 4.1 | 170 | 6.8575 | 0 | 0 | 268.2 | 0 | 1 | 8.3
7731 | 11/19 | 02:00:00 | 281.65 | 98811 | 4.7 | 7 | 6.8574 | 0 | 0 | 268.39 | 0 | 1 | 8.5
7732 | 11/19 | 03:00:00 | 281.85 | 98812 | 5.2 | 101 | 6.8573 | 0 | 0 | 268.581 | 0 | 1 | 8.7
7733 | 11/19 | 04:00:00 | 281.95 | 98814 | 5.7 | 72 | 6.8571 | 0 | 0 | 268.676 | 0 | 1 | 8.8
7734 | 11/19 | 05:00:00 | 282.15 | 98815 | 6.2 | 310 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
7735 | 11/19 | 06:00:00 | 282.15 | 98815 | 6.2 | 330 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
7736 | 11/19 | 07:00:00 | 282.15 | 98815 | 4.6 | 310 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
7737 | 11/19 | 08:00:00 | 280.15 | 98798 | 4.1 | 290 | 5.9703 | 0 | 0 | 265.671 | 0 | 1 | 7
7738 | 11/19 | 09:00:00 | 280.15 | 98798 | 6.2 | 300 | 5.5661 | 133.2 | 147.6 | 265.444 | 0 | 1 | 7
7739 | 11/19 | 10:00:00 | 280.15 | 98798 | 5.7 | 300 | 5.1865 | 428.4 | 1004.4 | 265.216 | 0 | 1 | 7
7740 | 11/19 | 11:00:00 | 281.15 | 98806 | 5.7 | 290 | 5.1861 | 561.6 | 529.2 | 266.667 | 0 | 1 | 8
7741 | 11/19 | 12:00:00 | 282.15 | 98815 | 6.2 | 310 | 5.1856 | 720 | 1216.8 | 267.495 | 0 | 1 | 9
7742 | 11/19 | 13:00:00 | 282.15 | 98815 | 4.6 | 300 | 5.5651 | 651.6 | 594 | 267.846 | 0 | 1 | 9
7743 | 11/19 | 14:00:00 | 283.15 | 98824 | 4.6 | 300 | 5.5646 | 619.2 | 1364.4 | 268.287 | 0 | 1 | 10
7744 | 11/19 | 15:00:00 | 282.15 | 98815 | 4.6 | 300 | 5.1856 | 349.2 | 799.2 | 267.11 | 0 | 1 | 9
7745 | 11/19 | 16:00:00 | 281.15 | 98806 | 4.1 | 270 | 5.5656 | 82.8 | 46.8 | 266.392 | 0 | 1 | 8
7746 | 11/19 | 17:00:00 | 280.15 | 98798 | 5.7 | 290 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
7747 | 11/19 | 18:00:00 | 280.15 | 98798 | 4.1 | 280 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
7748 | 11/19 | 19:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
7749 | 11/19 | 20:00:00 | 280.15 | 98798 | 7.2 | 280 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
7750 | 11/19 | 21:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
7751 | 11/19 | 22:00:00 | 280.15 | 98798 | 7.7 | 270 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
7752 | 11/19 | 23:00:00 | 280.15 | 98798 | 7.7 | 270 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
7753 | 11/19 | 24:00:00 | 280.35 | 98799 | 8.3 | 183 | 5.6448 | 0 | 0 | 266.41 | 0 | 1 | 7.2
7754 | 11/20 | 01:00:00 | 280.45 | 98801 | 8.9 | 275 | 5.6845 | 0 | 0 | 266.528 | 0 | 1 | 7.3
7755 | 11/20 | 02:00:00 | 280.65 | 98802 | 9.5 | 338 | 5.7648 | 0 | 0 | 266.764 | 0 | 1 | 7.5
7756 | 11/20 | 03:00:00 | 280.85 | 98803 | 10.1 | 180 | 5.846 | 0 | 0 | 266.999 | 0 | 1 | 7.7
7757 | 11/20 | 04:00:00 | 280.95 | 98805 | 10.7 | 265 | 5.887 | 0 | 0 | 267.117 | 0 | 1 | 7.8
7758 | 11/20 | 05:00:00 | 281.15 | 98806 | 11.3 | 280 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
7759 | 11/20 | 06:00:00 | 280.15 | 98798 | 10.3 | 270 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
7760 | 11/20 | 07:00:00 | 281.15 | 98806 | 8.7 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
7761 | 11/20 | 08:00:00 | 282.15 | 98815 | 10.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
7762 | 11/20 | 09:00:00 | 282.15 | 98815 | 11.3 | 280 | 6.3994 | 122.4 | 118.8 | 267.795 | 0 | 1 | 9
7763 | 11/20 | 10:00:00 | 283.15 | 98824 | 10.3 | 270 | 6.8564 | 414 | 993.6 | 268.971 | 0 | 1 | 10
7764 | 11/20 | 11:00:00 | 283.15 | 98824 | 7.7 | 270 | 6.8564 | 619.2 | 1180.8 | 269.234 | 0 | 1 | 10
7765 | 11/20 | 12:00:00 | 283.15 | 98824 | 7.7 | 270 | 6.8564 | 410.4 | 46.8 | 269.71 | 0 | 1 | 10
7766 | 11/20 | 13:00:00 | 283.15 | 98824 | 9.8 | 280 | 6.8564 | 399.6 | 39.6 | 269.71 | 0 | 1 | 10
7767 | 11/20 | 14:00:00 | 283.15 | 98824 | 9.8 | 260 | 6.8564 | 313.2 | 10.8 | 269.71 | 0 | 1 | 10
7768 | 11/20 | 15:00:00 | 283.15 | 98824 | 9.8 | 260 | 6.8564 | 176.4 | 0 | 269.71 | 0 | 1 | 10
7769 | 11/20 | 16:00:00 | 282.15 | 98815 | 10.3 | 280 | 6.3994 | 43.2 | 0 | 268.532 | 0 | 1 | 9
7770 | 11/20 | 17:00:00 | 282.15 | 98815 | 10.8 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
7771 | 11/20 | 18:00:00 | 282.15 | 98815 | 12.9 | 270 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
7772 | 11/20 | 19:00:00 | 282.15 | 98815 | 13.9 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
7773 | 11/20 | 20:00:00 | 282.15 | 98815 | 11.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
7774 | 11/20 | 21:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
7775 | 11/20 | 22:00:00 | 283.15 | 98824 | 8.2 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7776 | 11/20 | 23:00:00 | 283.15 | 98824 | 10.3 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7777 | 11/20 | 24:00:00 | 283.15 | 98824 | 10.2 | 143 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7778 | 11/21 | 01:00:00 | 283.15 | 98824 | 10.1 | 148 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7779 | 11/21 | 02:00:00 | 283.15 | 98824 | 10.1 | 349 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7780 | 11/21 | 03:00:00 | 283.15 | 98824 | 10 | 145 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7781 | 11/21 | 04:00:00 | 283.15 | 98824 | 9.9 | 207 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
7782 | 11/21 | 05:00:00 | 283.15 | 98824 | 9.8 | 290 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
7783 | 11/21 | 06:00:00 | 282.15 | 98815 | 6.7 | 270 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
7784 | 11/21 | 07:00:00 | 282.15 | 98815 | 7.7 | 280 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
7785 | 11/21 | 08:00:00 | 282.15 | 98815 | 8.2 | 280 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
7786 | 11/21 | 09:00:00 | 282.15 | 98815 | 9.3 | 280 | 5.1856 | 118.8 | 118.8 | 267.11 | 0 | 1 | 9
7787 | 11/21 | 10:00:00 | 282.15 | 98815 | 12.3 | 290 | 5.1856 | 403.2 | 982.8 | 267.11 | 0 | 1 | 9
7788 | 11/21 | 11:00:00 | 282.15 | 98815 | 12.9 | 290 | 4.8294 | 648 | 1458 | 266.878 | 0 | 1 | 9
7789 | 11/21 | 12:00:00 | 282.15 | 98815 | 12.9 | 280 | 5.1856 | 774 | 1652.4 | 267.11 | 0 | 1 | 9
7790 | 11/21 | 13:00:00 | 282.15 | 98815 | 11.3 | 280 | 5.1856 | 712.8 | 1353.6 | 267.371 | 0 | 1 | 9
7791 | 11/21 | 14:00:00 | 282.15 | 98815 | 11.3 | 280 | 5.1856 | 558 | 1144.8 | 267.371 | 0 | 1 | 9
7792 | 11/21 | 15:00:00 | 282.15 | 98815 | 9.3 | 270 | 5.1856 | 309.6 | 327.6 | 267.371 | 0 | 1 | 9
7793 | 11/21 | 16:00:00 | 281.15 | 98806 | 8.7 | 280 | 5.5656 | 72 | 3.6 | 266.653 | 0 | 1 | 8
7794 | 11/21 | 17:00:00 | 281.15 | 98806 | 9.8 | 270 | 5.1861 | 0 | 0 | 266.163 | 0 | 1 | 8
7795 | 11/21 | 18:00:00 | 281.15 | 98806 | 12.9 | 270 | 5.5656 | 0 | 0 | 266.392 | 0 | 1 | 8
7796 | 11/21 | 19:00:00 | 281.15 | 98806 | 13.4 | 270 | 5.1861 | 0 | 0 | 266.163 | 0 | 1 | 8
7797 | 11/21 | 20:00:00 | 281.15 | 98806 | 11.3 | 280 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
7798 | 11/21 | 21:00:00 | 281.15 | 98806 | 11.3 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
7799 | 11/21 | 22:00:00 | 281.15 | 98806 | 10.8 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
7800 | 11/21 | 23:00:00 | 281.15 | 98806 | 10.3 | 270 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
7801 | 11/21 | 24:00:00 | 280.95 | 98805 | 9.9 | 167 | 5.7646 | 0 | 0 | 266.937 | 0 | 1 | 7.8
7802 | 11/22 | 01:00:00 | 280.85 | 98803 | 9.6 | 124 | 5.5658 | 0 | 0 | 266.728 | 0 | 1 | 7.7
7803 | 11/22 | 02:00:00 | 280.65 | 98802 | 9.2 | 189 | 5.3731 | 0 | 0 | 266.423 | 0 | 1 | 7.5
7804 | 11/22 | 03:00:00 | 280.45 | 98801 | 8.9 | 257 | 5.1863 | 0 | 0 | 266.003 | 0 | 1 | 7.3
7805 | 11/22 | 04:00:00 | 280.35 | 98799 | 8.6 | 257 | 5.0055 | 0 | 0 | 265.793 | 0 | 1 | 7.2
7806 | 11/22 | 05:00:00 | 280.15 | 98798 | 8.2 | 310 | 4.8303 | 0 | 0 | 265.246 | 0 | 1 | 7
7807 | 11/22 | 06:00:00 | 279.15 | 98789 | 10.8 | 320 | 3.2912 | 0 | 0 | 262.874 | 0 | 1 | 6
7808 | 11/22 | 07:00:00 | 278.15 | 98780 | 11.3 | 310 | 3.2915 | 0 | 0 | 261.933 | 0 | 1 | 5
7809 | 11/22 | 08:00:00 | 278.15 | 98780 | 8.2 | 300 | 3.2915 | 0 | 0 | 261.933 | 0 | 1 | 5
7810 | 11/22 | 09:00:00 | 278.15 | 98780 | 10.8 | 300 | 3.2915 | 111.6 | 82.8 | 262.063 | 0 | 1 | 5
7811 | 11/22 | 10:00:00 | 278.15 | 98780 | 12.9 | 310 | 3.0253 | 392.4 | 860.4 | 261.696 | 0 | 1 | 5
7812 | 11/22 | 11:00:00 | 278.15 | 98780 | 11.3 | 310 | 2.7791 | 648 | 1346.4 | 261.323 | 0 | 1 | 5
7813 | 11/22 | 12:00:00 | 278.15 | 98780 | 9.8 | 300 | 2.5513 | 727.2 | 1443.6 | 261.473 | 0 | 1 | 5
7814 | 11/22 | 13:00:00 | 277.15 | 98771 | 6.2 | 310 | 4.1838 | 702 | 1051.2 | 261.946 | 0 | 1 | 4
7815 | 11/22 | 14:00:00 | 277.15 | 98771 | 6.2 | 290 | 4.1838 | 550.8 | 997.2 | 261.946 | 0 | 1 | 4
7816 | 11/22 | 15:00:00 | 279.15 | 98789 | 6.2 | 310 | 4.183 | 298.8 | 324 | 263.837 | 0 | 1 | 6
7817 | 11/22 | 16:00:00 | 276.15 | 98762 | 7.7 | 350 | 3.8899 | 36 | 0 | 261.231 | 0 | 1 | 3
7818 | 11/22 | 17:00:00 | 276.15 | 98762 | 7.7 | 330 | 3.5796 | 0 | 0 | 260.999 | 0 | 1 | 3
7819 | 11/22 | 18:00:00 | 276.15 | 98762 | 5.7 | 330 | 3.2921 | 0 | 0 | 260.764 | 0 | 1 | 3
7820 | 11/22 | 19:00:00 | 275.15 | 98752 | 4.6 | 330 | 3.2924 | 0 | 0 | 259.107 | 0 | 1 | 2
7821 | 11/22 | 20:00:00 | 274.15 | 98743 | 5.1 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
7822 | 11/22 | 21:00:00 | 274.15 | 98743 | 4.6 | 290 | 3.0265 | 0 | 0 | 258.305 | 0 | 1 | 1
7823 | 11/22 | 22:00:00 | 273.15 | 98734 | 4.1 | 280 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
7824 | 11/22 | 23:00:00 | 273.15 | 98734 | 5.7 | 290 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
7825 | 11/22 | 24:00:00 | 274.15 | 98743 | 6.2 | 290 | 3.0265 | 0 | 0 | 258.305 | 0 | 1 | 1
7826 | 11/23 | 01:00:00 | 274.15 | 98743 | 5.9 | 0 | 3.0781 | 0 | 0 | 258.352 | 0 | 1 | 1
7827 | 11/23 | 02:00:00 | 274.15 | 98743 | 5.6 | 211 | 3.157 | 0 | 0 | 258.538 | 0 | 1 | 1
7828 | 11/23 | 03:00:00 | 274.15 | 98743 | 5.4 | 223 | 3.2378 | 0 | 0 | 258.608 | 0 | 1 | 1
7829 | 11/23 | 04:00:00 | 274.15 | 98743 | 5.1 | 320 | 3.2927 | 0 | 0 | 258.166 | 0 | 1 | 1
7830 | 11/23 | 05:00:00 | 275.15 | 98752 | 7.2 | 310 | 3.2924 | 0 | 0 | 259.107 | 0 | 1 | 2
7831 | 11/23 | 06:00:00 | 274.15 | 98743 | 5.1 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
7832 | 11/23 | 07:00:00 | 274.15 | 98743 | 8.7 | 330 | 3.0265 | 0 | 0 | 257.932 | 0 | 1 | 1
7833 | 11/23 | 08:00:00 | 274.15 | 98743 | 7.7 | 300 | 3.2927 | 0 | 0 | 258.166 | 0 | 1 | 1
7834 | 11/23 | 09:00:00 | 274.15 | 98743 | 7.2 | 330 | 2.7801 | 100.8 | 50.4 | 257.95 | 0 | 1 | 1
7835 | 11/23 | 10:00:00 | 275.15 | 98752 | 5.1 | 330 | 3.0262 | 356.4 | 626.4 | 259.127 | 0 | 1 | 2
7836 | 11/23 | 11:00:00 | 275.15 | 98752 | 7.7 | 330 | 4.1846 | 622.8 | 1270.8 | 259.802 | 0 | 1 | 2
7837 | 11/23 | 12:00:00 | 275.15 | 98752 | 8.7 | 340 | 4.4981 | 748.8 | 1407.6 | 260.03 | 0 | 1 | 2
7838 | 11/23 | 13:00:00 | 275.15 | 98752 | 6.7 | 340 | 4.4981 | 730.8 | 1382.4 | 260.03 | 0 | 1 | 2
7839 | 11/23 | 14:00:00 | 275.15 | 98752 | 7.2 | 340 | 4.4981 | 572.4 | 1360.8 | 260.03 | 0 | 1 | 2
7840 | 11/23 | 15:00:00 | 274.15 | 98743 | 7.2 | 330 | 4.185 | 309.6 | 734.4 | 258.857 | 0 | 1 | 1
7841 | 11/23 | 16:00:00 | 273.15 | 98734 | 6.7 | 330 | 3.891 | 68.4 | 0 | 257.685 | 0 | 1 | 0
7842 | 11/23 | 17:00:00 | 273.15 | 98734 | 7.7 | 340 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
7843 | 11/23 | 18:00:00 | 273.15 | 98734 | 7.2 | 330 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
7844 | 11/23 | 19:00:00 | 273.15 | 98734 | 6.7 | 330 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
7845 | 11/23 | 20:00:00 | 272.15 | 98724 | 5.7 | 290 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
7846 | 11/23 | 21:00:00 | 272.15 | 98724 | 6.7 | 310 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
7847 | 11/23 | 22:00:00 | 271.15 | 98715 | 3.1 | 270 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7848 | 11/23 | 23:00:00 | 272.15 | 98724 | 3.1 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
7849 | 11/23 | 24:00:00 | 271.15 | 98715 | 4.1 | 270 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7850 | 11/24 | 01:00:00 | 271.15 | 98715 | 3.6 | 260 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7851 | 11/24 | 02:00:00 | 271.15 | 98715 | 3.6 | 250 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7852 | 11/24 | 03:00:00 | 271.15 | 98715 | 1.5 | 269 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7853 | 11/24 | 04:00:00 | 272.15 | 98724 | 2.6 | 200 | 3.581 | 0 | 0 | 256.513 | 0 | 1 | -1
7854 | 11/24 | 05:00:00 | 272.15 | 98724 | 3.6 | 200 | 3.581 | 0 | 0 | 256.764 | 0 | 1 | -1
7855 | 11/24 | 06:00:00 | 272.15 | 98724 | 6.2 | 190 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
7856 | 11/24 | 07:00:00 | 272.15 | 98724 | 3.6 | 170 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
7857 | 11/24 | 08:00:00 | 272.15 | 98724 | 4.1 | 170 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
7858 | 11/24 | 09:00:00 | 273.15 | 98734 | 2.6 | 220 | 3.891 | 54 | 0 | 258.394 | 0 | 1 | 0
7859 | 11/24 | 10:00:00 | 274.15 | 98743 | 3.6 | 260 | 4.185 | 367.2 | 882 | 258.857 | 0 | 1 | 1
7860 | 11/24 | 11:00:00 | 276.15 | 98762 | 5.1 | 280 | 4.4977 | 608.4 | 1414.8 | 260.975 | 0 | 1 | 3
7861 | 11/24 | 12:00:00 | 278.15 | 98780 | 5.7 | 310 | 4.8311 | 694.8 | 1350 | 263.352 | 0 | 1 | 5
7862 | 11/24 | 13:00:00 | 279.15 | 98789 | 8.2 | 280 | 4.8307 | 716.4 | 1591.2 | 264.041 | 0 | 1 | 6
7863 | 11/24 | 14:00:00 | 278.15 | 98780 | 9.8 | 280 | 4.4968 | 561.6 | 1346.4 | 262.865 | 0 | 1 | 5
7864 | 11/24 | 15:00:00 | 278.15 | 98780 | 9.8 | 290 | 4.4968 | 284.4 | 450 | 263.123 | 0 | 1 | 5
7865 | 11/24 | 16:00:00 | 278.15 | 98780 | 8.2 | 290 | 4.4968 | 61.2 | 0 | 263.123 | 0 | 1 | 5
7866 | 11/24 | 17:00:00 | 277.15 | 98771 | 8.7 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1 | 4
7867 | 11/24 | 18:00:00 | 278.15 | 98780 | 8.2 | 290 | 4.1834 | 0 | 0 | 262.634 | 0 | 1 | 5
7868 | 11/24 | 19:00:00 | 278.15 | 98780 | 9.3 | 290 | 3.8892 | 0 | 0 | 262.659 | 0 | 1 | 5
7869 | 11/24 | 20:00:00 | 277.15 | 98771 | 8.7 | 300 | 3.8896 | 0 | 0 | 261.458 | 0 | 1 | 4
7870 | 11/24 | 21:00:00 | 277.15 | 98771 | 7.2 | 280 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
7871 | 11/24 | 22:00:00 | 277.15 | 98771 | 7.7 | 280 | 3.8896 | 0 | 0 | 261.458 | 0 | 1 | 4
7872 | 11/24 | 23:00:00 | 277.15 | 98771 | 6.7 | 290 | 3.8896 | 0 | 0 | 261.458 | 0 | 1 | 4
7873 | 11/24 | 24:00:00 | 277.15 | 98771 | 7.2 | 300 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
7874 | 11/25 | 01:00:00 | 277.15 | 98771 | 5.7 | 300 | 3.8896 | 0 | 0 | 261.714 | 0 | 1 | 4
7875 | 11/25 | 02:00:00 | 276.15 | 98762 | 4.6 | 320 | 3.8899 | 0 | 0 | 260.515 | 0 | 1 | 3
7876 | 11/25 | 03:00:00 | 277.15 | 98771 | 5.7 | 350 | 4.1838 | 0 | 0 | 261.946 | 0 | 1 | 4
7877 | 11/25 | 04:00:00 | 277.15 | 98771 | 5.7 | 10 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
7878 | 11/25 | 05:00:00 | 277.15 | 98771 | 7.2 | 10 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
7879 | 11/25 | 06:00:00 | 276.15 | 98762 | 5.7 | 30 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
7880 | 11/25 | 07:00:00 | 276.15 | 98762 | 5.1 | 30 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
7881 | 11/25 | 08:00:00 | 276.15 | 98762 | 4.6 | 20 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
7882 | 11/25 | 09:00:00 | 276.15 | 98762 | 4.6 | 20 | 3.8899 | 97.2 | 75.6 | 260.515 | 0 | 1 | 3
7883 | 11/25 | 10:00:00 | 276.15 | 98762 | 4.6 | 30 | 3.8899 | 334.8 | 698.4 | 260.77 | 0 | 1 | 3
7884 | 11/25 | 11:00:00 | 278.15 | 98780 | 6.2 | 360 | 4.1834 | 561.6 | 1170 | 262.891 | 0 | 1 | 5
7885 | 11/25 | 12:00:00 | 277.15 | 98771 | 6.2 | 360 | 3.8896 | 684 | 1044 | 261.714 | 0 | 1 | 4
7886 | 11/25 | 13:00:00 | 278.15 | 98780 | 5.1 | 10 | 3.5789 | 669.6 | 1033.2 | 262.425 | 0 | 1 | 5
7887 | 11/25 | 14:00:00 | 277.15 | 98771 | 5.7 | 340 | 3.5793 | 550.8 | 1170 | 261.225 | 0 | 1 | 4
7888 | 11/25 | 15:00:00 | 277.15 | 98771 | 6.2 | 350 | 3.5793 | 291.6 | 702 | 261.225 | 0 | 1 | 4
7889 | 11/25 | 16:00:00 | 277.15 | 98771 | 9.3 | 350 | 4.1838 | 57.6 | 0 | 261.946 | 0 | 1 | 4
7890 | 11/25 | 17:00:00 | 275.15 | 98752 | 7.7 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
7891 | 11/25 | 18:00:00 | 276.15 | 98762 | 8.2 | 350 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
7892 | 11/25 | 19:00:00 | 275.15 | 98752 | 8.2 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
7893 | 11/25 | 20:00:00 | 275.15 | 98752 | 5.7 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
7894 | 11/25 | 21:00:00 | 275.15 | 98752 | 7.2 | 330 | 3.5799 | 0 | 0 | 259.34 | 0 | 1 | 2
7895 | 11/25 | 22:00:00 | 276.15 | 98762 | 8.2 | 330 | 3.2921 | 0 | 0 | 260.049 | 0 | 1 | 3
7896 | 11/25 | 23:00:00 | 276.15 | 98762 | 8.7 | 340 | 3.2921 | 0 | 0 | 260.049 | 0 | 1 | 3
7897 | 11/25 | 24:00:00 | 276.15 | 98762 | 7.7 | 330 | 3.2921 | 0 | 0 | 260.304 | 0 | 1 | 3
7898 | 11/26 | 01:00:00 | 276.15 | 98762 | 7.7 | 340 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
7899 | 11/26 | 02:00:00 | 276.15 | 98762 | 8.7 | 350 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
7900 | 11/26 | 03:00:00 | 276.15 | 98762 | 7.7 | 340 | 3.5796 | 0 | 0 | 260.283 | 0 | 1 | 3
7901 | 11/26 | 04:00:00 | 276.15 | 98762 | 7.2 | 330 | 3.5796 | 0 | 0 | 260.283 | 0 | 1 | 3
7902 | 11/26 | 05:00:00 | 275.15 | 98752 | 7.2 | 330 | 3.5799 | 0 | 0 | 259.34 | 0 | 1 | 2
7903 | 11/26 | 06:00:00 | 275.15 | 98752 | 7.7 | 320 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
7904 | 11/26 | 07:00:00 | 275.15 | 98752 | 7.7 | 320 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
7905 | 11/26 | 08:00:00 | 275.15 | 98752 | 7.7 | 310 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
7906 | 11/26 | 09:00:00 | 275.15 | 98752 | 8.2 | 320 | 3.2924 | 90 | 43.2 | 259.361 | 0 | 1 | 2
7907 | 11/26 | 10:00:00 | 276.15 | 98762 | 7.2 | 320 | 3.5796 | 345.6 | 842.4 | 260.283 | 0 | 1 | 3
7908 | 11/26 | 11:00:00 | 277.15 | 98771 | 7.2 | 330 | 3.5793 | 586.8 | 1407.6 | 261.225 | 0 | 1 | 4
7909 | 11/26 | 12:00:00 | 278.15 | 98780 | 8.2 | 340 | 3.5789 | 712.8 | 1249.2 | 262.168 | 0 | 1 | 5
7910 | 11/26 | 13:00:00 | 278.15 | 98780 | 6.7 | 340 | 3.5789 | 698.4 | 1227.6 | 262.168 | 0 | 1 | 5
7911 | 11/26 | 14:00:00 | 278.15 | 98780 | 6.7 | 340 | 3.5789 | 543.6 | 1159.2 | 262.168 | 0 | 1 | 5
7912 | 11/26 | 15:00:00 | 278.15 | 98780 | 6.2 | 340 | 3.2915 | 280.8 | 586.8 | 262.063 | 0 | 1 | 5
7913 | 11/26 | 16:00:00 | 277.15 | 98771 | 3.1 | 290 | 3.5793 | 54 | 0 | 261.603 | 0 | 1 | 4
7914 | 11/26 | 17:00:00 | 275.15 | 98752 | 4.1 | 280 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
7915 | 11/26 | 18:00:00 | 275.15 | 98752 | 4.6 | 290 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
7916 | 11/26 | 19:00:00 | 275.15 | 98752 | 5.1 | 280 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
7917 | 11/26 | 20:00:00 | 275.15 | 98752 | 4.6 | 270 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
7918 | 11/26 | 21:00:00 | 274.15 | 98743 | 4.1 | 270 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
7919 | 11/26 | 22:00:00 | 274.15 | 98743 | 5.1 | 250 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
7920 | 11/26 | 23:00:00 | 277.15 | 98771 | 6.2 | 260 | 4.1838 | 0 | 0 | 261.946 | 0 | 1 | 4
7921 | 11/26 | 24:00:00 | 278.15 | 98780 | 7.7 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
7922 | 11/27 | 01:00:00 | 278.75 | 98785 | 7.9 | 269 | 5.4121 | 0 | 0 | 264.861 | 0 | 1 | 5.6
7923 | 11/27 | 02:00:00 | 279.35 | 98790 | 8.1 | 237 | 5.6453 | 0 | 0 | 265.567 | 0 | 1 | 6.2
7924 | 11/27 | 03:00:00 | 279.95 | 98796 | 8.3 | 174 | 5.8875 | 0 | 0 | 266.274 | 0 | 1 | 6.8
7925 | 11/27 | 04:00:00 | 280.55 | 98801 | 8.5 | 241 | 6.139 | 0 | 0 | 266.981 | 0 | 1 | 7.4
7926 | 11/27 | 05:00:00 | 281.15 | 98806 | 8.7 | 280 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7927 | 11/27 | 06:00:00 | 281.15 | 98806 | 9.8 | 280 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
7928 | 11/27 | 07:00:00 | 281.15 | 98806 | 10.3 | 280 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
7929 | 11/27 | 08:00:00 | 282.15 | 98815 | 9.3 | 290 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
7930 | 11/27 | 09:00:00 | 281.15 | 98806 | 5.7 | 300 | 6.4 | 82.8 | 28.8 | 267.107 | 0 | 1 | 8
7931 | 11/27 | 10:00:00 | 282.15 | 98815 | 4.1 | 270 | 6.8571 | 313.2 | 550.8 | 268.283 | 0 | 1 | 9
7932 | 11/27 | 11:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.8571 | 295.2 | 10.8 | 268.758 | 0 | 1 | 9
7933 | 11/27 | 12:00:00 | 282.15 | 98815 | 2.1 | 230 | 6.8571 | 363.6 | 28.8 | 268.758 | 0 | 1 | 9
7934 | 11/27 | 13:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.8571 | 352.8 | 28.8 | 268.758 | 0 | 1 | 9
7935 | 11/27 | 14:00:00 | 282.15 | 98815 | 6.2 | 260 | 7.3438 | 273.6 | 0 | 268.983 | 0 | 1 | 9
7936 | 11/27 | 15:00:00 | 282.15 | 98815 | 6.2 | 260 | 6.8571 | 144 | 0 | 268.758 | 0 | 1 | 9
7937 | 11/27 | 16:00:00 | 281.15 | 98806 | 8.2 | 250 | 6.8577 | 28.8 | 0 | 267.805 | 0 | 1 | 8
7938 | 11/27 | 17:00:00 | 281.15 | 98806 | 7.2 | 260 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
7939 | 11/27 | 18:00:00 | 281.15 | 98806 | 5.7 | 240 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7940 | 11/27 | 19:00:00 | 281.15 | 98806 | 3.6 | 230 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7941 | 11/27 | 20:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
7942 | 11/27 | 21:00:00 | 282.15 | 98815 | 9.3 | 260 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
7943 | 11/27 | 22:00:00 | 281.15 | 98806 | 9.3 | 260 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
7944 | 11/27 | 23:00:00 | 281.15 | 98806 | 11.3 | 260 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
7945 | 11/27 | 24:00:00 | 281.15 | 98806 | 8.2 | 250 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
7946 | 11/28 | 01:00:00 | 281.15 | 98806 | 7.9 | 258 | 5.8869 | 0 | 0 | 267.195 | 0 | 1 | 8
7947 | 11/28 | 02:00:00 | 281.15 | 98806 | 7.6 | 128 | 5.8051 | 0 | 0 | 267.15 | 0 | 1 | 8
7948 | 11/28 | 03:00:00 | 281.15 | 98806 | 7.3 | 75 | 5.7242 | 0 | 0 | 267.104 | 0 | 1 | 8
7949 | 11/28 | 04:00:00 | 281.15 | 98806 | 7 | 94 | 5.6444 | 0 | 0 | 267.058 | 0 | 1 | 8
7950 | 11/28 | 05:00:00 | 281.15 | 98806 | 6.7 | 240 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
7951 | 11/28 | 06:00:00 | 281.15 | 98806 | 5.7 | 230 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
7952 | 11/28 | 07:00:00 | 280.15 | 98798 | 5.7 | 240 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
7953 | 11/28 | 08:00:00 | 280.15 | 98798 | 7.7 | 230 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
7954 | 11/28 | 09:00:00 | 280.15 | 98798 | 7.7 | 220 | 6.4005 | 79.2 | 57.6 | 266.157 | 0 | 1 | 7
7955 | 11/28 | 10:00:00 | 281.15 | 98806 | 9.8 | 220 | 5.9698 | 169.2 | 0 | 267.353 | 0 | 1 | 8
7956 | 11/28 | 11:00:00 | 282.15 | 98815 | 9.8 | 220 | 5.9692 | 291.6 | 7.2 | 268.304 | 0 | 1 | 9
7957 | 11/28 | 12:00:00 | 281.15 | 98806 | 7.7 | 220 | 5.9698 | 356.4 | 28.8 | 267.353 | 0 | 1 | 8
7958 | 11/28 | 13:00:00 | 281.15 | 98806 | 5.1 | 240 | 6.4 | 349.2 | 28.8 | 267.58 | 0 | 1 | 8
7959 | 11/28 | 14:00:00 | 281.15 | 98806 | 10.3 | 250 | 5.5656 | 518.4 | 982.8 | 266.392 | 0 | 1 | 8
7960 | 11/28 | 15:00:00 | 280.15 | 98798 | 6.7 | 260 | 5.5661 | 252 | 399.6 | 265.704 | 0 | 1 | 7
7961 | 11/28 | 16:00:00 | 280.15 | 98798 | 7.7 | 260 | 5.1865 | 46.8 | 0 | 265.476 | 0 | 1 | 7
7962 | 11/28 | 17:00:00 | 279.15 | 98789 | 6.2 | 250 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
7963 | 11/28 | 18:00:00 | 278.15 | 98780 | 4.6 | 240 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
7964 | 11/28 | 19:00:00 | 277.15 | 98771 | 4.1 | 240 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
7965 | 11/28 | 20:00:00 | 276.15 | 98762 | 4.1 | 250 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
7966 | 11/28 | 21:00:00 | 276.15 | 98762 | 4.1 | 230 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
7967 | 11/28 | 22:00:00 | 276.15 | 98762 | 2.1 | 190 | 4.1841 | 0 | 0 | 260.746 | 0 | 1 | 3
7968 | 11/28 | 23:00:00 | 275.15 | 98752 | 3.1 | 200 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
7969 | 11/28 | 24:00:00 | 275.15 | 98752 | 2.6 | 190 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
7970 | 11/29 | 01:00:00 | 275.15 | 98752 | 3.1 | 210 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
7971 | 11/29 | 02:00:00 | 275.15 | 98752 | 4.1 | 220 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
7972 | 11/29 | 03:00:00 | 274.15 | 98743 | 4.1 | 220 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
7973 | 11/29 | 04:00:00 | 274.15 | 98743 | 3.1 | 240 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
7974 | 11/29 | 05:00:00 | 274.15 | 98743 | 3.1 | 220 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
7975 | 11/29 | 06:00:00 | 274.15 | 98743 | 3.1 | 250 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
7976 | 11/29 | 07:00:00 | 274.15 | 98743 | 3.1 | 230 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
7977 | 11/29 | 08:00:00 | 274.15 | 98743 | 4.1 | 220 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
7978 | 11/29 | 09:00:00 | 273.15 | 98734 | 2.6 | 220 | 3.891 | 79.2 | 118.8 | 257.685 | 0 | 1 | 0
7979 | 11/29 | 10:00:00 | 273.15 | 98734 | 2.6 | 150 | 3.5806 | 316.8 | 781.2 | 257.455 | 0 | 1 | 0
7980 | 11/29 | 11:00:00 | 275.15 | 98752 | 1 | 322 | 3.8903 | 550.8 | 1188 | 259.572 | 0 | 1 | 2
7981 | 11/29 | 12:00:00 | 277.15 | 98771 | 2.1 | 260 | 3.8896 | 680.4 | 1213.2 | 261.458 | 0 | 1 | 4
7982 | 11/29 | 13:00:00 | 277.15 | 98771 | 2.6 | 180 | 4.1838 | 666 | 1555.2 | 261.69 | 0 | 1 | 4
7983 | 11/29 | 14:00:00 | 277.15 | 98771 | 1.5 | 170 | 4.1838 | 482.4 | 925.2 | 261.946 | 0 | 1 | 4
7984 | 11/29 | 15:00:00 | 277.15 | 98771 | 1 | 276 | 4.4973 | 248.4 | 270 | 262.177 | 0 | 1 | 4
7985 | 11/29 | 16:00:00 | 276.15 | 98762 | 1.5 | 130 | 4.1841 | 43.2 | 0 | 261.001 | 0 | 1 | 3
7986 | 11/29 | 17:00:00 | 275.15 | 98752 | 1.5 | 110 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
7987 | 11/29 | 18:00:00 | 275.15 | 98752 | 1.5 | 178 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
7988 | 11/29 | 19:00:00 | 274.15 | 98743 | 0.5 | 208 | 4.185 | 0 | 0 | 259.674 | 0 | 1 | 1
7989 | 11/29 | 20:00:00 | 273.15 | 98734 | 0.5 | 18 | 3.891 | 0 | 0 | 257.273 | 0 | 1 | 0
7990 | 11/29 | 21:00:00 | 273.15 | 98734 | 1 | 153 | 3.891 | 0 | 0 | 258.498 | 0 | 1 | 0
7991 | 11/29 | 22:00:00 | 272.15 | 98724 | 1.5 | 250 | 3.581 | 0 | 0 | 257.322 | 0 | 1 | -1
7992 | 11/29 | 23:00:00 | 271.15 | 98715 | 2.6 | 240 | 3.2936 | 0 | 0 | 256.043 | 0 | 1 | -2
7993 | 11/29 | 24:00:00 | 271.15 | 98715 | 0.5 | 211 | 3.2936 | 0 | 0 | 254.933 | 0 | 1 | -2
7994 | 11/30 | 01:00:00 | 271.15 | 98715 | 1 | 290 | 3.2936 | 0 | 0 | 254.933 | 0 | 1 | -2
7995 | 11/30 | 02:00:00 | 271.15 | 98715 | 1.5 | 260 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7996 | 11/30 | 03:00:00 | 271.15 | 98715 | 1 | 320 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7997 | 11/30 | 04:00:00 | 271.15 | 98715 | 1 | 270 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7998 | 11/30 | 05:00:00 | 271.15 | 98715 | 0.5 | 69 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
7999 | 11/30 | 06:00:00 | 271.15 | 98715 | 2.1 | 290 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
8000 | 11/30 | 07:00:00 | 271.15 | 98715 | 1.5 | 260 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
8001 | 11/30 | 08:00:00 | 270.15 | 98705 | 1.5 | 280 | 3.0276 | 0 | 0 | 253.763 | 0 | 1 | -3
8002 | 11/30 | 09:00:00 | 270.15 | 98705 | 1.5 | 300 | 2.7812 | 75.6 | 46.8 | 253.532 | 0 | 1 | -3
8003 | 11/30 | 10:00:00 | 270.15 | 98705 | 0.5 | 351 | 3.0276 | 309.6 | 795.6 | 253.763 | 0 | 1 | -3
8004 | 11/30 | 11:00:00 | 273.15 | 98734 | 1 | 313 | 3.5806 | 547.2 | 1220.4 | 257.044 | 0 | 1 | 0
8005 | 11/30 | 12:00:00 | 274.15 | 98743 | 1 | 238 | 3.2927 | 676.8 | 1256.4 | 257.754 | 0 | 1 | 1
8006 | 11/30 | 13:00:00 | 275.15 | 98752 | 1 | 41 | 4.1846 | 662.4 | 1224 | 259.387 | 0 | 1 | 2
8007 | 11/30 | 14:00:00 | 275.15 | 98752 | 2.1 | 350 | 3.8903 | 511.2 | 1184.4 | 259.157 | 0 | 1 | 2
8008 | 11/30 | 15:00:00 | 275.15 | 98752 | 1.5 | 20 | 3.8903 | 154.8 | 0 | 260.286 | 0 | 1 | 2
8009 | 11/30 | 16:00:00 | 274.15 | 98743 | 1.5 | 350 | 3.8907 | 18 | 0 | 259.445 | 0 | 1 | 1
8010 | 11/30 | 17:00:00 | 274.15 | 98743 | 0.5 | 340 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
8011 | 11/30 | 18:00:00 | 274.15 | 98743 | 1.5 | 350 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
8012 | 11/30 | 19:00:00 | 273.35 | 98736 | 2.4 | 278 | 3.5805 | 0 | 0 | 258.352 | 0 | 1 | 0.2
8013 | 11/30 | 20:00:00 | 273.35 | 98736 | 2.6 | 347 | 3.5805 | 0 | 0 | 258.352 | 0 | 1 | 0.2
8014 | 11/30 | 21:00:00 | 273.35 | 98736 | 2.7 | 340 | 3.5212 | 0 | 0 | 258.198 | 0 | 1 | 0.2
8015 | 11/30 | 22:00:00 | 273.35 | 98736 | 4 | 342 | 3.5805 | 0 | 0 | 258.352 | 0 | 1 | 0.2
8016 | 11/30 | 23:00:00 | 273.65 | 98739 | 5.1 | 345 | 3.6406 | 0 | 0 | 258.682 | 0 | 1 | 0.5
8017 | 11/30 | 24:00:00 | 274.15 | 98743 | 6.6 | 342 | 3.7325 | 0 | 0 | 259.115 | 0 | 1 | 1
8018 | 12/1 | 01:00:00 | 274.65 | 98748 | 7.2 | 350 | 3.8905 | 0 | 0 | 259.354 | 0 | 1 | 1.5
8019 | 12/1 | 02:00:00 | 274.95 | 98750 | 6.8 | 347 | 3.8904 | 0 | 0 | 259.637 | 0 | 1 | 1.8
8020 | 12/1 | 03:00:00 | 275.15 | 98752 | 6.2 | 347 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8021 | 12/1 | 04:00:00 | 275.15 | 98752 | 5.8 | 342 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8022 | 12/1 | 05:00:00 | 275.15 | 98752 | 5.7 | 342 | 3.948 | 0 | 0 | 259.872 | 0 | 1 | 2
8023 | 12/1 | 06:00:00 | 275.15 | 98752 | 5.4 | 340 | 4.0352 | 0 | 0 | 259.687 | 0 | 1 | 2
8024 | 12/1 | 07:00:00 | 275.15 | 98752 | 6.2 | 330 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8025 | 12/1 | 08:00:00 | 275.15 | 98752 | 5.1 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
8026 | 12/1 | 09:00:00 | 275.15 | 98752 | 5.1 | 340 | 4.1846 | 61.2 | 0 | 260.056 | 0 | 1 | 2
8027 | 12/1 | 10:00:00 | 275.15 | 98752 | 5.7 | 340 | 4.1846 | 270 | 338.4 | 260.056 | 0 | 1 | 2
8028 | 12/1 | 11:00:00 | 276.15 | 98762 | 6.7 | 340 | 4.1841 | 518.4 | 1137.6 | 260.746 | 0 | 1 | 3
8029 | 12/1 | 12:00:00 | 276.15 | 98762 | 6.2 | 350 | 4.1841 | 648 | 1177.2 | 260.746 | 0 | 1 | 3
8030 | 12/1 | 13:00:00 | 277.15 | 98771 | 7.2 | 360 | 4.1838 | 637.2 | 1162.8 | 261.69 | 0 | 1 | 4
8031 | 12/1 | 14:00:00 | 277.15 | 98771 | 7.2 | 10 | 3.8896 | 489.6 | 1087.2 | 261.458 | 0 | 1 | 4
8032 | 12/1 | 15:00:00 | 277.15 | 98771 | 5.1 | 360 | 3.8896 | 244.8 | 601.2 | 261.458 | 0 | 1 | 4
8033 | 12/1 | 16:00:00 | 276.15 | 98762 | 5.1 | 330 | 3.8899 | 39.6 | 0 | 260.515 | 0 | 1 | 3
8034 | 12/1 | 17:00:00 | 276.15 | 98762 | 4.6 | 320 | 3.5796 | 0 | 0 | 260.283 | 0 | 1 | 3
8035 | 12/1 | 18:00:00 | 276.15 | 98762 | 4.1 | 300 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
8036 | 12/1 | 19:00:00 | 275.15 | 98752 | 3.6 | 260 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
8037 | 12/1 | 20:00:00 | 275.15 | 98752 | 4.1 | 270 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
8038 | 12/1 | 21:00:00 | 276.15 | 98762 | 4.1 | 280 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
8039 | 12/1 | 22:00:00 | 275.15 | 98752 | 5.1 | 290 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
8040 | 12/1 | 23:00:00 | 275.15 | 98752 | 4.6 | 280 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
8041 | 12/1 | 24:00:00 | 275.15 | 98752 | 4.1 | 260 | 3.2924 | 0 | 0 | 259.482 | 0 | 1 | 2
8042 | 12/2 | 01:00:00 | 276.15 | 98762 | 4.6 | 270 | 3.2921 | 0 | 0 | 260.304 | 0 | 1 | 3
8043 | 12/2 | 02:00:00 | 276.15 | 98762 | 4.3 | 25 | 3.4331 | 0 | 0 | 260.542 | 0 | 1 | 3
8044 | 12/2 | 03:00:00 | 276.15 | 98762 | 4.1 | 270 | 3.5796 | 0 | 0 | 260.659 | 0 | 1 | 3
8045 | 12/2 | 04:00:00 | 276.15 | 98762 | 4.6 | 280 | 3.5796 | 0 | 0 | 260.538 | 0 | 1 | 3
8046 | 12/2 | 05:00:00 | 276.15 | 98762 | 3.6 | 280 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
8047 | 12/2 | 06:00:00 | 276.15 | 98762 | 4.1 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
8048 | 12/2 | 07:00:00 | 276.15 | 98762 | 5.1 | 290 | 4.4977 | 0 | 0 | 260.975 | 0 | 1 | 3
8049 | 12/2 | 08:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
8050 | 12/2 | 09:00:00 | 276.15 | 98762 | 3.6 | 290 | 4.4977 | 61.2 | 0 | 260.975 | 0 | 1 | 3
8051 | 12/2 | 10:00:00 | 277.15 | 98771 | 4.1 | 290 | 4.8316 | 277.2 | 680.4 | 262.149 | 0 | 1 | 4
8052 | 12/2 | 11:00:00 | 278.15 | 98780 | 3.1 | 270 | 5.1875 | 507.6 | 1278 | 263.323 | 0 | 1 | 5
8053 | 12/2 | 12:00:00 | 279.15 | 98789 | 3.1 | 270 | 5.5666 | 633.6 | 1486.8 | 264.497 | 0 | 1 | 6
8054 | 12/2 | 13:00:00 | 279.15 | 98789 | 2.6 | 270 | 5.5666 | 586.8 | 1224 | 264.756 | 0 | 1 | 6
8055 | 12/2 | 14:00:00 | 280.15 | 98798 | 4.6 | 310 | 5.5661 | 450 | 1004.4 | 265.704 | 0 | 1 | 7
8056 | 12/2 | 15:00:00 | 280.15 | 98798 | 4.6 | 300 | 5.1865 | 226.8 | 244.8 | 265.476 | 0 | 1 | 7
8057 | 12/2 | 16:00:00 | 279.15 | 98789 | 3.6 | 280 | 5.187 | 36 | 0 | 264.528 | 0 | 1 | 6
8058 | 12/2 | 17:00:00 | 279.15 | 98789 | 4.1 | 280 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
8059 | 12/2 | 18:00:00 | 279.15 | 98789 | 2.6 | 280 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
8060 | 12/2 | 19:00:00 | 279.15 | 98789 | 4.6 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
8061 | 12/2 | 20:00:00 | 279.15 | 98789 | 4.1 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
8062 | 12/2 | 21:00:00 | 279.15 | 98789 | 4.6 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
8063 | 12/2 | 22:00:00 | 279.15 | 98789 | 3.6 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
8064 | 12/2 | 23:00:00 | 279.15 | 98789 | 4.1 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1 | 6
8065 | 12/2 | 24:00:00 | 280.15 | 98798 | 4.6 | 280 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
8066 | 12/3 | 01:00:00 | 280.15 | 98798 | 4.1 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
8067 | 12/3 | 02:00:00 | 280.15 | 98798 | 6.7 | 290 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
8068 | 12/3 | 03:00:00 | 280.15 | 98798 | 5.7 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
8069 | 12/3 | 04:00:00 | 280.15 | 98798 | 7.2 | 280 | 5.5661 | 0 | 0 | 265.444 | 0 | 1 | 7
8070 | 12/3 | 05:00:00 | 281.15 | 98806 | 6.2 | 300 | 5.9698 | 0 | 0 | 266.62 | 0 | 1 | 8
8071 | 12/3 | 06:00:00 | 281.15 | 98806 | 5.7 | 300 | 5.9698 | 0 | 0 | 267.353 | 0 | 1 | 8
8072 | 12/3 | 07:00:00 | 280.15 | 98798 | 4.6 | 290 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
8073 | 12/3 | 08:00:00 | 280.15 | 98798 | 4.1 | 290 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
8074 | 12/3 | 09:00:00 | 281.15 | 98806 | 4.1 | 300 | 6.4 | 28.8 | 0 | 267.58 | 0 | 1 | 8
8075 | 12/3 | 10:00:00 | 281.15 | 98806 | 4.1 | 300 | 5.9698 | 140.4 | 0 | 267.353 | 0 | 1 | 8
8076 | 12/3 | 11:00:00 | 281.15 | 98806 | 3.6 | 310 | 5.9698 | 259.2 | 0 | 267.353 | 0 | 1 | 8
8077 | 12/3 | 12:00:00 | 281.15 | 98806 | 1.5 | 59 | 5.5656 | 327.6 | 25.2 | 267.125 | 0 | 1 | 8
8078 | 12/3 | 13:00:00 | 281.15 | 98806 | 1.5 | 10 | 5.1861 | 579.6 | 961.2 | 266.423 | 0 | 1 | 8
8079 | 12/3 | 14:00:00 | 281.15 | 98806 | 1 | 134 | 5.1861 | 446.4 | 997.2 | 266.423 | 0 | 1 | 8
8080 | 12/3 | 15:00:00 | 281.15 | 98806 | 1 | 320 | 5.1861 | 219.6 | 237.6 | 266.423 | 0 | 1 | 8
8081 | 12/3 | 16:00:00 | 281.15 | 98806 | 1 | 270 | 5.1861 | 32.4 | 0 | 266.423 | 0 | 1 | 8
8082 | 12/3 | 17:00:00 | 278.15 | 98780 | 2.6 | 270 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
8083 | 12/3 | 18:00:00 | 278.15 | 98780 | 3.1 | 300 | 4.8311 | 0 | 0 | 263.818 | 0 | 1 | 5
8084 | 12/3 | 19:00:00 | 277.15 | 98771 | 3.1 | 280 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
8085 | 12/3 | 20:00:00 | 277.15 | 98771 | 4.1 | 270 | 4.8316 | 0 | 0 | 262.976 | 0 | 1 | 4
8086 | 12/3 | 21:00:00 | 276.15 | 98762 | 3.6 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1 | 3
8087 | 12/3 | 22:00:00 | 276.15 | 98762 | 3.1 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8088 | 12/3 | 23:00:00 | 276.15 | 98762 | 5.1 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8089 | 12/3 | 24:00:00 | 275.15 | 98752 | 4.1 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
8090 | 12/4 | 01:00:00 | 275.15 | 98752 | 4.1 | 260 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
8091 | 12/4 | 02:00:00 | 275.15 | 98752 | 3.1 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
8092 | 12/4 | 03:00:00 | 275.15 | 98752 | 4.1 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
8093 | 12/4 | 04:00:00 | 275.15 | 98752 | 3.6 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
8094 | 12/4 | 05:00:00 | 275.15 | 98752 | 3.6 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
8095 | 12/4 | 06:00:00 | 278.15 | 98780 | 6.2 | 280 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
8096 | 12/4 | 07:00:00 | 277.15 | 98771 | 4.1 | 260 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
8097 | 12/4 | 08:00:00 | 277.15 | 98771 | 6.2 | 260 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
8098 | 12/4 | 09:00:00 | 278.15 | 98780 | 5.1 | 270 | 5.1875 | 28.8 | 0 | 264.047 | 0 | 1 | 5
8099 | 12/4 | 10:00:00 | 279.15 | 98789 | 6.7 | 280 | 5.5666 | 136.8 | 0 | 265.224 | 0 | 1 | 6
8100 | 12/4 | 11:00:00 | 279.15 | 98789 | 6.2 | 280 | 5.5666 | 154.8 | 0 | 265.332 | 0 | 1 | 6
8101 | 12/4 | 12:00:00 | 280.15 | 98798 | 6.7 | 290 | 5.9703 | 320.4 | 32.4 | 266.402 | 0 | 1 | 7
8102 | 12/4 | 13:00:00 | 281.15 | 98806 | 5.1 | 300 | 5.9698 | 572.4 | 1180.8 | 266.881 | 0 | 1 | 8
8103 | 12/4 | 14:00:00 | 281.15 | 98806 | 6.7 | 290 | 5.9698 | 464.4 | 1184.4 | 266.62 | 0 | 1 | 8
8104 | 12/4 | 15:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.9698 | 216 | 338.4 | 266.881 | 0 | 1 | 8
8105 | 12/4 | 16:00:00 | 281.15 | 98806 | 6.2 | 280 | 5.5656 | 18 | 0 | 267.125 | 0 | 1 | 8
8106 | 12/4 | 17:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
8107 | 12/4 | 18:00:00 | 280.15 | 98798 | 6.7 | 280 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
8108 | 12/4 | 19:00:00 | 280.15 | 98798 | 5.7 | 280 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
8109 | 12/4 | 20:00:00 | 280.15 | 98798 | 4.1 | 280 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
8110 | 12/4 | 21:00:00 | 280.15 | 98798 | 4.6 | 300 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
8111 | 12/4 | 22:00:00 | 280.15 | 98798 | 2.6 | 260 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
8112 | 12/4 | 23:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.9703 | 0 | 0 | 266.402 | 0 | 1 | 7
8113 | 12/4 | 24:00:00 | 280.15 | 98798 | 3.1 | 260 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
8114 | 12/5 | 01:00:00 | 281.15 | 98806 | 5.7 | 250 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
8115 | 12/5 | 02:00:00 | 280.15 | 98798 | 9.3 | 270 | 5.9703 | 0 | 0 | 266.51 | 0 | 1 | 7
8116 | 12/5 | 03:00:00 | 280.15 | 98798 | 7.2 | 270 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
8117 | 12/5 | 04:00:00 | 280.15 | 98798 | 8.2 | 270 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
8118 | 12/5 | 05:00:00 | 280.15 | 98798 | 9.8 | 270 | 5.1865 | 0 | 0 | 265.476 | 0 | 1 | 7
8119 | 12/5 | 06:00:00 | 280.15 | 98798 | 8.2 | 270 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
8120 | 12/5 | 07:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
8121 | 12/5 | 08:00:00 | 280.15 | 98798 | 8.2 | 270 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
8122 | 12/5 | 09:00:00 | 279.15 | 98789 | 8.8 | 260 | 5.187 | 14.4 | 0 | 265.104 | 0 | 1 | 6
8123 | 12/5 | 10:00:00 | 279.15 | 98789 | 8.8 | 260 | 5.187 | 133.2 | 0 | 264.996 | 0 | 1 | 6
8124 | 12/5 | 11:00:00 | 279.15 | 98789 | 9.8 | 260 | 5.187 | 252 | 0 | 264.996 | 0 | 1 | 6
8125 | 12/5 | 12:00:00 | 280.15 | 98798 | 10.3 | 260 | 4.8303 | 320.4 | 21.6 | 265.715 | 0 | 1 | 7
8126 | 12/5 | 13:00:00 | 280.15 | 98798 | 12.9 | 260 | 5.1865 | 313.2 | 21.6 | 265.946 | 0 | 1 | 7
8127 | 12/5 | 14:00:00 | 280.15 | 98798 | 12.9 | 270 | 5.1865 | 241.2 | 0 | 265.946 | 0 | 1 | 7
8128 | 12/5 | 15:00:00 | 280.15 | 98798 | 7.2 | 270 | 4.8303 | 118.8 | 0 | 265.715 | 0 | 1 | 7
8129 | 12/5 | 16:00:00 | 279.15 | 98789 | 8.2 | 260 | 4.8307 | 14.4 | 0 | 264.767 | 0 | 1 | 6
8130 | 12/5 | 17:00:00 | 279.15 | 98789 | 5.7 | 240 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
8131 | 12/5 | 18:00:00 | 279.15 | 98789 | 8.8 | 260 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
8132 | 12/5 | 19:00:00 | 279.15 | 98789 | 10.3 | 260 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
8133 | 12/5 | 20:00:00 | 279.15 | 98789 | 8.8 | 260 | 4.8307 | 0 | 0 | 264.767 | 0 | 1 | 6
8134 | 12/5 | 21:00:00 | 280.15 | 98798 | 9.3 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
8135 | 12/5 | 22:00:00 | 280.15 | 98798 | 8.2 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
8136 | 12/5 | 23:00:00 | 280.15 | 98798 | 7.2 | 250 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
8137 | 12/5 | 24:00:00 | 280.15 | 98798 | 7.2 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1 | 7
8138 | 12/6 | 01:00:00 | 280.15 | 98798 | 8.2 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1 | 7
8139 | 12/6 | 02:00:00 | 281.15 | 98806 | 9.3 | 250 | 5.5656 | 0 | 0 | 267.125 | 0 | 1 | 8
8140 | 12/6 | 03:00:00 | 281.15 | 98806 | 7.7 | 250 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
8141 | 12/6 | 04:00:00 | 281.15 | 98806 | 10.3 | 260 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
8142 | 12/6 | 05:00:00 | 281.15 | 98806 | 7.7 | 260 | 5.5656 | 0 | 0 | 266.653 | 0 | 1 | 8
8143 | 12/6 | 06:00:00 | 280.15 | 98798 | 8.8 | 260 | 5.5661 | 0 | 0 | 265.704 | 0 | 1 | 7
8144 | 12/6 | 07:00:00 | 280.15 | 98798 | 8.8 | 260 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
8145 | 12/6 | 08:00:00 | 281.15 | 98806 | 7.2 | 250 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
8146 | 12/6 | 09:00:00 | 281.15 | 98806 | 6.2 | 250 | 5.9698 | 39.6 | 0 | 266.881 | 0 | 1 | 8
8147 | 12/6 | 10:00:00 | 281.15 | 98806 | 6.7 | 240 | 5.5656 | 230.4 | 619.2 | 266.653 | 0 | 1 | 8
8148 | 12/6 | 11:00:00 | 282.15 | 98815 | 6.7 | 240 | 5.5651 | 248.4 | 0 | 268.075 | 0 | 1 | 9
8149 | 12/6 | 12:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.9692 | 565.2 | 1180.8 | 267.83 | 0 | 1 | 9
8150 | 12/6 | 13:00:00 | 283.15 | 98824 | 7.2 | 230 | 5.9687 | 558 | 1022.4 | 268.779 | 0 | 1 | 10
8151 | 12/6 | 14:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.5651 | 428.4 | 975.6 | 267.601 | 0 | 1 | 9
8152 | 12/6 | 15:00:00 | 282.15 | 98815 | 5.7 | 220 | 5.9692 | 208.8 | 226.8 | 267.83 | 0 | 1 | 9
8153 | 12/6 | 16:00:00 | 283.15 | 98824 | 7.7 | 230 | 5.9687 | 14.4 | 0 | 269.255 | 0 | 1 | 10
8154 | 12/6 | 17:00:00 | 283.15 | 98824 | 6.7 | 230 | 5.9687 | 0 | 0 | 269.255 | 0 | 1 | 10
8155 | 12/6 | 18:00:00 | 282.15 | 98815 | 5.7 | 230 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
8156 | 12/6 | 19:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
8157 | 12/6 | 20:00:00 | 282.15 | 98815 | 8.8 | 220 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
8158 | 12/6 | 21:00:00 | 283.15 | 98824 | 10.8 | 220 | 5.9687 | 0 | 0 | 268.779 | 0 | 1 | 10
8159 | 12/6 | 22:00:00 | 283.15 | 98824 | 8.8 | 230 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
8160 | 12/6 | 23:00:00 | 283.15 | 98824 | 9.8 | 220 | 6.3988 | 0 | 0 | 269.483 | 0 | 1 | 10
8161 | 12/6 | 24:00:00 | 283.15 | 98824 | 8.8 | 210 | 6.3988 | 0 | 0 | 269.483 | 0 | 1 | 10
8162 | 12/7 | 01:00:00 | 283.15 | 98824 | 9.8 | 220 | 6.8564 | 0 | 0 | 269.82 | 0 | 1 | 10
8163 | 12/7 | 02:00:00 | 284.15 | 98833 | 8.2 | 210 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
8164 | 12/7 | 03:00:00 | 284.15 | 98833 | 8.8 | 210 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
8165 | 12/7 | 04:00:00 | 284.15 | 98833 | 8.2 | 220 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
8166 | 12/7 | 05:00:00 | 284.15 | 98833 | 9.8 | 220 | 7.3425 | 0 | 0 | 270.89 | 0 | 1 | 11
8167 | 12/7 | 06:00:00 | 284.15 | 98833 | 9.3 | 220 | 7.8598 | 0 | 0 | 271.115 | 0 | 1 | 11
8168 | 12/7 | 07:00:00 | 284.15 | 98833 | 8.2 | 230 | 7.8598 | 0 | 0 | 270.636 | 0 | 1 | 11
8169 | 12/7 | 08:00:00 | 281.15 | 98806 | 8.2 | 280 | 5.9698 | 0 | 0 | 266.881 | 0 | 1 | 8
8170 | 12/7 | 09:00:00 | 280.15 | 98798 | 6.7 | 280 | 5.1865 | 36 | 0 | 265.476 | 0 | 1 | 7
8171 | 12/7 | 10:00:00 | 279.15 | 98789 | 7.2 | 280 | 4.4964 | 223.2 | 252 | 264.069 | 0 | 1 | 6
8172 | 12/7 | 11:00:00 | 280.15 | 98798 | 6.2 | 260 | 4.496 | 439.2 | 1011.6 | 265.014 | 0 | 1 | 7
8173 | 12/7 | 12:00:00 | 280.15 | 98798 | 9.8 | 270 | 4.496 | 561.6 | 1044 | 265.014 | 0 | 1 | 7
8174 | 12/7 | 13:00:00 | 280.15 | 98798 | 9.8 | 280 | 4.496 | 558 | 1036.8 | 265.014 | 0 | 1 | 7
8175 | 12/7 | 14:00:00 | 279.15 | 98789 | 11.3 | 280 | 4.4964 | 424.8 | 982.8 | 264.069 | 0 | 1 | 6
8176 | 12/7 | 15:00:00 | 278.15 | 98780 | 11.3 | 280 | 4.4968 | 205.2 | 226.8 | 263.123 | 0 | 1 | 5
8177 | 12/7 | 16:00:00 | 278.15 | 98780 | 8.2 | 270 | 3.8892 | 25.2 | 0 | 262.659 | 0 | 1 | 5
8178 | 12/7 | 17:00:00 | 276.15 | 98762 | 9.3 | 290 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
8179 | 12/7 | 18:00:00 | 276.15 | 98762 | 10.3 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
8180 | 12/7 | 19:00:00 | 275.15 | 98752 | 9.8 | 280 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8181 | 12/7 | 20:00:00 | 274.15 | 98743 | 10.3 | 280 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8182 | 12/7 | 21:00:00 | 274.15 | 98743 | 9.3 | 270 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8183 | 12/7 | 22:00:00 | 274.15 | 98743 | 6.7 | 290 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
8184 | 12/7 | 23:00:00 | 273.15 | 98734 | 7.2 | 280 | 3.891 | 0 | 0 | 257.937 | 0 | 1 | 0
8185 | 12/7 | 24:00:00 | 273.15 | 98734 | 6.7 | 270 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
8186 | 12/8 | 01:00:00 | 273.15 | 98734 | 5.1 | 260 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
8187 | 12/8 | 02:00:00 | 274.15 | 98743 | 6.7 | 280 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
8188 | 12/8 | 03:00:00 | 274.15 | 98743 | 7.2 | 290 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
8189 | 12/8 | 04:00:00 | 274.15 | 98743 | 10.8 | 290 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8190 | 12/8 | 05:00:00 | 274.15 | 98743 | 8.2 | 290 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8191 | 12/8 | 06:00:00 | 274.15 | 98743 | 9.3 | 290 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8192 | 12/8 | 07:00:00 | 274.15 | 98743 | 6.7 | 290 | 3.0265 | 0 | 0 | 258.305 | 0 | 1 | 1
8193 | 12/8 | 08:00:00 | 273.15 | 98734 | 7.7 | 280 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8194 | 12/8 | 09:00:00 | 272.15 | 98724 | 8.2 | 270 | 2.7806 | 36 | 0 | 255.817 | 0 | 1 | -1
8195 | 12/8 | 10:00:00 | 273.15 | 98734 | 9.3 | 280 | 2.7804 | 205.2 | 194.4 | 257.128 | 0 | 1 | 0
8196 | 12/8 | 11:00:00 | 273.15 | 98734 | 6.2 | 290 | 2.7804 | 410.4 | 723.6 | 257.128 | 0 | 1 | 0
8197 | 12/8 | 12:00:00 | 274.15 | 98743 | 9.3 | 290 | 3.0265 | 525.6 | 1018.8 | 258.305 | 0 | 1 | 1
8198 | 12/8 | 13:00:00 | 274.15 | 98743 | 9.3 | 280 | 2.7801 | 550.8 | 1220.4 | 257.95 | 0 | 1 | 1
8199 | 12/8 | 14:00:00 | 274.15 | 98743 | 8.8 | 280 | 2.7801 | 453.6 | 1062 | 257.697 | 0 | 1 | 1
8200 | 12/8 | 15:00:00 | 274.15 | 98743 | 7.7 | 290 | 2.5522 | 219.6 | 496.8 | 257.461 | 0 | 1 | 1
8201 | 12/8 | 16:00:00 | 273.15 | 98734 | 6.7 | 280 | 2.5525 | 25.2 | 0 | 256.522 | 0 | 1 | 0
8202 | 12/8 | 17:00:00 | 273.15 | 98734 | 6.7 | 290 | 2.7804 | 0 | 0 | 256.757 | 0 | 1 | 0
8203 | 12/8 | 18:00:00 | 272.15 | 98724 | 7.2 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8204 | 12/8 | 19:00:00 | 272.15 | 98724 | 8.2 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8205 | 12/8 | 20:00:00 | 272.15 | 98724 | 7.7 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8206 | 12/8 | 21:00:00 | 272.15 | 98724 | 8.8 | 290 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8207 | 12/8 | 22:00:00 | 272.15 | 98724 | 9.3 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8208 | 12/8 | 23:00:00 | 271.15 | 98715 | 9.8 | 280 | 2.3423 | 0 | 0 | 254.775 | 0 | 1 | -2
8209 | 12/8 | 24:00:00 | 272.15 | 98724 | 6.7 | 280 | 2.3421 | 0 | 0 | 255.596 | 0 | 1 | -1
8210 | 12/9 | 01:00:00 | 272.15 | 98724 | 8.8 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8211 | 12/9 | 02:00:00 | 272.15 | 98724 | 6.7 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8212 | 12/9 | 03:00:00 | 272.15 | 98724 | 7.7 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8213 | 12/9 | 04:00:00 | 272.15 | 98724 | 5.7 | 260 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8214 | 12/9 | 05:00:00 | 272.15 | 98724 | 7.2 | 290 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8215 | 12/9 | 06:00:00 | 273.15 | 98734 | 7.2 | 280 | 2.5525 | 0 | 0 | 256.773 | 0 | 1 | 0
8216 | 12/9 | 07:00:00 | 272.15 | 98724 | 7.2 | 270 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8217 | 12/9 | 08:00:00 | 272.15 | 98724 | 4.6 | 270 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8218 | 12/9 | 09:00:00 | 271.15 | 98715 | 8.2 | 270 | 2.553 | 25.2 | 0 | 255.126 | 0 | 1 | -2
8219 | 12/9 | 10:00:00 | 272.15 | 98724 | 7.2 | 270 | 2.7806 | 180 | 122.4 | 256.302 | 0 | 1 | -1
8220 | 12/9 | 11:00:00 | 273.15 | 98734 | 5.1 | 280 | 2.7804 | 403.2 | 673.2 | 257.128 | 0 | 1 | 0
8221 | 12/9 | 12:00:00 | 273.15 | 98734 | 5.1 | 250 | 3.0267 | 586.8 | 1310.4 | 256.991 | 0 | 1 | 0
8222 | 12/9 | 13:00:00 | 273.15 | 98734 | 4.6 | 260 | 3.293 | 583.2 | 1134 | 257.224 | 0 | 1 | 0
8223 | 12/9 | 14:00:00 | 273.15 | 98734 | 5.7 | 260 | 3.293 | 446.4 | 1047.6 | 257.224 | 0 | 1 | 0
8224 | 12/9 | 15:00:00 | 273.15 | 98734 | 5.1 | 260 | 3.5806 | 201.6 | 252 | 257.707 | 0 | 1 | 0
8225 | 12/9 | 16:00:00 | 273.15 | 98734 | 3.6 | 270 | 3.5806 | 21.6 | 0 | 257.707 | 0 | 1 | 0
8226 | 12/9 | 17:00:00 | 273.15 | 98734 | 3.6 | 260 | 3.5806 | 0 | 0 | 257.707 | 0 | 1 | 0
8227 | 12/9 | 18:00:00 | 272.15 | 98724 | 3.6 | 270 | 3.2934 | 0 | 0 | 256.533 | 0 | 1 | -1
8228 | 12/9 | 19:00:00 | 272.15 | 98724 | 4.1 | 260 | 3.2934 | 0 | 0 | 256.533 | 0 | 1 | -1
8229 | 12/9 | 20:00:00 | 272.15 | 98724 | 3.6 | 240 | 3.2934 | 0 | 0 | 256.533 | 0 | 1 | -1
8230 | 12/9 | 21:00:00 | 272.15 | 98724 | 3.1 | 240 | 3.2934 | 0 | 0 | 256.533 | 0 | 1 | -1
8231 | 12/9 | 22:00:00 | 273.15 | 98734 | 4.1 | 240 | 3.5806 | 0 | 0 | 257.707 | 0 | 1 | 0
8232 | 12/9 | 23:00:00 | 272.15 | 98724 | 3.1 | 240 | 3.581 | 0 | 0 | 256.513 | 0 | 1 | -1
8233 | 12/9 | 24:00:00 | 273.15 | 98734 | 3.1 | 250 | 3.5806 | 0 | 0 | 257.455 | 0 | 1 | 0
8234 | 12/10 | 01:00:00 | 273.15 | 98734 | 4.1 | 250 | 3.5806 | 0 | 0 | 257.455 | 0 | 1 | 0
8235 | 12/10 | 02:00:00 | 273.15 | 98734 | 2.6 | 260 | 3.5806 | 0 | 0 | 257.455 | 0 | 1 | 0
8236 | 12/10 | 03:00:00 | 273.15 | 98734 | 2.1 | 270 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
8237 | 12/10 | 04:00:00 | 273.15 | 98734 | 2.1 | 250 | 3.5806 | 0 | 0 | 257.707 | 0 | 1 | 0
8238 | 12/10 | 05:00:00 | 273.15 | 98734 | 2.6 | 80 | 3.5806 | 0 | 0 | 257.707 | 0 | 1 | 0
8239 | 12/10 | 06:00:00 | 272.15 | 98724 | 3.1 | 90 | 3.581 | 0 | 0 | 257.218 | 0 | 1 | -1
8240 | 12/10 | 07:00:00 | 272.15 | 98724 | 3.6 | 80 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
8241 | 12/10 | 08:00:00 | 271.15 | 98715 | 3.6 | 50 | 3.2936 | 0 | 0 | 256.147 | 0 | 1 | -2
8242 | 12/10 | 09:00:00 | 271.15 | 98715 | 3.6 | 70 | 3.2936 | 10.8 | 0 | 256.147 | 0 | 1 | -2
8243 | 12/10 | 10:00:00 | 272.15 | 98724 | 3.6 | 40 | 3.2934 | 100.8 | 0 | 256.987 | 0 | 1 | -1
8244 | 12/10 | 11:00:00 | 271.15 | 98715 | 4.6 | 40 | 3.2936 | 234 | 0 | 256.043 | 0 | 1 | -2
8245 | 12/10 | 12:00:00 | 272.15 | 98724 | 3.6 | 40 | 3.2934 | 302.4 | 25.2 | 256.987 | 0 | 1 | -1
8246 | 12/10 | 13:00:00 | 272.15 | 98724 | 4.1 | 20 | 3.2934 | 302.4 | 18 | 256.987 | 0 | 1 | -1
8247 | 12/10 | 14:00:00 | 273.15 | 98734 | 4.1 | 20 | 3.293 | 417.6 | 896.4 | 257.476 | 0 | 1 | 0
8248 | 12/10 | 15:00:00 | 273.15 | 98734 | 3.6 | 20 | 3.293 | 111.6 | 0 | 257.931 | 0 | 1 | 0
8249 | 12/10 | 16:00:00 | 273.15 | 98734 | 3.6 | 360 | 3.293 | 10.8 | 0 | 257.931 | 0 | 1 | 0
8250 | 12/10 | 17:00:00 | 273.15 | 98734 | 4.1 | 360 | 2.7804 | 0 | 0 | 257.463 | 0 | 1 | 0
8251 | 12/10 | 18:00:00 | 273.15 | 98734 | 4.6 | 10 | 2.7804 | 0 | 0 | 257.463 | 0 | 1 | 0
8252 | 12/10 | 19:00:00 | 273.15 | 98734 | 3.6 | 10 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8253 | 12/10 | 20:00:00 | 272.15 | 98724 | 4.6 | 360 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8254 | 12/10 | 21:00:00 | 272.15 | 98724 | 2.6 | 30 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8255 | 12/10 | 22:00:00 | 271.15 | 98715 | 2.1 | 30 | 2.553 | 0 | 0 | 255.126 | 0 | 1 | -2
8256 | 12/10 | 23:00:00 | 271.15 | 98715 | 3.6 | 360 | 2.7809 | 0 | 0 | 255.471 | 0 | 1 | -2
8257 | 12/10 | 24:00:00 | 272.15 | 98724 | 4.1 | 360 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8258 | 12/11 | 01:00:00 | 272.15 | 98724 | 3.6 | 10 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8259 | 12/11 | 02:00:00 | 272.15 | 98724 | 4.1 | 10 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8260 | 12/11 | 03:00:00 | 271.15 | 98715 | 3.6 | 10 | 2.553 | 0 | 0 | 255.126 | 0 | 1 | -2
8261 | 12/11 | 04:00:00 | 272.15 | 98724 | 3.6 | 360 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8262 | 12/11 | 05:00:00 | 272.15 | 98724 | 4.1 | 360 | 2.5527 | 0 | 0 | 255.952 | 0 | 1 | -1
8263 | 12/11 | 06:00:00 | 272.15 | 98724 | 4.6 | 360 | 2.3421 | 0 | 0 | 255.596 | 0 | 1 | -1
8264 | 12/11 | 07:00:00 | 272.15 | 98724 | 4.6 | 360 | 2.3421 | 0 | 0 | 255.596 | 0 | 1 | -1
8265 | 12/11 | 08:00:00 | 272.15 | 98724 | 4.1 | 360 | 2.3421 | 0 | 0 | 255.596 | 0 | 1 | -1
8266 | 12/11 | 09:00:00 | 273.15 | 98734 | 4.6 | 350 | 2.3418 | 25.2 | 0 | 256.412 | 0 | 1 | 0
8267 | 12/11 | 10:00:00 | 273.15 | 98734 | 4.1 | 350 | 2.5525 | 201.6 | 234 | 256.773 | 0 | 1 | 0
8268 | 12/11 | 11:00:00 | 272.15 | 98724 | 4.1 | 340 | 2.3421 | 421.2 | 885.6 | 255.596 | 0 | 1 | -1
8269 | 12/11 | 12:00:00 | 273.15 | 98734 | 1.5 | 125 | 2.5525 | 543.6 | 1249.2 | 256.773 | 0 | 1 | 0
8270 | 12/11 | 13:00:00 | 273.15 | 98734 | 2.6 | 310 | 2.7804 | 507.6 | 1008 | 257.128 | 0 | 1 | 0
8271 | 12/11 | 14:00:00 | 273.15 | 98734 | 3.6 | 300 | 2.7804 | 388.8 | 799.2 | 257.128 | 0 | 1 | 0
8272 | 12/11 | 15:00:00 | 273.15 | 98734 | 4.1 | 310 | 2.5525 | 198 | 226.8 | 256.773 | 0 | 1 | 0
8273 | 12/11 | 16:00:00 | 272.15 | 98724 | 3.1 | 280 | 2.3421 | 21.6 | 0 | 255.596 | 0 | 1 | -1
8274 | 12/11 | 17:00:00 | 271.15 | 98715 | 5.1 | 320 | 2.553 | 0 | 0 | 255.126 | 0 | 1 | -2
8275 | 12/11 | 18:00:00 | 271.15 | 98715 | 3.1 | 270 | 2.553 | 0 | 0 | 255.126 | 0 | 1 | -2
8276 | 12/11 | 19:00:00 | 273.15 | 98734 | 5.7 | 340 | 3.0267 | 0 | 0 | 256.991 | 0 | 1 | 0
8277 | 12/11 | 20:00:00 | 273.15 | 98734 | 6.7 | 330 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8278 | 12/11 | 21:00:00 | 273.15 | 98734 | 5.7 | 320 | 3.293 | 0 | 0 | 257.823 | 0 | 1 | 0
8279 | 12/11 | 22:00:00 | 273.15 | 98734 | 6.2 | 320 | 3.293 | 0 | 0 | 257.224 | 0 | 1 | 0
8280 | 12/11 | 23:00:00 | 273.15 | 98734 | 5.7 | 320 | 3.293 | 0 | 0 | 257.224 | 0 | 1 | 0
8281 | 12/11 | 24:00:00 | 273.15 | 98734 | 5.7 | 310 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8282 | 12/12 | 01:00:00 | 272.15 | 98724 | 3.6 | 270 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
8283 | 12/12 | 02:00:00 | 271.15 | 98715 | 4.6 | 260 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
8284 | 12/12 | 03:00:00 | 271.15 | 98715 | 5.7 | 270 | 2.7809 | 0 | 0 | 255.471 | 0 | 1 | -2
8285 | 12/12 | 04:00:00 | 272.15 | 98724 | 5.7 | 300 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
8286 | 12/12 | 05:00:00 | 271.15 | 98715 | 5.7 | 290 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
8287 | 12/12 | 06:00:00 | 271.15 | 98715 | 3.6 | 260 | 2.7809 | 0 | 0 | 255.471 | 0 | 1 | -2
8288 | 12/12 | 07:00:00 | 270.15 | 98705 | 4.1 | 260 | 2.7812 | 0 | 0 | 254.636 | 0 | 1 | -3
8289 | 12/12 | 08:00:00 | 271.15 | 98715 | 4.6 | 260 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
8290 | 12/12 | 09:00:00 | 272.15 | 98724 | 5.1 | 270 | 3.0271 | 14.4 | 0 | 256.647 | 0 | 1 | -1
8291 | 12/12 | 10:00:00 | 271.15 | 98715 | 3.6 | 260 | 2.7809 | 136.8 | 0 | 255.471 | 0 | 1 | -2
8292 | 12/12 | 11:00:00 | 272.15 | 98724 | 3.6 | 250 | 3.0271 | 435.6 | 972 | 256.051 | 0 | 1 | -1
8293 | 12/12 | 12:00:00 | 273.15 | 98734 | 4.1 | 250 | 3.293 | 576 | 1332 | 256.813 | 0 | 1 | 0
8294 | 12/12 | 13:00:00 | 274.15 | 98743 | 4.1 | 250 | 3.5803 | 536.4 | 1213.2 | 258.651 | 0 | 1 | 1
8295 | 12/12 | 14:00:00 | 274.15 | 98743 | 3.1 | 250 | 3.5803 | 435.6 | 1029.6 | 258.398 | 0 | 1 | 1
8296 | 12/12 | 15:00:00 | 275.15 | 98752 | 4.6 | 230 | 3.5799 | 208.8 | 471.6 | 259.34 | 0 | 1 | 2
8297 | 12/12 | 16:00:00 | 274.15 | 98743 | 2.6 | 260 | 3.5803 | 21.6 | 0 | 258.398 | 0 | 1 | 1
8298 | 12/12 | 17:00:00 | 274.15 | 98743 | 3.6 | 240 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
8299 | 12/12 | 18:00:00 | 275.15 | 98752 | 4.6 | 240 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
8300 | 12/12 | 19:00:00 | 275.15 | 98752 | 5.1 | 230 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8301 | 12/12 | 20:00:00 | 276.15 | 98762 | 4.6 | 200 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8302 | 12/12 | 21:00:00 | 275.15 | 98752 | 5.1 | 190 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
8303 | 12/12 | 22:00:00 | 276.15 | 98762 | 4.6 | 200 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8304 | 12/12 | 23:00:00 | 276.15 | 98762 | 5.7 | 220 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
8305 | 12/12 | 24:00:00 | 276.15 | 98762 | 6.2 | 240 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
8306 | 12/13 | 01:00:00 | 276.15 | 98762 | 4.6 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
8307 | 12/13 | 02:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
8308 | 12/13 | 03:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
8309 | 12/13 | 04:00:00 | 277.15 | 98771 | 3.1 | 230 | 4.8316 | 0 | 0 | 262.405 | 0 | 1 | 4
8310 | 12/13 | 05:00:00 | 278.15 | 98780 | 5.1 | 250 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
8311 | 12/13 | 06:00:00 | 278.15 | 98780 | 5.1 | 250 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
8312 | 12/13 | 07:00:00 | 277.15 | 98771 | 4.6 | 230 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
8313 | 12/13 | 08:00:00 | 277.15 | 98771 | 5.1 | 230 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
8314 | 12/13 | 09:00:00 | 277.15 | 98771 | 4.1 | 200 | 4.8316 | 18 | 0 | 262.405 | 0 | 1 | 4
8315 | 12/13 | 10:00:00 | 277.15 | 98771 | 4.6 | 210 | 4.8316 | 190.8 | 496.8 | 262.405 | 0 | 1 | 4
8316 | 12/13 | 11:00:00 | 278.15 | 98780 | 5.1 | 210 | 4.8311 | 223.2 | 0 | 263.818 | 0 | 1 | 5
8317 | 12/13 | 12:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.187 | 291.6 | 14.4 | 264.996 | 0 | 1 | 6
8318 | 12/13 | 13:00:00 | 278.15 | 98780 | 6.2 | 230 | 5.1875 | 291.6 | 18 | 264.047 | 0 | 1 | 5
8319 | 12/13 | 14:00:00 | 276.15 | 98762 | 5.1 | 250 | 4.4977 | 406.8 | 741.6 | 261.231 | 0 | 1 | 3
8320 | 12/13 | 15:00:00 | 277.15 | 98771 | 6.2 | 260 | 4.8316 | 194.4 | 212.4 | 262.405 | 0 | 1 | 4
8321 | 12/13 | 16:00:00 | 276.15 | 98762 | 8.8 | 270 | 3.8899 | 21.6 | 0 | 260.515 | 0 | 1 | 3
8322 | 12/13 | 17:00:00 | 276.15 | 98762 | 5.7 | 260 | 3.8899 | 0 | 0 | 260.77 | 0 | 1 | 3
8323 | 12/13 | 18:00:00 | 275.15 | 98752 | 7.7 | 270 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8324 | 12/13 | 19:00:00 | 275.15 | 98752 | 4.1 | 260 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
8325 | 12/13 | 20:00:00 | 275.15 | 98752 | 6.7 | 260 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8326 | 12/13 | 21:00:00 | 274.15 | 98743 | 6.2 | 250 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8327 | 12/13 | 22:00:00 | 275.15 | 98752 | 4.1 | 250 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8328 | 12/13 | 23:00:00 | 275.15 | 98752 | 7.7 | 260 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8329 | 12/13 | 24:00:00 | 274.15 | 98743 | 9.3 | 280 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8330 | 12/14 | 01:00:00 | 275.15 | 98752 | 8.8 | 270 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
8331 | 12/14 | 02:00:00 | 275.15 | 98752 | 4.1 | 250 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8332 | 12/14 | 03:00:00 | 274.15 | 98743 | 2.6 | 230 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8333 | 12/14 | 04:00:00 | 275.15 | 98752 | 4.1 | 280 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
8334 | 12/14 | 05:00:00 | 275.15 | 98752 | 3.6 | 220 | 3.5799 | 0 | 0 | 259.34 | 0 | 1 | 2
8335 | 12/14 | 06:00:00 | 275.15 | 98752 | 2.6 | 240 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
8336 | 12/14 | 07:00:00 | 275.15 | 98752 | 2.6 | 240 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8337 | 12/14 | 08:00:00 | 276.15 | 98762 | 2.6 | 250 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
8338 | 12/14 | 09:00:00 | 275.15 | 98752 | 5.7 | 250 | 4.1846 | 14.4 | 0 | 260.056 | 0 | 1 | 2
8339 | 12/14 | 10:00:00 | 276.15 | 98762 | 6.2 | 260 | 4.1841 | 187.2 | 201.6 | 261.001 | 0 | 1 | 3
8340 | 12/14 | 11:00:00 | 277.15 | 98771 | 5.7 | 250 | 4.4973 | 399.6 | 943.2 | 262.177 | 0 | 1 | 4
8341 | 12/14 | 12:00:00 | 277.15 | 98771 | 5.7 | 230 | 4.1838 | 525.6 | 907.2 | 261.946 | 0 | 1 | 4
8342 | 12/14 | 13:00:00 | 277.15 | 98771 | 5.1 | 230 | 4.4973 | 525.6 | 1152 | 262.177 | 0 | 1 | 4
8343 | 12/14 | 14:00:00 | 277.15 | 98771 | 6.2 | 230 | 4.1838 | 223.2 | 0 | 262.41 | 0 | 1 | 4
8344 | 12/14 | 15:00:00 | 276.15 | 98762 | 4.1 | 220 | 4.4977 | 108 | 0 | 261.693 | 0 | 1 | 3
8345 | 12/14 | 16:00:00 | 276.15 | 98762 | 6.2 | 220 | 4.4977 | 10.8 | 0 | 261.693 | 0 | 1 | 3
8346 | 12/14 | 17:00:00 | 276.15 | 98762 | 5.7 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
8347 | 12/14 | 18:00:00 | 275.15 | 98752 | 4.6 | 260 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
8348 | 12/14 | 19:00:00 | 276.15 | 98762 | 4.6 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
8349 | 12/14 | 20:00:00 | 275.15 | 98752 | 3.6 | 270 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
8350 | 12/14 | 21:00:00 | 275.15 | 98752 | 5.1 | 270 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8351 | 12/14 | 22:00:00 | 275.15 | 98752 | 4.6 | 260 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
8352 | 12/14 | 23:00:00 | 275.15 | 98752 | 5.7 | 270 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
8353 | 12/14 | 24:00:00 | 274.15 | 98743 | 4.6 | 270 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8354 | 12/15 | 01:00:00 | 274.15 | 98743 | 4.1 | 290 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8355 | 12/15 | 02:00:00 | 274.15 | 98743 | 3.6 | 320 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
8356 | 12/15 | 03:00:00 | 274.15 | 98743 | 4.6 | 340 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
8357 | 12/15 | 04:00:00 | 275.15 | 98752 | 7.2 | 330 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8358 | 12/15 | 05:00:00 | 275.15 | 98752 | 7.2 | 340 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
8359 | 12/15 | 06:00:00 | 275.15 | 98752 | 6.2 | 330 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8360 | 12/15 | 07:00:00 | 275.15 | 98752 | 5.7 | 310 | 3.5799 | 0 | 0 | 259.34 | 0 | 1 | 2
8361 | 12/15 | 08:00:00 | 275.15 | 98752 | 4.6 | 320 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8362 | 12/15 | 09:00:00 | 275.15 | 98752 | 4.6 | 310 | 3.8903 | 10.8 | 0 | 259.826 | 0 | 1 | 2
8363 | 12/15 | 10:00:00 | 275.15 | 98752 | 7.2 | 330 | 4.1846 | 180 | 216 | 260.056 | 0 | 1 | 2
8364 | 12/15 | 11:00:00 | 275.15 | 98752 | 7.7 | 310 | 3.8903 | 417.6 | 990 | 259.572 | 0 | 1 | 2
8365 | 12/15 | 12:00:00 | 277.15 | 98771 | 7.2 | 310 | 4.4973 | 518.4 | 997.2 | 262.177 | 0 | 1 | 4
8366 | 12/15 | 13:00:00 | 276.15 | 98762 | 6.7 | 340 | 4.4977 | 522 | 1000.8 | 261.231 | 0 | 1 | 3
8367 | 12/15 | 14:00:00 | 277.15 | 98771 | 7.2 | 340 | 4.4973 | 399.6 | 932.4 | 262.177 | 0 | 1 | 4
8368 | 12/15 | 15:00:00 | 277.15 | 98771 | 6.7 | 340 | 4.1838 | 201.6 | 457.2 | 261.69 | 0 | 1 | 4
8369 | 12/15 | 16:00:00 | 276.15 | 98762 | 6.7 | 330 | 4.1841 | 21.6 | 0 | 260.746 | 0 | 1 | 3
8370 | 12/15 | 17:00:00 | 276.15 | 98762 | 7.2 | 320 | 3.8899 | 0 | 0 | 260.515 | 0 | 1 | 3
8371 | 12/15 | 18:00:00 | 275.15 | 98752 | 6.2 | 300 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
8372 | 12/15 | 19:00:00 | 275.15 | 98752 | 6.2 | 310 | 3.5799 | 0 | 0 | 259.832 | 0 | 1 | 2
8373 | 12/15 | 20:00:00 | 274.15 | 98743 | 5.7 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8374 | 12/15 | 21:00:00 | 274.15 | 98743 | 7.2 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8375 | 12/15 | 22:00:00 | 274.15 | 98743 | 6.7 | 300 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8376 | 12/15 | 23:00:00 | 274.15 | 98743 | 6.7 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8377 | 12/15 | 24:00:00 | 273.15 | 98734 | 7.2 | 310 | 3.293 | 0 | 0 | 257.823 | 0 | 1 | 0
8378 | 12/16 | 01:00:00 | 274.15 | 98743 | 5.7 | 290 | 3.0265 | 0 | 0 | 258.305 | 0 | 1 | 1
8379 | 12/16 | 02:00:00 | 274.15 | 98743 | 6.2 | 300 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8380 | 12/16 | 03:00:00 | 273.15 | 98734 | 6.7 | 310 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8381 | 12/16 | 04:00:00 | 273.15 | 98734 | 6.7 | 300 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8382 | 12/16 | 05:00:00 | 273.15 | 98734 | 6.7 | 300 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8383 | 12/16 | 06:00:00 | 272.15 | 98724 | 5.7 | 310 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8384 | 12/16 | 07:00:00 | 272.15 | 98724 | 3.1 | 260 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8385 | 12/16 | 08:00:00 | 273.15 | 98734 | 4.1 | 280 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8386 | 12/16 | 09:00:00 | 273.15 | 98734 | 4.6 | 260 | 3.0267 | 10.8 | 0 | 257.243 | 0 | 1 | 0
8387 | 12/16 | 10:00:00 | 274.15 | 98743 | 5.1 | 270 | 3.0265 | 180 | 212.4 | 258.185 | 0 | 1 | 1
8388 | 12/16 | 11:00:00 | 275.15 | 98752 | 4.6 | 280 | 3.5799 | 414 | 986.4 | 259.34 | 0 | 1 | 2
8389 | 12/16 | 12:00:00 | 275.15 | 98752 | 5.1 | 280 | 3.5799 | 550.8 | 1418.4 | 259.34 | 0 | 1 | 2
8390 | 12/16 | 13:00:00 | 276.15 | 98762 | 5.1 | 270 | 3.8899 | 522 | 1184.4 | 260.77 | 0 | 1 | 3
8391 | 12/16 | 14:00:00 | 276.15 | 98762 | 5.7 | 300 | 3.8899 | 399.6 | 946.8 | 260.77 | 0 | 1 | 3
8392 | 12/16 | 15:00:00 | 275.15 | 98752 | 5.1 | 300 | 4.1846 | 201.6 | 500.4 | 259.802 | 0 | 1 | 2
8393 | 12/16 | 16:00:00 | 275.15 | 98752 | 3.6 | 280 | 3.8903 | 21.6 | 0 | 259.572 | 0 | 1 | 2
8394 | 12/16 | 17:00:00 | 273.15 | 98734 | 3.1 | 290 | 3.5806 | 0 | 0 | 257.455 | 0 | 1 | 0
8395 | 12/16 | 18:00:00 | 273.15 | 98734 | 4.1 | 270 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
8396 | 12/16 | 19:00:00 | 273.15 | 98734 | 3.1 | 280 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
8397 | 12/16 | 20:00:00 | 273.15 | 98734 | 4.1 | 290 | 3.293 | 0 | 0 | 257.823 | 0 | 1 | 0
8398 | 12/16 | 21:00:00 | 273.15 | 98734 | 5.7 | 310 | 3.293 | 0 | 0 | 257.224 | 0 | 1 | 0
8399 | 12/16 | 22:00:00 | 273.15 | 98734 | 4.6 | 290 | 3.293 | 0 | 0 | 257.224 | 0 | 1 | 0
8400 | 12/16 | 23:00:00 | 271.15 | 98715 | 3.6 | 290 | 3.0273 | 0 | 0 | 254.702 | 0 | 1 | -2
8401 | 12/16 | 24:00:00 | 271.15 | 98715 | 3.1 | 280 | 3.0273 | 0 | 0 | 254.702 | 0 | 1 | -2
8402 | 12/17 | 01:00:00 | 270.15 | 98705 | 3.6 | 270 | 2.7812 | 0 | 0 | 253.532 | 0 | 1 | -3
8403 | 12/17 | 02:00:00 | 270.15 | 98705 | 3.6 | 270 | 2.7812 | 0 | 0 | 253.532 | 0 | 1 | -3
8404 | 12/17 | 03:00:00 | 272.15 | 98724 | 4.6 | 270 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
8405 | 12/17 | 04:00:00 | 272.15 | 98724 | 3.6 | 270 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
8406 | 12/17 | 05:00:00 | 274.15 | 98743 | 4.1 | 250 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
8407 | 12/17 | 06:00:00 | 274.15 | 98743 | 2.6 | 190 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
8408 | 12/17 | 07:00:00 | 274.15 | 98743 | 1.5 | 220 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8409 | 12/17 | 08:00:00 | 275.15 | 98752 | 4.6 | 230 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
8410 | 12/17 | 09:00:00 | 275.15 | 98752 | 2.1 | 240 | 4.1846 | 7.2 | 0 | 259.802 | 0 | 1 | 2
8411 | 12/17 | 10:00:00 | 276.15 | 98762 | 4.6 | 240 | 4.4977 | 172.8 | 270 | 261.231 | 0 | 1 | 3
8412 | 12/17 | 11:00:00 | 277.15 | 98771 | 3.6 | 230 | 4.8316 | 385.2 | 709.2 | 262.405 | 0 | 1 | 4
8413 | 12/17 | 12:00:00 | 277.15 | 98771 | 6.2 | 230 | 4.8316 | 284.4 | 14.4 | 262.87 | 0 | 1 | 4
8414 | 12/17 | 13:00:00 | 278.15 | 98780 | 5.7 | 230 | 5.1875 | 288 | 14.4 | 264.047 | 0 | 1 | 5
8415 | 12/17 | 14:00:00 | 279.15 | 98789 | 5.7 | 240 | 5.5666 | 219.6 | 0 | 265.224 | 0 | 1 | 6
8416 | 12/17 | 15:00:00 | 280.15 | 98798 | 6.7 | 240 | 5.5661 | 104.4 | 0 | 266.174 | 0 | 1 | 7
8417 | 12/17 | 16:00:00 | 280.15 | 98798 | 4.1 | 230 | 5.9703 | 10.8 | 0 | 266.402 | 0 | 1 | 7
8418 | 12/17 | 17:00:00 | 281.15 | 98806 | 4.6 | 270 | 6.8577 | 0 | 0 | 267.332 | 0 | 1 | 8
8419 | 12/17 | 18:00:00 | 282.15 | 98815 | 7.7 | 280 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
8420 | 12/17 | 19:00:00 | 280.15 | 98798 | 9.3 | 290 | 5.1865 | 0 | 0 | 265.834 | 0 | 1 | 7
8421 | 12/17 | 20:00:00 | 279.15 | 98789 | 9.3 | 320 | 4.4964 | 0 | 0 | 264.31 | 0 | 1 | 6
8422 | 12/17 | 21:00:00 | 277.15 | 98771 | 6.7 | 300 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
8423 | 12/17 | 22:00:00 | 277.15 | 98771 | 6.7 | 290 | 4.1838 | 0 | 0 | 262.3 | 0 | 1 | 4
8424 | 12/17 | 23:00:00 | 277.15 | 98771 | 6.7 | 290 | 3.8896 | 0 | 0 | 261.954 | 0 | 1 | 4
8425 | 12/17 | 24:00:00 | 276.15 | 98762 | 5.7 | 280 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
8426 | 12/18 | 01:00:00 | 276.15 | 98762 | 4.6 | 290 | 3.8899 | 0 | 0 | 261.122 | 0 | 1 | 3
8427 | 12/18 | 02:00:00 | 276.15 | 98762 | 5.7 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8428 | 12/18 | 03:00:00 | 275.15 | 98752 | 4.1 | 280 | 4.1846 | 0 | 0 | 260.622 | 0 | 1 | 2
8429 | 12/18 | 04:00:00 | 276.15 | 98762 | 4.1 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8430 | 12/18 | 05:00:00 | 275.15 | 98752 | 5.7 | 310 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
8431 | 12/18 | 06:00:00 | 275.15 | 98752 | 4.6 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
8432 | 12/18 | 07:00:00 | 275.15 | 98752 | 4.1 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
8433 | 12/18 | 08:00:00 | 275.15 | 98752 | 4.6 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1 | 2
8434 | 12/18 | 09:00:00 | 275.15 | 98752 | 4.1 | 290 | 3.8903 | 3.6 | 0 | 260.286 | 0 | 1 | 2
8435 | 12/18 | 10:00:00 | 274.15 | 98743 | 3.1 | 280 | 3.8907 | 79.2 | 0 | 259.445 | 0 | 1 | 1
8436 | 12/18 | 11:00:00 | 276.15 | 98762 | 3.6 | 270 | 4.1841 | 244.8 | 36 | 261.463 | 0 | 1 | 3
8437 | 12/18 | 12:00:00 | 278.15 | 98780 | 2.6 | 280 | 4.4968 | 403.2 | 316.8 | 263.478 | 0 | 1 | 5
8438 | 12/18 | 13:00:00 | 279.15 | 98789 | 2.6 | 270 | 4.8307 | 406.8 | 327.6 | 264.656 | 0 | 1 | 6
8439 | 12/18 | 14:00:00 | 279.15 | 98789 | 3.1 | 250 | 4.8307 | 313.2 | 237.6 | 264.656 | 0 | 1 | 6
8440 | 12/18 | 15:00:00 | 279.15 | 98789 | 2.6 | 260 | 4.8307 | 201.6 | 525.6 | 264.041 | 0 | 1 | 6
8441 | 12/18 | 16:00:00 | 278.15 | 98780 | 3.1 | 260 | 4.8311 | 7.2 | 0 | 263.925 | 0 | 1 | 5
8442 | 12/18 | 17:00:00 | 278.15 | 98780 | 6.2 | 290 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
8443 | 12/18 | 18:00:00 | 278.15 | 98780 | 5.7 | 280 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
8444 | 12/18 | 19:00:00 | 278.15 | 98780 | 5.7 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
8445 | 12/18 | 20:00:00 | 278.15 | 98780 | 6.7 | 270 | 5.1875 | 0 | 0 | 264.047 | 0 | 1 | 5
8446 | 12/18 | 21:00:00 | 278.15 | 98780 | 7.2 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1 | 5
8447 | 12/18 | 22:00:00 | 279.15 | 98789 | 9.8 | 270 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
8448 | 12/18 | 23:00:00 | 278.15 | 98780 | 8.8 | 270 | 5.1875 | 0 | 0 | 263.323 | 0 | 1 | 5
8449 | 12/18 | 24:00:00 | 279.15 | 98789 | 10.8 | 280 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
8450 | 12/19 | 01:00:00 | 279.15 | 98789 | 7.7 | 270 | 5.5666 | 0 | 0 | 265.332 | 0 | 1 | 6
8451 | 12/19 | 02:00:00 | 279.15 | 98789 | 9.3 | 280 | 5.5666 | 0 | 0 | 264.497 | 0 | 1 | 6
8452 | 12/19 | 03:00:00 | 279.15 | 98789 | 5.7 | 270 | 5.187 | 0 | 0 | 264.269 | 0 | 1 | 6
8453 | 12/19 | 04:00:00 | 279.15 | 98789 | 2.6 | 260 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
8454 | 12/19 | 05:00:00 | 278.15 | 98780 | 4.6 | 260 | 4.8311 | 0 | 0 | 263.352 | 0 | 1 | 5
8455 | 12/19 | 06:00:00 | 277.15 | 98771 | 4.6 | 260 | 4.8316 | 0 | 0 | 262.149 | 0 | 1 | 4
8456 | 12/19 | 07:00:00 | 278.15 | 98780 | 4.6 | 260 | 4.8311 | 0 | 0 | 263.095 | 0 | 1 | 5
8457 | 12/19 | 08:00:00 | 279.15 | 98789 | 7.2 | 280 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
8458 | 12/19 | 09:00:00 | 280.15 | 98798 | 4.1 | 250 | 5.5661 | 3.6 | 0 | 265.704 | 0 | 1 | 7
8459 | 12/19 | 10:00:00 | 280.15 | 98798 | 5.7 | 260 | 5.1865 | 93.6 | 0 | 265.946 | 0 | 1 | 7
8460 | 12/19 | 11:00:00 | 280.15 | 98798 | 9.8 | 270 | 5.9703 | 208.8 | 0 | 266.402 | 0 | 1 | 7
8461 | 12/19 | 12:00:00 | 280.15 | 98798 | 8.8 | 270 | 5.9703 | 504 | 885.6 | 265.931 | 0 | 1 | 7
8462 | 12/19 | 13:00:00 | 281.15 | 98806 | 8.8 | 280 | 6.4 | 284.4 | 14.4 | 267.58 | 0 | 1 | 8
8463 | 12/19 | 14:00:00 | 281.15 | 98806 | 9.8 | 270 | 6.4 | 219.6 | 0 | 267.58 | 0 | 1 | 8
8464 | 12/19 | 15:00:00 | 281.15 | 98806 | 9.8 | 270 | 6.4 | 201.6 | 428.4 | 266.846 | 0 | 1 | 8
8465 | 12/19 | 16:00:00 | 282.15 | 98815 | 8.8 | 270 | 6.3994 | 21.6 | 0 | 267.795 | 0 | 1 | 9
8466 | 12/19 | 17:00:00 | 282.15 | 98815 | 5.1 | 260 | 6.3994 | 0 | 0 | 267.795 | 0 | 1 | 9
8467 | 12/19 | 18:00:00 | 281.15 | 98806 | 5.1 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
8468 | 12/19 | 19:00:00 | 281.15 | 98806 | 4.6 | 240 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8469 | 12/19 | 20:00:00 | 281.15 | 98806 | 2.6 | 230 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
8470 | 12/19 | 21:00:00 | 281.15 | 98806 | 6.2 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1 | 8
8471 | 12/19 | 22:00:00 | 282.15 | 98815 | 5.7 | 250 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8472 | 12/19 | 23:00:00 | 282.15 | 98815 | 6.7 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8473 | 12/19 | 24:00:00 | 282.15 | 98815 | 8.8 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8474 | 12/20 | 01:00:00 | 282.15 | 98815 | 9.8 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8475 | 12/20 | 02:00:00 | 282.15 | 98815 | 6.7 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8476 | 12/20 | 03:00:00 | 282.15 | 98815 | 8.2 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8477 | 12/20 | 04:00:00 | 282.15 | 98815 | 5.7 | 260 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
8478 | 12/20 | 05:00:00 | 282.15 | 98815 | 6.2 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8479 | 12/20 | 06:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8480 | 12/20 | 07:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
8481 | 12/20 | 08:00:00 | 283.15 | 98824 | 3.1 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
8482 | 12/20 | 09:00:00 | 283.15 | 98824 | 2.6 | 250 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
8483 | 12/20 | 10:00:00 | 284.15 | 98833 | 5.7 | 250 | 7.3425 | 90 | 0 | 270.89 | 0 | 1 | 11
8484 | 12/20 | 11:00:00 | 284.15 | 98833 | 6.7 | 250 | 7.8598 | 205.2 | 0 | 271.115 | 0 | 1 | 11
8485 | 12/20 | 12:00:00 | 283.15 | 98824 | 5.7 | 250 | 7.3431 | 277.2 | 7.2 | 269.936 | 0 | 1 | 10
8486 | 12/20 | 13:00:00 | 283.15 | 98824 | 5.7 | 270 | 7.3431 | 280.8 | 10.8 | 269.936 | 0 | 1 | 10
8487 | 12/20 | 14:00:00 | 283.15 | 98824 | 4.6 | 270 | 7.3431 | 219.6 | 0 | 269.936 | 0 | 1 | 10
8488 | 12/20 | 15:00:00 | 283.15 | 98824 | 3.6 | 270 | 7.3431 | 104.4 | 0 | 269.936 | 0 | 1 | 10
8489 | 12/20 | 16:00:00 | 283.15 | 98824 | 2.1 | 290 | 7.3431 | 10.8 | 0 | 269.936 | 0 | 1 | 10
8490 | 12/20 | 17:00:00 | 283.15 | 98824 | 2.6 | 260 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
8491 | 12/20 | 18:00:00 | 283.15 | 98824 | 5.1 | 290 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10
8492 | 12/20 | 19:00:00 | 282.15 | 98815 | 2.1 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
8493 | 12/20 | 20:00:00 | 283.15 | 98824 | 3.6 | 250 | 6.8564 | 0 | 0 | 268.971 | 0 | 1 | 10
8494 | 12/20 | 21:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1 | 9
8495 | 12/20 | 22:00:00 | 282.15 | 98815 | 4.1 | 270 | 6.8571 | 0 | 0 | 268.867 | 0 | 1 | 9
8496 | 12/20 | 23:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
8497 | 12/20 | 24:00:00 | 281.15 | 98806 | 4.6 | 280 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
8498 | 12/21 | 01:00:00 | 281.15 | 98806 | 4.1 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1 | 8
8499 | 12/21 | 02:00:00 | 281.15 | 98806 | 3.6 | 290 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
8500 | 12/21 | 03:00:00 | 281.15 | 98806 | 3.1 | 270 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
8501 | 12/21 | 04:00:00 | 281.15 | 98806 | 0.5 | 87 | 6.4 | 0 | 0 | 266.846 | 0 | 1 | 8
8502 | 12/21 | 05:00:00 | 280.15 | 98798 | 2.6 | 280 | 6.4005 | 0 | 0 | 265.897 | 0 | 1 | 7
8503 | 12/21 | 06:00:00 | 281.15 | 98806 | 2.6 | 310 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
8504 | 12/21 | 07:00:00 | 280.15 | 98798 | 1 | 100 | 5.9703 | 0 | 0 | 265.931 | 0 | 1 | 7
8505 | 12/21 | 08:00:00 | 281.15 | 98806 | 2.1 | 170 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
8506 | 12/21 | 09:00:00 | 281.15 | 98806 | 1.5 | 140 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
8507 | 12/21 | 10:00:00 | 281.15 | 98806 | 0.5 | 143 | 6.4 | 90 | 0 | 267.58 | 0 | 1 | 8
8508 | 12/21 | 11:00:00 | 281.15 | 98806 | 0.5 | 179 | 6.8577 | 205.2 | 0 | 267.805 | 0 | 1 | 8
8509 | 12/21 | 12:00:00 | 281.15 | 98806 | 1 | 211 | 6.8577 | 277.2 | 7.2 | 267.805 | 0 | 1 | 8
8510 | 12/21 | 13:00:00 | 282.15 | 98815 | 2.1 | 190 | 6.8571 | 280.8 | 10.8 | 268.758 | 0 | 1 | 9
8511 | 12/21 | 14:00:00 | 282.15 | 98815 | 2.6 | 200 | 6.8571 | 219.6 | 0 | 268.758 | 0 | 1 | 9
8512 | 12/21 | 15:00:00 | 282.15 | 98815 | 2.1 | 240 | 7.3438 | 108 | 0 | 268.983 | 0 | 1 | 9
8513 | 12/21 | 16:00:00 | 283.15 | 98824 | 1.5 | 317 | 7.3431 | 10.8 | 0 | 269.936 | 0 | 1 | 10
8514 | 12/21 | 17:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
8515 | 12/21 | 18:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
8516 | 12/21 | 19:00:00 | 282.15 | 98815 | 4.1 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
8517 | 12/21 | 20:00:00 | 283.15 | 98824 | 4.1 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1 | 10
8518 | 12/21 | 21:00:00 | 282.15 | 98815 | 2.6 | 250 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
8519 | 12/21 | 22:00:00 | 282.15 | 98815 | 3.6 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
8520 | 12/21 | 23:00:00 | 282.15 | 98815 | 3.6 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
8521 | 12/21 | 24:00:00 | 282.15 | 98815 | 2.1 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
8522 | 12/22 | 01:00:00 | 282.15 | 98815 | 3.6 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1 | 9
8523 | 12/22 | 02:00:00 | 282.15 | 98815 | 3.6 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8524 | 12/22 | 03:00:00 | 282.15 | 98815 | 3.1 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8525 | 12/22 | 04:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8526 | 12/22 | 05:00:00 | 282.15 | 98815 | 3.6 | 300 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8527 | 12/22 | 06:00:00 | 282.15 | 98815 | 3.6 | 290 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8528 | 12/22 | 07:00:00 | 282.15 | 98815 | 1.5 | 148 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8529 | 12/22 | 08:00:00 | 282.15 | 98815 | 3.6 | 290 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8530 | 12/22 | 09:00:00 | 282.15 | 98815 | 4.1 | 300 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8531 | 12/22 | 10:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.8571 | 86.4 | 0 | 268.758 | 0 | 1 | 9
8532 | 12/22 | 11:00:00 | 282.15 | 98815 | 2.6 | 250 | 7.3438 | 205.2 | 0 | 268.983 | 0 | 1 | 9
8533 | 12/22 | 12:00:00 | 282.15 | 98815 | 3.1 | 260 | 7.3438 | 277.2 | 7.2 | 268.983 | 0 | 1 | 9
8534 | 12/22 | 13:00:00 | 282.15 | 98815 | 4.6 | 270 | 7.3438 | 280.8 | 10.8 | 268.983 | 0 | 1 | 9
8535 | 12/22 | 14:00:00 | 282.15 | 98815 | 7.2 | 280 | 6.8571 | 219.6 | 0 | 268.758 | 0 | 1 | 9
8536 | 12/22 | 15:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.8571 | 108 | 0 | 268.758 | 0 | 1 | 9
8537 | 12/22 | 16:00:00 | 282.15 | 98815 | 5.7 | 270 | 6.8571 | 14.4 | 0 | 268.758 | 0 | 1 | 9
8538 | 12/22 | 17:00:00 | 282.15 | 98815 | 3.6 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8539 | 12/22 | 18:00:00 | 282.15 | 98815 | 4.1 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8540 | 12/22 | 19:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8541 | 12/22 | 20:00:00 | 282.15 | 98815 | 6.7 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8542 | 12/22 | 21:00:00 | 280.15 | 98798 | 10.3 | 270 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
8543 | 12/22 | 22:00:00 | 280.15 | 98798 | 9.8 | 270 | 6.4005 | 0 | 0 | 266.628 | 0 | 1 | 7
8544 | 12/22 | 23:00:00 | 281.15 | 98806 | 10.8 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8545 | 12/22 | 24:00:00 | 281.15 | 98806 | 9.8 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8546 | 12/23 | 01:00:00 | 282.15 | 98815 | 9.3 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8547 | 12/23 | 02:00:00 | 281.15 | 98806 | 11.8 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8548 | 12/23 | 03:00:00 | 282.15 | 98815 | 14.4 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
8549 | 12/23 | 04:00:00 | 281.15 | 98806 | 13.9 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8550 | 12/23 | 05:00:00 | 281.15 | 98806 | 12.9 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8551 | 12/23 | 06:00:00 | 281.15 | 98806 | 9.8 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8552 | 12/23 | 07:00:00 | 281.15 | 98806 | 12.9 | 280 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8553 | 12/23 | 08:00:00 | 281.15 | 98806 | 12.4 | 280 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8554 | 12/23 | 09:00:00 | 281.15 | 98806 | 11.8 | 290 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8555 | 12/23 | 10:00:00 | 281.15 | 98806 | 7.7 | 270 | 6.4 | 86.4 | 0 | 267.58 | 0 | 1 | 8
8556 | 12/23 | 11:00:00 | 281.15 | 98806 | 10.3 | 260 | 6.4 | 205.2 | 0 | 267.58 | 0 | 1 | 8
8557 | 12/23 | 12:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.4 | 277.2 | 10.8 | 267.58 | 0 | 1 | 8
8558 | 12/23 | 13:00:00 | 281.15 | 98806 | 12.9 | 260 | 6.4 | 280.8 | 10.8 | 267.58 | 0 | 1 | 8
8559 | 12/23 | 14:00:00 | 281.15 | 98806 | 10.8 | 260 | 6.4 | 219.6 | 0 | 267.58 | 0 | 1 | 8
8560 | 12/23 | 15:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.4 | 108 | 0 | 267.58 | 0 | 1 | 8
8561 | 12/23 | 16:00:00 | 281.15 | 98806 | 8.2 | 260 | 6.4 | 14.4 | 0 | 267.58 | 0 | 1 | 8
8562 | 12/23 | 17:00:00 | 281.15 | 98806 | 7.7 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8563 | 12/23 | 18:00:00 | 281.15 | 98806 | 9.3 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8564 | 12/23 | 19:00:00 | 282.15 | 98815 | 8.8 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
8565 | 12/23 | 20:00:00 | 281.15 | 98806 | 11.8 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1 | 8
8566 | 12/23 | 21:00:00 | 282.15 | 98815 | 10.3 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
8567 | 12/23 | 22:00:00 | 282.15 | 98815 | 11.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
8568 | 12/23 | 23:00:00 | 282.15 | 98815 | 10.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1 | 9
8569 | 12/23 | 24:00:00 | 283.15 | 98824 | 11.3 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1 | 10
8570 | 12/24 | 01:00:00 | 282.15 | 98815 | 11.8 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1 | 9
8571 | 12/24 | 02:00:00 | 282.15 | 98815 | 9.8 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1 | 9
8572 | 12/24 | 03:00:00 | 283.15 | 98824 | 11.8 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
8573 | 12/24 | 04:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
8574 | 12/24 | 05:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
8575 | 12/24 | 06:00:00 | 282.15 | 98815 | 2.6 | 260 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
8576 | 12/24 | 07:00:00 | 282.15 | 98815 | 7.7 | 260 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
8577 | 12/24 | 08:00:00 | 283.15 | 98824 | 10.3 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
8578 | 12/24 | 09:00:00 | 283.15 | 98824 | 10.8 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1 | 10
8579 | 12/24 | 10:00:00 | 283.15 | 98824 | 11.8 | 250 | 6.3988 | 154.8 | 216 | 269.007 | 0 | 1 | 10
8580 | 12/24 | 11:00:00 | 284.15 | 98833 | 8.8 | 250 | 6.8558 | 367.2 | 810 | 270.185 | 0 | 1 | 11
8581 | 12/24 | 12:00:00 | 283.15 | 98824 | 8.8 | 230 | 6.8564 | 496.8 | 1083.6 | 269.234 | 0 | 1 | 10
8582 | 12/24 | 13:00:00 | 284.15 | 98833 | 8.2 | 230 | 6.8558 | 280.8 | 14.4 | 270.663 | 0 | 1 | 11
8583 | 12/24 | 14:00:00 | 284.15 | 98833 | 9.8 | 230 | 6.8558 | 399.6 | 720 | 270.185 | 0 | 1 | 11
8584 | 12/24 | 15:00:00 | 283.15 | 98824 | 7.2 | 240 | 6.3988 | 198 | 216 | 269.007 | 0 | 1 | 10
8585 | 12/24 | 16:00:00 | 283.15 | 98824 | 8.2 | 240 | 6.3988 | 25.2 | 0 | 269.007 | 0 | 1 | 10
8586 | 12/24 | 17:00:00 | 283.15 | 98824 | 7.7 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
8587 | 12/24 | 18:00:00 | 283.15 | 98824 | 7.2 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
8588 | 12/24 | 19:00:00 | 283.15 | 98824 | 6.7 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
8589 | 12/24 | 20:00:00 | 283.15 | 98824 | 6.7 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
8590 | 12/24 | 21:00:00 | 282.15 | 98815 | 7.2 | 230 | 5.9692 | 0 | 0 | 268.304 | 0 | 1 | 9
8591 | 12/24 | 22:00:00 | 283.15 | 98824 | 8.8 | 230 | 6.3988 | 0 | 0 | 269.483 | 0 | 1 | 10
8592 | 12/24 | 23:00:00 | 282.15 | 98815 | 7.7 | 230 | 6.3994 | 0 | 0 | 268.057 | 0 | 1 | 9
8593 | 12/24 | 24:00:00 | 282.15 | 98815 | 7.7 | 230 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
8594 | 12/25 | 01:00:00 | 282.15 | 98815 | 9.8 | 220 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
8595 | 12/25 | 02:00:00 | 282.15 | 98815 | 8.8 | 230 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
8596 | 12/25 | 03:00:00 | 282.15 | 98815 | 9.3 | 230 | 5.5651 | 0 | 0 | 267.339 | 0 | 1 | 9
8597 | 12/25 | 04:00:00 | 283.15 | 98824 | 10.3 | 230 | 5.9687 | 0 | 0 | 268.516 | 0 | 1 | 10
8598 | 12/25 | 05:00:00 | 283.15 | 98824 | 9.3 | 230 | 5.9687 | 0 | 0 | 268.516 | 0 | 1 | 10
8599 | 12/25 | 06:00:00 | 283.15 | 98824 | 8.8 | 230 | 5.9687 | 0 | 0 | 268.779 | 0 | 1 | 10
8600 | 12/25 | 07:00:00 | 282.15 | 98815 | 6.7 | 220 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
8601 | 12/25 | 08:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.9692 | 0 | 0 | 267.568 | 0 | 1 | 9
8602 | 12/25 | 09:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.5651 | 0 | 0 | 267.601 | 0 | 1 | 9
8603 | 12/25 | 10:00:00 | 282.15 | 98815 | 9.3 | 220 | 5.9692 | 165.6 | 198 | 267.568 | 0 | 1 | 9
8604 | 12/25 | 11:00:00 | 283.15 | 98824 | 6.2 | 230 | 5.9687 | 367.2 | 824.4 | 268.779 | 0 | 1 | 10
8605 | 12/25 | 12:00:00 | 283.15 | 98824 | 6.7 | 220 | 6.3988 | 529.2 | 1342.8 | 268.744 | 0 | 1 | 10
8606 | 12/25 | 13:00:00 | 284.15 | 98833 | 6.2 | 230 | 5.9681 | 543.6 | 1180.8 | 269.465 | 0 | 1 | 11
8607 | 12/25 | 14:00:00 | 283.15 | 98824 | 7.2 | 220 | 5.9687 | 428.4 | 1148.4 | 268.516 | 0 | 1 | 10
8608 | 12/25 | 15:00:00 | 283.15 | 98824 | 6.2 | 210 | 6.3988 | 201.6 | 327.6 | 269.007 | 0 | 1 | 10
8609 | 12/25 | 16:00:00 | 283.15 | 98824 | 8.2 | 200 | 5.9687 | 28.8 | 0 | 268.779 | 0 | 1 | 10
8610 | 12/25 | 17:00:00 | 282.15 | 98815 | 6.7 | 200 | 5.9692 | 0 | 0 | 267.83 | 0 | 1 | 9
8611 | 12/25 | 18:00:00 | 283.15 | 98824 | 8.2 | 190 | 5.9687 | 0 | 0 | 268.779 | 0 | 1 | 10
8612 | 12/25 | 19:00:00 | 283.15 | 98824 | 7.7 | 210 | 5.9687 | 0 | 0 | 268.779 | 0 | 1 | 10
8613 | 12/25 | 20:00:00 | 279.15 | 98789 | 4.6 | 260 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
8614 | 12/25 | 21:00:00 | 277.15 | 98771 | 7.7 | 260 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
8615 | 12/25 | 22:00:00 | 277.15 | 98771 | 6.7 | 280 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
8616 | 12/25 | 23:00:00 | 277.15 | 98771 | 6.7 | 270 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
8617 | 12/25 | 24:00:00 | 277.15 | 98771 | 7.7 | 270 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
8618 | 12/26 | 01:00:00 | 276.15 | 98762 | 7.2 | 270 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
8619 | 12/26 | 02:00:00 | 276.15 | 98762 | 7.7 | 260 | 4.4977 | 0 | 0 | 261.231 | 0 | 1 | 3
8620 | 12/26 | 03:00:00 | 276.15 | 98762 | 6.2 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
8621 | 12/26 | 04:00:00 | 276.15 | 98762 | 4.6 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8622 | 12/26 | 05:00:00 | 276.15 | 98762 | 4.6 | 260 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8623 | 12/26 | 06:00:00 | 275.15 | 98752 | 7.7 | 250 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
8624 | 12/26 | 07:00:00 | 275.15 | 98752 | 6.2 | 250 | 4.1846 | 0 | 0 | 260.056 | 0 | 1 | 2
8625 | 12/26 | 08:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
8626 | 12/26 | 09:00:00 | 275.15 | 98752 | 5.1 | 240 | 4.1846 | 0 | 0 | 260.516 | 0 | 1 | 2
8627 | 12/26 | 10:00:00 | 275.15 | 98752 | 4.1 | 240 | 4.1846 | 154.8 | 169.2 | 260.056 | 0 | 1 | 2
8628 | 12/26 | 11:00:00 | 275.15 | 98752 | 4.1 | 240 | 4.1846 | 370.8 | 849.6 | 260.056 | 0 | 1 | 2
8629 | 12/26 | 12:00:00 | 276.15 | 98762 | 5.7 | 240 | 4.4977 | 504 | 982.8 | 261.231 | 0 | 1 | 3
8630 | 12/26 | 13:00:00 | 277.15 | 98771 | 7.2 | 250 | 4.4973 | 518.4 | 1008 | 262.177 | 0 | 1 | 4
8631 | 12/26 | 14:00:00 | 277.15 | 98771 | 7.7 | 250 | 4.4973 | 406.8 | 975.6 | 262.177 | 0 | 1 | 4
8632 | 12/26 | 15:00:00 | 277.15 | 98771 | 6.7 | 250 | 4.4973 | 205.2 | 234 | 262.177 | 0 | 1 | 4
8633 | 12/26 | 16:00:00 | 277.15 | 98771 | 4.1 | 240 | 4.1838 | 28.8 | 0 | 261.946 | 0 | 1 | 4
8634 | 12/26 | 17:00:00 | 276.15 | 98762 | 2.6 | 240 | 4.1841 | 0 | 0 | 261.001 | 0 | 1 | 3
8635 | 12/26 | 18:00:00 | 275.15 | 98752 | 2.6 | 260 | 4.1846 | 0 | 0 | 259.802 | 0 | 1 | 2
8636 | 12/26 | 19:00:00 | 275.15 | 98752 | 2.1 | 220 | 3.8903 | 0 | 0 | 259.572 | 0 | 1 | 2
8637 | 12/26 | 20:00:00 | 274.15 | 98743 | 0.5 | 255 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
8638 | 12/26 | 21:00:00 | 274.15 | 98743 | 1.5 | 285 | 3.8907 | 0 | 0 | 259.445 | 0 | 1 | 1
8639 | 12/26 | 22:00:00 | 274.15 | 98743 | 3.1 | 30 | 3.8907 | 0 | 0 | 258.628 | 0 | 1 | 1
8640 | 12/26 | 23:00:00 | 274.15 | 98743 | 4.6 | 20 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
8641 | 12/26 | 24:00:00 | 274.15 | 98743 | 6.2 | 30 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
8642 | 12/27 | 01:00:00 | 274.15 | 98743 | 6.2 | 20 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
8643 | 12/27 | 02:00:00 | 274.15 | 98743 | 6.2 | 10 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
8644 | 12/27 | 03:00:00 | 274.15 | 98743 | 7.2 | 20 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
8645 | 12/27 | 04:00:00 | 274.15 | 98743 | 7.7 | 360 | 3.5803 | 0 | 0 | 259.108 | 0 | 1 | 1
8646 | 12/27 | 05:00:00 | 274.15 | 98743 | 7.2 | 10 | 3.5803 | 0 | 0 | 258.651 | 0 | 1 | 1
8647 | 12/27 | 06:00:00 | 275.15 | 98752 | 7.2 | 10 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
8648 | 12/27 | 07:00:00 | 275.15 | 98752 | 6.2 | 360 | 3.5799 | 0 | 0 | 259.594 | 0 | 1 | 2
8649 | 12/27 | 08:00:00 | 275.15 | 98752 | 7.7 | 360 | 3.8903 | 0 | 0 | 259.826 | 0 | 1 | 2
8650 | 12/27 | 09:00:00 | 274.15 | 98743 | 9.3 | 360 | 3.8907 | 0 | 0 | 258.882 | 0 | 1 | 1
8651 | 12/27 | 10:00:00 | 275.15 | 98752 | 8.8 | 340 | 3.2924 | 154.8 | 172.8 | 259.361 | 0 | 1 | 2
8652 | 12/27 | 11:00:00 | 274.15 | 98743 | 7.7 | 330 | 3.2927 | 392.4 | 943.2 | 258.166 | 0 | 1 | 1
8653 | 12/27 | 12:00:00 | 275.15 | 98752 | 5.7 | 300 | 3.0262 | 540 | 1425.6 | 258.873 | 0 | 1 | 2
8654 | 12/27 | 13:00:00 | 274.15 | 98743 | 7.2 | 310 | 3.0265 | 558 | 1116 | 257.932 | 0 | 1 | 1
8655 | 12/27 | 14:00:00 | 274.15 | 98743 | 8.2 | 310 | 2.7801 | 439.2 | 1062 | 257.697 | 0 | 1 | 1
8656 | 12/27 | 15:00:00 | 274.15 | 98743 | 7.2 | 300 | 3.0265 | 223.2 | 583.2 | 257.932 | 0 | 1 | 1
8657 | 12/27 | 16:00:00 | 274.15 | 98743 | 6.7 | 300 | 3.0265 | 28.8 | 0 | 258.305 | 0 | 1 | 1
8658 | 12/27 | 17:00:00 | 273.15 | 98734 | 7.7 | 290 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8659 | 12/27 | 18:00:00 | 273.15 | 98734 | 6.2 | 280 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8660 | 12/27 | 19:00:00 | 273.15 | 98734 | 7.7 | 300 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8661 | 12/27 | 20:00:00 | 273.15 | 98734 | 7.7 | 300 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8662 | 12/27 | 21:00:00 | 273.15 | 98734 | 8.8 | 300 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8663 | 12/27 | 22:00:00 | 273.15 | 98734 | 5.7 | 290 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8664 | 12/27 | 23:00:00 | 272.15 | 98724 | 5.7 | 270 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8665 | 12/27 | 24:00:00 | 272.15 | 98724 | 5.1 | 270 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8666 | 12/28 | 01:00:00 | 273.15 | 98734 | 4.6 | 270 | 2.7804 | 0 | 0 | 257.128 | 0 | 1 | 0
8667 | 12/28 | 02:00:00 | 272.65 | 98729 | 5.1 | 338 | 2.7805 | 0 | 0 | 256.773 | 0 | 1 | -0.5
8668 | 12/28 | 03:00:00 | 272.15 | 98724 | 5.7 | 300 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8669 | 12/28 | 04:00:00 | 272.65 | 98729 | 5.1 | 215 | 2.9013 | 0 | 0 | 256.89 | 0 | 1 | -0.5
8670 | 12/28 | 05:00:00 | 273.15 | 98734 | 4.6 | 310 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8671 | 12/28 | 06:00:00 | 273.15 | 98734 | 2.6 | 300 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8672 | 12/28 | 07:00:00 | 273.15 | 98734 | 3.6 | 270 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8673 | 12/28 | 08:00:00 | 273.15 | 98734 | 5.1 | 290 | 3.0267 | 0 | 0 | 257.478 | 0 | 1 | 0
8674 | 12/28 | 09:00:00 | 274.15 | 98743 | 8.2 | 290 | 3.0265 | 0 | 0 | 257.932 | 0 | 1 | 1
8675 | 12/28 | 10:00:00 | 274.15 | 98743 | 5.7 | 270 | 3.0265 | 165.6 | 226.8 | 257.932 | 0 | 1 | 1
8676 | 12/28 | 11:00:00 | 275.15 | 98752 | 4.6 | 260 | 3.2924 | 396 | 1047.6 | 259.107 | 0 | 1 | 2
8677 | 12/28 | 12:00:00 | 276.15 | 98762 | 6.7 | 280 | 3.2921 | 540 | 1087.2 | 260.049 | 0 | 1 | 3
8678 | 12/28 | 13:00:00 | 276.15 | 98762 | 5.7 | 290 | 3.5796 | 558 | 1108.8 | 260.283 | 0 | 1 | 3
8679 | 12/28 | 14:00:00 | 276.15 | 98762 | 6.7 | 290 | 3.2921 | 442.8 | 1058.4 | 260.049 | 0 | 1 | 3
8680 | 12/28 | 15:00:00 | 277.15 | 98771 | 3.1 | 300 | 3.2918 | 226.8 | 590.4 | 260.991 | 0 | 1 | 4
8681 | 12/28 | 16:00:00 | 276.15 | 98762 | 4.6 | 290 | 3.2921 | 36 | 0 | 260.049 | 0 | 1 | 3
8682 | 12/28 | 17:00:00 | 274.15 | 98743 | 5.1 | 290 | 3.2927 | 0 | 0 | 258.166 | 0 | 1 | 1
8683 | 12/28 | 18:00:00 | 274.15 | 98743 | 5.7 | 280 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8684 | 12/28 | 19:00:00 | 274.15 | 98743 | 5.7 | 270 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
8685 | 12/28 | 20:00:00 | 274.15 | 98743 | 8.2 | 270 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
8686 | 12/28 | 21:00:00 | 274.15 | 98743 | 5.7 | 270 | 3.5803 | 0 | 0 | 259 | 0 | 1 | 1
8687 | 12/28 | 22:00:00 | 274.15 | 98743 | 5.1 | 280 | 3.2927 | 0 | 0 | 258.655 | 0 | 1 | 1
8688 | 12/28 | 23:00:00 | 273.15 | 98734 | 4.6 | 270 | 3.293 | 0 | 0 | 257.823 | 0 | 1 | 0
8689 | 12/28 | 24:00:00 | 273.15 | 98734 | 3.6 | 230 | 3.293 | 0 | 0 | 257.823 | 0 | 1 | 0
8690 | 12/29 | 01:00:00 | 272.15 | 98724 | 3.6 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
8691 | 12/29 | 02:00:00 | 271.15 | 98715 | 2.1 | 200 | 3.0273 | 0 | 0 | 255.811 | 0 | 1 | -2
8692 | 12/29 | 03:00:00 | 272.15 | 98724 | 3.1 | 200 | 3.0271 | 0 | 0 | 256.647 | 0 | 1 | -1
8693 | 12/29 | 04:00:00 | 272.15 | 98724 | 1.5 | 227 | 2.7806 | 0 | 0 | 256.302 | 0 | 1 | -1
8694 | 12/29 | 05:00:00 | 271.15 | 98715 | 3.6 | 130 | 3.0273 | 0 | 0 | 255.36 | 0 | 1 | -2
8695 | 12/29 | 06:00:00 | 271.15 | 98715 | 3.1 | 130 | 3.0273 | 0 | 0 | 255.36 | 0 | 1 | -2
8696 | 12/29 | 07:00:00 | 272.15 | 98724 | 4.1 | 120 | 3.2934 | 0 | 0 | 257.091 | 0 | 1 | -1
8697 | 12/29 | 08:00:00 | 272.15 | 98724 | 5.1 | 130 | 3.2934 | 0 | 0 | 256.987 | 0 | 1 | -1
8698 | 12/29 | 09:00:00 | 273.15 | 98734 | 5.7 | 130 | 3.5806 | 0 | 0 | 258.163 | 0 | 1 | 0
8699 | 12/29 | 10:00:00 | 273.15 | 98734 | 4.1 | 130 | 3.5806 | 75.6 | 0 | 258.163 | 0 | 1 | 0
8700 | 12/29 | 11:00:00 | 272.15 | 98724 | 2.6 | 130 | 3.581 | 126 | 0 | 257.322 | 0 | 1 | -1
8701 | 12/29 | 12:00:00 | 273.15 | 98734 | 1.5 | 22 | 3.891 | 172.8 | 0 | 258.498 | 0 | 1 | 0
8702 | 12/29 | 13:00:00 | 273.15 | 98734 | 0.5 | 78 | 3.891 | 291.6 | 14.4 | 258.394 | 0 | 1 | 0
8703 | 12/29 | 14:00:00 | 274.15 | 98743 | 4.1 | 260 | 3.8907 | 417.6 | 903.6 | 258.882 | 0 | 1 | 1
8704 | 12/29 | 15:00:00 | 275.15 | 98752 | 4.6 | 250 | 4.4981 | 118.8 | 0 | 260.745 | 0 | 1 | 2
8705 | 12/29 | 16:00:00 | 276.15 | 98762 | 8.8 | 270 | 4.4977 | 21.6 | 0 | 261.693 | 0 | 1 | 3
8706 | 12/29 | 17:00:00 | 276.15 | 98762 | 6.2 | 270 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
8707 | 12/29 | 18:00:00 | 277.15 | 98771 | 3.6 | 250 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
8708 | 12/29 | 19:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
8709 | 12/29 | 20:00:00 | 278.15 | 98780 | 9.8 | 250 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
8710 | 12/29 | 21:00:00 | 278.15 | 98780 | 9.3 | 250 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
8711 | 12/29 | 22:00:00 | 278.15 | 98780 | 5.1 | 250 | 4.4968 | 0 | 0 | 263.123 | 0 | 1 | 5
8712 | 12/29 | 23:00:00 | 277.15 | 98771 | 5.1 | 230 | 4.1838 | 0 | 0 | 261.946 | 0 | 1 | 4
8713 | 12/29 | 24:00:00 | 277.15 | 98771 | 3.1 | 180 | 4.1838 | 0 | 0 | 261.69 | 0 | 1 | 4
8714 | 12/30 | 01:00:00 | 276.15 | 98762 | 2.6 | 230 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8715 | 12/30 | 02:00:00 | 276.15 | 98762 | 2.6 | 190 | 4.1841 | 0 | 0 | 261.463 | 0 | 1 | 3
8716 | 12/30 | 03:00:00 | 274.15 | 98743 | 2.6 | 180 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
8717 | 12/30 | 04:00:00 | 274.15 | 98743 | 4.1 | 140 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
8718 | 12/30 | 05:00:00 | 274.15 | 98743 | 4.1 | 130 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
8719 | 12/30 | 06:00:00 | 274.15 | 98743 | 3.6 | 100 | 3.8907 | 0 | 0 | 259.34 | 0 | 1 | 1
8720 | 12/30 | 07:00:00 | 273.15 | 98734 | 1.5 | 230 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
8721 | 12/30 | 08:00:00 | 273.15 | 98734 | 0.5 | 42 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
8722 | 12/30 | 09:00:00 | 273.15 | 98734 | 1 | 178 | 3.891 | 0 | 0 | 258.394 | 0 | 1 | 0
8723 | 12/30 | 10:00:00 | 275.15 | 98752 | 3.1 | 260 | 4.4981 | 86.4 | 0 | 260.745 | 0 | 1 | 2
8724 | 12/30 | 11:00:00 | 278.15 | 98780 | 8.2 | 260 | 5.5671 | 205.2 | 0 | 264.274 | 0 | 1 | 5
8725 | 12/30 | 12:00:00 | 280.15 | 98798 | 9.3 | 260 | 5.9703 | 280.8 | 14.4 | 266.402 | 0 | 1 | 7
8726 | 12/30 | 13:00:00 | 279.15 | 98789 | 5.7 | 250 | 5.9708 | 525.6 | 1148.4 | 264.982 | 0 | 1 | 6
8727 | 12/30 | 14:00:00 | 281.15 | 98806 | 11.8 | 260 | 5.5656 | 421.2 | 990 | 266.653 | 0 | 1 | 8
8728 | 12/30 | 15:00:00 | 281.15 | 98806 | 11.8 | 250 | 5.5656 | 219.6 | 252 | 266.653 | 0 | 1 | 8
8729 | 12/30 | 16:00:00 | 281.15 | 98806 | 10.8 | 260 | 5.1861 | 39.6 | 0 | 266.423 | 0 | 1 | 8
8730 | 12/30 | 17:00:00 | 280.15 | 98798 | 8.8 | 250 | 4.8303 | 0 | 0 | 265.246 | 0 | 1 | 7
8731 | 12/30 | 18:00:00 | 280.15 | 98798 | 7.7 | 260 | 4.8303 | 0 | 0 | 264.986 | 0 | 1 | 7
8732 | 12/30 | 19:00:00 | 280.15 | 98798 | 9.8 | 260 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
8733 | 12/30 | 20:00:00 | 280.15 | 98798 | 6.7 | 250 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
8734 | 12/30 | 21:00:00 | 280.15 | 98798 | 7.7 | 260 | 4.8303 | 0 | 0 | 265.488 | 0 | 1 | 7
8735 | 12/30 | 22:00:00 | 279.15 | 98789 | 0.5 | 126 | 4.4964 | 0 | 0 | 264.31 | 0 | 1 | 6
8736 | 12/30 | 23:00:00 | 279.15 | 98789 | 2.1 | 200 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
8737 | 12/30 | 24:00:00 | 279.15 | 98789 | 1.5 | 56 | 4.8307 | 0 | 0 | 264.656 | 0 | 1 | 6
8738 | 12/31 | 01:00:00 | 279.15 | 98789 | 3.1 | 150 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
8739 | 12/31 | 02:00:00 | 279.15 | 98789 | 7.2 | 140 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
8740 | 12/31 | 03:00:00 | 279.15 | 98789 | 6.7 | 150 | 5.5666 | 0 | 0 | 265.224 | 0 | 1 | 6
8741 | 12/31 | 04:00:00 | 281.15 | 98806 | 3.6 | 190 | 6.4 | 0 | 0 | 267.107 | 0 | 1 | 8
8742 | 12/31 | 05:00:00 | 283.15 | 98824 | 8.2 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1 | 10
8743 | 12/31 | 06:00:00 | 283.15 | 98824 | 9.8 | 230 | 6.3988 | 0 | 0 | 268.744 | 0 | 1 | 10
8744 | 12/31 | 07:00:00 | 283.15 | 98824 | 9.3 | 230 | 5.5646 | 0 | 0 | 268.287 | 0 | 1 | 10
8745 | 12/31 | 08:00:00 | 282.15 | 98815 | 9.8 | 230 | 5.1856 | 0 | 0 | 267.371 | 0 | 1 | 9
8746 | 12/31 | 09:00:00 | 281.15 | 98806 | 7.7 | 240 | 5.1861 | 0 | 0 | 266.423 | 0 | 1 | 8
8747 | 12/31 | 10:00:00 | 280.15 | 98798 | 6.7 | 240 | 4.8303 | 162 | 291.6 | 264.986 | 0 | 1 | 7
8748 | 12/31 | 11:00:00 | 280.15 | 98798 | 6.7 | 230 | 4.8303 | 396 | 1026 | 264.986 | 0 | 1 | 7
8749 | 12/31 | 12:00:00 | 281.15 | 98806 | 6.7 | 240 | 4.8299 | 511.2 | 1159.2 | 266.193 | 0 | 1 | 8
8750 | 12/31 | 13:00:00 | 281.15 | 98806 | 7.7 | 250 | 4.8299 | 565.2 | 1432.8 | 265.932 | 0 | 1 | 8
8751 | 12/31 | 14:00:00 | 281.15 | 98806 | 5.7 | 250 | 4.4957 | 453.6 | 1227.6 | 265.7 | 0 | 1 | 8
8752 | 12/31 | 15:00:00 | 281.15 | 98806 | 5.7 | 250 | 4.8299 | 223.2 | 385.2 | 266.193 | 0 | 1 | 8
8753 | 12/31 | 16:00:00 | 280.15 | 98798 | 3.6 | 240 | 5.1865 | 39.6 | 0 | 265.476 | 0 | 1 | 7
8754 | 12/31 | 17:00:00 | 279.15 | 98789 | 2.6 | 240 | 5.187 | 0 | 0 | 264.528 | 0 | 1 | 6
8755 | 12/31 | 18:00:00 | 279.15 | 98789 | 6.2 | 220 | 4.8307 | 0 | 0 | 264.041 | 0 | 1 | 6
8756 | 12/31 | 19:00:00 | 279.15 | 98789 | 4.1 | 210 | 4.8307 | 0 | 0 | 264.299 | 0 | 1 | 6
8757 | 12/31 | 20:00:00 | 279.15 | 98789 | 5.7 | 220 | 5.187 | 0 | 0 | 264.996 | 0 | 1 | 6
8758 | 12/31 | 21:00:00 | 277.15 | 98771 | 8.8 | 250 | 4.4973 | 0 | 0 | 262.64 | 0 | 1 | 4
8759 | 12/31 | 22:00:00 | 276.15 | 98762 | 5.1 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1 | 3
8760 | 12/31 | 23:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.8316 | 0 | 0 | 262.87 | 0 | 1 | 4
8761 | 12/31 | 24:00:00 | 277.15 | 98771 | 9.8 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1 | 4
8762 | 12/31 | 24:00:00 | 283.15 | 98824 | 4.6 | 230 | 7.3431 | 0 | 0 | 269.46 | 0 | 1 | 10

## Daily Schedule
Daily Schedule
First Session | 09:00 - 10:30
Second Session | 10:45 - 12:00
Third Session | 13:00 - 14:00
Forth Session | 14:15 - 15:15

## Supporting Tables
CONTAM Input Data
Data Types
Leakage | Airflow elements
Wind pressure coefficients
Ventilation | Duct losses
Fan curves
Schedules for openings and ventilation systems
Contaminant Dispersal | Contaminant source
Filter efficiencies
Reaction and depostion rates
Schedules for elements

## Weather Data (Original)
!Date | Time | Ta [K] | Pb [Pa] | Ws [m/s] | Wd [deg] | Hr [g/kg] | Ith [kJ/m^2] | Idn [kJ/m^2] | Ts [K] | Rn [-] | Sn [-]
1/1 | 00:00:00 | 277.15 | 98771 | 9.8 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/1 | 01:00:00 | 283.15 | 98824 | 4.6 | 230 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
1/1 | 02:00:00 | 283.15 | 98824 | 6.2 | 230 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
1/1 | 03:00:00 | 282.15 | 98815 | 7.7 | 240 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
1/1 | 04:00:00 | 282.15 | 98815 | 7.7 | 230 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
1/1 | 05:00:00 | 282.15 | 98815 | 5.7 | 230 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
1/1 | 06:00:00 | 281.15 | 98806 | 6.2 | 230 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
1/1 | 07:00:00 | 281.15 | 98806 | 7.7 | 230 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
1/1 | 08:00:00 | 281.15 | 98806 | 6.2 | 220 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
1/1 | 09:00:00 | 281.15 | 98806 | 7.2 | 230 | 6.4 | 0 | 0 | 267.107 | 0 | 1
1/1 | 10:00:00 | 281.15 | 98806 | 7.2 | 230 | 5.9698 | 154.8 | 219.6 | 266.881 | 0 | 1
1/1 | 11:00:00 | 280.15 | 98798 | 6.2 | 240 | 5.9703 | 374.4 | 889.2 | 265.931 | 0 | 1
1/1 | 12:00:00 | 281.15 | 98806 | 7.7 | 220 | 6.4 | 514.8 | 903.6 | 267.107 | 0 | 1
1/1 | 13:00:00 | 281.15 | 98806 | 6.2 | 230 | 6.4 | 298.8 | 25.2 | 267.58 | 0 | 1
1/1 | 14:00:00 | 279.15 | 98789 | 8.2 | 250 | 5.5666 | 435.6 | 792 | 264.756 | 0 | 1
1/1 | 15:00:00 | 279.15 | 98789 | 6.7 | 250 | 5.5666 | 234 | 273.6 | 264.756 | 0 | 1
1/1 | 16:00:00 | 279.15 | 98789 | 5.7 | 230 | 5.187 | 50.4 | 0 | 264.269 | 0 | 1
1/1 | 17:00:00 | 279.15 | 98789 | 4.1 | 240 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
1/1 | 18:00:00 | 279.15 | 98789 | 4.6 | 240 | 5.187 | 0 | 0 | 264.269 | 0 | 1
1/1 | 19:00:00 | 278.15 | 98780 | 4.6 | 240 | 5.1875 | 0 | 0 | 263.323 | 0 | 1
1/1 | 20:00:00 | 278.15 | 98780 | 6.2 | 240 | 5.1875 | 0 | 0 | 263.323 | 0 | 1
1/1 | 21:00:00 | 278.15 | 98780 | 6.7 | 250 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
1/1 | 22:00:00 | 277.15 | 98771 | 6.7 | 240 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/1 | 23:00:00 | 277.15 | 98771 | 5.7 | 240 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/1 | 24:00:00 | 276.15 | 98762 | 5.1 | 260 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
1/2 | 01:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
1/2 | 02:00:00 | 276.15 | 98762 | 3.6 | 230 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
1/2 | 03:00:00 | 275.15 | 98752 | 4.1 | 210 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
1/2 | 04:00:00 | 275.15 | 98752 | 3.6 | 220 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/2 | 05:00:00 | 275.15 | 98752 | 4.6 | 230 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/2 | 06:00:00 | 275.15 | 98752 | 5.7 | 220 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/2 | 07:00:00 | 276.15 | 98762 | 8.2 | 230 | 3.8899 | 0 | 0 | 260.515 | 0 | 1
1/2 | 08:00:00 | 275.15 | 98752 | 5.7 | 230 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
1/2 | 09:00:00 | 274.15 | 98743 | 5.7 | 230 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
1/2 | 10:00:00 | 275.15 | 98752 | 4.1 | 230 | 4.1846 | 158.4 | 180 | 260.056 | 0 | 1
1/2 | 11:00:00 | 276.15 | 98762 | 6.2 | 240 | 4.1841 | 381.6 | 810 | 261.001 | 0 | 1
1/2 | 12:00:00 | 277.15 | 98771 | 7.2 | 230 | 3.8896 | 529.2 | 1216.8 | 261.714 | 0 | 1
1/2 | 13:00:00 | 277.15 | 98771 | 7.2 | 240 | 3.8896 | 550.8 | 961.2 | 261.714 | 0 | 1
1/2 | 14:00:00 | 277.15 | 98771 | 6.7 | 240 | 3.8896 | 446.4 | 1062 | 261.714 | 0 | 1
1/2 | 15:00:00 | 278.15 | 98780 | 7.2 | 240 | 3.5789 | 241.2 | 554.4 | 262.425 | 0 | 1
1/2 | 16:00:00 | 277.15 | 98771 | 9.8 | 240 | 3.5793 | 50.4 | 0 | 261.481 | 0 | 1
1/2 | 17:00:00 | 276.15 | 98762 | 7.2 | 240 | 3.5796 | 0 | 0 | 260.538 | 0 | 1
1/2 | 18:00:00 | 276.15 | 98762 | 8.7 | 240 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
1/2 | 19:00:00 | 276.15 | 98762 | 5.7 | 230 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
1/2 | 20:00:00 | 276.15 | 98762 | 6.7 | 230 | 3.8899 | 0 | 0 | 260.515 | 0 | 1
1/2 | 21:00:00 | 276.15 | 98762 | 5.1 | 240 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
1/2 | 22:00:00 | 276.15 | 98762 | 6.7 | 220 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
1/2 | 23:00:00 | 276.15 | 98762 | 6.2 | 220 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
1/2 | 24:00:00 | 276.15 | 98762 | 5.1 | 210 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
1/3 | 01:00:00 | 276.15 | 98762 | 4.1 | 180 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
1/3 | 02:00:00 | 277.15 | 98771 | 5.7 | 190 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/3 | 03:00:00 | 276.15 | 98762 | 6.7 | 170 | 4.832 | 0 | 0 | 261.921 | 0 | 1
1/3 | 04:00:00 | 277.15 | 98771 | 7.7 | 170 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
1/3 | 05:00:00 | 280.15 | 98798 | 11.3 | 190 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
1/3 | 06:00:00 | 281.15 | 98806 | 12.3 | 210 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/3 | 07:00:00 | 283.15 | 98824 | 10.3 | 220 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
1/3 | 08:00:00 | 284.15 | 98833 | 14.9 | 230 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
1/3 | 09:00:00 | 281.15 | 98806 | 14.9 | 260 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
1/3 | 10:00:00 | 280.15 | 98798 | 13.4 | 250 | 5.1865 | 162 | 237.6 | 265.476 | 0 | 1
1/3 | 11:00:00 | 280.15 | 98798 | 14.4 | 250 | 4.8303 | 385.2 | 928.8 | 265.246 | 0 | 1
1/3 | 12:00:00 | 279.15 | 98789 | 13.9 | 260 | 4.4964 | 529.2 | 1202.4 | 264.069 | 0 | 1
1/3 | 13:00:00 | 279.15 | 98789 | 13.9 | 260 | 4.183 | 554.4 | 964.8 | 263.837 | 0 | 1
1/3 | 14:00:00 | 278.15 | 98780 | 13.9 | 260 | 4.4968 | 450 | 1051.2 | 263.123 | 0 | 1
1/3 | 15:00:00 | 278.15 | 98780 | 13.4 | 270 | 3.8892 | 248.4 | 568.8 | 262.659 | 0 | 1
1/3 | 16:00:00 | 277.15 | 98771 | 13.9 | 270 | 3.5793 | 54 | 0 | 261.481 | 0 | 1
1/3 | 17:00:00 | 276.15 | 98762 | 13.9 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/3 | 18:00:00 | 276.15 | 98762 | 10.3 | 260 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/3 | 19:00:00 | 277.15 | 98771 | 12.3 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/3 | 20:00:00 | 278.15 | 98780 | 11.3 | 250 | 4.1834 | 0 | 0 | 262.891 | 0 | 1
1/3 | 21:00:00 | 278.15 | 98780 | 9.8 | 250 | 4.1834 | 0 | 0 | 262.891 | 0 | 1
1/3 | 22:00:00 | 276.15 | 98762 | 10.3 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
1/3 | 23:00:00 | 277.15 | 98771 | 11.3 | 280 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
1/3 | 24:00:00 | 276.15 | 98762 | 10.8 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/4 | 01:00:00 | 276.15 | 98762 | 13.4 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/4 | 02:00:00 | 276.15 | 98762 | 12.3 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/4 | 03:00:00 | 276.15 | 98762 | 10.3 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/4 | 04:00:00 | 277.15 | 98771 | 9.3 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/4 | 05:00:00 | 277.15 | 98771 | 9.8 | 280 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/4 | 06:00:00 | 277.15 | 98771 | 8.7 | 270 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
1/4 | 07:00:00 | 277.15 | 98771 | 7.7 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/4 | 08:00:00 | 278.15 | 98780 | 8.2 | 260 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/4 | 09:00:00 | 278.15 | 98780 | 5.7 | 250 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
1/4 | 10:00:00 | 278.15 | 98780 | 6.2 | 250 | 4.8311 | 90 | 0 | 263.818 | 0 | 1
1/4 | 11:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.8311 | 216 | 0 | 263.818 | 0 | 1
1/4 | 12:00:00 | 278.15 | 98780 | 8.7 | 250 | 4.8311 | 295.2 | 18 | 263.818 | 0 | 1
1/4 | 13:00:00 | 278.15 | 98780 | 9.8 | 250 | 5.1875 | 309.6 | 21.6 | 264.047 | 0 | 1
1/4 | 14:00:00 | 278.15 | 98780 | 9.8 | 250 | 5.1875 | 252 | 3.6 | 264.047 | 0 | 1
1/4 | 15:00:00 | 279.15 | 98789 | 11.3 | 250 | 5.187 | 140.4 | 0 | 264.996 | 0 | 1
1/4 | 16:00:00 | 278.15 | 98780 | 11.8 | 250 | 5.1875 | 32.4 | 0 | 264.047 | 0 | 1
1/4 | 17:00:00 | 279.15 | 98789 | 12.9 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/4 | 18:00:00 | 279.15 | 98789 | 15.9 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/4 | 19:00:00 | 279.15 | 98789 | 14.9 | 250 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
1/4 | 20:00:00 | 279.15 | 98789 | 14.9 | 250 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
1/4 | 21:00:00 | 280.15 | 98798 | 14.4 | 260 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
1/4 | 22:00:00 | 280.15 | 98798 | 17.5 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
1/4 | 23:00:00 | 280.15 | 98798 | 16.5 | 260 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
1/4 | 24:00:00 | 281.15 | 98806 | 17.5 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/5 | 01:00:00 | 282.15 | 98815 | 19 | 270 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
1/5 | 02:00:00 | 279.15 | 98789 | 17 | 290 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
1/5 | 03:00:00 | 278.15 | 98780 | 13.9 | 280 | 5.5671 | 0 | 0 | 263.807 | 0 | 1
1/5 | 04:00:00 | 280.15 | 98798 | 14.4 | 280 | 4.8303 | 0 | 0 | 265.246 | 0 | 1
1/5 | 05:00:00 | 280.15 | 98798 | 13.9 | 270 | 4.8303 | 0 | 0 | 265.715 | 0 | 1
1/5 | 06:00:00 | 278.15 | 98780 | 15.4 | 290 | 5.5671 | 0 | 0 | 263.807 | 0 | 1
1/5 | 07:00:00 | 278.15 | 98780 | 14.4 | 290 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
1/5 | 08:00:00 | 278.15 | 98780 | 15.9 | 280 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
1/5 | 09:00:00 | 278.15 | 98780 | 14.9 | 280 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
1/5 | 10:00:00 | 276.15 | 98762 | 13.9 | 280 | 4.832 | 165.6 | 252 | 261.459 | 0 | 1
1/5 | 11:00:00 | 276.15 | 98762 | 14.4 | 280 | 4.832 | 392.4 | 914.4 | 261.459 | 0 | 1
1/5 | 12:00:00 | 278.15 | 98780 | 14.9 | 280 | 4.8311 | 572.4 | 1479.6 | 263.095 | 0 | 1
1/5 | 13:00:00 | 279.15 | 98789 | 15.9 | 310 | 3.8889 | 604.8 | 1180.8 | 263.345 | 0 | 1
1/5 | 14:00:00 | 279.15 | 98789 | 11.8 | 320 | 3.8889 | 493.2 | 1159.2 | 263.345 | 0 | 1
1/5 | 15:00:00 | 279.15 | 98789 | 7.2 | 310 | 4.183 | 277.2 | 741.6 | 263.578 | 0 | 1
1/5 | 16:00:00 | 278.15 | 98780 | 8.7 | 310 | 3.5789 | 64.8 | 0 | 262.168 | 0 | 1
1/5 | 17:00:00 | 277.15 | 98771 | 7.7 | 290 | 3.2918 | 0 | 0 | 261.246 | 0 | 1
1/5 | 18:00:00 | 276.15 | 98762 | 7.2 | 280 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
1/5 | 19:00:00 | 276.15 | 98762 | 9.3 | 280 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
1/5 | 20:00:00 | 276.15 | 98762 | 7.2 | 290 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
1/5 | 21:00:00 | 276.15 | 98762 | 7.2 | 280 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
1/5 | 22:00:00 | 276.15 | 98762 | 8.7 | 290 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
1/5 | 23:00:00 | 277.15 | 98771 | 10.3 | 290 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
1/5 | 24:00:00 | 277.15 | 98771 | 9.3 | 300 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
1/6 | 01:00:00 | 276.15 | 98762 | 8.2 | 300 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
1/6 | 02:00:00 | 276.15 | 98762 | 8.7 | 290 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
1/6 | 03:00:00 | 275.15 | 98752 | 6.2 | 280 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
1/6 | 04:00:00 | 275.15 | 98752 | 7.2 | 300 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
1/6 | 05:00:00 | 275.15 | 98752 | 4.1 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
1/6 | 06:00:00 | 275.15 | 98752 | 5.1 | 290 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
1/6 | 07:00:00 | 275.15 | 98752 | 7.2 | 290 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
1/6 | 08:00:00 | 275.15 | 98752 | 7.7 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
1/6 | 09:00:00 | 274.15 | 98743 | 6.2 | 290 | 3.5803 | 0 | 0 | 259 | 0 | 1
1/6 | 10:00:00 | 274.15 | 98743 | 4.6 | 290 | 3.8907 | 75.6 | 0 | 259.445 | 0 | 1
1/6 | 11:00:00 | 276.15 | 98762 | 4.6 | 270 | 4.1841 | 421.2 | 1044 | 260.746 | 0 | 1
1/6 | 12:00:00 | 278.15 | 98780 | 5.7 | 260 | 4.8311 | 579.6 | 1465.2 | 263.095 | 0 | 1
1/6 | 13:00:00 | 278.15 | 98780 | 4.1 | 250 | 4.8311 | 572.4 | 1000.8 | 263.352 | 0 | 1
1/6 | 14:00:00 | 279.15 | 98789 | 6.2 | 250 | 5.187 | 259.2 | 7.2 | 264.996 | 0 | 1
1/6 | 15:00:00 | 280.15 | 98798 | 7.7 | 260 | 5.5661 | 266.4 | 522 | 265.704 | 0 | 1
1/6 | 16:00:00 | 279.15 | 98789 | 9.3 | 260 | 5.187 | 36 | 0 | 264.996 | 0 | 1
1/6 | 17:00:00 | 279.15 | 98789 | 6.2 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/6 | 18:00:00 | 279.15 | 98789 | 5.1 | 240 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
1/6 | 19:00:00 | 280.15 | 98798 | 8.7 | 250 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
1/6 | 20:00:00 | 280.15 | 98798 | 8.2 | 250 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
1/6 | 21:00:00 | 281.15 | 98806 | 5.7 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/6 | 22:00:00 | 282.15 | 98815 | 7.2 | 250 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/6 | 23:00:00 | 282.15 | 98815 | 8.2 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/6 | 24:00:00 | 282.15 | 98815 | 8.7 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/7 | 01:00:00 | 282.15 | 98815 | 6.7 | 280 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/7 | 02:00:00 | 281.15 | 98806 | 7.7 | 280 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
1/7 | 03:00:00 | 280.15 | 98798 | 11.8 | 270 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
1/7 | 04:00:00 | 280.15 | 98798 | 13.4 | 280 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
1/7 | 05:00:00 | 279.15 | 98789 | 10.3 | 290 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
1/7 | 06:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1
1/7 | 07:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1
1/7 | 08:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.8307 | 0 | 0 | 264.299 | 0 | 1
1/7 | 09:00:00 | 278.15 | 98780 | 9.3 | 280 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
1/7 | 10:00:00 | 279.15 | 98789 | 10.3 | 280 | 4.8307 | 93.6 | 0 | 264.767 | 0 | 1
1/7 | 11:00:00 | 279.15 | 98789 | 9.3 | 290 | 4.8307 | 223.2 | 0 | 264.767 | 0 | 1
1/7 | 12:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.187 | 306 | 25.2 | 264.996 | 0 | 1
1/7 | 13:00:00 | 279.15 | 98789 | 7.7 | 290 | 5.187 | 579.6 | 1252.8 | 264.528 | 0 | 1
1/7 | 14:00:00 | 280.15 | 98798 | 13.4 | 280 | 4.8303 | 478.8 | 1105.2 | 265.246 | 0 | 1
1/7 | 15:00:00 | 279.15 | 98789 | 13.4 | 270 | 4.8307 | 273.6 | 626.4 | 264.299 | 0 | 1
1/7 | 16:00:00 | 279.15 | 98789 | 11.3 | 260 | 4.8307 | 72 | 18 | 264.041 | 0 | 1
1/7 | 17:00:00 | 279.15 | 98789 | 11.3 | 270 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
1/7 | 18:00:00 | 279.15 | 98789 | 10.8 | 270 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
1/7 | 19:00:00 | 279.15 | 98789 | 10.3 | 270 | 4.8307 | 0 | 0 | 264.299 | 0 | 1
1/7 | 20:00:00 | 279.15 | 98789 | 9.8 | 270 | 4.8307 | 0 | 0 | 264.767 | 0 | 1
1/7 | 21:00:00 | 279.15 | 98789 | 12.9 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
1/7 | 22:00:00 | 279.15 | 98789 | 7.2 | 260 | 5.187 | 0 | 0 | 264.528 | 0 | 1
1/7 | 23:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/7 | 24:00:00 | 279.15 | 98789 | 11.3 | 280 | 5.187 | 0 | 0 | 264.528 | 0 | 1
1/8 | 01:00:00 | 279.15 | 98789 | 9.3 | 280 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
1/8 | 02:00:00 | 279.15 | 98789 | 9.3 | 290 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/8 | 03:00:00 | 279.15 | 98789 | 10.8 | 290 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/8 | 04:00:00 | 279.15 | 98789 | 11.3 | 290 | 5.187 | 0 | 0 | 264.528 | 0 | 1
1/8 | 05:00:00 | 279.15 | 98789 | 3.6 | 290 | 5.187 | 0 | 0 | 264.528 | 0 | 1
1/8 | 06:00:00 | 279.15 | 98789 | 4.6 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
1/8 | 07:00:00 | 279.15 | 98789 | 5.7 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
1/8 | 08:00:00 | 279.15 | 98789 | 6.7 | 290 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
1/8 | 09:00:00 | 279.15 | 98789 | 5.1 | 290 | 5.187 | 0 | 0 | 264.528 | 0 | 1
1/8 | 10:00:00 | 279.15 | 98789 | 5.7 | 290 | 5.5666 | 97.2 | 0 | 265.224 | 0 | 1
1/8 | 11:00:00 | 280.15 | 98798 | 3.6 | 270 | 5.5661 | 226.8 | 0 | 266.174 | 0 | 1
1/8 | 12:00:00 | 280.15 | 98798 | 6.2 | 270 | 5.9703 | 309.6 | 21.6 | 266.402 | 0 | 1
1/8 | 13:00:00 | 280.15 | 98798 | 4.6 | 250 | 5.9703 | 324 | 28.8 | 266.402 | 0 | 1
1/8 | 14:00:00 | 281.15 | 98806 | 8.2 | 270 | 6.4 | 270 | 3.6 | 267.58 | 0 | 1
1/8 | 15:00:00 | 281.15 | 98806 | 7.2 | 270 | 6.8577 | 154.8 | 0 | 267.805 | 0 | 1
1/8 | 16:00:00 | 281.15 | 98806 | 8.7 | 270 | 6.8577 | 39.6 | 0 | 267.805 | 0 | 1
1/8 | 17:00:00 | 281.15 | 98806 | 8.7 | 270 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/8 | 18:00:00 | 281.15 | 98806 | 8.2 | 270 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
1/8 | 19:00:00 | 281.15 | 98806 | 6.2 | 260 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
1/8 | 20:00:00 | 281.15 | 98806 | 6.7 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/8 | 21:00:00 | 281.15 | 98806 | 4.1 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/8 | 22:00:00 | 281.15 | 98806 | 8.2 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1
1/8 | 23:00:00 | 281.15 | 98806 | 10.8 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1
1/8 | 24:00:00 | 281.15 | 98806 | 12.9 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/9 | 01:00:00 | 280.15 | 98798 | 12.3 | 260 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
1/9 | 02:00:00 | 280.15 | 98798 | 9.3 | 270 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
1/9 | 03:00:00 | 280.15 | 98798 | 13.9 | 270 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
1/9 | 04:00:00 | 280.15 | 98798 | 11.3 | 270 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
1/9 | 05:00:00 | 280.15 | 98798 | 12.9 | 270 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
1/9 | 06:00:00 | 280.15 | 98798 | 12.9 | 270 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
1/9 | 07:00:00 | 280.15 | 98798 | 10.3 | 270 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
1/9 | 08:00:00 | 281.15 | 98806 | 9.3 | 260 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
1/9 | 09:00:00 | 281.15 | 98806 | 7.7 | 250 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
1/9 | 10:00:00 | 281.15 | 98806 | 6.7 | 250 | 6.4 | 97.2 | 0 | 267.58 | 0 | 1
1/9 | 11:00:00 | 281.15 | 98806 | 5.7 | 260 | 6.4 | 226.8 | 0 | 267.58 | 0 | 1
1/9 | 12:00:00 | 281.15 | 98806 | 6.7 | 280 | 6.8577 | 313.2 | 25.2 | 267.805 | 0 | 1
1/9 | 13:00:00 | 282.15 | 98815 | 6.7 | 280 | 6.3994 | 594 | 1260 | 268.057 | 0 | 1
1/9 | 14:00:00 | 281.15 | 98806 | 6.7 | 280 | 5.9698 | 493.2 | 882 | 266.881 | 0 | 1
1/9 | 15:00:00 | 281.15 | 98806 | 6.7 | 280 | 5.5656 | 158.4 | 0 | 267.125 | 0 | 1
1/9 | 16:00:00 | 281.15 | 98806 | 4.6 | 270 | 5.5656 | 79.2 | 151.2 | 266.392 | 0 | 1
1/9 | 17:00:00 | 279.15 | 98789 | 7.7 | 270 | 5.187 | 0 | 0 | 264.269 | 0 | 1
1/9 | 18:00:00 | 278.15 | 98780 | 6.7 | 270 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
1/9 | 19:00:00 | 277.15 | 98771 | 2.6 | 270 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
1/9 | 20:00:00 | 276.15 | 98762 | 2.6 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
1/9 | 21:00:00 | 276.15 | 98762 | 2.6 | 270 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
1/9 | 22:00:00 | 277.15 | 98771 | 2.1 | 260 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
1/9 | 23:00:00 | 276.15 | 98762 | 2.1 | 260 | 4.832 | 0 | 0 | 261.203 | 0 | 1
1/9 | 24:00:00 | 276.15 | 98762 | 2.6 | 240 | 4.832 | 0 | 0 | 261.203 | 0 | 1
1/10 | 01:00:00 | 277.15 | 98771 | 6.7 | 260 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
1/10 | 02:00:00 | 277.15 | 98771 | 5.7 | 260 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
1/10 | 03:00:00 | 278.15 | 98780 | 5.1 | 260 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
1/10 | 04:00:00 | 279.15 | 98789 | 6.7 | 250 | 5.187 | 0 | 0 | 264.528 | 0 | 1
1/10 | 05:00:00 | 279.15 | 98789 | 5.7 | 260 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
1/10 | 06:00:00 | 279.15 | 98789 | 4.6 | 250 | 5.187 | 0 | 0 | 264.528 | 0 | 1
1/10 | 07:00:00 | 279.15 | 98789 | 4.6 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/10 | 08:00:00 | 279.15 | 98789 | 8.7 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/10 | 09:00:00 | 279.15 | 98789 | 7.2 | 260 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/10 | 10:00:00 | 279.15 | 98789 | 7.2 | 260 | 4.8307 | 183.6 | 298.8 | 264.299 | 0 | 1
1/10 | 11:00:00 | 280.15 | 98798 | 8.7 | 260 | 4.8303 | 421.2 | 1004.4 | 265.246 | 0 | 1
1/10 | 12:00:00 | 280.15 | 98798 | 6.7 | 260 | 4.8303 | 576 | 1004.4 | 265.246 | 0 | 1
1/10 | 13:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.5661 | 334.8 | 36 | 266.174 | 0 | 1
1/10 | 14:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.9703 | 277.2 | 7.2 | 266.402 | 0 | 1
1/10 | 15:00:00 | 281.15 | 98806 | 6.2 | 240 | 6.4 | 165.6 | 0 | 267.58 | 0 | 1
1/10 | 16:00:00 | 281.15 | 98806 | 6.7 | 250 | 6.4 | 43.2 | 0 | 267.58 | 0 | 1
1/10 | 17:00:00 | 281.15 | 98806 | 6.7 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/10 | 18:00:00 | 281.15 | 98806 | 7.2 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/10 | 19:00:00 | 281.15 | 98806 | 7.7 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/10 | 20:00:00 | 282.15 | 98815 | 8.7 | 250 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/10 | 21:00:00 | 282.15 | 98815 | 8.7 | 250 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
1/10 | 22:00:00 | 282.15 | 98815 | 9.3 | 250 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
1/10 | 23:00:00 | 281.15 | 98806 | 7.2 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/10 | 24:00:00 | 281.15 | 98806 | 3.6 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/11 | 01:00:00 | 281.15 | 98806 | 3.6 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/11 | 02:00:00 | 281.15 | 98806 | 4.1 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/11 | 03:00:00 | 282.15 | 98815 | 6.7 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
1/11 | 04:00:00 | 282.15 | 98815 | 7.2 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/11 | 05:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/11 | 06:00:00 | 281.15 | 98806 | 10.3 | 270 | 6.8577 | 0 | 0 | 267.071 | 0 | 1
1/11 | 07:00:00 | 281.15 | 98806 | 6.7 | 280 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
1/11 | 08:00:00 | 281.15 | 98806 | 5.7 | 280 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/11 | 09:00:00 | 282.15 | 98815 | 8.2 | 260 | 6.8571 | 3.6 | 0 | 268.758 | 0 | 1
1/11 | 10:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 104.4 | 0 | 268.758 | 0 | 1
1/11 | 11:00:00 | 282.15 | 98815 | 6.7 | 260 | 7.3438 | 234 | 0 | 268.983 | 0 | 1
1/11 | 12:00:00 | 282.15 | 98815 | 7.7 | 260 | 7.3438 | 320.4 | 25.2 | 268.983 | 0 | 1
1/11 | 13:00:00 | 282.15 | 98815 | 6.2 | 260 | 7.3438 | 338.4 | 28.8 | 268.983 | 0 | 1
1/11 | 14:00:00 | 282.15 | 98815 | 4.1 | 250 | 7.3438 | 284.4 | 7.2 | 268.983 | 0 | 1
1/11 | 15:00:00 | 282.15 | 98815 | 9.3 | 260 | 6.8571 | 169.2 | 0 | 268.758 | 0 | 1
1/11 | 16:00:00 | 282.15 | 98815 | 5.1 | 250 | 6.8571 | 46.8 | 0 | 268.758 | 0 | 1
1/11 | 17:00:00 | 282.15 | 98815 | 6.7 | 250 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
1/11 | 18:00:00 | 282.15 | 98815 | 7.7 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
1/11 | 19:00:00 | 282.15 | 98815 | 7.2 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
1/11 | 20:00:00 | 282.15 | 98815 | 8.2 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/11 | 21:00:00 | 282.15 | 98815 | 8.7 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
1/11 | 22:00:00 | 282.15 | 98815 | 7.2 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
1/11 | 23:00:00 | 281.15 | 98806 | 9.3 | 250 | 6.4 | 0 | 0 | 267.107 | 0 | 1
1/11 | 24:00:00 | 281.15 | 98806 | 8.7 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/12 | 01:00:00 | 281.15 | 98806 | 6.7 | 240 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/12 | 02:00:00 | 281.15 | 98806 | 5.1 | 230 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/12 | 03:00:00 | 281.15 | 98806 | 5.7 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/12 | 04:00:00 | 282.15 | 98815 | 12.9 | 250 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/12 | 05:00:00 | 282.15 | 98815 | 14.4 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/12 | 06:00:00 | 282.15 | 98815 | 15.9 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
1/12 | 07:00:00 | 282.15 | 98815 | 18.5 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/12 | 08:00:00 | 282.15 | 98815 | 15.9 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/12 | 09:00:00 | 281.15 | 98806 | 14.9 | 290 | 5.5656 | 7.2 | 0 | 266.653 | 0 | 1
1/12 | 10:00:00 | 281.15 | 98806 | 8.7 | 290 | 5.1861 | 194.4 | 324 | 266.423 | 0 | 1
1/12 | 11:00:00 | 280.15 | 98798 | 8.7 | 280 | 5.1865 | 460.8 | 1245.6 | 265.216 | 0 | 1
1/12 | 12:00:00 | 281.15 | 98806 | 10.8 | 300 | 5.1861 | 626.4 | 1555.2 | 266.163 | 0 | 1
1/12 | 13:00:00 | 281.15 | 98806 | 9.3 | 310 | 5.1861 | 662.4 | 1386 | 266.163 | 0 | 1
1/12 | 14:00:00 | 280.15 | 98798 | 7.2 | 300 | 4.8303 | 558 | 1432.8 | 264.986 | 0 | 1
1/12 | 15:00:00 | 280.15 | 98798 | 7.7 | 290 | 4.496 | 338.4 | 903.6 | 264.755 | 0 | 1
1/12 | 16:00:00 | 279.15 | 98789 | 6.7 | 290 | 4.183 | 86.4 | 57.6 | 263.959 | 0 | 1
1/12 | 17:00:00 | 278.15 | 98780 | 7.2 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
1/12 | 18:00:00 | 277.15 | 98771 | 6.2 | 290 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
1/12 | 19:00:00 | 277.15 | 98771 | 8.2 | 290 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
1/12 | 20:00:00 | 276.15 | 98762 | 5.7 | 280 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
1/12 | 21:00:00 | 276.15 | 98762 | 5.7 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
1/12 | 22:00:00 | 275.15 | 98752 | 5.7 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
1/12 | 23:00:00 | 276.15 | 98762 | 8.2 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
1/12 | 24:00:00 | 275.15 | 98752 | 5.7 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
1/13 | 01:00:00 | 276.15 | 98762 | 5.7 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
1/13 | 02:00:00 | 275.15 | 98752 | 4.1 | 290 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
1/13 | 03:00:00 | 275.15 | 98752 | 3.6 | 310 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
1/13 | 04:00:00 | 275.15 | 98752 | 3.6 | 290 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
1/13 | 05:00:00 | 275.15 | 98752 | 4.6 | 300 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
1/13 | 06:00:00 | 275.15 | 98752 | 5.7 | 320 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/13 | 07:00:00 | 274.15 | 98743 | 3.6 | 310 | 3.5803 | 0 | 0 | 259 | 0 | 1
1/13 | 08:00:00 | 274.15 | 98743 | 3.6 | 300 | 3.5803 | 0 | 0 | 259 | 0 | 1
1/13 | 09:00:00 | 273.15 | 98734 | 3.6 | 310 | 3.5806 | 3.6 | 0 | 258.163 | 0 | 1
1/13 | 10:00:00 | 273.15 | 98734 | 3.1 | 300 | 3.5806 | 97.2 | 0 | 258.163 | 0 | 1
1/13 | 11:00:00 | 274.15 | 98743 | 3.6 | 310 | 3.5803 | 298.8 | 118.8 | 259 | 0 | 1
1/13 | 12:00:00 | 275.15 | 98752 | 3.6 | 310 | 3.8903 | 388.8 | 147.6 | 260.286 | 0 | 1
1/13 | 13:00:00 | 276.15 | 98762 | 2.1 | 310 | 3.8899 | 504 | 403.2 | 261.122 | 0 | 1
1/13 | 14:00:00 | 277.15 | 98771 | 2.6 | 360 | 3.5793 | 525.6 | 936 | 261.603 | 0 | 1
1/13 | 15:00:00 | 277.15 | 98771 | 1.5 | 159 | 3.5793 | 320.4 | 705.6 | 261.603 | 0 | 1
1/13 | 16:00:00 | 276.15 | 98762 | 1 | 271 | 3.5796 | 86.4 | 32.4 | 260.659 | 0 | 1
1/13 | 17:00:00 | 275.15 | 98752 | 0.5 | 360 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
1/13 | 18:00:00 | 275.15 | 98752 | 0 | 142 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
1/13 | 19:00:00 | 274.15 | 98743 | 0 | 126 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
1/13 | 20:00:00 | 274.15 | 98743 | 0.5 | 206 | 3.5803 | 0 | 0 | 259 | 0 | 1
1/13 | 21:00:00 | 273.15 | 98734 | 0.5 | 200 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/13 | 22:00:00 | 274.15 | 98743 | 1 | 180 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
1/13 | 23:00:00 | 272.15 | 98724 | 1 | 220 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/13 | 24:00:00 | 272.15 | 98724 | 1.5 | 210 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
1/14 | 01:00:00 | 271.15 | 98715 | 2.1 | 240 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
1/14 | 02:00:00 | 272.15 | 98724 | 2.1 | 250 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
1/14 | 03:00:00 | 271.15 | 98715 | 2.1 | 250 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
1/14 | 04:00:00 | 272.15 | 98724 | 2.6 | 270 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
1/14 | 05:00:00 | 273.15 | 98734 | 1.5 | 260 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
1/14 | 06:00:00 | 272.15 | 98724 | 1.5 | 220 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
1/14 | 07:00:00 | 272.15 | 98724 | 0.5 | 131 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
1/14 | 08:00:00 | 271.15 | 98715 | 1 | 250 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
1/14 | 09:00:00 | 272.15 | 98724 | 1 | 260 | 3.0271 | 10.8 | 0 | 256.647 | 0 | 1
1/14 | 10:00:00 | 272.15 | 98724 | 0.5 | 230 | 3.0271 | 144 | 3.6 | 256.647 | 0 | 1
1/14 | 11:00:00 | 275.15 | 98752 | 0.5 | 193 | 3.5799 | 367.2 | 324 | 259.832 | 0 | 1
1/14 | 12:00:00 | 276.15 | 98762 | 0.5 | 49 | 3.5796 | 561.6 | 896.4 | 260.659 | 0 | 1
1/14 | 13:00:00 | 276.15 | 98762 | 1 | 108 | 3.5796 | 594 | 813.6 | 260.659 | 0 | 1
1/14 | 14:00:00 | 276.15 | 98762 | 1.5 | 43 | 3.5796 | 504 | 936 | 260.659 | 0 | 1
1/14 | 15:00:00 | 276.15 | 98762 | 2.1 | 160 | 3.5796 | 309.6 | 306 | 260.659 | 0 | 1
1/14 | 16:00:00 | 275.15 | 98752 | 2.1 | 130 | 3.5799 | 82.8 | 0 | 259.832 | 0 | 1
1/14 | 17:00:00 | 273.15 | 98734 | 2.6 | 130 | 3.293 | 0 | 0 | 257.823 | 0 | 1
1/14 | 18:00:00 | 273.15 | 98734 | 3.1 | 130 | 3.293 | 0 | 0 | 256.813 | 0 | 1
1/14 | 19:00:00 | 272.15 | 98724 | 2.6 | 140 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
1/14 | 20:00:00 | 272.15 | 98724 | 3.6 | 160 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
1/14 | 21:00:00 | 272.15 | 98724 | 2.6 | 160 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
1/14 | 22:00:00 | 270.15 | 98705 | 2.6 | 140 | 3.0276 | 0 | 0 | 254.971 | 0 | 1
1/14 | 23:00:00 | 271.15 | 98715 | 2.6 | 140 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
1/14 | 24:00:00 | 271.15 | 98715 | 2.6 | 150 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
1/15 | 01:00:00 | 270.15 | 98705 | 2.1 | 140 | 3.0276 | 0 | 0 | 253.763 | 0 | 1
1/15 | 02:00:00 | 270.15 | 98705 | 1.5 | 150 | 2.7812 | 0 | 0 | 253.532 | 0 | 1
1/15 | 03:00:00 | 270.15 | 98705 | 0.5 | 27 | 2.8531 | 0 | 0 | 253.601 | 0 | 1
1/15 | 04:00:00 | 269.15 | 98696 | 0 | 60 | 2.7814 | 0 | 0 | 252.593 | 0 | 1
1/15 | 05:00:00 | 270.15 | 98705 | 1 | 100 | 3.0276 | 0 | 0 | 253.763 | 0 | 1
1/15 | 06:00:00 | 269.15 | 98696 | 0.5 | 81 | 2.7814 | 0 | 0 | 252.593 | 0 | 1
1/15 | 07:00:00 | 269.15 | 98696 | 1 | 207 | 2.7814 | 0 | 0 | 252.593 | 0 | 1
1/15 | 08:00:00 | 269.15 | 98696 | 2.1 | 120 | 2.7814 | 0 | 0 | 253.245 | 0 | 1
1/15 | 09:00:00 | 270.15 | 98705 | 1 | 130 | 2.8289 | 7.2 | 0 | 254.682 | 0 | 1
1/15 | 10:00:00 | 271.15 | 98715 | 1 | 100 | 2.8772 | 118.8 | 0 | 255.672 | 0 | 1
1/15 | 11:00:00 | 271.15 | 98715 | 1.5 | 120 | 3.2936 | 460.8 | 1000.8 | 255.591 | 0 | 1
1/15 | 12:00:00 | 272.15 | 98724 | 1 | 100 | 3.5512 | 345.6 | 32.4 | 257.195 | 0 | 1
1/15 | 13:00:00 | 272.15 | 98724 | 1.5 | 120 | 3.581 | 367.2 | 54 | 257.218 | 0 | 1
1/15 | 14:00:00 | 273.15 | 98734 | 3.1 | 140 | 3.6713 | 313.2 | 32.4 | 258.233 | 0 | 1
1/15 | 15:00:00 | 274.15 | 98743 | 2.6 | 120 | 3.8907 | 194.4 | 0 | 259.34 | 0 | 1
1/15 | 16:00:00 | 273.15 | 98734 | 1.5 | 58 | 3.891 | 111.6 | 190.8 | 257.685 | 0 | 1
1/15 | 17:00:00 | 272.15 | 98724 | 3.1 | 90 | 3.581 | 0 | 0 | 256.103 | 0 | 1
1/15 | 18:00:00 | 272.15 | 98724 | 2.6 | 100 | 3.2934 | 0 | 0 | 255.873 | 0 | 1
1/15 | 19:00:00 | 271.15 | 98715 | 3.1 | 90 | 3.2936 | 0 | 0 | 254.933 | 0 | 1
1/15 | 20:00:00 | 271.15 | 98715 | 2.6 | 100 | 3.2936 | 0 | 0 | 254.933 | 0 | 1
1/15 | 21:00:00 | 272.15 | 98724 | 2.6 | 100 | 3.2934 | 0 | 0 | 255.873 | 0 | 1
1/15 | 22:00:00 | 272.15 | 98724 | 3.1 | 120 | 3.581 | 0 | 0 | 256.764 | 0 | 1
1/15 | 23:00:00 | 272.15 | 98724 | 2.1 | 110 | 3.581 | 0 | 0 | 257.218 | 0 | 1
1/15 | 24:00:00 | 273.15 | 98734 | 2.1 | 120 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/16 | 01:00:00 | 272.15 | 98724 | 2.1 | 110 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
1/16 | 02:00:00 | 270.15 | 98705 | 3.1 | 140 | 2.7812 | 0 | 0 | 254.636 | 0 | 1
1/16 | 03:00:00 | 270.15 | 98705 | 0.5 | 142 | 3.0276 | 0 | 0 | 253.763 | 0 | 1
1/16 | 04:00:00 | 272.15 | 98724 | 2.1 | 140 | 3.2934 | 0 | 0 | 255.873 | 0 | 1
1/16 | 05:00:00 | 271.15 | 98715 | 0.5 | 90 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
1/16 | 06:00:00 | 271.15 | 98715 | 1 | 58 | 3.2936 | 0 | 0 | 256.043 | 0 | 1
1/16 | 07:00:00 | 272.15 | 98724 | 1.5 | 100 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
1/16 | 08:00:00 | 271.15 | 98715 | 2.1 | 100 | 3.2936 | 0 | 0 | 256.043 | 0 | 1
1/16 | 09:00:00 | 271.15 | 98715 | 2.1 | 110 | 3.2936 | 18 | 0 | 255.591 | 0 | 1
1/16 | 10:00:00 | 272.15 | 98724 | 2.6 | 140 | 3.2934 | 230.4 | 561.6 | 256.282 | 0 | 1
1/16 | 11:00:00 | 273.15 | 98734 | 0 | 249 | 3.5806 | 500.4 | 1177.2 | 257.455 | 0 | 1
1/16 | 12:00:00 | 274.15 | 98743 | 2.1 | 150 | 3.8907 | 673.2 | 1670.4 | 258.628 | 0 | 1
1/16 | 13:00:00 | 275.15 | 98752 | 2.1 | 150 | 3.8903 | 723.6 | 1767.6 | 259.157 | 0 | 1
1/16 | 14:00:00 | 276.15 | 98762 | 3.6 | 160 | 3.8899 | 615.6 | 1616.4 | 260.099 | 0 | 1
1/16 | 15:00:00 | 276.15 | 98762 | 0.5 | 32 | 4.1841 | 385.2 | 1062 | 260.329 | 0 | 1
1/16 | 16:00:00 | 275.15 | 98752 | 1 | 109 | 3.8903 | 118.8 | 255.6 | 259.157 | 0 | 1
1/16 | 17:00:00 | 273.15 | 98734 | 3.1 | 150 | 3.5806 | 0 | 0 | 257.044 | 0 | 1
1/16 | 18:00:00 | 273.15 | 98734 | 0 | 299 | 3.492 | 0 | 0 | 256.975 | 0 | 1
1/16 | 19:00:00 | 271.15 | 98715 | 0 | 144 | 3.2936 | 0 | 0 | 254.933 | 0 | 1
1/16 | 20:00:00 | 272.15 | 98724 | 1 | 84 | 3.4344 | 0 | 0 | 255.988 | 0 | 1
1/16 | 21:00:00 | 271.15 | 98715 | 2.1 | 170 | 3.2936 | 0 | 0 | 254.933 | 0 | 1
1/16 | 22:00:00 | 271.15 | 98715 | 1 | 250 | 3.2936 | 0 | 0 | 254.933 | 0 | 1
1/16 | 23:00:00 | 272.15 | 98724 | 1.5 | 9 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/16 | 24:00:00 | 272.15 | 98724 | 3.1 | 210 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/17 | 01:00:00 | 271.15 | 98715 | 2.1 | 220 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
1/17 | 02:00:00 | 273.15 | 98734 | 3.6 | 210 | 3.4629 | 0 | 0 | 258.071 | 0 | 1
1/17 | 03:00:00 | 274.15 | 98743 | 5.7 | 230 | 4.0651 | 0 | 0 | 259.583 | 0 | 1
1/17 | 04:00:00 | 274.15 | 98743 | 3.6 | 220 | 4.185 | 0 | 0 | 259.674 | 0 | 1
1/17 | 05:00:00 | 273.15 | 98734 | 2.6 | 240 | 3.891 | 0 | 0 | 258.498 | 0 | 1
1/17 | 06:00:00 | 272.15 | 98724 | 0.5 | 190 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/17 | 07:00:00 | 272.15 | 98724 | 2.1 | 260 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/17 | 08:00:00 | 272.15 | 98724 | 0.5 | 116 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/17 | 09:00:00 | 271.15 | 98715 | 1 | 174 | 3.2936 | 7.2 | 0 | 256.147 | 0 | 1
1/17 | 10:00:00 | 272.15 | 98724 | 1 | 238 | 3.581 | 75.6 | 0 | 257.322 | 0 | 1
1/17 | 11:00:00 | 273.15 | 98734 | 1 | 161 | 3.891 | 162 | 0 | 258.498 | 0 | 1
1/17 | 12:00:00 | 273.15 | 98734 | 1.5 | 30 | 3.891 | 219.6 | 0 | 258.498 | 0 | 1
1/17 | 13:00:00 | 275.15 | 98752 | 1 | 200 | 4.4981 | 230.4 | 0 | 260.851 | 0 | 1
1/17 | 14:00:00 | 275.15 | 98752 | 2.6 | 160 | 4.4981 | 198 | 0 | 260.851 | 0 | 1
1/17 | 15:00:00 | 275.15 | 98752 | 2.1 | 220 | 4.4981 | 126 | 0 | 260.851 | 0 | 1
1/17 | 16:00:00 | 276.15 | 98762 | 1.5 | 176 | 4.4977 | 104.4 | 104.4 | 261.352 | 0 | 1
1/17 | 17:00:00 | 275.15 | 98752 | 3.6 | 260 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
1/17 | 18:00:00 | 273.15 | 98734 | 0.5 | 240 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/17 | 19:00:00 | 273.15 | 98734 | 1.5 | 121 | 3.492 | 0 | 0 | 258.094 | 0 | 1
1/17 | 20:00:00 | 273.15 | 98734 | 2.1 | 260 | 3.377 | 0 | 0 | 258.001 | 0 | 1
1/17 | 21:00:00 | 274.15 | 98743 | 3.6 | 250 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
1/17 | 22:00:00 | 273.15 | 98734 | 3.1 | 240 | 3.891 | 0 | 0 | 258.498 | 0 | 1
1/17 | 23:00:00 | 275.15 | 98752 | 3.1 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
1/17 | 24:00:00 | 274.15 | 98743 | 2.1 | 210 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
1/18 | 01:00:00 | 276.15 | 98762 | 4.1 | 210 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
1/18 | 02:00:00 | 277.15 | 98771 | 4.1 | 220 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/18 | 03:00:00 | 279.15 | 98789 | 4.6 | 230 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
1/18 | 04:00:00 | 279.15 | 98789 | 3.6 | 200 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
1/18 | 05:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
1/18 | 06:00:00 | 279.15 | 98789 | 6.2 | 240 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
1/18 | 07:00:00 | 279.15 | 98789 | 5.1 | 240 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
1/18 | 08:00:00 | 280.15 | 98798 | 7.2 | 250 | 6.4005 | 0 | 0 | 266.157 | 0 | 1
1/18 | 09:00:00 | 280.15 | 98798 | 5.7 | 240 | 6.4005 | 25.2 | 0 | 266.157 | 0 | 1
1/18 | 10:00:00 | 281.15 | 98806 | 4.6 | 240 | 6.4 | 126 | 0 | 267.58 | 0 | 1
1/18 | 11:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.8577 | 266.4 | 3.6 | 267.805 | 0 | 1
1/18 | 12:00:00 | 281.15 | 98806 | 2.1 | 210 | 6.8577 | 360 | 57.6 | 267.805 | 0 | 1
1/18 | 13:00:00 | 281.15 | 98806 | 6.2 | 270 | 6.8577 | 687.6 | 1119.6 | 267.332 | 0 | 1
1/18 | 14:00:00 | 281.15 | 98806 | 5.1 | 270 | 5.9698 | 630 | 1544.4 | 266.62 | 0 | 1
1/18 | 15:00:00 | 280.15 | 98798 | 5.1 | 260 | 5.5661 | 403.2 | 1112.4 | 265.444 | 0 | 1
1/18 | 16:00:00 | 280.15 | 98798 | 4.6 | 250 | 5.1865 | 129.6 | 212.4 | 265.216 | 0 | 1
1/18 | 17:00:00 | 279.15 | 98789 | 5.7 | 260 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
1/18 | 18:00:00 | 279.15 | 98789 | 7.7 | 270 | 5.187 | 0 | 0 | 264.269 | 0 | 1
1/18 | 19:00:00 | 278.15 | 98780 | 6.7 | 250 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
1/18 | 20:00:00 | 278.15 | 98780 | 5.1 | 250 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
1/18 | 21:00:00 | 278.15 | 98780 | 5.1 | 240 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
1/18 | 22:00:00 | 278.15 | 98780 | 2.1 | 230 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
1/18 | 23:00:00 | 278.15 | 98780 | 1.5 | 62 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
1/18 | 24:00:00 | 278.15 | 98780 | 4.1 | 240 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
1/19 | 01:00:00 | 279.15 | 98789 | 4.6 | 240 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/19 | 02:00:00 | 279.15 | 98789 | 5.7 | 260 | 5.187 | 0 | 0 | 264.269 | 0 | 1
1/19 | 03:00:00 | 278.15 | 98780 | 7.2 | 250 | 5.5671 | 0 | 0 | 263.807 | 0 | 1
1/19 | 04:00:00 | 279.15 | 98789 | 6.2 | 260 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
1/19 | 05:00:00 | 278.15 | 98780 | 5.1 | 260 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
1/19 | 06:00:00 | 278.15 | 98780 | 6.2 | 260 | 5.1875 | 0 | 0 | 263.323 | 0 | 1
1/19 | 07:00:00 | 278.15 | 98780 | 6.7 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
1/19 | 08:00:00 | 279.15 | 98789 | 9.8 | 270 | 5.187 | 0 | 0 | 264.528 | 0 | 1
1/19 | 09:00:00 | 279.15 | 98789 | 9.8 | 260 | 5.187 | 28.8 | 0 | 264.528 | 0 | 1
1/19 | 10:00:00 | 278.15 | 98780 | 8.2 | 280 | 4.8311 | 237.6 | 561.6 | 263.352 | 0 | 1
1/19 | 11:00:00 | 278.15 | 98780 | 7.7 | 270 | 4.8311 | 525.6 | 1382.4 | 263.095 | 0 | 1
1/19 | 12:00:00 | 278.15 | 98780 | 8.2 | 280 | 4.8311 | 705.6 | 1684.8 | 263.095 | 0 | 1
1/19 | 13:00:00 | 279.15 | 98789 | 8.7 | 270 | 4.4964 | 748.8 | 1760.4 | 263.81 | 0 | 1
1/19 | 14:00:00 | 279.15 | 98789 | 8.7 | 270 | 4.4964 | 608.4 | 1353.6 | 264.069 | 0 | 1
1/19 | 15:00:00 | 279.15 | 98789 | 6.7 | 250 | 4.8307 | 392.4 | 946.8 | 264.299 | 0 | 1
1/19 | 16:00:00 | 278.15 | 98780 | 8.7 | 260 | 4.8311 | 126 | 147.6 | 263.352 | 0 | 1
1/19 | 17:00:00 | 277.15 | 98771 | 10.8 | 260 | 4.8316 | 0 | 0 | 262.405 | 0 | 1
1/19 | 18:00:00 | 277.15 | 98771 | 9.8 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/19 | 19:00:00 | 274.15 | 98743 | 14.4 | 300 | 4.185 | 0 | 0 | 258.857 | 0 | 1
1/19 | 20:00:00 | 275.15 | 98752 | 7.7 | 280 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/19 | 21:00:00 | 276.15 | 98762 | 9.3 | 280 | 3.8899 | 0 | 0 | 260.515 | 0 | 1
1/19 | 22:00:00 | 275.15 | 98752 | 7.2 | 290 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/19 | 23:00:00 | 275.15 | 98752 | 7.2 | 290 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
1/19 | 24:00:00 | 275.15 | 98752 | 8.7 | 280 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
1/20 | 01:00:00 | 275.15 | 98752 | 8.2 | 270 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
1/20 | 02:00:00 | 276.15 | 98762 | 7.7 | 270 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
1/20 | 03:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/20 | 04:00:00 | 276.15 | 98762 | 10.3 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/20 | 05:00:00 | 275.15 | 98752 | 8.7 | 290 | 4.4981 | 0 | 0 | 260.745 | 0 | 1
1/20 | 06:00:00 | 275.15 | 98752 | 5.1 | 280 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
1/20 | 07:00:00 | 275.15 | 98752 | 3.6 | 290 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
1/20 | 08:00:00 | 276.15 | 98762 | 4.6 | 290 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
1/20 | 09:00:00 | 276.15 | 98762 | 4.6 | 310 | 4.4977 | 18 | 0 | 261.693 | 0 | 1
1/20 | 10:00:00 | 276.15 | 98762 | 4.1 | 290 | 4.832 | 136.8 | 0 | 261.921 | 0 | 1
1/20 | 11:00:00 | 276.15 | 98762 | 4.1 | 290 | 4.832 | 507.6 | 907.2 | 261.459 | 0 | 1
1/20 | 12:00:00 | 277.15 | 98771 | 3.1 | 280 | 5.1879 | 374.4 | 64.8 | 263.098 | 0 | 1
1/20 | 13:00:00 | 277.15 | 98771 | 3.6 | 290 | 5.1879 | 716.4 | 1166.4 | 262.633 | 0 | 1
1/20 | 14:00:00 | 278.15 | 98780 | 3.6 | 260 | 5.5671 | 342 | 50.4 | 264.274 | 0 | 1
1/20 | 15:00:00 | 278.15 | 98780 | 2.6 | 270 | 5.5671 | 223.2 | 0 | 264.274 | 0 | 1
1/20 | 16:00:00 | 279.15 | 98789 | 6.7 | 280 | 5.9708 | 72 | 0 | 265.451 | 0 | 1
1/20 | 17:00:00 | 279.15 | 98789 | 6.2 | 270 | 5.9708 | 0 | 0 | 264.982 | 0 | 1
1/20 | 18:00:00 | 280.15 | 98798 | 8.2 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
1/20 | 19:00:00 | 279.15 | 98789 | 8.2 | 270 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
1/20 | 20:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
1/20 | 21:00:00 | 280.15 | 98798 | 9.3 | 260 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
1/20 | 22:00:00 | 281.15 | 98806 | 9.3 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/20 | 23:00:00 | 281.15 | 98806 | 5.1 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/20 | 24:00:00 | 281.15 | 98806 | 4.6 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1
1/21 | 01:00:00 | 282.15 | 98815 | 9.8 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/21 | 02:00:00 | 282.15 | 98815 | 10.8 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/21 | 03:00:00 | 282.15 | 98815 | 10.3 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/21 | 04:00:00 | 282.15 | 98815 | 8.7 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
1/21 | 05:00:00 | 282.15 | 98815 | 10.3 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
1/21 | 06:00:00 | 282.15 | 98815 | 9.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
1/21 | 07:00:00 | 281.15 | 98806 | 11.3 | 280 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
1/21 | 08:00:00 | 280.15 | 98798 | 9.3 | 280 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
1/21 | 09:00:00 | 280.15 | 98798 | 13.4 | 280 | 4.496 | 39.6 | 0 | 264.755 | 0 | 1
1/21 | 10:00:00 | 280.15 | 98798 | 12.3 | 280 | 4.496 | 270 | 720 | 264.755 | 0 | 1
1/21 | 11:00:00 | 280.15 | 98798 | 12.3 | 280 | 4.496 | 550.8 | 1116 | 264.755 | 0 | 1
1/21 | 12:00:00 | 280.15 | 98798 | 11.8 | 270 | 4.496 | 381.6 | 72 | 265.483 | 0 | 1
1/21 | 13:00:00 | 279.15 | 98789 | 12.3 | 270 | 4.4964 | 406.8 | 54 | 264.536 | 0 | 1
1/21 | 14:00:00 | 279.15 | 98789 | 13.4 | 270 | 4.4964 | 352.8 | 43.2 | 264.536 | 0 | 1
1/21 | 15:00:00 | 279.15 | 98789 | 18.5 | 280 | 4.4964 | 417.6 | 777.6 | 264.069 | 0 | 1
1/21 | 16:00:00 | 278.15 | 98780 | 15.4 | 280 | 4.4968 | 79.2 | 0 | 263.588 | 0 | 1
1/21 | 17:00:00 | 277.15 | 98771 | 12.9 | 290 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/21 | 18:00:00 | 278.15 | 98780 | 14.4 | 280 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/21 | 19:00:00 | 278.15 | 98780 | 11.8 | 280 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/21 | 20:00:00 | 278.15 | 98780 | 12.9 | 280 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/21 | 21:00:00 | 278.15 | 98780 | 9.8 | 270 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/21 | 22:00:00 | 278.15 | 98780 | 9.8 | 290 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/21 | 23:00:00 | 278.15 | 98780 | 7.2 | 270 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/21 | 24:00:00 | 278.15 | 98780 | 6.2 | 280 | 4.1834 | 0 | 0 | 262.891 | 0 | 1
1/22 | 01:00:00 | 278.15 | 98780 | 10.3 | 270 | 4.1834 | 0 | 0 | 262.891 | 0 | 1
1/22 | 02:00:00 | 278.15 | 98780 | 10.8 | 270 | 4.1834 | 0 | 0 | 262.634 | 0 | 1
1/22 | 03:00:00 | 278.15 | 98780 | 9.8 | 270 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/22 | 04:00:00 | 278.15 | 98780 | 8.2 | 260 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
1/22 | 05:00:00 | 279.15 | 98789 | 9.8 | 260 | 5.187 | 0 | 0 | 264.996 | 0 | 1
1/22 | 06:00:00 | 279.15 | 98789 | 13.9 | 260 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
1/22 | 07:00:00 | 280.15 | 98798 | 12.3 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
1/22 | 08:00:00 | 280.15 | 98798 | 14.4 | 280 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
1/22 | 09:00:00 | 280.15 | 98798 | 16.5 | 270 | 5.1865 | 21.6 | 0 | 265.946 | 0 | 1
1/22 | 10:00:00 | 280.15 | 98798 | 14.9 | 270 | 5.1865 | 262.8 | 590.4 | 265.476 | 0 | 1
1/22 | 11:00:00 | 280.15 | 98798 | 15.4 | 270 | 5.1865 | 525.6 | 1198.8 | 265.476 | 0 | 1
1/22 | 12:00:00 | 280.15 | 98798 | 13.4 | 280 | 5.1865 | 702 | 1245.6 | 265.476 | 0 | 1
1/22 | 13:00:00 | 280.15 | 98798 | 11.3 | 280 | 5.5661 | 741.6 | 1285.2 | 265.704 | 0 | 1
1/22 | 14:00:00 | 280.15 | 98798 | 9.8 | 280 | 5.1865 | 644.4 | 1177.2 | 265.476 | 0 | 1
1/22 | 15:00:00 | 280.15 | 98798 | 8.2 | 280 | 4.496 | 457.2 | 1191.6 | 264.755 | 0 | 1
1/22 | 16:00:00 | 279.15 | 98789 | 6.7 | 290 | 4.4964 | 151.2 | 216 | 264.069 | 0 | 1
1/22 | 17:00:00 | 278.15 | 98780 | 8.7 | 270 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/22 | 18:00:00 | 278.15 | 98780 | 10.3 | 280 | 4.4968 | 0 | 0 | 262.865 | 0 | 1
1/22 | 19:00:00 | 278.15 | 98780 | 8.7 | 280 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
1/22 | 20:00:00 | 278.15 | 98780 | 8.7 | 290 | 4.4968 | 0 | 0 | 262.865 | 0 | 1
1/22 | 21:00:00 | 277.15 | 98771 | 7.7 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/22 | 22:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/22 | 23:00:00 | 277.15 | 98771 | 7.7 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
1/22 | 24:00:00 | 277.15 | 98771 | 6.7 | 260 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/23 | 01:00:00 | 277.15 | 98771 | 5.7 | 300 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
1/23 | 02:00:00 | 277.15 | 98771 | 5.1 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/23 | 03:00:00 | 277.15 | 98771 | 4.1 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/23 | 04:00:00 | 277.15 | 98771 | 6.2 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
1/23 | 05:00:00 | 277.15 | 98771 | 5.1 | 290 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
1/23 | 06:00:00 | 276.15 | 98762 | 6.2 | 270 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
1/23 | 07:00:00 | 276.15 | 98762 | 5.1 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
1/23 | 08:00:00 | 276.15 | 98762 | 5.1 | 270 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
1/23 | 09:00:00 | 277.15 | 98771 | 5.7 | 280 | 4.4973 | 46.8 | 0 | 261.92 | 0 | 1
1/23 | 10:00:00 | 277.15 | 98771 | 5.7 | 260 | 4.4973 | 273.6 | 619.2 | 262.177 | 0 | 1
1/23 | 11:00:00 | 277.15 | 98771 | 5.7 | 270 | 4.8316 | 540 | 1224 | 262.405 | 0 | 1
1/23 | 12:00:00 | 278.15 | 98780 | 5.7 | 270 | 4.4968 | 716.4 | 1274.4 | 263.123 | 0 | 1
1/23 | 13:00:00 | 278.15 | 98780 | 5.7 | 280 | 4.4968 | 759.6 | 1540.8 | 263.123 | 0 | 1
1/23 | 14:00:00 | 277.15 | 98771 | 6.7 | 280 | 4.8316 | 702 | 1670.4 | 262.149 | 0 | 1
1/23 | 15:00:00 | 277.15 | 98771 | 9.3 | 280 | 4.4973 | 471.6 | 1263.6 | 261.92 | 0 | 1
1/23 | 16:00:00 | 277.15 | 98771 | 7.2 | 290 | 4.1838 | 172.8 | 241.2 | 261.69 | 0 | 1
1/23 | 17:00:00 | 276.15 | 98762 | 7.2 | 280 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
1/23 | 18:00:00 | 276.15 | 98762 | 7.7 | 280 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
1/23 | 19:00:00 | 276.15 | 98762 | 8.2 | 290 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
1/23 | 20:00:00 | 275.15 | 98752 | 6.7 | 290 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/23 | 21:00:00 | 274.15 | 98743 | 4.6 | 290 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
1/23 | 22:00:00 | 275.15 | 98752 | 3.1 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
1/23 | 23:00:00 | 275.15 | 98752 | 6.2 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
1/23 | 24:00:00 | 275.15 | 98752 | 4.6 | 280 | 4.4981 | 0 | 0 | 260.851 | 0 | 1
1/24 | 01:00:00 | 276.15 | 98762 | 5.1 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
1/24 | 02:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
1/24 | 03:00:00 | 276.15 | 98762 | 3.6 | 250 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
1/24 | 04:00:00 | 276.15 | 98762 | 3.1 | 220 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
1/24 | 05:00:00 | 276.15 | 98762 | 4.1 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
1/24 | 06:00:00 | 276.15 | 98762 | 4.1 | 230 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
1/24 | 07:00:00 | 275.15 | 98752 | 2.1 | 210 | 4.4981 | 0 | 0 | 260.745 | 0 | 1
1/24 | 08:00:00 | 275.15 | 98752 | 3.1 | 160 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
1/24 | 09:00:00 | 275.15 | 98752 | 3.6 | 130 | 4.4981 | 28.8 | 0 | 260.745 | 0 | 1
1/24 | 10:00:00 | 275.15 | 98752 | 4.6 | 130 | 4.4981 | 154.8 | 0 | 260.745 | 0 | 1
1/24 | 11:00:00 | 275.15 | 98752 | 5.7 | 120 | 4.4981 | 306 | 25.2 | 260.745 | 0 | 1
1/24 | 12:00:00 | 275.15 | 98752 | 4.1 | 120 | 4.4981 | 244.8 | 0 | 260.851 | 0 | 1
1/24 | 13:00:00 | 275.15 | 98752 | 3.6 | 110 | 4.4981 | 428.4 | 64.8 | 260.745 | 0 | 1
1/24 | 14:00:00 | 275.15 | 98752 | 3.1 | 130 | 4.4981 | 226.8 | 0 | 260.851 | 0 | 1
1/24 | 15:00:00 | 276.15 | 98762 | 1 | 120 | 4.832 | 154.8 | 0 | 262.027 | 0 | 1
1/24 | 16:00:00 | 276.15 | 98762 | 1 | 109 | 4.832 | 93.6 | 0 | 261.921 | 0 | 1
1/24 | 17:00:00 | 276.15 | 98762 | 0.5 | 256 | 4.832 | 0 | 0 | 262.027 | 0 | 1
1/24 | 18:00:00 | 276.15 | 98762 | 1 | 334 | 4.832 | 0 | 0 | 261.921 | 0 | 1
1/24 | 19:00:00 | 276.15 | 98762 | 0.5 | 242 | 4.832 | 0 | 0 | 262.027 | 0 | 1
1/24 | 20:00:00 | 276.15 | 98762 | 1.5 | 247 | 4.832 | 0 | 0 | 262.027 | 0 | 1
1/24 | 21:00:00 | 276.15 | 98762 | 1 | 205 | 4.832 | 0 | 0 | 262.027 | 0 | 1
1/24 | 22:00:00 | 277.15 | 98771 | 1 | 123 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
1/24 | 23:00:00 | 277.15 | 98771 | 1.5 | 335 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
1/24 | 24:00:00 | 277.15 | 98771 | 1.5 | 150 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
1/25 | 01:00:00 | 278.15 | 98780 | 2.1 | 160 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
1/25 | 02:00:00 | 279.15 | 98789 | 2.6 | 200 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
1/25 | 03:00:00 | 279.15 | 98789 | 2.6 | 180 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
1/25 | 04:00:00 | 280.15 | 98798 | 2.1 | 210 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
1/25 | 05:00:00 | 281.15 | 98806 | 3.6 | 220 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
1/25 | 06:00:00 | 281.15 | 98806 | 3.1 | 220 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
1/25 | 07:00:00 | 280.15 | 98798 | 3.6 | 220 | 6.4005 | 0 | 0 | 266.157 | 0 | 1
1/25 | 08:00:00 | 281.15 | 98806 | 4.1 | 230 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
1/25 | 09:00:00 | 280.15 | 98798 | 3.6 | 220 | 5.9703 | 28.8 | 0 | 266.402 | 0 | 1
1/25 | 10:00:00 | 280.15 | 98798 | 5.7 | 210 | 5.9703 | 288 | 644.4 | 265.931 | 0 | 1
1/25 | 11:00:00 | 281.15 | 98806 | 3.6 | 170 | 5.9698 | 561.6 | 961.2 | 266.881 | 0 | 1
1/25 | 12:00:00 | 281.15 | 98806 | 4.6 | 190 | 5.9698 | 410.4 | 57.6 | 267.353 | 0 | 1
1/25 | 13:00:00 | 281.15 | 98806 | 6.7 | 200 | 5.5656 | 435.6 | 57.6 | 267.125 | 0 | 1
1/25 | 14:00:00 | 282.15 | 98815 | 6.2 | 210 | 5.5651 | 381.6 | 43.2 | 268.075 | 0 | 1
1/25 | 15:00:00 | 282.15 | 98815 | 6.2 | 200 | 5.9692 | 259.2 | 3.6 | 268.304 | 0 | 1
1/25 | 16:00:00 | 282.15 | 98815 | 6.7 | 190 | 5.9692 | 100.8 | 0 | 268.304 | 0 | 1
1/25 | 17:00:00 | 282.15 | 98815 | 5.1 | 200 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
1/25 | 18:00:00 | 282.15 | 98815 | 6.7 | 190 | 5.5651 | 0 | 0 | 268.075 | 0 | 1
1/25 | 19:00:00 | 282.15 | 98815 | 5.7 | 190 | 5.5651 | 0 | 0 | 268.075 | 0 | 1
1/25 | 20:00:00 | 282.15 | 98815 | 5.1 | 190 | 5.5651 | 0 | 0 | 268.075 | 0 | 1
1/25 | 21:00:00 | 282.15 | 98815 | 4.6 | 180 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
1/25 | 22:00:00 | 282.15 | 98815 | 5.7 | 180 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
1/25 | 23:00:00 | 281.15 | 98806 | 6.7 | 170 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
1/25 | 24:00:00 | 281.15 | 98806 | 5.7 | 170 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
1/26 | 01:00:00 | 280.15 | 98798 | 5.7 | 170 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
1/26 | 02:00:00 | 279.15 | 98789 | 3.6 | 250 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
1/26 | 03:00:00 | 277.15 | 98771 | 4.6 | 260 | 4.8316 | 0 | 0 | 262.405 | 0 | 1
1/26 | 04:00:00 | 277.15 | 98771 | 2.6 | 270 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
1/26 | 05:00:00 | 276.15 | 98762 | 2.1 | 210 | 4.832 | 0 | 0 | 261.459 | 0 | 1
1/26 | 06:00:00 | 276.15 | 98762 | 2.6 | 210 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
1/26 | 07:00:00 | 276.15 | 98762 | 3.1 | 230 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
1/26 | 08:00:00 | 275.15 | 98752 | 2.6 | 230 | 4.4981 | 0 | 0 | 260.03 | 0 | 1
1/26 | 09:00:00 | 275.15 | 98752 | 2.6 | 170 | 4.1846 | 61.2 | 0 | 259.802 | 0 | 1
1/26 | 10:00:00 | 274.15 | 98743 | 2.6 | 160 | 4.185 | 320.4 | 849.6 | 258.857 | 0 | 1
1/26 | 11:00:00 | 277.15 | 98771 | 3.6 | 150 | 4.4973 | 612 | 1540.8 | 261.92 | 0 | 1
1/26 | 12:00:00 | 277.15 | 98771 | 3.6 | 170 | 4.4973 | 759.6 | 1209.6 | 262.177 | 0 | 1
1/26 | 13:00:00 | 278.15 | 98780 | 5.7 | 210 | 4.4968 | 446.4 | 93.6 | 263.588 | 0 | 1
1/26 | 14:00:00 | 278.15 | 98780 | 5.7 | 220 | 4.4968 | 705.6 | 1155.6 | 263.123 | 0 | 1
1/26 | 15:00:00 | 278.15 | 98780 | 7.2 | 230 | 4.1834 | 486 | 982.8 | 262.891 | 0 | 1
1/26 | 16:00:00 | 277.15 | 98771 | 6.7 | 240 | 3.5793 | 194.4 | 244.8 | 261.481 | 0 | 1
1/26 | 17:00:00 | 277.15 | 98771 | 7.2 | 240 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
1/26 | 18:00:00 | 277.15 | 98771 | 6.7 | 240 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
1/26 | 19:00:00 | 275.15 | 98752 | 7.7 | 250 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
1/26 | 20:00:00 | 275.15 | 98752 | 4.6 | 230 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
1/26 | 21:00:00 | 275.15 | 98752 | 5.7 | 240 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
1/26 | 22:00:00 | 275.15 | 98752 | 5.1 | 240 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/26 | 23:00:00 | 275.15 | 98752 | 4.6 | 240 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/26 | 24:00:00 | 274.15 | 98743 | 1.5 | 247 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
1/27 | 01:00:00 | 275.15 | 98752 | 4.1 | 210 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
1/27 | 02:00:00 | 275.15 | 98752 | 3.6 | 220 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
1/27 | 03:00:00 | 275.15 | 98752 | 4.1 | 240 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
1/27 | 04:00:00 | 275.15 | 98752 | 5.1 | 250 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
1/27 | 05:00:00 | 275.15 | 98752 | 4.6 | 240 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
1/27 | 06:00:00 | 276.15 | 98762 | 5.1 | 260 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
1/27 | 07:00:00 | 276.15 | 98762 | 4.1 | 260 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
1/27 | 08:00:00 | 275.15 | 98752 | 5.7 | 270 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
1/27 | 09:00:00 | 275.15 | 98752 | 3.1 | 250 | 4.1846 | 64.8 | 0 | 260.056 | 0 | 1
1/27 | 10:00:00 | 276.15 | 98762 | 4.1 | 250 | 4.4977 | 313.2 | 705.6 | 261.231 | 0 | 1
1/27 | 11:00:00 | 277.15 | 98771 | 4.6 | 250 | 4.8316 | 590.4 | 1296 | 262.405 | 0 | 1
1/27 | 12:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.4968 | 770.4 | 1216.8 | 263.123 | 0 | 1
1/27 | 13:00:00 | 277.15 | 98771 | 5.7 | 250 | 4.4973 | 453.6 | 93.6 | 262.64 | 0 | 1
1/27 | 14:00:00 | 277.15 | 98771 | 5.7 | 250 | 4.1838 | 723.6 | 1353.6 | 261.946 | 0 | 1
1/27 | 15:00:00 | 274.15 | 98743 | 4.6 | 280 | 4.185 | 277.2 | 10.8 | 259.569 | 0 | 1
1/27 | 16:00:00 | 274.15 | 98743 | 2.6 | 250 | 4.185 | 205.2 | 331.2 | 259.111 | 0 | 1
1/27 | 17:00:00 | 275.15 | 98752 | 2.1 | 180 | 4.4981 | 0 | 0 | 260.745 | 0 | 1
1/27 | 18:00:00 | 274.15 | 98743 | 2.6 | 220 | 4.185 | 0 | 0 | 259.111 | 0 | 1
1/27 | 19:00:00 | 274.15 | 98743 | 1 | 260 | 4.185 | 0 | 0 | 259.569 | 0 | 1
1/27 | 20:00:00 | 274.15 | 98743 | 1.5 | 180 | 4.185 | 0 | 0 | 258.857 | 0 | 1
1/27 | 21:00:00 | 274.15 | 98743 | 4.1 | 360 | 4.185 | 0 | 0 | 258.857 | 0 | 1
1/27 | 22:00:00 | 275.15 | 98752 | 4.1 | 360 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
1/27 | 23:00:00 | 275.15 | 98752 | 5.1 | 350 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
1/27 | 24:00:00 | 275.15 | 98752 | 3.6 | 10 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
1/28 | 01:00:00 | 275.15 | 98752 | 5.1 | 360 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
1/28 | 02:00:00 | 274.15 | 98743 | 4.6 | 340 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
1/28 | 03:00:00 | 275.15 | 98752 | 3.6 | 320 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
1/28 | 04:00:00 | 275.15 | 98752 | 3.6 | 340 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
1/28 | 05:00:00 | 274.15 | 98743 | 2.6 | 340 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
1/28 | 06:00:00 | 273.15 | 98734 | 3.1 | 300 | 3.891 | 0 | 0 | 257.937 | 0 | 1
1/28 | 07:00:00 | 274.15 | 98743 | 3.6 | 320 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
1/28 | 08:00:00 | 274.15 | 98743 | 3.6 | 340 | 3.5803 | 0 | 0 | 258.398 | 0 | 1
1/28 | 09:00:00 | 275.15 | 98752 | 3.6 | 350 | 3.5799 | 72 | 25.2 | 259.34 | 0 | 1
1/28 | 10:00:00 | 275.15 | 98752 | 3.6 | 330 | 3.5799 | 345.6 | 910.8 | 259.34 | 0 | 1
1/28 | 11:00:00 | 276.15 | 98762 | 2.6 | 310 | 4.1841 | 640.8 | 1386 | 260.746 | 0 | 1
1/28 | 12:00:00 | 276.15 | 98762 | 3.1 | 290 | 4.1841 | 835.2 | 1447.2 | 260.746 | 0 | 1
1/28 | 13:00:00 | 277.15 | 98771 | 1.5 | 164 | 4.1838 | 885.6 | 1929.6 | 261.69 | 0 | 1
1/28 | 14:00:00 | 278.15 | 98780 | 1.5 | 139 | 4.1834 | 784.8 | 1810.8 | 262.634 | 0 | 1
1/28 | 15:00:00 | 277.15 | 98771 | 1.5 | 182 | 4.1838 | 547.2 | 1227.6 | 261.69 | 0 | 1
1/28 | 16:00:00 | 278.15 | 98780 | 1 | 268 | 4.1834 | 230.4 | 529.2 | 262.634 | 0 | 1
1/28 | 17:00:00 | 277.15 | 98771 | 2.1 | 310 | 3.8896 | 3.6 | 0 | 261.458 | 0 | 1
1/28 | 18:00:00 | 275.15 | 98752 | 3.6 | 310 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
1/28 | 19:00:00 | 274.15 | 98743 | 1.5 | 300 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
1/28 | 20:00:00 | 273.15 | 98734 | 2.1 | 300 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/28 | 21:00:00 | 273.15 | 98734 | 2.6 | 290 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/28 | 22:00:00 | 272.15 | 98724 | 2.6 | 290 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/28 | 23:00:00 | 273.15 | 98734 | 2.1 | 290 | 3.891 | 0 | 0 | 258.498 | 0 | 1
1/28 | 24:00:00 | 272.15 | 98724 | 1.5 | 270 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/29 | 01:00:00 | 271.15 | 98715 | 2.1 | 270 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
1/29 | 02:00:00 | 272.15 | 98724 | 2.1 | 300 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/29 | 03:00:00 | 273.15 | 98734 | 1 | 320 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/29 | 04:00:00 | 273.15 | 98734 | 0.5 | 250 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/29 | 05:00:00 | 273.15 | 98734 | 0 | 138 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/29 | 06:00:00 | 272.15 | 98724 | 1 | 210 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/29 | 07:00:00 | 272.15 | 98724 | 1 | 190 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/29 | 08:00:00 | 273.15 | 98734 | 0.5 | 150 | 3.6408 | 0 | 0 | 258.314 | 0 | 1
1/29 | 09:00:00 | 273.15 | 98734 | 0.5 | 130 | 3.7329 | 25.2 | 0 | 258.383 | 0 | 1
1/29 | 10:00:00 | 274.15 | 98743 | 0.5 | 157 | 3.8267 | 176.4 | 0 | 259.293 | 0 | 1
1/29 | 11:00:00 | 274.15 | 98743 | 0 | 226 | 3.8907 | 655.2 | 1450.8 | 258.628 | 0 | 1
1/29 | 12:00:00 | 274.15 | 98743 | 0.5 | 100 | 3.8907 | 853.2 | 1886.4 | 258.628 | 0 | 1
1/29 | 13:00:00 | 275.15 | 98752 | 0.5 | 40 | 4.1846 | 903.6 | 1987.2 | 259.802 | 0 | 1
1/29 | 14:00:00 | 275.15 | 98752 | 1.5 | 40 | 4.1846 | 752.4 | 1342.8 | 260.056 | 0 | 1
1/29 | 15:00:00 | 275.15 | 98752 | 2.1 | 70 | 4.1846 | 529.2 | 1040.4 | 260.056 | 0 | 1
1/29 | 16:00:00 | 274.15 | 98743 | 2.6 | 80 | 4.185 | 230.4 | 295.2 | 259.111 | 0 | 1
1/29 | 17:00:00 | 274.15 | 98743 | 1.5 | 70 | 4.185 | 3.6 | 0 | 259.674 | 0 | 1
1/29 | 18:00:00 | 274.15 | 98743 | 2.1 | 80 | 4.185 | 0 | 0 | 259.674 | 0 | 1
1/29 | 19:00:00 | 274.15 | 98743 | 2.6 | 90 | 4.185 | 0 | 0 | 259.674 | 0 | 1
1/29 | 20:00:00 | 275.15 | 98752 | 4.1 | 120 | 4.4981 | 0 | 0 | 260.745 | 0 | 1
1/29 | 21:00:00 | 274.15 | 98743 | 4.1 | 130 | 4.185 | 0 | 0 | 259.569 | 0 | 1
1/29 | 22:00:00 | 274.15 | 98743 | 4.6 | 130 | 4.185 | 0 | 0 | 259.569 | 0 | 1
1/29 | 23:00:00 | 274.15 | 98743 | 3.1 | 150 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
1/29 | 24:00:00 | 273.15 | 98734 | 2.6 | 90 | 3.891 | 0 | 0 | 257.937 | 0 | 1
1/30 | 01:00:00 | 272.15 | 98724 | 2.6 | 120 | 3.581 | 0 | 0 | 256.513 | 0 | 1
1/30 | 02:00:00 | 273.15 | 98734 | 1.5 | 100 | 3.891 | 0 | 0 | 257.685 | 0 | 1
1/30 | 03:00:00 | 273.15 | 98734 | 1.5 | 70 | 3.891 | 0 | 0 | 257.937 | 0 | 1
1/30 | 04:00:00 | 273.15 | 98734 | 1.5 | 70 | 3.891 | 0 | 0 | 258.498 | 0 | 1
1/30 | 05:00:00 | 272.15 | 98724 | 1.5 | 196 | 3.581 | 0 | 0 | 257.322 | 0 | 1
1/30 | 06:00:00 | 273.15 | 98734 | 2.1 | 60 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
1/30 | 07:00:00 | 272.15 | 98724 | 2.1 | 60 | 3.581 | 0 | 0 | 257.218 | 0 | 1
1/30 | 08:00:00 | 272.15 | 98724 | 1.5 | 204 | 3.581 | 0 | 0 | 257.218 | 0 | 1
1/30 | 09:00:00 | 273.15 | 98734 | 2.6 | 60 | 3.891 | 43.2 | 0 | 258.394 | 0 | 1
1/30 | 10:00:00 | 273.15 | 98734 | 1.5 | 60 | 3.891 | 194.4 | 0 | 258.394 | 0 | 1
1/30 | 11:00:00 | 273.15 | 98734 | 2.6 | 60 | 3.891 | 352.8 | 21.6 | 258.394 | 0 | 1
1/30 | 12:00:00 | 274.15 | 98743 | 2.1 | 60 | 3.5803 | 457.2 | 75.6 | 259.108 | 0 | 1
1/30 | 13:00:00 | 274.15 | 98743 | 2.6 | 60 | 3.5803 | 482.4 | 86.4 | 259.108 | 0 | 1
1/30 | 14:00:00 | 274.15 | 98743 | 2.1 | 60 | 3.5803 | 428.4 | 46.8 | 259.108 | 0 | 1
1/30 | 15:00:00 | 275.15 | 98752 | 3.1 | 60 | 3.5799 | 579.6 | 1328.4 | 259.34 | 0 | 1
1/30 | 16:00:00 | 275.15 | 98752 | 2.6 | 60 | 3.5799 | 255.6 | 601.2 | 259.34 | 0 | 1
1/30 | 17:00:00 | 275.15 | 98752 | 2.6 | 50 | 3.5799 | 18 | 0 | 259.34 | 0 | 1
1/30 | 18:00:00 | 274.15 | 98743 | 3.1 | 30 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
1/30 | 19:00:00 | 274.15 | 98743 | 3.1 | 40 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
1/30 | 20:00:00 | 274.15 | 98743 | 2.1 | 50 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
1/30 | 21:00:00 | 273.15 | 98734 | 1.5 | 8 | 3.891 | 0 | 0 | 257.937 | 0 | 1
1/30 | 22:00:00 | 273.15 | 98734 | 1 | 40 | 3.5806 | 0 | 0 | 257.707 | 0 | 1
1/30 | 23:00:00 | 273.15 | 98734 | 1.5 | 105 | 3.5806 | 0 | 0 | 257.707 | 0 | 1
1/30 | 24:00:00 | 273.15 | 98734 | 2.1 | 70 | 3.891 | 0 | 0 | 258.394 | 0 | 1
1/31 | 01:00:00 | 273.15 | 98734 | 3.1 | 70 | 3.891 | 0 | 0 | 258.394 | 0 | 1
1/31 | 02:00:00 | 273.15 | 98734 | 3.1 | 80 | 3.293 | 0 | 0 | 257.931 | 0 | 1
1/31 | 03:00:00 | 273.15 | 98734 | 3.6 | 70 | 3.293 | 0 | 0 | 257.931 | 0 | 1
1/31 | 04:00:00 | 273.15 | 98734 | 3.1 | 80 | 3.293 | 0 | 0 | 257.931 | 0 | 1
1/31 | 05:00:00 | 272.15 | 98724 | 2.6 | 80 | 3.581 | 0 | 0 | 257.218 | 0 | 1
1/31 | 06:00:00 | 272.15 | 98724 | 2.6 | 70 | 3.581 | 0 | 0 | 257.218 | 0 | 1
1/31 | 07:00:00 | 272.15 | 98724 | 3.1 | 70 | 3.581 | 0 | 0 | 257.218 | 0 | 1
1/31 | 08:00:00 | 272.15 | 98724 | 3.1 | 70 | 3.581 | 0 | 0 | 257.218 | 0 | 1
1/31 | 09:00:00 | 272.15 | 98724 | 2.6 | 70 | 3.581 | 82.8 | 54 | 256.764 | 0 | 1
1/31 | 10:00:00 | 273.15 | 98734 | 3.1 | 70 | 3.891 | 360 | 810 | 257.937 | 0 | 1
1/31 | 11:00:00 | 273.15 | 98734 | 4.6 | 80 | 3.5806 | 648 | 1252.8 | 257.707 | 0 | 1
1/31 | 12:00:00 | 273.15 | 98734 | 4.6 | 80 | 3.5806 | 464.4 | 54 | 258.163 | 0 | 1
1/31 | 13:00:00 | 274.15 | 98743 | 5.7 | 80 | 3.2927 | 889.2 | 1076.4 | 258.419 | 0 | 1
1/31 | 14:00:00 | 274.15 | 98743 | 7.2 | 90 | 3.2927 | 439.2 | 46.8 | 258.876 | 0 | 1
1/31 | 15:00:00 | 273.15 | 98734 | 5.1 | 90 | 3.0267 | 313.2 | 14.4 | 257.698 | 0 | 1
1/31 | 16:00:00 | 273.15 | 98734 | 5.1 | 80 | 3.5806 | 140.4 | 0 | 258.163 | 0 | 1
1/31 | 17:00:00 | 273.15 | 98734 | 5.7 | 80 | 3.5806 | 10.8 | 0 | 258.163 | 0 | 1
1/31 | 18:00:00 | 273.15 | 98734 | 5.1 | 70 | 3.891 | 0 | 0 | 258.394 | 0 | 1
1/31 | 19:00:00 | 272.95 | 98732 | 4.1 | 65 | 3.8271 | 0 | 0 | 257.703 | 0 | 1
1/31 | 20:00:00 | 272.95 | 98732 | 4 | 67 | 3.8271 | 0 | 0 | 258.158 | 0 | 1
1/31 | 21:00:00 | 272.95 | 98732 | 4.1 | 70 | 3.8271 | 0 | 0 | 258.158 | 0 | 1
1/31 | 22:00:00 | 273.15 | 98734 | 6 | 127 | 3.891 | 0 | 0 | 258.394 | 0 | 1
1/31 | 23:00:00 | 273.35 | 98736 | 7.8 | 185 | 3.9486 | 0 | 0 | 258.172 | 0 | 1
1/31 | 24:00:00 | 273.95 | 98741 | 9.8 | 242 | 4.1247 | 0 | 0 | 259.334 | 0 | 1
2/1 | 01:00:00 | 274.15 | 98743 | 11.4 | 302 | 4.185 | 0 | 0 | 258.857 | 0 | 1
2/1 | 02:00:00 | 274.15 | 98743 | 11.1 | 302 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
2/1 | 03:00:00 | 274.15 | 98743 | 10.7 | 305 | 3.6405 | 0 | 0 | 258.697 | 0 | 1
2/1 | 04:00:00 | 274.15 | 98743 | 9.9 | 307 | 3.4337 | 0 | 0 | 258.992 | 0 | 1
2/1 | 05:00:00 | 274.15 | 98743 | 8.9 | 307 | 3.2927 | 0 | 0 | 258.876 | 0 | 1
2/1 | 06:00:00 | 274.15 | 98743 | 8.6 | 315 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
2/1 | 07:00:00 | 274.15 | 98743 | 7.7 | 310 | 3.2927 | 0 | 0 | 258.876 | 0 | 1
2/1 | 08:00:00 | 274.15 | 98743 | 7.2 | 310 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
2/1 | 09:00:00 | 274.15 | 98743 | 9.3 | 330 | 4.185 | 50.4 | 0 | 259.569 | 0 | 1
2/1 | 10:00:00 | 274.15 | 98743 | 9.3 | 330 | 3.2927 | 374.4 | 774 | 258.419 | 0 | 1
2/1 | 11:00:00 | 275.15 | 98752 | 6.7 | 310 | 4.1846 | 662.4 | 1396.8 | 260.056 | 0 | 1
2/1 | 12:00:00 | 274.15 | 98743 | 8.2 | 320 | 3.2927 | 856.8 | 1281.6 | 258.419 | 0 | 1
2/1 | 13:00:00 | 275.15 | 98752 | 9.3 | 320 | 3.0262 | 907.2 | 1335.6 | 259.127 | 0 | 1
2/1 | 14:00:00 | 275.15 | 98752 | 7.2 | 330 | 3.5799 | 806.4 | 1231.2 | 259.594 | 0 | 1
2/1 | 15:00:00 | 275.15 | 98752 | 7.7 | 330 | 4.4981 | 608.4 | 1515.6 | 260.03 | 0 | 1
2/1 | 16:00:00 | 274.15 | 98743 | 7.7 | 320 | 4.185 | 284.4 | 730.8 | 258.857 | 0 | 1
2/1 | 17:00:00 | 273.15 | 98734 | 7.2 | 320 | 3.891 | 32.4 | 0 | 257.685 | 0 | 1
2/1 | 18:00:00 | 272.15 | 98724 | 4.6 | 300 | 3.581 | 0 | 0 | 257.322 | 0 | 1
2/1 | 19:00:00 | 272.15 | 98724 | 5.7 | 290 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
2/1 | 20:00:00 | 272.15 | 98724 | 6.7 | 300 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
2/1 | 21:00:00 | 271.15 | 98715 | 6.7 | 310 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
2/1 | 22:00:00 | 271.15 | 98715 | 5.7 | 300 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
2/1 | 23:00:00 | 271.15 | 98715 | 6.7 | 310 | 3.2936 | 0 | 0 | 255.341 | 0 | 1
2/1 | 24:00:00 | 271.15 | 98715 | 6.7 | 300 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
2/2 | 01:00:00 | 270.15 | 98705 | 6.2 | 310 | 3.0276 | 0 | 0 | 254.971 | 0 | 1
2/2 | 02:00:00 | 271.15 | 98715 | 6.7 | 310 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
2/2 | 03:00:00 | 270.15 | 98705 | 4.1 | 260 | 2.7812 | 0 | 0 | 254.636 | 0 | 1
2/2 | 04:00:00 | 270.15 | 98705 | 5.1 | 300 | 3.0276 | 0 | 0 | 254.971 | 0 | 1
2/2 | 05:00:00 | 271.15 | 98715 | 6.2 | 300 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
2/2 | 06:00:00 | 271.15 | 98715 | 5.7 | 310 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
2/2 | 07:00:00 | 270.15 | 98705 | 4.6 | 300 | 3.0276 | 0 | 0 | 254.971 | 0 | 1
2/2 | 08:00:00 | 271.15 | 98715 | 5.1 | 300 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
2/2 | 09:00:00 | 271.15 | 98715 | 5.7 | 310 | 3.2936 | 32.4 | 0 | 256.147 | 0 | 1
2/2 | 10:00:00 | 272.15 | 98724 | 4.6 | 300 | 3.581 | 129.6 | 0 | 257.322 | 0 | 1
2/2 | 11:00:00 | 272.15 | 98724 | 5.7 | 310 | 3.0271 | 475.2 | 280.8 | 256.647 | 0 | 1
2/2 | 12:00:00 | 273.15 | 98734 | 4.1 | 310 | 3.891 | 925.2 | 1692 | 257.685 | 0 | 1
2/2 | 13:00:00 | 274.15 | 98743 | 5.1 | 330 | 4.185 | 975.6 | 2034 | 258.857 | 0 | 1
2/2 | 14:00:00 | 274.15 | 98743 | 4.1 | 330 | 4.185 | 871.2 | 1378.8 | 258.857 | 0 | 1
2/2 | 15:00:00 | 274.15 | 98743 | 5.1 | 310 | 4.185 | 201.6 | 0 | 259.674 | 0 | 1
2/2 | 16:00:00 | 274.15 | 98743 | 5.1 | 310 | 4.185 | 298.8 | 172.8 | 258.857 | 0 | 1
2/2 | 17:00:00 | 273.15 | 98734 | 5.1 | 320 | 3.891 | 36 | 0 | 257.685 | 0 | 1
2/2 | 18:00:00 | 273.15 | 98734 | 6.2 | 320 | 3.891 | 0 | 0 | 257.685 | 0 | 1
2/2 | 19:00:00 | 273.15 | 98734 | 5.1 | 310 | 3.891 | 0 | 0 | 258.498 | 0 | 1
2/2 | 20:00:00 | 273.15 | 98734 | 4.6 | 310 | 3.891 | 0 | 0 | 257.685 | 0 | 1
2/2 | 21:00:00 | 273.15 | 98734 | 4.6 | 320 | 3.891 | 0 | 0 | 258.498 | 0 | 1
2/2 | 22:00:00 | 272.15 | 98724 | 3.6 | 320 | 3.581 | 0 | 0 | 256.513 | 0 | 1
2/2 | 23:00:00 | 272.15 | 98724 | 4.1 | 320 | 3.581 | 0 | 0 | 257.322 | 0 | 1
2/2 | 24:00:00 | 273.15 | 98734 | 5.7 | 350 | 3.891 | 0 | 0 | 258.498 | 0 | 1
2/3 | 01:00:00 | 273.15 | 98734 | 5.7 | 340 | 3.891 | 0 | 0 | 258.498 | 0 | 1
2/3 | 02:00:00 | 272.15 | 98724 | 4.6 | 320 | 3.581 | 0 | 0 | 257.322 | 0 | 1
2/3 | 03:00:00 | 272.15 | 98724 | 4.6 | 310 | 3.581 | 0 | 0 | 257.322 | 0 | 1
2/3 | 04:00:00 | 272.15 | 98724 | 4.6 | 320 | 3.581 | 0 | 0 | 256.513 | 0 | 1
2/3 | 05:00:00 | 272.15 | 98724 | 4.1 | 330 | 3.581 | 0 | 0 | 256.513 | 0 | 1
2/3 | 06:00:00 | 272.15 | 98724 | 4.1 | 350 | 3.581 | 0 | 0 | 256.513 | 0 | 1
2/3 | 07:00:00 | 273.15 | 98734 | 4.6 | 360 | 3.891 | 0 | 0 | 257.937 | 0 | 1
2/3 | 08:00:00 | 273.15 | 98734 | 4.6 | 350 | 3.891 | 0 | 0 | 257.937 | 0 | 1
2/3 | 09:00:00 | 273.15 | 98734 | 4.1 | 340 | 3.891 | 100.8 | 79.2 | 257.937 | 0 | 1
2/3 | 10:00:00 | 274.15 | 98743 | 4.6 | 350 | 4.185 | 396 | 806.4 | 259.111 | 0 | 1
2/3 | 11:00:00 | 274.15 | 98743 | 4.1 | 350 | 4.185 | 694.8 | 1260 | 259.111 | 0 | 1
2/3 | 12:00:00 | 275.15 | 98752 | 4.1 | 350 | 4.4981 | 939.6 | 1954.8 | 260.03 | 0 | 1
2/3 | 13:00:00 | 276.15 | 98762 | 3.6 | 360 | 3.2921 | 925.2 | 1465.2 | 260.304 | 0 | 1
2/3 | 14:00:00 | 277.15 | 98771 | 3.1 | 360 | 3.0256 | 882 | 1886.4 | 260.885 | 0 | 1
2/3 | 15:00:00 | 276.15 | 98762 | 4.1 | 340 | 2.7796 | 651.6 | 1404 | 259.577 | 0 | 1
2/3 | 16:00:00 | 275.15 | 98752 | 5.1 | 340 | 3.2924 | 313.2 | 813.6 | 259.107 | 0 | 1
2/3 | 17:00:00 | 275.15 | 98752 | 4.6 | 350 | 3.2924 | 21.6 | 0 | 259.82 | 0 | 1
2/3 | 18:00:00 | 275.15 | 98752 | 3.1 | 350 | 3.2924 | 0 | 0 | 259.82 | 0 | 1
2/3 | 19:00:00 | 274.15 | 98743 | 3.6 | 330 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
2/3 | 20:00:00 | 274.15 | 98743 | 4.6 | 340 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
2/3 | 21:00:00 | 274.15 | 98743 | 5.7 | 360 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
2/3 | 22:00:00 | 274.15 | 98743 | 5.7 | 350 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
2/3 | 23:00:00 | 274.15 | 98743 | 3.6 | 360 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/3 | 24:00:00 | 274.15 | 98743 | 4.6 | 350 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
2/4 | 01:00:00 | 274.15 | 98743 | 5.1 | 350 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
2/4 | 02:00:00 | 273.15 | 98734 | 6.2 | 350 | 3.5806 | 0 | 0 | 257.707 | 0 | 1
2/4 | 03:00:00 | 273.15 | 98734 | 5.1 | 360 | 3.891 | 0 | 0 | 257.937 | 0 | 1
2/4 | 04:00:00 | 274.15 | 98743 | 6.2 | 350 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
2/4 | 05:00:00 | 273.15 | 98734 | 6.2 | 360 | 3.0267 | 0 | 0 | 256.991 | 0 | 1
2/4 | 06:00:00 | 273.15 | 98734 | 5.1 | 330 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
2/4 | 07:00:00 | 273.15 | 98734 | 6.7 | 340 | 3.293 | 0 | 0 | 257.224 | 0 | 1
2/4 | 08:00:00 | 273.15 | 98734 | 7.2 | 340 | 3.5806 | 0 | 0 | 257.455 | 0 | 1
2/4 | 09:00:00 | 273.15 | 98734 | 5.7 | 330 | 3.891 | 108 | 86.4 | 257.937 | 0 | 1
2/4 | 10:00:00 | 274.15 | 98743 | 7.2 | 350 | 3.2927 | 439.2 | 1022.4 | 258.166 | 0 | 1
2/4 | 11:00:00 | 275.15 | 98752 | 7.7 | 350 | 3.5799 | 756 | 1760.4 | 259.34 | 0 | 1
2/4 | 12:00:00 | 276.15 | 98762 | 5.1 | 340 | 3.0259 | 910.8 | 1332 | 260.068 | 0 | 1
2/4 | 13:00:00 | 275.15 | 98752 | 4.6 | 340 | 3.0262 | 961.2 | 1375.2 | 259.127 | 0 | 1
2/4 | 14:00:00 | 276.15 | 98762 | 4.1 | 350 | 3.5796 | 860.4 | 1666.8 | 260.538 | 0 | 1
2/4 | 15:00:00 | 276.15 | 98762 | 4.1 | 330 | 3.5796 | 626.4 | 1180.8 | 260.538 | 0 | 1
2/4 | 16:00:00 | 276.15 | 98762 | 3.6 | 350 | 3.5796 | 309.6 | 694.8 | 260.538 | 0 | 1
2/4 | 17:00:00 | 275.15 | 98752 | 4.1 | 340 | 3.5799 | 50.4 | 0 | 259.34 | 0 | 1
2/4 | 18:00:00 | 275.15 | 98752 | 3.6 | 340 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
2/4 | 19:00:00 | 275.15 | 98752 | 5.1 | 360 | 3.5799 | 0 | 0 | 259.34 | 0 | 1
2/4 | 20:00:00 | 275.15 | 98752 | 4.1 | 360 | 3.5799 | 0 | 0 | 259.34 | 0 | 1
2/4 | 21:00:00 | 275.15 | 98752 | 4.6 | 350 | 3.2924 | 0 | 0 | 259.107 | 0 | 1
2/4 | 22:00:00 | 275.15 | 98752 | 5.1 | 350 | 3.2924 | 0 | 0 | 259.107 | 0 | 1
2/4 | 23:00:00 | 274.15 | 98743 | 4.1 | 300 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
2/4 | 24:00:00 | 274.15 | 98743 | 4.6 | 300 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
2/5 | 01:00:00 | 274.15 | 98743 | 5.1 | 310 | 3.0265 | 0 | 0 | 258.305 | 0 | 1
2/5 | 02:00:00 | 274.15 | 98743 | 6.2 | 320 | 3.0265 | 0 | 0 | 258.305 | 0 | 1
2/5 | 03:00:00 | 274.15 | 98743 | 5.7 | 310 | 3.0265 | 0 | 0 | 258.305 | 0 | 1
2/5 | 04:00:00 | 274.15 | 98743 | 4.1 | 320 | 3.0265 | 0 | 0 | 258.305 | 0 | 1
2/5 | 05:00:00 | 274.15 | 98743 | 4.6 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
2/5 | 06:00:00 | 275.15 | 98752 | 4.6 | 310 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
2/5 | 07:00:00 | 275.15 | 98752 | 5.1 | 310 | 3.2924 | 0 | 0 | 259.361 | 0 | 1
2/5 | 08:00:00 | 275.15 | 98752 | 5.7 | 340 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
2/5 | 09:00:00 | 276.15 | 98762 | 6.2 | 360 | 3.8899 | 111.6 | 86.4 | 260.77 | 0 | 1
2/5 | 10:00:00 | 276.15 | 98762 | 4.1 | 360 | 4.1841 | 424.8 | 853.2 | 261.001 | 0 | 1
2/5 | 11:00:00 | 277.15 | 98771 | 4.1 | 10 | 4.1838 | 727.2 | 1476 | 261.946 | 0 | 1
2/5 | 12:00:00 | 277.15 | 98771 | 5.1 | 10 | 4.4973 | 921.6 | 1335.6 | 262.177 | 0 | 1
2/5 | 13:00:00 | 278.15 | 98780 | 5.7 | 10 | 4.4968 | 540 | 90 | 263.588 | 0 | 1
2/5 | 14:00:00 | 278.15 | 98780 | 6.2 | 10 | 4.8311 | 482.4 | 68.4 | 263.818 | 0 | 1
2/5 | 15:00:00 | 278.15 | 98780 | 4.6 | 30 | 4.8311 | 356.4 | 21.6 | 263.818 | 0 | 1
2/5 | 16:00:00 | 276.15 | 98762 | 2.6 | 80 | 4.832 | 176.4 | 0 | 261.921 | 0 | 1
2/5 | 17:00:00 | 275.15 | 98752 | 2.6 | 90 | 4.4981 | 28.8 | 0 | 260.745 | 0 | 1
2/5 | 18:00:00 | 275.15 | 98752 | 2.6 | 90 | 4.4981 | 0 | 0 | 260.745 | 0 | 1
2/5 | 19:00:00 | 274.15 | 98743 | 1.5 | 155 | 4.185 | 0 | 0 | 259.111 | 0 | 1
2/5 | 20:00:00 | 274.15 | 98743 | 2.1 | 40 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/5 | 21:00:00 | 274.15 | 98743 | 2.1 | 70 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/5 | 22:00:00 | 274.15 | 98743 | 1.5 | 216 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/5 | 23:00:00 | 274.15 | 98743 | 1 | 124 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/5 | 24:00:00 | 274.15 | 98743 | 1.5 | 40 | 4.185 | 0 | 0 | 259.111 | 0 | 1
2/6 | 01:00:00 | 273.15 | 98734 | 2.1 | 30 | 3.891 | 0 | 0 | 257.685 | 0 | 1
2/6 | 02:00:00 | 273.15 | 98734 | 1 | 20 | 3.891 | 0 | 0 | 257.685 | 0 | 1
2/6 | 03:00:00 | 273.15 | 98734 | 1.5 | 59 | 3.891 | 0 | 0 | 258.498 | 0 | 1
2/6 | 04:00:00 | 272.15 | 98724 | 1 | 30 | 3.581 | 0 | 0 | 257.322 | 0 | 1
2/6 | 05:00:00 | 272.15 | 98724 | 1.5 | 10 | 3.581 | 0 | 0 | 257.322 | 0 | 1
2/6 | 06:00:00 | 272.15 | 98724 | 2.1 | 350 | 3.581 | 0 | 0 | 257.322 | 0 | 1
2/6 | 07:00:00 | 273.15 | 98734 | 2.6 | 360 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
2/6 | 08:00:00 | 272.15 | 98724 | 2.1 | 360 | 3.581 | 0 | 0 | 256.764 | 0 | 1
2/6 | 09:00:00 | 273.15 | 98734 | 2.1 | 20 | 3.891 | 118.8 | 115.2 | 257.937 | 0 | 1
2/6 | 10:00:00 | 273.15 | 98734 | 2.1 | 10 | 3.891 | 468 | 1065.6 | 257.685 | 0 | 1
2/6 | 11:00:00 | 274.15 | 98743 | 1.5 | 156 | 4.185 | 788.4 | 1616.4 | 258.857 | 0 | 1
2/6 | 12:00:00 | 276.15 | 98762 | 1.5 | 26 | 4.1841 | 604.8 | 252 | 261.463 | 0 | 1
2/6 | 13:00:00 | 276.15 | 98762 | 2.6 | 40 | 4.1841 | 993.6 | 1461.6 | 261.001 | 0 | 1
2/6 | 14:00:00 | 277.15 | 98771 | 1.5 | 299 | 4.1838 | 892.8 | 1684.8 | 261.946 | 0 | 1
2/6 | 15:00:00 | 276.15 | 98762 | 2.6 | 40 | 4.1841 | 658.8 | 1209.6 | 261.001 | 0 | 1
2/6 | 16:00:00 | 277.15 | 98771 | 2.6 | 70 | 4.1838 | 334.8 | 745.2 | 261.946 | 0 | 1
2/6 | 17:00:00 | 276.15 | 98762 | 1 | 32 | 4.1841 | 64.8 | 0 | 260.746 | 0 | 1
2/6 | 18:00:00 | 275.15 | 98752 | 1.5 | 360 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
2/6 | 19:00:00 | 275.15 | 98752 | 2.1 | 360 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
2/6 | 20:00:00 | 275.15 | 98752 | 2.1 | 360 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
2/6 | 21:00:00 | 276.15 | 98762 | 1.5 | 360 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/6 | 22:00:00 | 276.15 | 98762 | 2.6 | 360 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
2/6 | 23:00:00 | 276.15 | 98762 | 2.6 | 360 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
2/6 | 24:00:00 | 276.15 | 98762 | 2.1 | 350 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
2/7 | 01:00:00 | 276.15 | 98762 | 2.1 | 360 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
2/7 | 02:00:00 | 276.15 | 98762 | 2.1 | 360 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
2/7 | 03:00:00 | 276.15 | 98762 | 1.5 | 350 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
2/7 | 04:00:00 | 276.15 | 98762 | 2.1 | 340 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
2/7 | 05:00:00 | 275.15 | 98752 | 3.1 | 350 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/7 | 06:00:00 | 274.15 | 98743 | 3.6 | 320 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/7 | 07:00:00 | 275.15 | 98752 | 1 | 340 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
2/7 | 08:00:00 | 274.15 | 98743 | 2.6 | 300 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/7 | 09:00:00 | 275.15 | 98752 | 2.1 | 290 | 4.1846 | 68.4 | 0 | 260.516 | 0 | 1
2/7 | 10:00:00 | 275.15 | 98752 | 2.6 | 310 | 4.1846 | 252 | 0 | 260.516 | 0 | 1
2/7 | 11:00:00 | 276.15 | 98762 | 2.6 | 330 | 4.4977 | 421.2 | 36 | 261.693 | 0 | 1
2/7 | 12:00:00 | 276.15 | 98762 | 3.1 | 350 | 4.4977 | 532.8 | 79.2 | 261.693 | 0 | 1
2/7 | 13:00:00 | 277.15 | 98771 | 2.1 | 350 | 4.4973 | 561.6 | 118.8 | 262.64 | 0 | 1
2/7 | 14:00:00 | 278.15 | 98780 | 1.5 | 54 | 4.8311 | 504 | 108 | 263.818 | 0 | 1
2/7 | 15:00:00 | 279.15 | 98789 | 2.6 | 270 | 4.8307 | 716.4 | 1191.6 | 264.041 | 0 | 1
2/7 | 16:00:00 | 278.15 | 98780 | 4.1 | 280 | 4.8311 | 226.8 | 86.4 | 263.818 | 0 | 1
2/7 | 17:00:00 | 277.15 | 98771 | 4.1 | 280 | 4.8316 | 32.4 | 0 | 262.976 | 0 | 1
2/7 | 18:00:00 | 276.15 | 98762 | 3.6 | 290 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
2/7 | 19:00:00 | 277.15 | 98771 | 5.1 | 310 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
2/7 | 20:00:00 | 278.15 | 98780 | 3.6 | 10 | 4.1834 | 0 | 0 | 263.132 | 0 | 1
2/7 | 21:00:00 | 277.15 | 98771 | 3.6 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
2/7 | 22:00:00 | 277.15 | 98771 | 4.6 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
2/7 | 23:00:00 | 277.15 | 98771 | 6.2 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
2/7 | 24:00:00 | 277.15 | 98771 | 6.2 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
2/8 | 01:00:00 | 277.15 | 98771 | 5.1 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
2/8 | 02:00:00 | 277.15 | 98771 | 4.6 | 330 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
2/8 | 03:00:00 | 275.15 | 98752 | 3.6 | 310 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
2/8 | 04:00:00 | 276.15 | 98762 | 4.6 | 330 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
2/8 | 05:00:00 | 276.15 | 98762 | 3.1 | 330 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
2/8 | 06:00:00 | 273.15 | 98734 | 3.1 | 270 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
2/8 | 07:00:00 | 273.15 | 98734 | 4.1 | 280 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
2/8 | 08:00:00 | 272.15 | 98724 | 3.1 | 270 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
2/8 | 09:00:00 | 272.15 | 98724 | 3.6 | 290 | 3.2934 | 64.8 | 0 | 256.987 | 0 | 1
2/8 | 10:00:00 | 274.15 | 98743 | 2.6 | 270 | 3.8907 | 212.4 | 0 | 259.445 | 0 | 1
2/8 | 11:00:00 | 275.15 | 98752 | 4.6 | 260 | 3.8903 | 504 | 208.8 | 260.286 | 0 | 1
2/8 | 12:00:00 | 278.15 | 98780 | 5.7 | 270 | 4.1834 | 878.4 | 1022.4 | 263.132 | 0 | 1
2/8 | 13:00:00 | 278.15 | 98780 | 7.2 | 280 | 4.1834 | 1094.4 | 2077.2 | 262.634 | 0 | 1
2/8 | 14:00:00 | 277.15 | 98771 | 7.7 | 270 | 4.1838 | 990 | 2066.4 | 261.69 | 0 | 1
2/8 | 15:00:00 | 277.15 | 98771 | 6.7 | 260 | 4.4973 | 734.4 | 1324.8 | 261.92 | 0 | 1
2/8 | 16:00:00 | 276.15 | 98762 | 7.2 | 260 | 4.4977 | 201.6 | 0 | 261.693 | 0 | 1
2/8 | 17:00:00 | 275.15 | 98752 | 11.3 | 280 | 4.4981 | 75.6 | 86.4 | 260.285 | 0 | 1
2/8 | 18:00:00 | 275.15 | 98752 | 10.3 | 270 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
2/8 | 19:00:00 | 275.15 | 98752 | 6.2 | 280 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
2/8 | 20:00:00 | 276.15 | 98762 | 8.8 | 280 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
2/8 | 21:00:00 | 277.15 | 98771 | 8.2 | 270 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
2/8 | 22:00:00 | 277.15 | 98771 | 8.8 | 280 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/8 | 23:00:00 | 277.15 | 98771 | 8.2 | 280 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
2/8 | 24:00:00 | 277.15 | 98771 | 6.7 | 270 | 4.8316 | 0 | 0 | 262.405 | 0 | 1
2/9 | 01:00:00 | 276.15 | 98762 | 7.2 | 270 | 4.832 | 0 | 0 | 262.027 | 0 | 1
2/9 | 02:00:00 | 276.15 | 98762 | 7.2 | 280 | 4.832 | 0 | 0 | 262.027 | 0 | 1
2/9 | 03:00:00 | 276.15 | 98762 | 7.2 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
2/9 | 04:00:00 | 276.15 | 98762 | 7.7 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
2/9 | 05:00:00 | 276.15 | 98762 | 11.3 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
2/9 | 06:00:00 | 276.15 | 98762 | 9.3 | 280 | 4.832 | 0 | 0 | 261.203 | 0 | 1
2/9 | 07:00:00 | 276.15 | 98762 | 10.3 | 280 | 4.832 | 0 | 0 | 261.459 | 0 | 1
2/9 | 08:00:00 | 276.15 | 98762 | 11.3 | 280 | 4.832 | 0 | 0 | 261.203 | 0 | 1
2/9 | 09:00:00 | 277.15 | 98771 | 5.1 | 280 | 4.8316 | 154.8 | 241.2 | 262.149 | 0 | 1
2/9 | 10:00:00 | 277.15 | 98771 | 7.2 | 270 | 4.8316 | 514.8 | 1263.6 | 262.149 | 0 | 1
2/9 | 11:00:00 | 278.15 | 98780 | 5.1 | 280 | 5.1875 | 842.4 | 1825.2 | 263.323 | 0 | 1
2/9 | 12:00:00 | 279.15 | 98789 | 5.1 | 280 | 5.187 | 1054.8 | 2080.8 | 264.269 | 0 | 1
2/9 | 13:00:00 | 280.15 | 98798 | 6.7 | 280 | 5.1865 | 1108.8 | 2145.6 | 265.216 | 0 | 1
2/9 | 14:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.5656 | 1004.4 | 2059.2 | 266.392 | 0 | 1
2/9 | 15:00:00 | 281.15 | 98806 | 7.7 | 270 | 5.5656 | 752.4 | 1713.6 | 266.392 | 0 | 1
2/9 | 16:00:00 | 280.15 | 98798 | 6.7 | 290 | 5.5661 | 403.2 | 1047.6 | 265.444 | 0 | 1
2/9 | 17:00:00 | 279.15 | 98789 | 6.2 | 270 | 5.187 | 86.4 | 147.6 | 264.269 | 0 | 1
2/9 | 18:00:00 | 277.15 | 98771 | 6.7 | 290 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
2/9 | 19:00:00 | 276.15 | 98762 | 5.7 | 280 | 4.832 | 0 | 0 | 261.203 | 0 | 1
2/9 | 20:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.832 | 0 | 0 | 261.203 | 0 | 1
2/9 | 21:00:00 | 276.15 | 98762 | 5.1 | 270 | 4.832 | 0 | 0 | 262.027 | 0 | 1
2/9 | 22:00:00 | 275.15 | 98752 | 5.7 | 280 | 4.4981 | 0 | 0 | 259.615 | 0 | 1
2/9 | 23:00:00 | 274.15 | 98743 | 5.1 | 280 | 4.185 | 0 | 0 | 259.674 | 0 | 1
2/9 | 24:00:00 | 275.15 | 98752 | 5.1 | 270 | 4.4981 | 0 | 0 | 260.745 | 0 | 1
2/10 | 01:00:00 | 275.15 | 98752 | 4.1 | 290 | 4.4981 | 0 | 0 | 260.745 | 0 | 1
2/10 | 02:00:00 | 276.15 | 98762 | 6.7 | 280 | 4.832 | 0 | 0 | 261.921 | 0 | 1
2/10 | 03:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.832 | 0 | 0 | 261.921 | 0 | 1
2/10 | 04:00:00 | 276.15 | 98762 | 6.2 | 270 | 4.832 | 0 | 0 | 261.921 | 0 | 1
2/10 | 05:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.832 | 0 | 0 | 261.921 | 0 | 1
2/10 | 06:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.832 | 0 | 0 | 261.921 | 0 | 1
2/10 | 07:00:00 | 275.15 | 98752 | 3.1 | 280 | 4.4981 | 0 | 0 | 260.03 | 0 | 1
2/10 | 08:00:00 | 275.15 | 98752 | 0.5 | 226 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
2/10 | 09:00:00 | 275.15 | 98752 | 1.5 | 352 | 4.4981 | 86.4 | 0 | 260.745 | 0 | 1
2/10 | 10:00:00 | 276.15 | 98762 | 3.1 | 280 | 4.832 | 277.2 | 7.2 | 261.921 | 0 | 1
2/10 | 11:00:00 | 276.15 | 98762 | 3.1 | 270 | 4.832 | 450 | 39.6 | 261.921 | 0 | 1
2/10 | 12:00:00 | 276.15 | 98762 | 3.1 | 260 | 4.832 | 561.6 | 115.2 | 261.921 | 0 | 1
2/10 | 13:00:00 | 277.15 | 98771 | 3.6 | 260 | 5.1879 | 590.4 | 118.8 | 263.098 | 0 | 1
2/10 | 14:00:00 | 278.15 | 98780 | 4.1 | 260 | 5.1875 | 964.8 | 1353.6 | 263.581 | 0 | 1
2/10 | 15:00:00 | 278.15 | 98780 | 4.6 | 270 | 5.1875 | 727.2 | 1458 | 263.581 | 0 | 1
2/10 | 16:00:00 | 277.15 | 98771 | 4.1 | 250 | 4.8316 | 396 | 896.4 | 262.405 | 0 | 1
2/10 | 17:00:00 | 277.15 | 98771 | 4.1 | 270 | 4.8316 | 86.4 | 72 | 262.405 | 0 | 1
2/10 | 18:00:00 | 276.15 | 98762 | 3.6 | 270 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
2/10 | 19:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
2/10 | 20:00:00 | 275.15 | 98752 | 5.1 | 280 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
2/10 | 21:00:00 | 274.15 | 98743 | 2.1 | 260 | 4.185 | 0 | 0 | 259.111 | 0 | 1
2/10 | 22:00:00 | 274.15 | 98743 | 2.6 | 270 | 4.185 | 0 | 0 | 259.111 | 0 | 1
2/10 | 23:00:00 | 274.15 | 98743 | 2.1 | 240 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/10 | 24:00:00 | 274.15 | 98743 | 2.6 | 240 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/11 | 01:00:00 | 273.15 | 98734 | 2.1 | 240 | 3.891 | 0 | 0 | 258.394 | 0 | 1
2/11 | 02:00:00 | 273.15 | 98734 | 2.1 | 230 | 3.891 | 0 | 0 | 258.394 | 0 | 1
2/11 | 03:00:00 | 273.15 | 98734 | 2.6 | 240 | 3.891 | 0 | 0 | 258.394 | 0 | 1
2/11 | 04:00:00 | 274.15 | 98743 | 2.6 | 230 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/11 | 05:00:00 | 274.15 | 98743 | 2.6 | 210 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/11 | 06:00:00 | 274.15 | 98743 | 3.6 | 220 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/11 | 07:00:00 | 274.15 | 98743 | 2.1 | 210 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/11 | 08:00:00 | 274.15 | 98743 | 4.1 | 220 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/11 | 09:00:00 | 274.15 | 98743 | 4.6 | 230 | 3.8907 | 93.6 | 0 | 259.34 | 0 | 1
2/11 | 10:00:00 | 275.15 | 98752 | 3.6 | 230 | 3.8903 | 288 | 3.6 | 260.286 | 0 | 1
2/11 | 11:00:00 | 275.15 | 98752 | 3.6 | 250 | 3.8903 | 464.4 | 39.6 | 260.286 | 0 | 1
2/11 | 12:00:00 | 275.15 | 98752 | 4.6 | 240 | 3.8903 | 576 | 54 | 260.286 | 0 | 1
2/11 | 13:00:00 | 275.15 | 98752 | 3.6 | 250 | 3.8903 | 604.8 | 129.6 | 260.286 | 0 | 1
2/11 | 14:00:00 | 275.15 | 98752 | 4.1 | 250 | 3.8903 | 993.6 | 1238.4 | 259.826 | 0 | 1
2/11 | 15:00:00 | 275.15 | 98752 | 4.6 | 240 | 3.8903 | 417.6 | 43.2 | 260.286 | 0 | 1
2/11 | 16:00:00 | 275.15 | 98752 | 3.6 | 240 | 3.8903 | 230.4 | 0 | 260.286 | 0 | 1
2/11 | 17:00:00 | 275.15 | 98752 | 2.6 | 250 | 3.8903 | 54 | 0 | 260.286 | 0 | 1
2/11 | 18:00:00 | 275.15 | 98752 | 3.6 | 240 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
2/11 | 19:00:00 | 275.15 | 98752 | 1.5 | 91 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/11 | 20:00:00 | 275.15 | 98752 | 2.6 | 200 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
2/11 | 21:00:00 | 275.15 | 98752 | 1 | 251 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/11 | 22:00:00 | 275.15 | 98752 | 0 | 98 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/11 | 23:00:00 | 275.15 | 98752 | 1.5 | 101 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/11 | 24:00:00 | 275.15 | 98752 | 1 | 144 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/12 | 01:00:00 | 275.15 | 98752 | 1.5 | 99 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/12 | 02:00:00 | 275.15 | 98752 | 0.5 | 217 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/12 | 03:00:00 | 275.15 | 98752 | 1.5 | 210 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/12 | 04:00:00 | 275.15 | 98752 | 1.5 | 250 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/12 | 05:00:00 | 275.15 | 98752 | 1.5 | 112 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/12 | 06:00:00 | 275.15 | 98752 | 1.5 | 74 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/12 | 07:00:00 | 274.15 | 98743 | 0.5 | 200 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/12 | 08:00:00 | 275.15 | 98752 | 0.5 | 270 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
2/12 | 09:00:00 | 275.15 | 98752 | 1.5 | 270 | 4.1846 | 100.8 | 0 | 260.516 | 0 | 1
2/12 | 10:00:00 | 276.15 | 98762 | 1.5 | 82 | 4.1841 | 298.8 | 3.6 | 261.463 | 0 | 1
2/12 | 11:00:00 | 276.15 | 98762 | 1.5 | 0 | 4.1841 | 475.2 | 39.6 | 261.463 | 0 | 1
2/12 | 12:00:00 | 277.15 | 98771 | 1.5 | 41 | 4.1838 | 586.8 | 54 | 262.41 | 0 | 1
2/12 | 13:00:00 | 277.15 | 98771 | 2.6 | 170 | 3.8896 | 615.6 | 57.6 | 262.177 | 0 | 1
2/12 | 14:00:00 | 277.15 | 98771 | 2.1 | 170 | 3.8896 | 561.6 | 50.4 | 262.177 | 0 | 1
2/12 | 15:00:00 | 277.15 | 98771 | 2.1 | 170 | 3.8896 | 428.4 | 32.4 | 262.177 | 0 | 1
2/12 | 16:00:00 | 277.15 | 98771 | 2.1 | 140 | 3.8896 | 237.6 | 0 | 262.177 | 0 | 1
2/12 | 17:00:00 | 276.15 | 98762 | 2.6 | 140 | 3.8899 | 57.6 | 0 | 261.231 | 0 | 1
2/12 | 18:00:00 | 276.15 | 98762 | 3.1 | 140 | 3.8899 | 0 | 0 | 261.231 | 0 | 1
2/12 | 19:00:00 | 276.15 | 98762 | 1.5 | 160 | 3.8899 | 0 | 0 | 261.231 | 0 | 1
2/12 | 20:00:00 | 276.15 | 98762 | 2.1 | 180 | 3.5796 | 0 | 0 | 260.999 | 0 | 1
2/12 | 21:00:00 | 276.15 | 98762 | 2.6 | 160 | 3.8899 | 0 | 0 | 261.231 | 0 | 1
2/12 | 22:00:00 | 275.15 | 98752 | 3.6 | 180 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
2/12 | 23:00:00 | 275.15 | 98752 | 3.1 | 160 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
2/12 | 24:00:00 | 274.15 | 98743 | 3.6 | 160 | 3.8907 | 0 | 0 | 258.215 | 0 | 1
2/13 | 01:00:00 | 273.15 | 98734 | 5.1 | 160 | 3.5806 | 0 | 0 | 257.707 | 0 | 1
2/13 | 02:00:00 | 274.15 | 98743 | 4.1 | 150 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
2/13 | 03:00:00 | 274.15 | 98743 | 3.6 | 150 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
2/13 | 04:00:00 | 274.15 | 98743 | 5.1 | 140 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/13 | 05:00:00 | 274.15 | 98743 | 6.2 | 140 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/13 | 06:00:00 | 274.15 | 98743 | 5.7 | 140 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/13 | 07:00:00 | 274.15 | 98743 | 6.2 | 130 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/13 | 08:00:00 | 274.15 | 98743 | 5.7 | 130 | 4.185 | 0 | 0 | 259.569 | 0 | 1
2/13 | 09:00:00 | 274.15 | 98743 | 4.6 | 120 | 4.185 | 108 | 0 | 259.569 | 0 | 1
2/13 | 10:00:00 | 275.15 | 98752 | 6.2 | 140 | 4.4981 | 306 | 18 | 260.745 | 0 | 1
2/13 | 11:00:00 | 276.15 | 98762 | 5.7 | 130 | 4.832 | 482.4 | 64.8 | 261.921 | 0 | 1
2/13 | 12:00:00 | 277.15 | 98771 | 5.7 | 130 | 5.1879 | 594 | 122.4 | 263.098 | 0 | 1
2/13 | 13:00:00 | 277.15 | 98771 | 6.7 | 130 | 5.1879 | 626.4 | 129.6 | 263.098 | 0 | 1
2/13 | 14:00:00 | 278.15 | 98780 | 5.7 | 130 | 5.5671 | 568.8 | 115.2 | 264.274 | 0 | 1
2/13 | 15:00:00 | 278.15 | 98780 | 6.2 | 120 | 5.5671 | 435.6 | 36 | 264.274 | 0 | 1
2/13 | 16:00:00 | 279.15 | 98789 | 5.1 | 120 | 5.5666 | 244.8 | 0 | 265.224 | 0 | 1
2/13 | 17:00:00 | 279.15 | 98789 | 6.7 | 120 | 5.5666 | 61.2 | 0 | 265.224 | 0 | 1
2/13 | 18:00:00 | 278.15 | 98780 | 7.7 | 120 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/13 | 19:00:00 | 278.15 | 98780 | 6.2 | 110 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/13 | 20:00:00 | 278.15 | 98780 | 5.7 | 110 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/13 | 21:00:00 | 278.15 | 98780 | 4.6 | 130 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/13 | 22:00:00 | 278.15 | 98780 | 4.1 | 110 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/13 | 23:00:00 | 278.15 | 98780 | 4.1 | 90 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/13 | 24:00:00 | 278.15 | 98780 | 4.6 | 90 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/14 | 01:00:00 | 278.15 | 98780 | 3.6 | 80 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
2/14 | 02:00:00 | 277.15 | 98771 | 3.6 | 80 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/14 | 03:00:00 | 277.15 | 98771 | 3.1 | 60 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/14 | 04:00:00 | 277.15 | 98771 | 3.1 | 50 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/14 | 05:00:00 | 277.15 | 98771 | 4.1 | 40 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/14 | 06:00:00 | 277.15 | 98771 | 3.6 | 40 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/14 | 07:00:00 | 277.15 | 98771 | 4.1 | 40 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/14 | 08:00:00 | 277.15 | 98771 | 4.1 | 50 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/14 | 09:00:00 | 277.15 | 98771 | 3.6 | 50 | 5.1879 | 68.4 | 0 | 263.204 | 0 | 1
2/14 | 10:00:00 | 278.15 | 98780 | 3.1 | 60 | 5.5671 | 190.8 | 0 | 264.381 | 0 | 1
2/14 | 11:00:00 | 278.15 | 98780 | 3.1 | 40 | 5.5671 | 493.2 | 75.6 | 264.274 | 0 | 1
2/14 | 12:00:00 | 278.15 | 98780 | 4.6 | 40 | 5.5671 | 604.8 | 122.4 | 264.274 | 0 | 1
2/14 | 13:00:00 | 278.15 | 98780 | 3.6 | 50 | 5.5671 | 388.8 | 0 | 264.381 | 0 | 1
2/14 | 14:00:00 | 278.15 | 98780 | 2.6 | 60 | 5.5671 | 579.6 | 241.2 | 264.274 | 0 | 1
2/14 | 15:00:00 | 279.15 | 98789 | 3.6 | 70 | 5.9708 | 799.2 | 1191.6 | 264.982 | 0 | 1
2/14 | 16:00:00 | 280.15 | 98798 | 4.1 | 80 | 5.9703 | 255.6 | 0 | 266.402 | 0 | 1
2/14 | 17:00:00 | 279.15 | 98789 | 3.6 | 80 | 5.9708 | 64.8 | 0 | 265.451 | 0 | 1
2/14 | 18:00:00 | 279.15 | 98789 | 4.1 | 60 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
2/14 | 19:00:00 | 279.15 | 98789 | 4.1 | 70 | 5.9708 | 0 | 0 | 264.982 | 0 | 1
2/14 | 20:00:00 | 278.15 | 98780 | 4.6 | 80 | 5.5671 | 0 | 0 | 263.807 | 0 | 1
2/14 | 21:00:00 | 278.15 | 98780 | 3.6 | 80 | 5.5671 | 0 | 0 | 263.807 | 0 | 1
2/14 | 22:00:00 | 278.15 | 98780 | 3.1 | 80 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/14 | 23:00:00 | 278.15 | 98780 | 3.6 | 90 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/14 | 24:00:00 | 278.15 | 98780 | 2.6 | 90 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
2/15 | 01:00:00 | 278.15 | 98780 | 2.6 | 70 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
2/15 | 02:00:00 | 278.15 | 98780 | 3.1 | 80 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
2/15 | 03:00:00 | 278.15 | 98780 | 3.1 | 80 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
2/15 | 04:00:00 | 277.15 | 98771 | 2.6 | 90 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/15 | 05:00:00 | 277.15 | 98771 | 2.6 | 90 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/15 | 06:00:00 | 277.15 | 98771 | 1.5 | 90 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/15 | 07:00:00 | 277.15 | 98771 | 1.5 | 149 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/15 | 08:00:00 | 277.15 | 98771 | 2.6 | 70 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
2/15 | 09:00:00 | 277.15 | 98771 | 1.5 | 152 | 5.1879 | 75.6 | 0 | 263.204 | 0 | 1
2/15 | 10:00:00 | 277.15 | 98771 | 2.6 | 80 | 5.1879 | 198 | 0 | 263.204 | 0 | 1
2/15 | 11:00:00 | 277.15 | 98771 | 2.6 | 80 | 5.1879 | 504 | 75.6 | 263.098 | 0 | 1
2/15 | 12:00:00 | 278.15 | 98780 | 4.6 | 90 | 5.5671 | 615.6 | 126 | 264.274 | 0 | 1
2/15 | 13:00:00 | 278.15 | 98780 | 2.6 | 90 | 5.5671 | 648 | 133.2 | 264.274 | 0 | 1
2/15 | 14:00:00 | 279.15 | 98789 | 4.6 | 120 | 5.5666 | 590.4 | 118.8 | 265.224 | 0 | 1
2/15 | 15:00:00 | 279.15 | 98789 | 4.1 | 110 | 5.5666 | 453.6 | 39.6 | 265.224 | 0 | 1
2/15 | 16:00:00 | 279.15 | 98789 | 3.1 | 140 | 5.5666 | 262.8 | 0 | 265.224 | 0 | 1
2/15 | 17:00:00 | 279.15 | 98789 | 3.6 | 110 | 5.5666 | 68.4 | 0 | 265.224 | 0 | 1
2/15 | 18:00:00 | 278.15 | 98780 | 4.1 | 110 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
2/15 | 19:00:00 | 277.15 | 98771 | 3.6 | 120 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/15 | 20:00:00 | 277.15 | 98771 | 3.6 | 120 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
2/15 | 21:00:00 | 277.15 | 98771 | 2.6 | 140 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/15 | 22:00:00 | 277.15 | 98771 | 4.1 | 150 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/15 | 23:00:00 | 277.15 | 98771 | 3.1 | 150 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/15 | 24:00:00 | 277.15 | 98771 | 2.1 | 160 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/16 | 01:00:00 | 277.15 | 98771 | 3.1 | 160 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/16 | 02:00:00 | 278.15 | 98780 | 2.6 | 180 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
2/16 | 03:00:00 | 277.15 | 98771 | 3.6 | 190 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
2/16 | 04:00:00 | 277.15 | 98771 | 3.6 | 170 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
2/16 | 05:00:00 | 277.15 | 98771 | 4.1 | 160 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
2/16 | 06:00:00 | 277.15 | 98771 | 3.1 | 170 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
2/16 | 07:00:00 | 277.15 | 98771 | 3.1 | 150 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/16 | 08:00:00 | 277.15 | 98771 | 3.6 | 140 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/16 | 09:00:00 | 277.15 | 98771 | 3.6 | 160 | 5.1879 | 129.6 | 0 | 263.098 | 0 | 1
2/16 | 10:00:00 | 277.15 | 98771 | 2.6 | 190 | 5.1879 | 334.8 | 18 | 263.098 | 0 | 1
2/16 | 11:00:00 | 278.15 | 98780 | 3.1 | 230 | 5.5671 | 514.8 | 72 | 264.274 | 0 | 1
2/16 | 12:00:00 | 279.15 | 98789 | 4.6 | 280 | 5.5666 | 630 | 262.8 | 265.224 | 0 | 1
2/16 | 13:00:00 | 279.15 | 98789 | 4.6 | 260 | 5.5666 | 1188 | 1562.4 | 264.756 | 0 | 1
2/16 | 14:00:00 | 279.15 | 98789 | 5.1 | 270 | 5.187 | 1087.2 | 1605.6 | 264.528 | 0 | 1
2/16 | 15:00:00 | 279.15 | 98789 | 5.1 | 270 | 4.8307 | 842.4 | 1350 | 264.299 | 0 | 1
2/16 | 16:00:00 | 278.15 | 98780 | 5.7 | 270 | 5.1875 | 522 | 1252.8 | 263.323 | 0 | 1
2/16 | 17:00:00 | 278.15 | 98780 | 6.7 | 280 | 4.8311 | 140.4 | 190.8 | 263.095 | 0 | 1
2/16 | 18:00:00 | 278.15 | 98780 | 4.1 | 280 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
2/16 | 19:00:00 | 276.15 | 98762 | 6.2 | 280 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
2/16 | 20:00:00 | 276.15 | 98762 | 6.7 | 280 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
2/16 | 21:00:00 | 276.15 | 98762 | 7.2 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
2/16 | 22:00:00 | 275.15 | 98752 | 4.1 | 290 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
2/16 | 23:00:00 | 275.15 | 98752 | 4.1 | 280 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
2/16 | 24:00:00 | 275.15 | 98752 | 4.6 | 290 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
2/17 | 01:00:00 | 274.15 | 98743 | 6.2 | 280 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
2/17 | 02:00:00 | 273.15 | 98734 | 3.1 | 250 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
2/17 | 03:00:00 | 273.15 | 98734 | 3.6 | 280 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
2/17 | 04:00:00 | 274.15 | 98743 | 3.6 | 300 | 3.5803 | 0 | 0 | 259 | 0 | 1
2/17 | 05:00:00 | 274.15 | 98743 | 3.1 | 280 | 3.5803 | 0 | 0 | 258.398 | 0 | 1
2/17 | 06:00:00 | 274.15 | 98743 | 6.7 | 280 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/17 | 07:00:00 | 274.15 | 98743 | 8.8 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/17 | 08:00:00 | 274.15 | 98743 | 7.2 | 260 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/17 | 09:00:00 | 275.15 | 98752 | 8.2 | 260 | 4.1846 | 262.8 | 576 | 259.802 | 0 | 1
2/17 | 10:00:00 | 276.15 | 98762 | 6.7 | 260 | 4.4977 | 666 | 1562.4 | 260.975 | 0 | 1
2/17 | 11:00:00 | 278.15 | 98780 | 5.7 | 260 | 4.4968 | 954 | 1458 | 263.123 | 0 | 1
2/17 | 12:00:00 | 278.15 | 98780 | 6.7 | 260 | 4.4968 | 1159.2 | 1670.4 | 263.123 | 0 | 1
2/17 | 13:00:00 | 279.15 | 98789 | 6.7 | 250 | 4.4964 | 1213.2 | 1710 | 264.069 | 0 | 1
2/17 | 14:00:00 | 279.15 | 98789 | 7.2 | 270 | 4.4964 | 1112.4 | 1634.4 | 264.069 | 0 | 1
2/17 | 15:00:00 | 279.15 | 98789 | 7.7 | 270 | 4.4964 | 864 | 1598.4 | 264.069 | 0 | 1
2/17 | 16:00:00 | 279.15 | 98789 | 6.7 | 260 | 4.4964 | 511.2 | 1112.4 | 264.069 | 0 | 1
2/17 | 17:00:00 | 278.15 | 98780 | 7.2 | 260 | 4.4968 | 151.2 | 226.8 | 262.865 | 0 | 1
2/17 | 18:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.4968 | 0 | 0 | 262.865 | 0 | 1
2/17 | 19:00:00 | 278.15 | 98780 | 8.2 | 250 | 4.4968 | 0 | 0 | 262.865 | 0 | 1
2/17 | 20:00:00 | 278.15 | 98780 | 4.6 | 240 | 4.1834 | 0 | 0 | 262.634 | 0 | 1
2/17 | 21:00:00 | 278.15 | 98780 | 5.7 | 240 | 4.1834 | 0 | 0 | 262.634 | 0 | 1
2/17 | 22:00:00 | 278.15 | 98780 | 3.6 | 230 | 4.1834 | 0 | 0 | 262.634 | 0 | 1
2/17 | 23:00:00 | 277.15 | 98771 | 5.7 | 240 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
2/17 | 24:00:00 | 277.15 | 98771 | 6.2 | 230 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
2/18 | 01:00:00 | 277.15 | 98771 | 5.7 | 240 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
2/18 | 02:00:00 | 277.15 | 98771 | 5.1 | 220 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
2/18 | 03:00:00 | 276.15 | 98762 | 5.7 | 230 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/18 | 04:00:00 | 276.15 | 98762 | 4.1 | 230 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/18 | 05:00:00 | 276.15 | 98762 | 3.6 | 220 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/18 | 06:00:00 | 277.15 | 98771 | 6.2 | 230 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
2/18 | 07:00:00 | 277.15 | 98771 | 4.1 | 240 | 4.8316 | 0 | 0 | 262.405 | 0 | 1
2/18 | 08:00:00 | 277.15 | 98771 | 6.7 | 230 | 4.8316 | 7.2 | 0 | 262.405 | 0 | 1
2/18 | 09:00:00 | 278.15 | 98780 | 7.2 | 230 | 5.1875 | 262.8 | 687.6 | 263.581 | 0 | 1
2/18 | 10:00:00 | 279.15 | 98789 | 5.1 | 240 | 5.187 | 356.4 | 46.8 | 264.996 | 0 | 1
2/18 | 11:00:00 | 281.15 | 98806 | 5.1 | 230 | 5.5656 | 968.4 | 1389.6 | 266.653 | 0 | 1
2/18 | 12:00:00 | 281.15 | 98806 | 5.1 | 240 | 5.5656 | 1173.6 | 1656 | 266.653 | 0 | 1
2/18 | 13:00:00 | 281.15 | 98806 | 6.7 | 240 | 5.5656 | 1227.6 | 1692 | 266.653 | 0 | 1
2/18 | 14:00:00 | 282.15 | 98815 | 5.1 | 240 | 5.9692 | 1123.2 | 1609.2 | 267.83 | 0 | 1
2/18 | 15:00:00 | 282.15 | 98815 | 6.7 | 220 | 5.9692 | 874.8 | 1580.4 | 267.83 | 0 | 1
2/18 | 16:00:00 | 282.15 | 98815 | 8.2 | 220 | 5.9692 | 525.6 | 860.4 | 267.83 | 0 | 1
2/18 | 17:00:00 | 281.15 | 98806 | 7.2 | 220 | 5.9698 | 86.4 | 0 | 267.353 | 0 | 1
2/18 | 18:00:00 | 281.15 | 98806 | 7.7 | 230 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
2/18 | 19:00:00 | 281.15 | 98806 | 6.7 | 220 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
2/18 | 20:00:00 | 280.15 | 98798 | 7.7 | 240 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
2/18 | 21:00:00 | 280.15 | 98798 | 8.2 | 230 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
2/18 | 22:00:00 | 279.15 | 98789 | 6.7 | 230 | 5.187 | 0 | 0 | 264.528 | 0 | 1
2/18 | 23:00:00 | 279.15 | 98789 | 4.1 | 260 | 5.187 | 0 | 0 | 264.528 | 0 | 1
2/18 | 24:00:00 | 279.15 | 98789 | 4.6 | 220 | 5.187 | 0 | 0 | 264.528 | 0 | 1
2/19 | 01:00:00 | 278.15 | 98780 | 6.2 | 210 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
2/19 | 02:00:00 | 279.15 | 98789 | 7.2 | 210 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
2/19 | 03:00:00 | 279.15 | 98789 | 11.3 | 220 | 4.4964 | 0 | 0 | 264.31 | 0 | 1
2/19 | 04:00:00 | 279.15 | 98789 | 11.8 | 220 | 4.8307 | 0 | 0 | 264.299 | 0 | 1
2/19 | 05:00:00 | 279.15 | 98789 | 9.3 | 220 | 5.187 | 0 | 0 | 264.996 | 0 | 1
2/19 | 06:00:00 | 279.15 | 98789 | 7.7 | 220 | 5.187 | 0 | 0 | 264.996 | 0 | 1
2/19 | 07:00:00 | 279.15 | 98789 | 7.7 | 210 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
2/19 | 08:00:00 | 279.15 | 98789 | 5.7 | 200 | 5.5666 | 7.2 | 0 | 265.224 | 0 | 1
2/19 | 09:00:00 | 279.15 | 98789 | 5.1 | 200 | 5.5666 | 154.8 | 0 | 265.224 | 0 | 1
2/19 | 10:00:00 | 279.15 | 98789 | 6.2 | 220 | 5.5666 | 367.2 | 21.6 | 265.224 | 0 | 1
2/19 | 11:00:00 | 279.15 | 98789 | 5.1 | 220 | 5.9708 | 547.2 | 219.6 | 265.451 | 0 | 1
2/19 | 12:00:00 | 278.15 | 98780 | 4.6 | 250 | 5.5671 | 1195.2 | 1551.6 | 263.807 | 0 | 1
2/19 | 13:00:00 | 278.15 | 98780 | 6.7 | 250 | 5.5671 | 1249.2 | 1958.4 | 263.807 | 0 | 1
2/19 | 14:00:00 | 278.15 | 98780 | 4.6 | 230 | 5.1875 | 1216.8 | 2163.6 | 263.323 | 0 | 1
2/19 | 15:00:00 | 279.15 | 98789 | 6.2 | 230 | 5.5666 | 896.4 | 1267.2 | 264.756 | 0 | 1
2/19 | 16:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.5666 | 298.8 | 18 | 265.224 | 0 | 1
2/19 | 17:00:00 | 278.15 | 98780 | 3.6 | 240 | 5.1875 | 165.6 | 349.2 | 263.581 | 0 | 1
2/19 | 18:00:00 | 277.15 | 98771 | 4.1 | 220 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
2/19 | 19:00:00 | 278.15 | 98780 | 6.2 | 230 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
2/19 | 20:00:00 | 277.15 | 98771 | 4.6 | 250 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
2/19 | 21:00:00 | 277.15 | 98771 | 2.6 | 250 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
2/19 | 22:00:00 | 276.15 | 98762 | 3.1 | 220 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
2/19 | 23:00:00 | 276.15 | 98762 | 1.5 | 250 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/19 | 24:00:00 | 276.15 | 98762 | 3.1 | 250 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/20 | 01:00:00 | 275.15 | 98752 | 2.1 | 250 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
2/20 | 02:00:00 | 275.15 | 98752 | 2.6 | 250 | 4.4981 | 0 | 0 | 260.03 | 0 | 1
2/20 | 03:00:00 | 275.15 | 98752 | 4.1 | 260 | 4.4981 | 0 | 0 | 260.03 | 0 | 1
2/20 | 04:00:00 | 275.15 | 98752 | 3.1 | 250 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
2/20 | 05:00:00 | 275.15 | 98752 | 3.1 | 230 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
2/20 | 06:00:00 | 275.15 | 98752 | 3.1 | 230 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
2/20 | 07:00:00 | 275.15 | 98752 | 5.1 | 250 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
2/20 | 08:00:00 | 275.15 | 98752 | 4.6 | 260 | 4.1846 | 21.6 | 0 | 260.056 | 0 | 1
2/20 | 09:00:00 | 275.15 | 98752 | 6.7 | 260 | 4.1846 | 295.2 | 547.2 | 260.056 | 0 | 1
2/20 | 10:00:00 | 276.15 | 98762 | 7.7 | 250 | 4.4977 | 723.6 | 1641.6 | 260.975 | 0 | 1
2/20 | 11:00:00 | 276.15 | 98762 | 5.7 | 250 | 4.4977 | 1015.2 | 1537.2 | 261.231 | 0 | 1
2/20 | 12:00:00 | 277.15 | 98771 | 7.2 | 260 | 4.4973 | 1220.4 | 1699.2 | 262.177 | 0 | 1
2/20 | 13:00:00 | 277.15 | 98771 | 8.2 | 260 | 4.4973 | 1278 | 1735.2 | 262.177 | 0 | 1
2/20 | 14:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.1834 | 1173.6 | 1461.6 | 262.891 | 0 | 1
2/20 | 15:00:00 | 278.15 | 98780 | 6.7 | 250 | 4.4968 | 921.6 | 1411.2 | 263.123 | 0 | 1
2/20 | 16:00:00 | 277.15 | 98771 | 7.2 | 260 | 4.1838 | 597.6 | 1242 | 261.69 | 0 | 1
2/20 | 17:00:00 | 277.15 | 98771 | 6.2 | 260 | 4.1838 | 190.8 | 241.2 | 261.69 | 0 | 1
2/20 | 18:00:00 | 276.15 | 98762 | 6.7 | 260 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
2/20 | 19:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
2/20 | 20:00:00 | 276.15 | 98762 | 4.1 | 250 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/20 | 21:00:00 | 275.15 | 98752 | 2.1 | 230 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
2/20 | 22:00:00 | 275.15 | 98752 | 3.6 | 250 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
2/20 | 23:00:00 | 275.15 | 98752 | 2.6 | 240 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
2/20 | 24:00:00 | 275.15 | 98752 | 3.1 | 260 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
2/21 | 01:00:00 | 275.15 | 98752 | 1.5 | 285 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
2/21 | 02:00:00 | 275.15 | 98752 | 4.6 | 270 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
2/21 | 03:00:00 | 275.15 | 98752 | 4.1 | 270 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
2/21 | 04:00:00 | 274.15 | 98743 | 4.1 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/21 | 05:00:00 | 274.15 | 98743 | 6.2 | 270 | 4.185 | 0 | 0 | 259.111 | 0 | 1
2/21 | 06:00:00 | 274.15 | 98743 | 4.1 | 280 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/21 | 07:00:00 | 274.15 | 98743 | 5.1 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/21 | 08:00:00 | 273.15 | 98734 | 5.7 | 270 | 3.891 | 32.4 | 0 | 257.685 | 0 | 1
2/21 | 09:00:00 | 274.15 | 98743 | 4.6 | 270 | 3.8907 | 327.6 | 712.8 | 258.628 | 0 | 1
2/21 | 10:00:00 | 275.15 | 98752 | 7.2 | 280 | 3.8903 | 745.2 | 1461.6 | 259.572 | 0 | 1
2/21 | 11:00:00 | 276.15 | 98762 | 6.7 | 280 | 4.1841 | 1098 | 2134.8 | 260.746 | 0 | 1
2/21 | 12:00:00 | 277.15 | 98771 | 9.3 | 280 | 4.1838 | 1245.6 | 1501.2 | 261.946 | 0 | 1
2/21 | 13:00:00 | 277.15 | 98771 | 7.7 | 280 | 3.8896 | 1303.2 | 1544.4 | 261.714 | 0 | 1
2/21 | 14:00:00 | 278.15 | 98780 | 6.2 | 300 | 3.5789 | 1198.8 | 1486.8 | 262.425 | 0 | 1
2/21 | 15:00:00 | 278.15 | 98780 | 5.7 | 290 | 3.8892 | 943.2 | 1692 | 262.659 | 0 | 1
2/21 | 16:00:00 | 278.15 | 98780 | 8.8 | 290 | 3.5789 | 579.6 | 993.6 | 262.425 | 0 | 1
2/21 | 17:00:00 | 276.15 | 98762 | 6.2 | 280 | 3.8899 | 190.8 | 205.2 | 260.77 | 0 | 1
2/21 | 18:00:00 | 275.15 | 98752 | 6.7 | 280 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
2/21 | 19:00:00 | 275.15 | 98752 | 6.7 | 280 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
2/21 | 20:00:00 | 275.15 | 98752 | 6.2 | 280 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
2/21 | 21:00:00 | 274.15 | 98743 | 5.1 | 260 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
2/21 | 22:00:00 | 274.15 | 98743 | 6.2 | 270 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
2/21 | 23:00:00 | 274.15 | 98743 | 6.2 | 270 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
2/21 | 24:00:00 | 274.15 | 98743 | 5.1 | 270 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
2/22 | 01:00:00 | 274.15 | 98743 | 6.2 | 270 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
2/22 | 02:00:00 | 275.15 | 98752 | 5.7 | 260 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
2/22 | 03:00:00 | 275.15 | 98752 | 4.6 | 250 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
2/22 | 04:00:00 | 275.15 | 98752 | 4.1 | 250 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
2/22 | 05:00:00 | 275.15 | 98752 | 3.1 | 262 | 4.3388 | 0 | 0 | 260.736 | 0 | 1
2/22 | 06:00:00 | 275.15 | 98752 | 2.1 | 190 | 4.4981 | 0 | 0 | 260.745 | 0 | 1
2/22 | 07:00:00 | 274.15 | 98743 | 5.7 | 240 | 4.185 | 0 | 0 | 259.111 | 0 | 1
2/22 | 08:00:00 | 274.15 | 98743 | 5.1 | 220 | 4.185 | 36 | 0 | 259.111 | 0 | 1
2/22 | 09:00:00 | 275.15 | 98752 | 4.1 | 210 | 3.8903 | 345.6 | 745.2 | 259.572 | 0 | 1
2/22 | 10:00:00 | 275.15 | 98752 | 3.6 | 210 | 3.8903 | 766.8 | 1486.8 | 259.572 | 0 | 1
2/22 | 11:00:00 | 276.15 | 98762 | 5.1 | 200 | 4.1841 | 1123.2 | 2152.8 | 260.746 | 0 | 1
2/22 | 12:00:00 | 276.15 | 98762 | 6.2 | 190 | 3.8899 | 1270.8 | 1573.2 | 260.77 | 0 | 1
2/22 | 13:00:00 | 276.15 | 98762 | 7.7 | 200 | 4.1841 | 734.4 | 90 | 261.463 | 0 | 1
2/22 | 14:00:00 | 275.15 | 98752 | 7.7 | 180 | 4.4981 | 673.2 | 136.8 | 260.745 | 0 | 1
2/22 | 15:00:00 | 274.15 | 98743 | 6.7 | 170 | 4.185 | 532.8 | 144 | 259.569 | 0 | 1
2/22 | 16:00:00 | 275.15 | 98752 | 7.7 | 180 | 4.4981 | 331.2 | 21.6 | 260.745 | 0 | 1
2/22 | 17:00:00 | 277.15 | 98771 | 7.2 | 200 | 4.8316 | 111.6 | 0 | 262.87 | 0 | 1
2/22 | 18:00:00 | 277.15 | 98771 | 6.7 | 210 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
2/22 | 19:00:00 | 278.15 | 98780 | 5.1 | 220 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
2/22 | 20:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.9708 | 0 | 0 | 264.982 | 0 | 1
2/22 | 21:00:00 | 280.15 | 98798 | 6.7 | 240 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
2/22 | 22:00:00 | 279.15 | 98789 | 9.8 | 260 | 5.187 | 0 | 0 | 264.528 | 0 | 1
2/22 | 23:00:00 | 278.15 | 98780 | 11.8 | 260 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
2/22 | 24:00:00 | 276.15 | 98762 | 12.4 | 260 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/23 | 01:00:00 | 276.15 | 98762 | 13.4 | 260 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
2/23 | 02:00:00 | 276.15 | 98762 | 9.3 | 260 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
2/23 | 03:00:00 | 275.15 | 98752 | 6.7 | 250 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
2/23 | 04:00:00 | 275.15 | 98752 | 3.6 | 351 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
2/23 | 05:00:00 | 275.15 | 98752 | 3.6 | 230 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
2/23 | 06:00:00 | 275.15 | 98752 | 5.1 | 210 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
2/23 | 07:00:00 | 275.15 | 98752 | 6.2 | 230 | 3.5799 | 0 | 0 | 260.054 | 0 | 1
2/23 | 08:00:00 | 275.15 | 98752 | 6.2 | 230 | 3.5799 | 43.2 | 0 | 259.594 | 0 | 1
2/23 | 09:00:00 | 275.15 | 98752 | 6.2 | 220 | 3.5799 | 342 | 637.2 | 259.594 | 0 | 1
2/23 | 10:00:00 | 276.15 | 98762 | 6.7 | 230 | 3.5796 | 745.2 | 1267.2 | 260.538 | 0 | 1
2/23 | 11:00:00 | 277.15 | 98771 | 9.3 | 230 | 3.5793 | 1083.6 | 1400.4 | 261.481 | 0 | 1
2/23 | 12:00:00 | 278.15 | 98780 | 7.7 | 230 | 3.2915 | 1296 | 1544.4 | 262.189 | 0 | 1
2/23 | 13:00:00 | 278.15 | 98780 | 10.3 | 240 | 3.2915 | 1350 | 1587.6 | 262.189 | 0 | 1
2/23 | 14:00:00 | 278.15 | 98780 | 11.3 | 240 | 3.2915 | 1242 | 1508.4 | 262.189 | 0 | 1
2/23 | 15:00:00 | 279.15 | 98789 | 10.3 | 230 | 3.2912 | 1044 | 2084.4 | 262.874 | 0 | 1
2/23 | 16:00:00 | 278.15 | 98780 | 9.3 | 230 | 3.2915 | 655.2 | 1242 | 261.933 | 0 | 1
2/23 | 17:00:00 | 278.15 | 98780 | 9.8 | 220 | 3.0253 | 230.4 | 475.2 | 261.696 | 0 | 1
2/23 | 18:00:00 | 277.15 | 98771 | 9.8 | 220 | 3.2918 | 0 | 0 | 260.991 | 0 | 1
2/23 | 19:00:00 | 276.15 | 98762 | 11.8 | 220 | 3.5796 | 0 | 0 | 260.283 | 0 | 1
2/23 | 20:00:00 | 276.15 | 98762 | 10.3 | 210 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/23 | 21:00:00 | 275.15 | 98752 | 8.2 | 220 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
2/23 | 22:00:00 | 276.15 | 98762 | 8.2 | 220 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/23 | 23:00:00 | 276.15 | 98762 | 7.7 | 230 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/23 | 24:00:00 | 276.15 | 98762 | 7.7 | 230 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/24 | 01:00:00 | 276.15 | 98762 | 7.2 | 240 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/24 | 02:00:00 | 275.15 | 98752 | 7.7 | 250 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
2/24 | 03:00:00 | 276.15 | 98762 | 9.8 | 260 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/24 | 04:00:00 | 276.15 | 98762 | 11.3 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/24 | 05:00:00 | 276.15 | 98762 | 11.8 | 270 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/24 | 06:00:00 | 276.15 | 98762 | 13.9 | 270 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/24 | 07:00:00 | 276.15 | 98762 | 9.8 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/24 | 08:00:00 | 276.15 | 98762 | 7.2 | 270 | 4.1841 | 50.4 | 0 | 261.001 | 0 | 1
2/24 | 09:00:00 | 277.15 | 98771 | 8.8 | 270 | 4.4973 | 356.4 | 766.8 | 262.177 | 0 | 1
2/24 | 10:00:00 | 277.15 | 98771 | 10.8 | 270 | 4.8316 | 759.6 | 1447.2 | 262.405 | 0 | 1
2/24 | 11:00:00 | 278.15 | 98780 | 11.8 | 280 | 4.4968 | 1098 | 1828.8 | 263.123 | 0 | 1
2/24 | 12:00:00 | 277.15 | 98771 | 8.2 | 260 | 4.8316 | 1306.8 | 1728 | 262.405 | 0 | 1
2/24 | 13:00:00 | 278.15 | 98780 | 11.3 | 270 | 4.1834 | 1364.4 | 1569.6 | 262.891 | 0 | 1
2/24 | 14:00:00 | 277.15 | 98771 | 11.8 | 260 | 4.4973 | 1256.4 | 1702.8 | 262.177 | 0 | 1
2/24 | 15:00:00 | 278.15 | 98780 | 9.8 | 260 | 4.1834 | 1000.8 | 1321.2 | 262.891 | 0 | 1
2/24 | 16:00:00 | 277.15 | 98771 | 9.8 | 260 | 4.1838 | 630 | 1108.8 | 261.946 | 0 | 1
2/24 | 17:00:00 | 277.15 | 98771 | 10.3 | 260 | 4.1838 | 230.4 | 255.6 | 261.946 | 0 | 1
2/24 | 18:00:00 | 277.15 | 98771 | 9.8 | 260 | 4.1838 | 0 | 0 | 261.946 | 0 | 1
2/24 | 19:00:00 | 276.15 | 98762 | 8.8 | 260 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
2/24 | 20:00:00 | 276.15 | 98762 | 7.7 | 260 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/24 | 21:00:00 | 276.15 | 98762 | 6.2 | 250 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/24 | 22:00:00 | 276.15 | 98762 | 3.1 | 230 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
2/24 | 23:00:00 | 277.15 | 98771 | 4.1 | 230 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
2/24 | 24:00:00 | 277.15 | 98771 | 4.6 | 220 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
2/25 | 01:00:00 | 276.15 | 98762 | 3.6 | 210 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/25 | 02:00:00 | 276.15 | 98762 | 3.1 | 220 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
2/25 | 03:00:00 | 276.15 | 98762 | 4.1 | 210 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
2/25 | 04:00:00 | 277.15 | 98771 | 2.6 | 220 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
2/25 | 05:00:00 | 278.15 | 98780 | 3.1 | 250 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
2/25 | 06:00:00 | 278.15 | 98780 | 3.6 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
2/25 | 07:00:00 | 278.15 | 98780 | 6.7 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
2/25 | 08:00:00 | 277.15 | 98771 | 4.1 | 280 | 5.1879 | 57.6 | 0 | 262.633 | 0 | 1
2/25 | 09:00:00 | 278.15 | 98780 | 5.1 | 260 | 5.1875 | 396 | 957.6 | 263.323 | 0 | 1
2/25 | 10:00:00 | 279.15 | 98789 | 3.6 | 260 | 5.5666 | 777.6 | 1436.4 | 264.756 | 0 | 1
2/25 | 11:00:00 | 280.15 | 98798 | 4.6 | 280 | 5.5661 | 1116 | 1821.6 | 265.704 | 0 | 1
2/25 | 12:00:00 | 281.15 | 98806 | 4.6 | 270 | 5.5656 | 1324.8 | 1728 | 266.653 | 0 | 1
2/25 | 13:00:00 | 281.15 | 98806 | 3.6 | 280 | 5.5656 | 1378.8 | 1771.2 | 266.653 | 0 | 1
2/25 | 14:00:00 | 281.15 | 98806 | 3.6 | 250 | 5.1861 | 1274.4 | 1702.8 | 266.423 | 0 | 1
2/25 | 15:00:00 | 281.15 | 98806 | 4.1 | 260 | 5.5656 | 1015.2 | 1724.4 | 266.653 | 0 | 1
2/25 | 16:00:00 | 281.15 | 98806 | 4.6 | 250 | 5.5656 | 644.4 | 1278 | 266.653 | 0 | 1
2/25 | 17:00:00 | 281.15 | 98806 | 2.6 | 250 | 5.5656 | 241.2 | 360 | 266.653 | 0 | 1
2/25 | 18:00:00 | 280.15 | 98798 | 2.1 | 200 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
2/25 | 19:00:00 | 280.15 | 98798 | 2.6 | 170 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
2/25 | 20:00:00 | 280.15 | 98798 | 2.6 | 160 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
2/25 | 21:00:00 | 280.15 | 98798 | 4.1 | 170 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
2/25 | 22:00:00 | 280.15 | 98798 | 3.6 | 180 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
2/25 | 23:00:00 | 281.15 | 98806 | 4.1 | 190 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
2/25 | 24:00:00 | 281.15 | 98806 | 4.6 | 220 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
2/26 | 01:00:00 | 282.15 | 98815 | 4.1 | 210 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
2/26 | 02:00:00 | 282.15 | 98815 | 4.6 | 210 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
2/26 | 03:00:00 | 282.15 | 98815 | 5.1 | 210 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
2/26 | 04:00:00 | 282.15 | 98815 | 5.7 | 210 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
2/26 | 05:00:00 | 282.15 | 98815 | 7.2 | 220 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
2/26 | 06:00:00 | 282.15 | 98815 | 6.2 | 210 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
2/26 | 07:00:00 | 283.15 | 98824 | 6.2 | 230 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
2/26 | 08:00:00 | 283.15 | 98824 | 7.7 | 230 | 7.3431 | 36 | 0 | 269.936 | 0 | 1
2/26 | 09:00:00 | 282.15 | 98815 | 5.7 | 230 | 7.3438 | 216 | 0 | 268.983 | 0 | 1
2/26 | 10:00:00 | 282.15 | 98815 | 8.8 | 270 | 6.8571 | 442.8 | 72 | 268.758 | 0 | 1
2/26 | 11:00:00 | 279.15 | 98789 | 10.3 | 280 | 5.5666 | 1137.6 | 1486.8 | 264.756 | 0 | 1
2/26 | 12:00:00 | 279.15 | 98789 | 9.8 | 280 | 5.187 | 1350 | 1749.6 | 264.528 | 0 | 1
2/26 | 13:00:00 | 280.15 | 98798 | 9.8 | 290 | 4.8303 | 1407.6 | 1807.2 | 265.246 | 0 | 1
2/26 | 14:00:00 | 279.15 | 98789 | 8.2 | 280 | 4.8307 | 1296 | 1717.2 | 264.299 | 0 | 1
2/26 | 15:00:00 | 279.15 | 98789 | 9.8 | 280 | 4.183 | 1040.4 | 1350 | 263.837 | 0 | 1
2/26 | 16:00:00 | 279.15 | 98789 | 10.8 | 280 | 3.8889 | 669.6 | 1159.2 | 263.603 | 0 | 1
2/26 | 17:00:00 | 277.15 | 98771 | 8.2 | 270 | 3.8896 | 259.2 | 295.2 | 261.714 | 0 | 1
2/26 | 18:00:00 | 277.15 | 98771 | 7.7 | 270 | 3.5793 | 0 | 0 | 261.481 | 0 | 1
2/26 | 19:00:00 | 276.15 | 98762 | 6.2 | 270 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
2/26 | 20:00:00 | 275.15 | 98752 | 3.6 | 250 | 3.5799 | 0 | 0 | 260.054 | 0 | 1
2/26 | 21:00:00 | 274.15 | 98743 | 4.1 | 270 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
2/26 | 22:00:00 | 275.15 | 98752 | 5.1 | 260 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
2/26 | 23:00:00 | 275.15 | 98752 | 5.7 | 260 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
2/26 | 24:00:00 | 275.15 | 98752 | 6.7 | 260 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
2/27 | 01:00:00 | 274.15 | 98743 | 5.1 | 260 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
2/27 | 02:00:00 | 274.15 | 98743 | 5.1 | 260 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
2/27 | 03:00:00 | 274.15 | 98743 | 5.7 | 270 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
2/27 | 04:00:00 | 274.15 | 98743 | 5.1 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/27 | 05:00:00 | 274.15 | 98743 | 7.2 | 260 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/27 | 06:00:00 | 274.15 | 98743 | 7.7 | 270 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
2/27 | 07:00:00 | 275.15 | 98752 | 7.7 | 270 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
2/27 | 08:00:00 | 275.15 | 98752 | 8.8 | 270 | 3.8903 | 79.2 | 43.2 | 259.572 | 0 | 1
2/27 | 09:00:00 | 275.15 | 98752 | 7.7 | 260 | 4.1846 | 410.4 | 759.6 | 260.056 | 0 | 1
2/27 | 10:00:00 | 277.15 | 98771 | 9.3 | 260 | 4.4973 | 824.4 | 1526.4 | 262.177 | 0 | 1
2/27 | 11:00:00 | 277.15 | 98771 | 8.2 | 260 | 4.1838 | 1166.4 | 1432.8 | 261.946 | 0 | 1
2/27 | 12:00:00 | 277.15 | 98771 | 7.2 | 260 | 4.1838 | 1378.8 | 1569.6 | 261.946 | 0 | 1
2/27 | 13:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.1834 | 1432.8 | 1609.2 | 262.891 | 0 | 1
2/27 | 14:00:00 | 278.15 | 98780 | 6.7 | 250 | 4.4968 | 1321.2 | 1738.8 | 263.123 | 0 | 1
2/27 | 15:00:00 | 279.15 | 98789 | 6.2 | 240 | 3.8889 | 1062 | 1368 | 263.603 | 0 | 1
2/27 | 16:00:00 | 279.15 | 98789 | 7.7 | 250 | 3.8889 | 727.2 | 1411.2 | 263.345 | 0 | 1
2/27 | 17:00:00 | 278.15 | 98780 | 4.6 | 240 | 3.8892 | 288 | 597.6 | 262.402 | 0 | 1
2/27 | 18:00:00 | 278.15 | 98780 | 3.1 | 220 | 4.1834 | 7.2 | 0 | 262.891 | 0 | 1
2/27 | 19:00:00 | 277.15 | 98771 | 3.6 | 200 | 3.8896 | 0 | 0 | 261.458 | 0 | 1
2/27 | 20:00:00 | 277.15 | 98771 | 3.6 | 200 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
2/27 | 21:00:00 | 277.15 | 98771 | 4.6 | 180 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
2/27 | 22:00:00 | 277.15 | 98771 | 5.7 | 210 | 4.1838 | 0 | 0 | 262.41 | 0 | 1
2/27 | 23:00:00 | 278.15 | 98780 | 5.7 | 210 | 4.1834 | 0 | 0 | 263.356 | 0 | 1
2/27 | 24:00:00 | 277.15 | 98771 | 6.2 | 200 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
2/28 | 01:00:00 | 278.15 | 98780 | 5.7 | 220 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
2/28 | 02:00:00 | 278.15 | 98780 | 4.6 | 210 | 4.4968 | 0 | 0 | 262.445 | 0 | 1
2/28 | 03:00:00 | 278.15 | 98780 | 3.6 | 210 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
2/28 | 04:00:00 | 278.15 | 98780 | 4.6 | 220 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
2/28 | 05:00:00 | 278.15 | 98780 | 3.6 | 200 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
2/28 | 06:00:00 | 278.15 | 98780 | 3.6 | 200 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
2/28 | 07:00:00 | 279.15 | 98789 | 4.1 | 210 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
2/28 | 08:00:00 | 278.15 | 98780 | 2.1 | 170 | 5.1875 | 79.2 | 18 | 263.581 | 0 | 1
2/28 | 09:00:00 | 280.15 | 98798 | 3.6 | 210 | 5.9703 | 428.4 | 878.4 | 265.931 | 0 | 1
2/28 | 10:00:00 | 280.15 | 98798 | 4.6 | 220 | 5.9703 | 838.8 | 1512 | 265.931 | 0 | 1
2/28 | 11:00:00 | 281.15 | 98806 | 5.7 | 220 | 5.9698 | 1180.8 | 1850.4 | 266.881 | 0 | 1
2/28 | 12:00:00 | 281.15 | 98806 | 4.6 | 220 | 5.9698 | 1389.6 | 1756.8 | 266.881 | 0 | 1
2/28 | 13:00:00 | 282.15 | 98815 | 6.2 | 230 | 5.5651 | 1443.6 | 1810.8 | 267.601 | 0 | 1
2/28 | 14:00:00 | 282.15 | 98815 | 4.6 | 230 | 5.9692 | 1332 | 1710 | 267.83 | 0 | 1
2/28 | 15:00:00 | 282.15 | 98815 | 3.6 | 210 | 5.9692 | 1072.8 | 1756.8 | 267.83 | 0 | 1
2/28 | 16:00:00 | 281.15 | 98806 | 4.6 | 200 | 5.9698 | 698.4 | 1332 | 266.881 | 0 | 1
2/28 | 17:00:00 | 281.15 | 98806 | 7.2 | 200 | 5.5656 | 284.4 | 424.8 | 266.653 | 0 | 1
2/28 | 18:00:00 | 281.15 | 98806 | 7.2 | 200 | 5.5656 | 7.2 | 0 | 267.125 | 0 | 1
2/28 | 19:00:00 | 280.65 | 98802 | 7.1 | 202 | 5.8872 | 0 | 0 | 266.832 | 0 | 1
2/28 | 20:00:00 | 281.15 | 98806 | 8.3 | 217 | 6.0537 | 0 | 0 | 267.398 | 0 | 1
2/28 | 21:00:00 | 281.35 | 98808 | 9.4 | 230 | 6.0536 | 0 | 0 | 267.589 | 0 | 1
2/28 | 22:00:00 | 279.65 | 98793 | 8.2 | 245 | 5.3736 | 0 | 0 | 265.116 | 0 | 1
2/28 | 23:00:00 | 277.95 | 98777 | 7.2 | 260 | 4.6615 | 0 | 0 | 263.048 | 0 | 1
2/28 | 24:00:00 | 275.95 | 98759 | 5.2 | 272 | 4.035 | 0 | 0 | 260.697 | 0 | 1
3/1 | 01:00:00 | 274.15 | 98743 | 3.5 | 282 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
3/1 | 02:00:00 | 274.15 | 98743 | 3.7 | 290 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
3/1 | 03:00:00 | 274.15 | 98743 | 3.7 | 285 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
3/1 | 04:00:00 | 274.15 | 98743 | 3.5 | 277 | 3.6405 | 0 | 0 | 259.155 | 0 | 1
3/1 | 05:00:00 | 274.15 | 98743 | 3.1 | 275 | 3.7325 | 0 | 0 | 259.224 | 0 | 1
3/1 | 06:00:00 | 274.15 | 98743 | 2.7 | 270 | 3.8267 | 0 | 0 | 259.293 | 0 | 1
3/1 | 07:00:00 | 274.15 | 98743 | 2.6 | 270 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
3/1 | 08:00:00 | 274.15 | 98743 | 2.6 | 280 | 3.8907 | 90 | 25.2 | 258.882 | 0 | 1
3/1 | 09:00:00 | 274.15 | 98743 | 2.6 | 270 | 3.8907 | 450 | 763.2 | 258.882 | 0 | 1
3/1 | 10:00:00 | 275.15 | 98752 | 4.1 | 270 | 3.8903 | 921.6 | 1641.6 | 259.572 | 0 | 1
3/1 | 11:00:00 | 277.15 | 98771 | 4.1 | 290 | 3.8896 | 1288.8 | 2314.8 | 261.458 | 0 | 1
3/1 | 12:00:00 | 278.15 | 98780 | 4.1 | 270 | 3.8892 | 1425.6 | 1605.6 | 262.659 | 0 | 1
3/1 | 13:00:00 | 278.15 | 98780 | 4.6 | 260 | 3.5789 | 1479.6 | 1648.8 | 262.425 | 0 | 1
3/1 | 14:00:00 | 277.15 | 98771 | 4.1 | 300 | 3.5793 | 1368 | 1569.6 | 261.481 | 0 | 1
3/1 | 15:00:00 | 277.15 | 98771 | 4.1 | 290 | 3.5793 | 1105.2 | 1393.2 | 261.481 | 0 | 1
3/1 | 16:00:00 | 277.15 | 98771 | 2.6 | 310 | 3.8896 | 723.6 | 1209.6 | 261.714 | 0 | 1
3/1 | 17:00:00 | 278.15 | 98780 | 4.1 | 260 | 4.4968 | 298.8 | 453.6 | 263.123 | 0 | 1
3/1 | 18:00:00 | 277.15 | 98771 | 3.6 | 260 | 3.8896 | 21.6 | 0 | 261.458 | 0 | 1
3/1 | 19:00:00 | 275.15 | 98752 | 2.1 | 270 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
3/1 | 20:00:00 | 275.15 | 98752 | 3.6 | 280 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
3/1 | 21:00:00 | 273.15 | 98734 | 3.6 | 290 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
3/1 | 22:00:00 | 274.15 | 98743 | 4.1 | 290 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
3/1 | 23:00:00 | 273.15 | 98734 | 3.6 | 300 | 3.6713 | 0 | 0 | 258.337 | 0 | 1
3/1 | 24:00:00 | 273.35 | 98735 | 3.2 | 37 | 3.764 | 0 | 0 | 258.596 | 0 | 1
3/2 | 01:00:00 | 273.45 | 98737 | 2.9 | 104 | 3.8588 | 0 | 0 | 258.759 | 0 | 1
3/2 | 02:00:00 | 273.65 | 98739 | 2.5 | 316 | 3.9198 | 0 | 0 | 258.994 | 0 | 1
3/2 | 03:00:00 | 273.85 | 98740 | 2.2 | 274 | 4.0065 | 0 | 0 | 259.253 | 0 | 1
3/2 | 04:00:00 | 273.95 | 98742 | 1.9 | 108 | 4.0948 | 0 | 0 | 259.416 | 0 | 1
3/2 | 05:00:00 | 274.15 | 98743 | 1.5 | 350 | 4.185 | 0 | 0 | 259.569 | 0 | 1
3/2 | 06:00:00 | 273.15 | 98734 | 2.1 | 30 | 3.891 | 0 | 0 | 258.394 | 0 | 1
3/2 | 07:00:00 | 273.15 | 98734 | 2.1 | 10 | 3.891 | 0 | 0 | 258.394 | 0 | 1
3/2 | 08:00:00 | 273.15 | 98734 | 1.5 | 102 | 3.891 | 97.2 | 39.6 | 257.937 | 0 | 1
3/2 | 09:00:00 | 273.15 | 98734 | 1.5 | 310 | 3.891 | 496.8 | 1022.4 | 257.685 | 0 | 1
3/2 | 10:00:00 | 274.15 | 98743 | 1 | 131 | 3.5803 | 946.8 | 1670.4 | 258.398 | 0 | 1
3/2 | 11:00:00 | 275.15 | 98752 | 1.5 | 176 | 3.5799 | 1314 | 2343.6 | 259.34 | 0 | 1
3/2 | 12:00:00 | 277.15 | 98771 | 2.1 | 30 | 4.8316 | 1530 | 2545.2 | 262.149 | 0 | 1
3/2 | 13:00:00 | 277.15 | 98771 | 1.5 | 47 | 3.0256 | 1598.4 | 2660.4 | 260.755 | 0 | 1
3/2 | 14:00:00 | 278.15 | 98780 | 1 | 251 | 2.7791 | 1483.2 | 2566.8 | 261.457 | 0 | 1
3/2 | 15:00:00 | 278.15 | 98780 | 0.5 | 237 | 2.7791 | 1209.6 | 2289.6 | 261.323 | 0 | 1
3/2 | 16:00:00 | 278.15 | 98780 | 1.5 | 25 | 2.7791 | 795.6 | 1530 | 261.323 | 0 | 1
3/2 | 17:00:00 | 277.15 | 98771 | 1.5 | 238 | 2.7793 | 334.8 | 698.4 | 260.517 | 0 | 1
3/2 | 18:00:00 | 276.15 | 98762 | 1.5 | 90 | 3.0259 | 25.2 | 0 | 260.068 | 0 | 1
3/2 | 19:00:00 | 275.15 | 98752 | 1 | 80 | 3.0262 | 0 | 0 | 259.127 | 0 | 1
3/2 | 20:00:00 | 275.15 | 98752 | 1 | 130 | 2.7799 | 0 | 0 | 258.766 | 0 | 1
3/2 | 21:00:00 | 275.15 | 98752 | 1 | 80 | 3.0262 | 0 | 0 | 259.127 | 0 | 1
3/2 | 22:00:00 | 275.15 | 98752 | 0.5 | 110 | 2.7799 | 0 | 0 | 258.766 | 0 | 1
3/2 | 23:00:00 | 273.15 | 98734 | 1 | 114 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
3/2 | 24:00:00 | 272.95 | 98732 | 1.1 | 32 | 2.8282 | 0 | 0 | 256.987 | 0 | 1
3/3 | 01:00:00 | 272.85 | 98731 | 1.2 | 240 | 2.8524 | 0 | 0 | 257.032 | 0 | 1
3/3 | 02:00:00 | 272.65 | 98729 | 1.2 | 203 | 2.9013 | 0 | 0 | 256.89 | 0 | 1
3/3 | 03:00:00 | 272.45 | 98728 | 1.3 | 284 | 2.951 | 0 | 0 | 256.748 | 0 | 1
3/3 | 04:00:00 | 272.35 | 98726 | 1.4 | 348 | 2.9762 | 0 | 0 | 256.789 | 0 | 1
3/3 | 05:00:00 | 272.15 | 98724 | 1.5 | 120 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/3 | 06:00:00 | 272.15 | 98724 | 0 | 192 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/3 | 07:00:00 | 272.15 | 98724 | 0 | 285 | 2.7806 | 0 | 0 | 255.817 | 0 | 1
3/3 | 08:00:00 | 272.15 | 98724 | 0 | 188 | 3.0271 | 108 | 75.6 | 256.051 | 0 | 1
3/3 | 09:00:00 | 272.15 | 98724 | 0 | 142 | 3.0271 | 342 | 136.8 | 256.647 | 0 | 1
3/3 | 10:00:00 | 273.15 | 98734 | 0 | 303 | 3.0267 | 777.6 | 612 | 257.478 | 0 | 1
3/3 | 11:00:00 | 275.15 | 98752 | 1.5 | 264 | 3.2924 | 1170 | 1245.6 | 259.482 | 0 | 1
3/3 | 12:00:00 | 276.15 | 98762 | 2.6 | 130 | 3.5796 | 1342.8 | 1267.2 | 260.659 | 0 | 1
3/3 | 13:00:00 | 276.15 | 98762 | 2.6 | 150 | 3.5796 | 1620 | 2336.4 | 260.283 | 0 | 1
3/3 | 14:00:00 | 276.15 | 98762 | 3.6 | 120 | 3.5796 | 1497.6 | 2548.8 | 260.283 | 0 | 1
3/3 | 15:00:00 | 276.15 | 98762 | 2.1 | 110 | 3.5796 | 1216.8 | 2224.8 | 260.283 | 0 | 1
3/3 | 16:00:00 | 276.15 | 98762 | 2.6 | 120 | 3.8899 | 806.4 | 1490.4 | 260.515 | 0 | 1
3/3 | 17:00:00 | 276.15 | 98762 | 3.1 | 90 | 3.8899 | 349.2 | 712.8 | 260.515 | 0 | 1
3/3 | 18:00:00 | 275.15 | 98752 | 2.1 | 90 | 3.8903 | 32.4 | 0 | 259.572 | 0 | 1
3/3 | 19:00:00 | 275.15 | 98752 | 2.6 | 80 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
3/3 | 20:00:00 | 274.15 | 98743 | 3.1 | 90 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
3/3 | 21:00:00 | 274.15 | 98743 | 3.6 | 90 | 3.5803 | 0 | 0 | 259 | 0 | 1
3/3 | 22:00:00 | 273.15 | 98734 | 0 | 272 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
3/3 | 23:00:00 | 273.15 | 98734 | 2.1 | 60 | 3.891 | 0 | 0 | 258.394 | 0 | 1
3/3 | 24:00:00 | 273.15 | 98734 | 1.8 | 233 | 3.827 | 0 | 0 | 258.452 | 0 | 1
3/4 | 01:00:00 | 273.15 | 98734 | 1.4 | 276 | 3.7954 | 0 | 0 | 258.429 | 0 | 1
3/4 | 02:00:00 | 273.15 | 98734 | 1 | 105 | 3.7329 | 0 | 0 | 258.383 | 0 | 1
3/4 | 03:00:00 | 273.15 | 98734 | 0.7 | 270 | 3.6713 | 0 | 0 | 258.337 | 0 | 1
3/4 | 04:00:00 | 273.15 | 98734 | 0.3 | 211 | 3.6408 | 0 | 0 | 258.314 | 0 | 1
3/4 | 05:00:00 | 273.15 | 98734 | 0 | 106 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
3/4 | 06:00:00 | 273.15 | 98734 | 0 | 340 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
3/4 | 07:00:00 | 273.15 | 98734 | 2.1 | 40 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
3/4 | 08:00:00 | 273.15 | 98734 | 1.5 | 146 | 3.5806 | 61.2 | 0 | 258.163 | 0 | 1
3/4 | 09:00:00 | 273.15 | 98734 | 1.5 | 20 | 3.5806 | 536.4 | 1090.8 | 257.455 | 0 | 1
3/4 | 10:00:00 | 275.15 | 98752 | 1 | 190 | 3.5799 | 993.6 | 1710 | 259.34 | 0 | 1
3/4 | 11:00:00 | 276.15 | 98762 | 2.1 | 90 | 3.5796 | 1360.8 | 2383.2 | 260.283 | 0 | 1
3/4 | 12:00:00 | 277.15 | 98771 | 1.5 | 16 | 3.5793 | 1587.6 | 2624.4 | 261.225 | 0 | 1
3/4 | 13:00:00 | 277.15 | 98771 | 0 | 36 | 3.5793 | 1641.6 | 2667.6 | 261.225 | 0 | 1
3/4 | 14:00:00 | 277.15 | 98771 | 0 | 81 | 3.2918 | 1522.8 | 2574 | 260.991 | 0 | 1
3/4 | 15:00:00 | 278.15 | 98780 | 1 | 2 | 3.5789 | 1238.4 | 2246.4 | 262.168 | 0 | 1
3/4 | 16:00:00 | 278.15 | 98780 | 1 | 287 | 3.2915 | 828 | 1522.8 | 261.933 | 0 | 1
3/4 | 17:00:00 | 278.15 | 98780 | 1 | 311 | 3.2915 | 363.6 | 748.8 | 261.933 | 0 | 1
3/4 | 18:00:00 | 277.15 | 98771 | 0.5 | 80 | 3.5793 | 36 | 0 | 261.603 | 0 | 1
3/4 | 19:00:00 | 276.15 | 98762 | 0.5 | 70 | 3.2921 | 0 | 0 | 260.304 | 0 | 1
3/4 | 20:00:00 | 276.15 | 98762 | 0.5 | 339 | 3.0259 | 0 | 0 | 260.068 | 0 | 1
3/4 | 21:00:00 | 275.15 | 98752 | 2.1 | 260 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
3/4 | 22:00:00 | 273.15 | 98734 | 2.6 | 280 | 3.293 | 0 | 0 | 257.823 | 0 | 1
3/4 | 23:00:00 | 272.15 | 98724 | 3.1 | 280 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/4 | 24:00:00 | 272.15 | 98724 | 3.3 | 188 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/5 | 01:00:00 | 272.15 | 98724 | 3.4 | 282 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/5 | 02:00:00 | 272.15 | 98724 | 3.6 | 333 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/5 | 03:00:00 | 272.15 | 98724 | 3.8 | 136 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/5 | 04:00:00 | 272.15 | 98724 | 3.9 | 321 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/5 | 05:00:00 | 272.15 | 98724 | 4.1 | 290 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/5 | 06:00:00 | 272.15 | 98724 | 4.1 | 290 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/5 | 07:00:00 | 272.15 | 98724 | 4.1 | 290 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/5 | 08:00:00 | 272.15 | 98724 | 4.6 | 290 | 3.0271 | 86.4 | 0 | 256.647 | 0 | 1
3/5 | 09:00:00 | 273.15 | 98734 | 4.6 | 270 | 3.293 | 367.2 | 151.2 | 257.823 | 0 | 1
3/5 | 10:00:00 | 274.15 | 98743 | 4.1 | 260 | 3.5803 | 644.4 | 273.6 | 259 | 0 | 1
3/5 | 11:00:00 | 276.15 | 98762 | 5.7 | 270 | 3.5796 | 1191.6 | 1195.2 | 260.659 | 0 | 1
3/5 | 12:00:00 | 278.15 | 98780 | 5.7 | 280 | 3.5789 | 1540.8 | 2041.2 | 262.425 | 0 | 1
3/5 | 13:00:00 | 279.15 | 98789 | 8.2 | 290 | 3.8889 | 1580.4 | 2239.2 | 263.603 | 0 | 1
3/5 | 14:00:00 | 279.15 | 98789 | 9.3 | 290 | 4.183 | 1396.8 | 1479.6 | 263.959 | 0 | 1
3/5 | 15:00:00 | 279.15 | 98789 | 8.7 | 300 | 4.183 | 1252.8 | 2095.2 | 263.578 | 0 | 1
3/5 | 16:00:00 | 279.15 | 98789 | 8.2 | 300 | 4.4964 | 842.4 | 1738.8 | 263.81 | 0 | 1
3/5 | 17:00:00 | 279.15 | 98789 | 7.7 | 280 | 4.4964 | 378 | 860.4 | 263.81 | 0 | 1
3/5 | 18:00:00 | 278.15 | 98780 | 6.2 | 270 | 4.8311 | 28.8 | 0 | 263.818 | 0 | 1
3/5 | 19:00:00 | 277.15 | 98771 | 5.1 | 280 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
3/5 | 20:00:00 | 277.15 | 98771 | 6.7 | 300 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/5 | 21:00:00 | 278.15 | 98780 | 7.7 | 300 | 4.1834 | 0 | 0 | 262.634 | 0 | 1
3/5 | 22:00:00 | 277.15 | 98771 | 8.2 | 310 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
3/5 | 23:00:00 | 278.15 | 98780 | 8.2 | 320 | 4.1834 | 0 | 0 | 262.634 | 0 | 1
3/5 | 24:00:00 | 277.95 | 98778 | 7.7 | 90 | 4.1835 | 0 | 0 | 262.943 | 0 | 1
3/6 | 01:00:00 | 277.85 | 98777 | 7.2 | 227 | 4.1835 | 0 | 0 | 262.848 | 0 | 1
3/6 | 02:00:00 | 277.65 | 98775 | 6.7 | 359 | 4.1836 | 0 | 0 | 262.659 | 0 | 1
3/6 | 03:00:00 | 277.45 | 98774 | 6.1 | 62 | 4.1836 | 0 | 0 | 262.47 | 0 | 1
3/6 | 04:00:00 | 277.35 | 98772 | 5.6 | 105 | 4.1837 | 0 | 0 | 262.375 | 0 | 1
3/6 | 05:00:00 | 277.15 | 98771 | 5.1 | 320 | 4.1838 | 0 | 0 | 261.946 | 0 | 1
3/6 | 06:00:00 | 277.15 | 98771 | 5.1 | 330 | 4.1838 | 0 | 0 | 262.41 | 0 | 1
3/6 | 07:00:00 | 277.15 | 98771 | 3.6 | 320 | 4.1838 | 0 | 0 | 262.41 | 0 | 1
3/6 | 08:00:00 | 277.15 | 98771 | 2.6 | 310 | 4.4973 | 75.6 | 0 | 262.64 | 0 | 1
3/6 | 09:00:00 | 277.15 | 98771 | 2.1 | 350 | 4.4973 | 302.4 | 7.2 | 262.64 | 0 | 1
3/6 | 10:00:00 | 276.15 | 98762 | 2.1 | 60 | 4.832 | 540 | 50.4 | 261.921 | 0 | 1
3/6 | 11:00:00 | 276.15 | 98762 | 2.1 | 120 | 4.832 | 734.4 | 140.4 | 261.921 | 0 | 1
3/6 | 12:00:00 | 275.15 | 98752 | 2.6 | 130 | 4.4981 | 849.6 | 158.4 | 260.745 | 0 | 1
3/6 | 13:00:00 | 275.15 | 98752 | 2.1 | 110 | 4.4981 | 878.4 | 162 | 260.745 | 0 | 1
3/6 | 14:00:00 | 276.15 | 98762 | 2.1 | 130 | 4.4977 | 813.6 | 154.8 | 261.693 | 0 | 1
3/6 | 15:00:00 | 276.15 | 98762 | 2.1 | 130 | 4.4977 | 666 | 129.6 | 261.693 | 0 | 1
3/6 | 16:00:00 | 276.15 | 98762 | 1 | 139 | 4.4977 | 450 | 32.4 | 261.693 | 0 | 1
3/6 | 17:00:00 | 276.15 | 98762 | 4.1 | 100 | 3.8899 | 205.2 | 0 | 261.231 | 0 | 1
3/6 | 18:00:00 | 276.15 | 98762 | 3.1 | 110 | 3.5796 | 28.8 | 0 | 260.999 | 0 | 1
3/6 | 19:00:00 | 275.15 | 98752 | 2.1 | 110 | 3.2924 | 0 | 0 | 259.107 | 0 | 1
3/6 | 20:00:00 | 274.15 | 98743 | 3.1 | 110 | 3.2927 | 0 | 0 | 258.166 | 0 | 1
3/6 | 21:00:00 | 273.15 | 98734 | 3.1 | 130 | 3.0267 | 0 | 0 | 256.991 | 0 | 1
3/6 | 22:00:00 | 272.15 | 98724 | 2.6 | 130 | 3.0271 | 0 | 0 | 256.051 | 0 | 1
3/6 | 23:00:00 | 270.15 | 98705 | 0 | 214 | 2.7812 | 0 | 0 | 253.937 | 0 | 1
3/6 | 24:00:00 | 269.95 | 98704 | 0 | 329 | 2.7342 | 0 | 0 | 254.401 | 0 | 1
3/7 | 01:00:00 | 269.85 | 98702 | 0 | 358 | 2.711 | 0 | 0 | 254.283 | 0 | 1
3/7 | 02:00:00 | 269.65 | 98701 | 0 | 70 | 2.6651 | 0 | 0 | 254.048 | 0 | 1
3/7 | 03:00:00 | 269.45 | 98699 | 0 | 299 | 2.6199 | 0 | 0 | 253.813 | 0 | 1
3/7 | 04:00:00 | 269.35 | 98697 | 0 | 337 | 2.5976 | 0 | 0 | 253.695 | 0 | 1
3/7 | 05:00:00 | 269.15 | 98696 | 0 | 277 | 2.5535 | 0 | 0 | 253.46 | 0 | 1
3/7 | 06:00:00 | 269.15 | 98696 | 0 | 270 | 2.3427 | 0 | 0 | 253.12 | 0 | 1
3/7 | 07:00:00 | 269.15 | 98696 | 0 | 46 | 2.5535 | 0 | 0 | 253.46 | 0 | 1
3/7 | 08:00:00 | 268.15 | 98686 | 0 | 65 | 2.343 | 72 | 0 | 252.285 | 0 | 1
3/7 | 09:00:00 | 270.15 | 98705 | 0 | 239 | 2.5532 | 410.4 | 234 | 254.295 | 0 | 1
3/7 | 10:00:00 | 272.15 | 98724 | 0 | 273 | 2.5527 | 957.6 | 1195.2 | 255.952 | 0 | 1
3/7 | 11:00:00 | 273.15 | 98734 | 1 | 5 | 2.7804 | 1274.4 | 1263.6 | 257.128 | 0 | 1
3/7 | 12:00:00 | 274.15 | 98743 | 0.5 | 39 | 3.0265 | 1472.4 | 1342.8 | 258.305 | 0 | 1
3/7 | 13:00:00 | 275.15 | 98752 | 0.5 | 210 | 3.0262 | 1605.6 | 1785.6 | 259.127 | 0 | 1
3/7 | 14:00:00 | 276.15 | 98762 | 1 | 40 | 3.8899 | 1180.8 | 824.4 | 261.122 | 0 | 1
3/7 | 15:00:00 | 276.15 | 98762 | 0 | 126 | 2.7796 | 1292.4 | 1886.4 | 259.706 | 0 | 1
3/7 | 16:00:00 | 277.15 | 98771 | 0 | 358 | 2.7793 | 889.2 | 1594.8 | 260.517 | 0 | 1
3/7 | 17:00:00 | 277.15 | 98771 | 0 | 11 | 2.7793 | 414 | 795.6 | 260.517 | 0 | 1
3/7 | 18:00:00 | 276.15 | 98762 | 0 | 48 | 2.7796 | 57.6 | 0 | 259.706 | 0 | 1
3/7 | 19:00:00 | 274.15 | 98743 | 0.5 | 220 | 3.5803 | 0 | 0 | 259 | 0 | 1
3/7 | 20:00:00 | 273.15 | 98734 | 0 | 144 | 2.5525 | 0 | 0 | 256.773 | 0 | 1
3/7 | 21:00:00 | 272.15 | 98724 | 0 | 217 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
3/7 | 22:00:00 | 272.15 | 98724 | 0 | 313 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
3/7 | 23:00:00 | 272.15 | 98724 | 0 | 255 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
3/7 | 24:00:00 | 271.65 | 98720 | 0.2 | 165 | 2.9512 | 0 | 0 | 256.106 | 0 | 1
3/8 | 01:00:00 | 271.15 | 98715 | 0.3 | 243 | 2.8528 | 0 | 0 | 255.648 | 0 | 1
3/8 | 02:00:00 | 270.65 | 98710 | 0.5 | 322 | 2.781 | 0 | 0 | 255.107 | 0 | 1
3/8 | 03:00:00 | 270.15 | 98705 | 0.7 | 295 | 2.7109 | 0 | 0 | 254.566 | 0 | 1
3/8 | 04:00:00 | 269.65 | 98701 | 0.8 | 345 | 2.6199 | 0 | 0 | 254.001 | 0 | 1
3/8 | 05:00:00 | 269.15 | 98696 | 1 | 320 | 2.5535 | 0 | 0 | 253.46 | 0 | 1
3/8 | 06:00:00 | 269.15 | 98696 | 1 | 300 | 2.7814 | 0 | 0 | 253.796 | 0 | 1
3/8 | 07:00:00 | 268.15 | 98686 | 1 | 310 | 2.5537 | 0 | 0 | 252.621 | 0 | 1
3/8 | 08:00:00 | 270.15 | 98705 | 1 | 355 | 2.7812 | 79.2 | 0 | 254.636 | 0 | 1
3/8 | 09:00:00 | 272.15 | 98724 | 0.5 | 310 | 3.581 | 198 | 0 | 257.322 | 0 | 1
3/8 | 10:00:00 | 274.15 | 98743 | 0.5 | 289 | 4.185 | 345.6 | 0 | 259.674 | 0 | 1
3/8 | 11:00:00 | 275.15 | 98752 | 1.5 | 166 | 4.4981 | 464.4 | 0 | 260.851 | 0 | 1
3/8 | 12:00:00 | 276.15 | 98762 | 2.1 | 20 | 2.7796 | 1674 | 2048.4 | 259.706 | 0 | 1
3/8 | 13:00:00 | 277.15 | 98771 | 2.1 | 70 | 2.7793 | 1746 | 2761.2 | 260.517 | 0 | 1
3/8 | 14:00:00 | 278.15 | 98780 | 2.1 | 40 | 2.7791 | 1634.4 | 2714.4 | 261.323 | 0 | 1
3/8 | 15:00:00 | 278.15 | 98780 | 2.6 | 60 | 2.3407 | 1350 | 2466 | 260.703 | 0 | 1
3/8 | 16:00:00 | 279.15 | 98789 | 3.1 | 50 | 2.551 | 921.6 | 1684.8 | 261.882 | 0 | 1
3/8 | 17:00:00 | 279.15 | 98789 | 2.6 | 40 | 2.551 | 435.6 | 867.6 | 261.882 | 0 | 1
3/8 | 18:00:00 | 279.15 | 98789 | 2.1 | 70 | 2.7788 | 68.4 | 0 | 262.262 | 0 | 1
3/8 | 19:00:00 | 277.15 | 98771 | 2.1 | 50 | 3.0256 | 0 | 0 | 261.472 | 0 | 1
3/8 | 20:00:00 | 276.15 | 98762 | 2.1 | 40 | 3.0259 | 0 | 0 | 260.068 | 0 | 1
3/8 | 21:00:00 | 275.15 | 98752 | 2.6 | 10 | 2.7799 | 0 | 0 | 258.766 | 0 | 1
3/8 | 22:00:00 | 275.15 | 98752 | 2.6 | 10 | 2.7799 | 0 | 0 | 258.766 | 0 | 1
3/8 | 23:00:00 | 275.15 | 98752 | 2.6 | 360 | 3.0262 | 0 | 0 | 259.69 | 0 | 1
3/8 | 24:00:00 | 275.15 | 98752 | 2.6 | 101 | 3.2375 | 0 | 0 | 259.435 | 0 | 1
3/9 | 01:00:00 | 275.15 | 98752 | 2.6 | 263 | 3.4914 | 0 | 0 | 259.762 | 0 | 1
3/9 | 02:00:00 | 275.15 | 98752 | 2.6 | 48 | 3.7322 | 0 | 0 | 260.061 | 0 | 1
3/9 | 03:00:00 | 275.15 | 98752 | 2.6 | 86 | 3.9769 | 0 | 0 | 260.355 | 0 | 1
3/9 | 04:00:00 | 275.15 | 98752 | 2.6 | 175 | 4.2457 | 0 | 0 | 260.668 | 0 | 1
3/9 | 05:00:00 | 275.15 | 98752 | 2.6 | 10 | 4.4981 | 0 | 0 | 260.285 | 0 | 1
3/9 | 06:00:00 | 275.15 | 98752 | 3.1 | 360 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
3/9 | 07:00:00 | 275.15 | 98752 | 2.6 | 10 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
3/9 | 08:00:00 | 274.15 | 98743 | 2.1 | 10 | 4.185 | 187.2 | 205.2 | 258.857 | 0 | 1
3/9 | 09:00:00 | 276.15 | 98762 | 3.1 | 20 | 4.1841 | 644.4 | 1148.4 | 260.746 | 0 | 1
3/9 | 10:00:00 | 277.15 | 98771 | 2.6 | 20 | 4.1838 | 1108.8 | 1944 | 261.69 | 0 | 1
3/9 | 11:00:00 | 278.15 | 98780 | 2.1 | 20 | 3.8892 | 1483.2 | 2466 | 262.402 | 0 | 1
3/9 | 12:00:00 | 279.15 | 98789 | 3.1 | 10 | 3.5786 | 1710 | 2109.6 | 263.11 | 0 | 1
3/9 | 13:00:00 | 279.15 | 98789 | 4.1 | 30 | 4.183 | 918 | 583.2 | 264.303 | 0 | 1
3/9 | 14:00:00 | 280.15 | 98798 | 3.6 | 20 | 4.8303 | 1627.2 | 1825.2 | 264.986 | 0 | 1
3/9 | 15:00:00 | 279.15 | 98789 | 4.1 | 20 | 4.8307 | 698.4 | 273.6 | 264.767 | 0 | 1
3/9 | 16:00:00 | 279.15 | 98789 | 4.1 | 20 | 4.8307 | 478.8 | 61.2 | 264.767 | 0 | 1
3/9 | 17:00:00 | 279.15 | 98789 | 3.6 | 20 | 4.8307 | 417.6 | 644.4 | 264.299 | 0 | 1
3/9 | 18:00:00 | 278.15 | 98780 | 2.6 | 20 | 4.8311 | 68.4 | 0 | 263.352 | 0 | 1
3/9 | 19:00:00 | 278.15 | 98780 | 4.1 | 20 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
3/9 | 20:00:00 | 276.15 | 98762 | 2.6 | 10 | 4.832 | 0 | 0 | 261.203 | 0 | 1
3/9 | 21:00:00 | 276.15 | 98762 | 3.1 | 10 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
3/9 | 22:00:00 | 276.15 | 98762 | 2.6 | 20 | 4.832 | 0 | 0 | 261.921 | 0 | 1
3/9 | 23:00:00 | 276.15 | 98762 | 2.1 | 20 | 4.832 | 0 | 0 | 261.921 | 0 | 1
3/9 | 24:00:00 | 275.95 | 98760 | 2.4 | 289 | 4.7296 | 0 | 0 | 261.769 | 0 | 1
3/10 | 01:00:00 | 275.85 | 98758 | 2.6 | 56 | 4.5959 | 0 | 0 | 261.583 | 0 | 1
3/10 | 02:00:00 | 275.65 | 98757 | 2.8 | 59 | 4.4979 | 0 | 0 | 261.325 | 0 | 1
3/10 | 03:00:00 | 275.45 | 98755 | 3.1 | 264 | 4.4018 | 0 | 0 | 261.067 | 0 | 1
3/10 | 04:00:00 | 275.35 | 98754 | 3.3 | 189 | 4.2764 | 0 | 0 | 260.88 | 0 | 1
3/10 | 05:00:00 | 275.15 | 98752 | 3.6 | 10 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
3/10 | 06:00:00 | 275.15 | 98752 | 3.6 | 10 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
3/10 | 07:00:00 | 274.15 | 98743 | 2.1 | 20 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
3/10 | 08:00:00 | 275.15 | 98752 | 1 | 55 | 3.8903 | 194.4 | 176.4 | 259.826 | 0 | 1
3/10 | 09:00:00 | 275.15 | 98752 | 1 | 10 | 3.8903 | 626.4 | 1080 | 259.826 | 0 | 1
3/10 | 10:00:00 | 277.15 | 98771 | 0.5 | 109 | 3.8896 | 594 | 68.4 | 262.177 | 0 | 1
3/10 | 11:00:00 | 277.15 | 98771 | 1 | 38 | 4.1838 | 1418.4 | 1616.4 | 261.946 | 0 | 1
3/10 | 12:00:00 | 279.15 | 98789 | 2.6 | 60 | 4.4964 | 1724.4 | 2610 | 263.81 | 0 | 1
3/10 | 13:00:00 | 279.15 | 98789 | 3.6 | 70 | 4.4964 | 1778.4 | 2635.2 | 263.81 | 0 | 1
3/10 | 14:00:00 | 280.15 | 98798 | 2.6 | 40 | 4.1826 | 1558.8 | 1652.4 | 264.782 | 0 | 1
3/10 | 15:00:00 | 279.15 | 98789 | 3.1 | 20 | 3.8889 | 1285.2 | 1468.8 | 263.603 | 0 | 1
3/10 | 16:00:00 | 279.15 | 98789 | 2.6 | 60 | 3.8889 | 889.2 | 1353.6 | 263.603 | 0 | 1
3/10 | 17:00:00 | 279.15 | 98789 | 1 | 227 | 4.183 | 432 | 752.4 | 263.837 | 0 | 1
3/10 | 18:00:00 | 279.15 | 98789 | 0.5 | 290 | 4.183 | 75.6 | 0 | 263.837 | 0 | 1
3/10 | 19:00:00 | 277.15 | 98771 | 0 | 155 | 4.1838 | 0 | 0 | 261.946 | 0 | 1
3/10 | 20:00:00 | 276.15 | 98762 | 0 | 141 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
3/10 | 21:00:00 | 276.15 | 98762 | 0 | 348 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
3/10 | 22:00:00 | 275.15 | 98752 | 0 | 134 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
3/10 | 23:00:00 | 274.15 | 98743 | 0 | 210 | 3.5803 | 0 | 0 | 259 | 0 | 1
3/10 | 24:00:00 | 273.95 | 98742 | 0.3 | 177 | 3.4917 | 0 | 0 | 258.741 | 0 | 1
3/11 | 01:00:00 | 273.85 | 98740 | 0.7 | 6 | 3.3768 | 0 | 0 | 258.554 | 0 | 1
3/11 | 02:00:00 | 273.65 | 98739 | 1 | 129 | 3.2929 | 0 | 0 | 258.295 | 0 | 1
3/11 | 03:00:00 | 273.45 | 98737 | 1.4 | 149 | 3.2109 | 0 | 0 | 257.925 | 0 | 1
3/11 | 04:00:00 | 273.35 | 98735 | 1.8 | 263 | 3.1044 | 0 | 0 | 257.737 | 0 | 1
3/11 | 05:00:00 | 273.15 | 98734 | 2.1 | 330 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
3/11 | 06:00:00 | 272.15 | 98724 | 2.1 | 320 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
3/11 | 07:00:00 | 272.15 | 98724 | 1.5 | 320 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
3/11 | 08:00:00 | 272.15 | 98724 | 2.6 | 310 | 3.0271 | 147.6 | 0 | 256.647 | 0 | 1
3/11 | 09:00:00 | 274.15 | 98743 | 1.5 | 176 | 3.2927 | 540 | 478.8 | 258.655 | 0 | 1
3/11 | 10:00:00 | 276.15 | 98762 | 2.6 | 360 | 3.2921 | 1076.4 | 1364.4 | 260.304 | 0 | 1
3/11 | 11:00:00 | 277.15 | 98771 | 1 | 188 | 3.5793 | 1407.6 | 1519.2 | 261.603 | 0 | 1
3/11 | 12:00:00 | 278.15 | 98780 | 1.5 | 128 | 3.5789 | 1756.8 | 2372.4 | 262.168 | 0 | 1
3/11 | 13:00:00 | 279.15 | 98789 | 2.1 | 10 | 3.5786 | 1810.8 | 2764.8 | 263.11 | 0 | 1
3/11 | 14:00:00 | 280.15 | 98798 | 2.6 | 10 | 3.5783 | 1681.2 | 2084.4 | 264.053 | 0 | 1
3/11 | 15:00:00 | 280.15 | 98798 | 1.5 | 5 | 3.5783 | 727.2 | 82.8 | 264.779 | 0 | 1
3/11 | 16:00:00 | 280.15 | 98798 | 3.6 | 320 | 3.5783 | 504 | 50.4 | 264.779 | 0 | 1
3/11 | 17:00:00 | 278.15 | 98780 | 6.2 | 320 | 3.0253 | 478.8 | 990 | 261.696 | 0 | 1
3/11 | 18:00:00 | 278.15 | 98780 | 5.1 | 300 | 3.2915 | 86.4 | 32.4 | 261.933 | 0 | 1
3/11 | 19:00:00 | 277.15 | 98771 | 4.1 | 280 | 3.2918 | 0 | 0 | 260.991 | 0 | 1
3/11 | 20:00:00 | 276.15 | 98762 | 4.1 | 290 | 3.5796 | 0 | 0 | 260.283 | 0 | 1
3/11 | 21:00:00 | 277.15 | 98771 | 6.2 | 280 | 3.5793 | 0 | 0 | 261.481 | 0 | 1
3/11 | 22:00:00 | 277.15 | 98771 | 6.7 | 280 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
3/11 | 23:00:00 | 277.15 | 98771 | 7.2 | 270 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
3/11 | 24:00:00 | 277.15 | 98771 | 7 | 184 | 4.0345 | 0 | 0 | 262.07 | 0 | 1
3/12 | 01:00:00 | 277.15 | 98771 | 6.9 | 148 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
3/12 | 02:00:00 | 277.15 | 98771 | 6.7 | 140 | 4.338 | 0 | 0 | 262.415 | 0 | 1
3/12 | 03:00:00 | 277.15 | 98771 | 6.5 | 33 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
3/12 | 04:00:00 | 277.15 | 98771 | 6.4 | 269 | 4.6617 | 0 | 0 | 262.755 | 0 | 1
3/12 | 05:00:00 | 277.15 | 98771 | 6.2 | 300 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
3/12 | 06:00:00 | 277.15 | 98771 | 5.7 | 300 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
3/12 | 07:00:00 | 277.15 | 98771 | 5.1 | 310 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
3/12 | 08:00:00 | 277.15 | 98771 | 4.6 | 320 | 4.4973 | 122.4 | 0 | 262.64 | 0 | 1
3/12 | 09:00:00 | 277.15 | 98771 | 4.1 | 320 | 4.8316 | 370.8 | 25.2 | 262.87 | 0 | 1
3/12 | 10:00:00 | 277.15 | 98771 | 6.7 | 360 | 4.8316 | 615.6 | 57.6 | 262.87 | 0 | 1
3/12 | 11:00:00 | 278.15 | 98780 | 7.2 | 360 | 5.1875 | 810 | 147.6 | 264.047 | 0 | 1
3/12 | 12:00:00 | 279.15 | 98789 | 8.2 | 10 | 5.187 | 925.2 | 162 | 264.996 | 0 | 1
3/12 | 13:00:00 | 279.15 | 98789 | 7.2 | 360 | 4.8307 | 954 | 342 | 264.767 | 0 | 1
3/12 | 14:00:00 | 279.15 | 98789 | 8.2 | 10 | 4.8307 | 1594.8 | 1764 | 264.299 | 0 | 1
3/12 | 15:00:00 | 279.15 | 98789 | 6.2 | 360 | 4.8307 | 1321.2 | 1558.8 | 264.299 | 0 | 1
3/12 | 16:00:00 | 278.15 | 98780 | 5.1 | 10 | 5.1875 | 511.2 | 90 | 264.047 | 0 | 1
3/12 | 17:00:00 | 278.15 | 98780 | 5.1 | 10 | 4.8311 | 460.8 | 698.4 | 263.352 | 0 | 1
3/12 | 18:00:00 | 277.15 | 98771 | 5.7 | 360 | 4.4973 | 86.4 | 0 | 262.177 | 0 | 1
3/12 | 19:00:00 | 277.15 | 98771 | 2.6 | 360 | 4.1838 | 0 | 0 | 261.946 | 0 | 1
3/12 | 20:00:00 | 277.15 | 98771 | 2.1 | 340 | 4.1838 | 0 | 0 | 262.41 | 0 | 1
3/12 | 21:00:00 | 277.15 | 98771 | 2.1 | 350 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
3/12 | 22:00:00 | 276.15 | 98762 | 4.6 | 350 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
3/12 | 23:00:00 | 276.15 | 98762 | 3.6 | 330 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
3/12 | 24:00:00 | 276.15 | 98762 | 3.1 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
3/13 | 01:00:00 | 276.15 | 98762 | 2.6 | 330 | 3.8899 | 0 | 0 | 261.231 | 0 | 1
3/13 | 02:00:00 | 275.15 | 98752 | 2.1 | 290 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
3/13 | 03:00:00 | 274.15 | 98743 | 1.5 | 280 | 3.5803 | 0 | 0 | 258.398 | 0 | 1
3/13 | 04:00:00 | 273.15 | 98734 | 3.1 | 260 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
3/13 | 05:00:00 | 272.15 | 98724 | 2.6 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
3/13 | 06:00:00 | 272.15 | 98724 | 2.6 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
3/13 | 07:00:00 | 272.15 | 98724 | 3.6 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
3/13 | 08:00:00 | 274.15 | 98743 | 3.6 | 260 | 3.5803 | 162 | 0 | 259 | 0 | 1
3/13 | 09:00:00 | 276.15 | 98762 | 5.1 | 260 | 4.1841 | 730.8 | 1378.8 | 260.746 | 0 | 1
3/13 | 10:00:00 | 277.15 | 98771 | 5.7 | 270 | 4.4973 | 1202.4 | 2005.2 | 261.92 | 0 | 1
3/13 | 11:00:00 | 277.15 | 98771 | 7.2 | 270 | 4.8316 | 1573.2 | 2491.2 | 262.149 | 0 | 1
3/13 | 12:00:00 | 278.15 | 98780 | 7.2 | 280 | 4.8311 | 1692 | 2145.6 | 263.352 | 0 | 1
3/13 | 13:00:00 | 280.15 | 98798 | 6.7 | 270 | 4.8303 | 1843.2 | 2653.2 | 264.986 | 0 | 1
3/13 | 14:00:00 | 281.15 | 98806 | 6.7 | 270 | 4.8299 | 1717.2 | 2649.6 | 265.932 | 0 | 1
3/13 | 15:00:00 | 281.15 | 98806 | 7.2 | 280 | 4.8299 | 1422 | 2196 | 265.932 | 0 | 1
3/13 | 16:00:00 | 281.15 | 98806 | 6.7 | 280 | 4.8299 | 939.6 | 1281.6 | 266.193 | 0 | 1
3/13 | 17:00:00 | 280.15 | 98798 | 6.2 | 270 | 5.1865 | 262.8 | 0 | 265.946 | 0 | 1
3/13 | 18:00:00 | 279.15 | 98789 | 6.2 | 280 | 5.187 | 90 | 7.2 | 264.528 | 0 | 1
3/13 | 19:00:00 | 278.15 | 98780 | 6.2 | 260 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
3/13 | 20:00:00 | 277.15 | 98771 | 7.2 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/13 | 21:00:00 | 277.15 | 98771 | 6.7 | 290 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/13 | 22:00:00 | 277.15 | 98771 | 3.1 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/13 | 23:00:00 | 277.15 | 98771 | 6.2 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/13 | 24:00:00 | 277.15 | 98771 | 5.7 | 290 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
3/14 | 01:00:00 | 276.15 | 98762 | 6.7 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
3/14 | 02:00:00 | 276.15 | 98762 | 8.2 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
3/14 | 03:00:00 | 277.15 | 98771 | 8.7 | 280 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
3/14 | 04:00:00 | 276.15 | 98762 | 7.7 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
3/14 | 05:00:00 | 276.15 | 98762 | 8.2 | 280 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
3/14 | 06:00:00 | 276.15 | 98762 | 6.2 | 280 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
3/14 | 07:00:00 | 276.15 | 98762 | 6.7 | 280 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
3/14 | 08:00:00 | 276.15 | 98762 | 6.2 | 280 | 4.4977 | 273.6 | 432 | 260.975 | 0 | 1
3/14 | 09:00:00 | 277.15 | 98771 | 8.2 | 270 | 4.8316 | 752.4 | 1501.2 | 262.149 | 0 | 1
3/14 | 10:00:00 | 279.15 | 98789 | 7.7 | 280 | 5.187 | 1224 | 2030.4 | 264.269 | 0 | 1
3/14 | 11:00:00 | 280.15 | 98798 | 8.7 | 300 | 4.8303 | 1598.4 | 2505.6 | 264.986 | 0 | 1
3/14 | 12:00:00 | 281.15 | 98806 | 8.7 | 290 | 4.8299 | 1821.6 | 2635.2 | 265.932 | 0 | 1
3/14 | 13:00:00 | 283.15 | 98824 | 8.2 | 290 | 5.1851 | 1756.8 | 2260.8 | 268.319 | 0 | 1
3/14 | 14:00:00 | 283.15 | 98824 | 9.8 | 300 | 4.4948 | 1641.6 | 1918.8 | 267.852 | 0 | 1
3/14 | 15:00:00 | 283.15 | 98824 | 8.7 | 300 | 4.829 | 1360.8 | 1951.2 | 268.086 | 0 | 1
3/14 | 16:00:00 | 283.15 | 98824 | 8.2 | 270 | 5.1851 | 957.6 | 1522.8 | 268.319 | 0 | 1
3/14 | 17:00:00 | 282.15 | 98815 | 7.7 | 310 | 5.1856 | 493.2 | 943.2 | 267.371 | 0 | 1
3/14 | 18:00:00 | 280.15 | 98798 | 3.6 | 280 | 5.1865 | 104.4 | 54 | 265.216 | 0 | 1
3/14 | 19:00:00 | 280.15 | 98798 | 5.1 | 280 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
3/14 | 20:00:00 | 279.15 | 98789 | 7.2 | 280 | 5.187 | 0 | 0 | 264.269 | 0 | 1
3/14 | 21:00:00 | 279.15 | 98789 | 6.7 | 280 | 5.187 | 0 | 0 | 264.996 | 0 | 1
3/14 | 22:00:00 | 278.15 | 98780 | 6.2 | 280 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
3/14 | 23:00:00 | 279.15 | 98789 | 6.7 | 280 | 5.187 | 0 | 0 | 264.996 | 0 | 1
3/14 | 24:00:00 | 278.95 | 98787 | 7 | 168 | 5.114 | 0 | 0 | 264.761 | 0 | 1
3/15 | 01:00:00 | 278.85 | 98786 | 7.2 | 257 | 5.0779 | 0 | 0 | 264.643 | 0 | 1
3/15 | 02:00:00 | 278.65 | 98784 | 7.4 | 166 | 5.0063 | 0 | 0 | 264.407 | 0 | 1
3/15 | 03:00:00 | 278.45 | 98783 | 7.7 | 62 | 4.9355 | 0 | 0 | 264.172 | 0 | 1
3/15 | 04:00:00 | 278.35 | 98781 | 7.9 | 61 | 4.9005 | 0 | 0 | 264.054 | 0 | 1
3/15 | 05:00:00 | 278.15 | 98780 | 8.2 | 270 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
3/15 | 06:00:00 | 278.15 | 98780 | 6.7 | 270 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
3/15 | 07:00:00 | 277.15 | 98771 | 6.7 | 260 | 4.8316 | 3.6 | 0 | 262.149 | 0 | 1
3/15 | 08:00:00 | 278.15 | 98780 | 9.3 | 270 | 4.8311 | 273.6 | 601.2 | 263.352 | 0 | 1
3/15 | 09:00:00 | 278.15 | 98780 | 7.7 | 270 | 5.1875 | 403.2 | 39.6 | 264.047 | 0 | 1
3/15 | 10:00:00 | 279.15 | 98789 | 10.8 | 270 | 5.187 | 651.6 | 61.2 | 264.996 | 0 | 1
3/15 | 11:00:00 | 279.15 | 98789 | 8.2 | 260 | 5.187 | 846 | 151.2 | 264.996 | 0 | 1
3/15 | 12:00:00 | 280.15 | 98798 | 6.2 | 270 | 5.1865 | 961.2 | 338.4 | 265.946 | 0 | 1
3/15 | 13:00:00 | 280.15 | 98798 | 9.3 | 280 | 5.1865 | 1778.4 | 1836 | 265.476 | 0 | 1
3/15 | 14:00:00 | 280.15 | 98798 | 10.8 | 280 | 4.8303 | 1760.4 | 2599.2 | 264.986 | 0 | 1
3/15 | 15:00:00 | 280.15 | 98798 | 9.3 | 270 | 4.8303 | 1465.2 | 2394 | 264.986 | 0 | 1
3/15 | 16:00:00 | 280.15 | 98798 | 10.3 | 280 | 4.496 | 1036.8 | 1857.6 | 264.755 | 0 | 1
3/15 | 17:00:00 | 280.15 | 98798 | 11.8 | 270 | 4.8303 | 540 | 1180.8 | 264.986 | 0 | 1
3/15 | 18:00:00 | 279.15 | 98789 | 9.3 | 270 | 4.8307 | 108 | 93.6 | 264.041 | 0 | 1
3/15 | 19:00:00 | 279.15 | 98789 | 9.3 | 280 | 4.4964 | 0 | 0 | 263.81 | 0 | 1
3/15 | 20:00:00 | 278.15 | 98780 | 6.7 | 290 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
3/15 | 21:00:00 | 278.15 | 98780 | 9.3 | 280 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
3/15 | 22:00:00 | 278.15 | 98780 | 7.2 | 280 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
3/15 | 23:00:00 | 278.15 | 98780 | 6.2 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
3/15 | 24:00:00 | 277.95 | 98778 | 5.8 | 154 | 4.9007 | 0 | 0 | 263.674 | 0 | 1
3/16 | 01:00:00 | 277.85 | 98777 | 5.3 | 280 | 4.9358 | 0 | 0 | 263.602 | 0 | 1
3/16 | 02:00:00 | 277.65 | 98775 | 4.9 | 100 | 5.0067 | 0 | 0 | 263.565 | 0 | 1
3/16 | 03:00:00 | 277.45 | 98774 | 4.5 | 37 | 5.0785 | 0 | 0 | 263.421 | 0 | 1
3/16 | 04:00:00 | 277.35 | 98772 | 4 | 288 | 5.1148 | 0 | 0 | 263.349 | 0 | 1
3/16 | 05:00:00 | 277.15 | 98771 | 3.6 | 260 | 5.1879 | 0 | 0 | 262.633 | 0 | 1
3/16 | 06:00:00 | 277.15 | 98771 | 3.6 | 260 | 5.1879 | 0 | 0 | 262.633 | 0 | 1
3/16 | 07:00:00 | 276.15 | 98762 | 3.1 | 290 | 4.832 | 10.8 | 0 | 261.203 | 0 | 1
3/16 | 08:00:00 | 277.15 | 98771 | 3.1 | 270 | 5.1879 | 162 | 0 | 263.098 | 0 | 1
3/16 | 09:00:00 | 278.15 | 98780 | 6.2 | 260 | 5.1875 | 795.6 | 1242 | 263.323 | 0 | 1
3/16 | 10:00:00 | 279.15 | 98789 | 5.7 | 270 | 5.187 | 1274.4 | 2181.6 | 264.269 | 0 | 1
3/16 | 11:00:00 | 280.15 | 98798 | 3.6 | 270 | 5.1865 | 1645.2 | 2520 | 265.216 | 0 | 1
3/16 | 12:00:00 | 282.15 | 98815 | 2.6 | 260 | 4.8294 | 1760.4 | 1836 | 267.139 | 0 | 1
3/16 | 13:00:00 | 282.15 | 98815 | 2.6 | 96 | 4.4952 | 1004.4 | 349.2 | 267.379 | 0 | 1
3/16 | 14:00:00 | 282.15 | 98815 | 3.1 | 230 | 4.1819 | 936 | 165.6 | 267.144 | 0 | 1
3/16 | 15:00:00 | 282.15 | 98815 | 3.6 | 240 | 3.8878 | 1407.6 | 1587.6 | 266.436 | 0 | 1
3/16 | 16:00:00 | 282.15 | 98815 | 2.1 | 160 | 4.1819 | 1058.4 | 1591.2 | 266.411 | 0 | 1
3/16 | 17:00:00 | 282.15 | 98815 | 3.6 | 180 | 3.8878 | 558 | 997.2 | 266.175 | 0 | 1
3/16 | 18:00:00 | 281.15 | 98806 | 3.6 | 200 | 3.8882 | 115.2 | 64.8 | 265.232 | 0 | 1
3/16 | 19:00:00 | 280.15 | 98798 | 2.1 | 200 | 3.5783 | 0 | 0 | 264.053 | 0 | 1
3/16 | 20:00:00 | 279.15 | 98789 | 3.1 | 180 | 3.8889 | 0 | 0 | 263.603 | 0 | 1
3/16 | 21:00:00 | 279.15 | 98789 | 3.1 | 190 | 3.8889 | 0 | 0 | 263.603 | 0 | 1
3/16 | 22:00:00 | 278.15 | 98780 | 3.6 | 180 | 3.8892 | 0 | 0 | 262.781 | 0 | 1
3/16 | 23:00:00 | 278.15 | 98780 | 3.1 | 200 | 3.8892 | 0 | 0 | 262.781 | 0 | 1
3/16 | 24:00:00 | 278.35 | 98781 | 3.1 | 201 | 3.9468 | 0 | 0 | 263.017 | 0 | 1
3/17 | 01:00:00 | 278.45 | 98783 | 3.1 | 231 | 3.9756 | 0 | 0 | 263.134 | 0 | 1
3/17 | 02:00:00 | 278.65 | 98784 | 3.1 | 143 | 4.0339 | 0 | 0 | 263.37 | 0 | 1
3/17 | 03:00:00 | 278.85 | 98786 | 3.1 | 87 | 4.093 | 0 | 0 | 263.606 | 0 | 1
3/17 | 04:00:00 | 278.95 | 98787 | 3.1 | 35 | 4.1228 | 0 | 0 | 263.724 | 0 | 1
3/17 | 05:00:00 | 279.15 | 98789 | 3.1 | 210 | 4.183 | 0 | 0 | 264.303 | 0 | 1
3/17 | 06:00:00 | 279.15 | 98789 | 3.1 | 240 | 4.4964 | 0 | 0 | 264.069 | 0 | 1
3/17 | 07:00:00 | 279.15 | 98789 | 5.7 | 220 | 4.4964 | 10.8 | 0 | 264.536 | 0 | 1
3/17 | 08:00:00 | 280.15 | 98798 | 4.1 | 220 | 4.8303 | 306 | 417.6 | 265.246 | 0 | 1
3/17 | 09:00:00 | 280.15 | 98798 | 4.1 | 230 | 5.1865 | 774 | 1357.2 | 265.476 | 0 | 1
3/17 | 10:00:00 | 282.15 | 98815 | 4.1 | 230 | 5.5651 | 1220.4 | 1468.8 | 267.601 | 0 | 1
3/17 | 11:00:00 | 282.15 | 98815 | 7.7 | 240 | 5.9692 | 871.2 | 147.6 | 268.304 | 0 | 1
3/17 | 12:00:00 | 283.15 | 98824 | 7.2 | 250 | 5.9687 | 986.4 | 165.6 | 269.255 | 0 | 1
3/17 | 13:00:00 | 284.15 | 98833 | 5.1 | 240 | 5.9681 | 1008 | 165.6 | 270.206 | 0 | 1
3/17 | 14:00:00 | 285.15 | 98841 | 6.2 | 250 | 5.9676 | 939.6 | 327.6 | 271.157 | 0 | 1
3/17 | 15:00:00 | 286.15 | 98850 | 6.2 | 250 | 5.5631 | 1501.2 | 1915.2 | 271.13 | 0 | 1
3/17 | 16:00:00 | 285.15 | 98841 | 7.7 | 250 | 5.1842 | 1072.8 | 1872 | 269.95 | 0 | 1
3/17 | 17:00:00 | 285.15 | 98841 | 6.7 | 240 | 5.1842 | 572.4 | 1188 | 269.95 | 0 | 1
3/17 | 18:00:00 | 285.15 | 98841 | 4.6 | 240 | 4.8281 | 126 | 154.8 | 269.716 | 0 | 1
3/17 | 19:00:00 | 283.15 | 98824 | 0 | 20 | 5.5646 | 0 | 0 | 268.675 | 0 | 1
3/17 | 20:00:00 | 283.15 | 98824 | 2.6 | 220 | 5.5646 | 0 | 0 | 268.675 | 0 | 1
3/17 | 21:00:00 | 282.15 | 98815 | 1 | 223 | 5.5651 | 0 | 0 | 267.846 | 0 | 1
3/17 | 22:00:00 | 282.15 | 98815 | 5.7 | 220 | 5.5651 | 0 | 0 | 267.846 | 0 | 1
3/17 | 23:00:00 | 282.15 | 98815 | 3.1 | 230 | 5.5651 | 0 | 0 | 267.846 | 0 | 1
3/17 | 24:00:00 | 282.15 | 98815 | 4.6 | 220 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
3/18 | 01:00:00 | 282.15 | 98815 | 4 | 115 | 5.6439 | 0 | 0 | 267.892 | 0 | 1
3/18 | 02:00:00 | 282.15 | 98815 | 3.4 | 4 | 5.7237 | 0 | 0 | 267.938 | 0 | 1
3/18 | 03:00:00 | 282.15 | 98815 | 2.7 | 221 | 5.8045 | 0 | 0 | 267.984 | 0 | 1
3/18 | 04:00:00 | 282.15 | 98815 | 2.1 | 161 | 5.8864 | 0 | 0 | 268.029 | 0 | 1
3/18 | 05:00:00 | 282.15 | 98815 | 1.5 | 355 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
3/18 | 06:00:00 | 281.15 | 98806 | 2.1 | 160 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
3/18 | 07:00:00 | 280.15 | 98798 | 3.1 | 140 | 5.5661 | 28.8 | 0 | 265.444 | 0 | 1
3/18 | 08:00:00 | 280.15 | 98798 | 4.1 | 130 | 5.9703 | 349.2 | 763.2 | 265.247 | 0 | 1
3/18 | 09:00:00 | 281.15 | 98806 | 4.1 | 140 | 5.9698 | 838.8 | 1641.6 | 266.62 | 0 | 1
3/18 | 10:00:00 | 283.15 | 98824 | 3.6 | 150 | 5.9687 | 1335.6 | 2304 | 268.088 | 0 | 1
3/18 | 11:00:00 | 286.15 | 98850 | 4.1 | 210 | 5.1837 | 1692 | 2545.2 | 270.896 | 0 | 1
3/18 | 12:00:00 | 288.15 | 98867 | 4.6 | 200 | 5.1829 | 1933.2 | 2822.4 | 272.649 | 0 | 1
3/18 | 13:00:00 | 287.15 | 98858 | 8.7 | 220 | 5.1833 | 1969.2 | 2822.4 | 271.843 | 0 | 1
3/18 | 14:00:00 | 286.15 | 98850 | 7.2 | 220 | 5.1837 | 1825.2 | 2692.8 | 270.896 | 0 | 1
3/18 | 15:00:00 | 285.15 | 98841 | 8.2 | 200 | 5.5636 | 1522.8 | 2257.2 | 270.182 | 0 | 1
3/18 | 16:00:00 | 285.15 | 98841 | 6.2 | 200 | 5.9676 | 1026 | 1558.8 | 270.678 | 0 | 1
3/18 | 17:00:00 | 284.15 | 98833 | 5.7 | 190 | 5.9681 | 586.8 | 1198.8 | 269.465 | 0 | 1
3/18 | 18:00:00 | 284.15 | 98833 | 7.7 | 190 | 5.9681 | 129.6 | 111.6 | 269.728 | 0 | 1
3/18 | 19:00:00 | 284.15 | 98833 | 6.2 | 200 | 5.9681 | 0 | 0 | 270.206 | 0 | 1
3/18 | 20:00:00 | 284.15 | 98833 | 5.1 | 200 | 5.5641 | 0 | 0 | 269.975 | 0 | 1
3/18 | 21:00:00 | 283.15 | 98824 | 5.1 | 220 | 6.3988 | 0 | 0 | 269.483 | 0 | 1
3/18 | 22:00:00 | 282.15 | 98815 | 8.7 | 210 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
3/18 | 23:00:00 | 282.15 | 98815 | 9.3 | 220 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
3/18 | 24:00:00 | 281.95 | 98814 | 8.4 | 223 | 6.181 | 0 | 0 | 268.115 | 0 | 1
3/19 | 01:00:00 | 281.85 | 98812 | 7.6 | 141 | 5.9694 | 0 | 0 | 267.906 | 0 | 1
3/19 | 02:00:00 | 281.65 | 98811 | 6.7 | 70 | 5.7642 | 0 | 0 | 267.602 | 0 | 1
3/19 | 03:00:00 | 281.45 | 98809 | 5.8 | 262 | 5.5654 | 0 | 0 | 267.181 | 0 | 1
3/19 | 04:00:00 | 281.35 | 98808 | 5 | 64 | 5.3727 | 0 | 0 | 266.972 | 0 | 1
3/19 | 05:00:00 | 281.15 | 98806 | 4.1 | 220 | 5.1861 | 0 | 0 | 266.895 | 0 | 1
3/19 | 06:00:00 | 281.15 | 98806 | 4.6 | 230 | 4.8299 | 0 | 0 | 266.664 | 0 | 1
3/19 | 07:00:00 | 280.15 | 98798 | 3.6 | 240 | 4.8303 | 36 | 0 | 264.986 | 0 | 1
3/19 | 08:00:00 | 280.15 | 98798 | 5.7 | 230 | 4.8303 | 363.6 | 759.6 | 264.986 | 0 | 1
3/19 | 09:00:00 | 281.15 | 98806 | 4.1 | 230 | 4.8299 | 867.6 | 1692 | 265.932 | 0 | 1
3/19 | 10:00:00 | 283.15 | 98824 | 9.3 | 250 | 4.829 | 1346.4 | 2257.2 | 267.824 | 0 | 1
3/19 | 11:00:00 | 283.15 | 98824 | 9.8 | 260 | 4.4948 | 1623.6 | 2084.4 | 267.852 | 0 | 1
3/19 | 12:00:00 | 284.15 | 98833 | 7.2 | 250 | 4.4944 | 1944 | 2671.2 | 268.535 | 0 | 1
3/19 | 13:00:00 | 284.15 | 98833 | 8.2 | 250 | 4.1811 | 1990.8 | 2826 | 268.3 | 0 | 1
3/19 | 14:00:00 | 285.15 | 98841 | 7.7 | 250 | 4.1808 | 1854 | 2739.6 | 269.244 | 0 | 1
3/19 | 15:00:00 | 284.15 | 98833 | 5.7 | 250 | 4.4944 | 1551.6 | 2451.6 | 268.535 | 0 | 1
3/19 | 16:00:00 | 283.15 | 98824 | 5.7 | 260 | 4.829 | 1112.4 | 1911.6 | 267.824 | 0 | 1
3/19 | 17:00:00 | 282.15 | 98815 | 3.1 | 260 | 5.1856 | 604.8 | 1234.8 | 267.11 | 0 | 1
3/19 | 18:00:00 | 282.15 | 98815 | 1 | 225 | 5.1856 | 147.6 | 241.2 | 267.11 | 0 | 1
3/19 | 19:00:00 | 281.15 | 98806 | 0 | 66 | 5.1861 | 0 | 0 | 266.163 | 0 | 1
3/19 | 20:00:00 | 281.15 | 98806 | 0 | 342 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
3/19 | 21:00:00 | 280.15 | 98798 | 0 | 239 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
3/19 | 22:00:00 | 280.15 | 98798 | 2.1 | 80 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
3/19 | 23:00:00 | 279.15 | 98789 | 1.5 | 40 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
3/19 | 24:00:00 | 278.95 | 98787 | 1.6 | 250 | 5.8881 | 0 | 0 | 265.323 | 0 | 1
3/20 | 01:00:00 | 278.85 | 98786 | 1.7 | 117 | 5.8471 | 0 | 0 | 265.205 | 0 | 1
3/20 | 02:00:00 | 278.65 | 98784 | 1.8 | 226 | 5.7658 | 0 | 0 | 264.97 | 0 | 1
3/20 | 03:00:00 | 278.45 | 98783 | 1.9 | 262 | 5.6856 | 0 | 0 | 264.735 | 0 | 1
3/20 | 04:00:00 | 278.35 | 98781 | 2 | 357 | 5.6459 | 0 | 0 | 264.617 | 0 | 1
3/20 | 05:00:00 | 278.15 | 98780 | 2.1 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
3/20 | 06:00:00 | 278.15 | 98780 | 2.1 | 50 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
3/20 | 07:00:00 | 278.15 | 98780 | 1.5 | 210 | 5.5671 | 21.6 | 0 | 264.274 | 0 | 1
3/20 | 08:00:00 | 278.15 | 98780 | 1.5 | 60 | 5.5671 | 198 | 0 | 264.274 | 0 | 1
3/20 | 09:00:00 | 278.15 | 98780 | 1.5 | 297 | 5.5671 | 464.4 | 32.4 | 264.274 | 0 | 1
3/20 | 10:00:00 | 278.15 | 98780 | 2.1 | 30 | 5.5671 | 716.4 | 64.8 | 264.274 | 0 | 1
3/20 | 11:00:00 | 279.15 | 98789 | 2.1 | 20 | 5.9708 | 907.2 | 154.8 | 265.451 | 0 | 1
3/20 | 12:00:00 | 279.15 | 98789 | 2.1 | 30 | 5.9708 | 1022.4 | 165.6 | 265.451 | 0 | 1
3/20 | 13:00:00 | 279.15 | 98789 | 4.6 | 10 | 5.9708 | 1044 | 230.4 | 265.451 | 0 | 1
3/20 | 14:00:00 | 279.15 | 98789 | 5.1 | 10 | 5.9708 | 972 | 162 | 265.451 | 0 | 1
3/20 | 15:00:00 | 279.15 | 98789 | 6.2 | 10 | 5.9708 | 817.2 | 144 | 265.451 | 0 | 1
3/20 | 16:00:00 | 279.15 | 98789 | 5.7 | 20 | 5.9708 | 590.4 | 50.4 | 265.451 | 0 | 1
3/20 | 17:00:00 | 278.15 | 98780 | 4.1 | 20 | 5.5671 | 324 | 10.8 | 264.274 | 0 | 1
3/20 | 18:00:00 | 278.15 | 98780 | 4.6 | 350 | 5.5671 | 82.8 | 0 | 264.274 | 0 | 1
3/20 | 19:00:00 | 278.15 | 98780 | 3.6 | 360 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
3/20 | 20:00:00 | 278.15 | 98780 | 3.6 | 360 | 5.5671 | 0 | 0 | 263.807 | 0 | 1
3/20 | 21:00:00 | 278.15 | 98780 | 1.5 | 350 | 5.1875 | 0 | 0 | 263.323 | 0 | 1
3/20 | 22:00:00 | 277.15 | 98771 | 3.6 | 330 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
3/20 | 23:00:00 | 276.15 | 98762 | 2.1 | 320 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
3/20 | 24:00:00 | 275.85 | 98758 | 2.3 | 235 | 4.4335 | 0 | 0 | 261.469 | 0 | 1
3/21 | 01:00:00 | 275.45 | 98755 | 2.4 | 322 | 4.4018 | 0 | 0 | 261.067 | 0 | 1
3/21 | 02:00:00 | 275.15 | 98752 | 2.6 | 63 | 4.3388 | 0 | 0 | 260.736 | 0 | 1
3/21 | 03:00:00 | 274.85 | 98749 | 2.8 | 264 | 4.2767 | 0 | 0 | 260.406 | 0 | 1
3/21 | 04:00:00 | 274.45 | 98746 | 2.9 | 333 | 4.2459 | 0 | 0 | 260.004 | 0 | 1
3/21 | 05:00:00 | 274.15 | 98743 | 3.1 | 270 | 4.185 | 0 | 0 | 259.674 | 0 | 1
3/21 | 06:00:00 | 274.15 | 98743 | 3.1 | 270 | 4.185 | 0 | 0 | 259.674 | 0 | 1
3/21 | 07:00:00 | 275.15 | 98752 | 3.1 | 260 | 4.1846 | 21.6 | 0 | 260.622 | 0 | 1
3/21 | 08:00:00 | 275.15 | 98752 | 2.6 | 250 | 4.1846 | 403.2 | 777.6 | 259.802 | 0 | 1
3/21 | 09:00:00 | 276.15 | 98762 | 2.1 | 250 | 4.4977 | 478.8 | 57.6 | 261.693 | 0 | 1
3/21 | 10:00:00 | 277.15 | 98771 | 4.1 | 240 | 5.1879 | 727.2 | 270 | 263.098 | 0 | 1
3/21 | 11:00:00 | 280.15 | 98798 | 4.1 | 250 | 5.5661 | 1760.4 | 2077.2 | 265.444 | 0 | 1
3/21 | 12:00:00 | 282.15 | 98815 | 4.6 | 250 | 5.5651 | 1864.8 | 2206.8 | 267.601 | 0 | 1
3/21 | 13:00:00 | 282.15 | 98815 | 5.1 | 250 | 5.1856 | 1908 | 2264.4 | 267.371 | 0 | 1
3/21 | 14:00:00 | 283.15 | 98824 | 5.7 | 250 | 4.829 | 1890 | 2430 | 267.824 | 0 | 1
3/21 | 15:00:00 | 283.15 | 98824 | 5.1 | 260 | 5.1851 | 1494 | 1645.2 | 268.319 | 0 | 1
3/21 | 16:00:00 | 283.15 | 98824 | 2.6 | 210 | 5.1851 | 601.2 | 216 | 268.793 | 0 | 1
3/21 | 17:00:00 | 283.15 | 98824 | 4.1 | 220 | 5.1851 | 601.2 | 842.4 | 268.319 | 0 | 1
3/21 | 18:00:00 | 283.15 | 98824 | 2.6 | 190 | 5.5646 | 158.4 | 133.2 | 268.55 | 0 | 1
3/21 | 19:00:00 | 283.15 | 98824 | 2.1 | 190 | 5.5646 | 0 | 0 | 267.859 | 0 | 1
3/21 | 20:00:00 | 282.15 | 98815 | 1.5 | 170 | 5.5651 | 0 | 0 | 268.075 | 0 | 1
3/21 | 21:00:00 | 282.15 | 98815 | 2.1 | 200 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
3/21 | 22:00:00 | 282.15 | 98815 | 4.1 | 210 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
3/21 | 23:00:00 | 281.15 | 98806 | 3.6 | 220 | 6.4 | 0 | 0 | 267.58 | 0 | 1
3/21 | 24:00:00 | 281.35 | 98808 | 3.6 | 188 | 6.3998 | 0 | 0 | 267.77 | 0 | 1
3/22 | 01:00:00 | 281.45 | 98809 | 3.6 | 33 | 6.3998 | 0 | 0 | 267.865 | 0 | 1
3/22 | 02:00:00 | 281.65 | 98811 | 3.6 | 350 | 6.3997 | 0 | 0 | 268.056 | 0 | 1
3/22 | 03:00:00 | 281.85 | 98812 | 3.6 | 120 | 6.3996 | 0 | 0 | 268.246 | 0 | 1
3/22 | 04:00:00 | 281.95 | 98814 | 3.6 | 13 | 6.3995 | 0 | 0 | 268.341 | 0 | 1
3/22 | 05:00:00 | 282.15 | 98815 | 3.6 | 170 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
3/22 | 06:00:00 | 281.15 | 98806 | 3.6 | 170 | 6.4 | 0 | 0 | 267.688 | 0 | 1
3/22 | 07:00:00 | 281.15 | 98806 | 3.6 | 170 | 5.9698 | 28.8 | 0 | 267.353 | 0 | 1
3/22 | 08:00:00 | 281.15 | 98806 | 4.1 | 190 | 5.9698 | 219.6 | 0 | 267.353 | 0 | 1
3/22 | 09:00:00 | 281.15 | 98806 | 5.7 | 200 | 5.5656 | 878.4 | 1123.2 | 266.653 | 0 | 1
3/22 | 10:00:00 | 281.15 | 98806 | 5.7 | 190 | 5.5656 | 1414.8 | 2149.2 | 266.392 | 0 | 1
3/22 | 11:00:00 | 282.15 | 98815 | 6.2 | 200 | 5.1856 | 1789.2 | 2574 | 267.11 | 0 | 1
3/22 | 12:00:00 | 282.15 | 98815 | 6.2 | 200 | 5.1856 | 1890 | 1854 | 267.371 | 0 | 1
3/22 | 13:00:00 | 281.15 | 98806 | 5.1 | 190 | 5.1861 | 1069.2 | 201.6 | 266.895 | 0 | 1
3/22 | 14:00:00 | 281.15 | 98806 | 6.7 | 200 | 5.9698 | 993.6 | 162 | 267.353 | 0 | 1
3/22 | 15:00:00 | 281.15 | 98806 | 5.7 | 210 | 5.9698 | 835.2 | 144 | 267.353 | 0 | 1
3/22 | 16:00:00 | 282.15 | 98815 | 8.2 | 210 | 6.3994 | 1094.4 | 1537.2 | 268.057 | 0 | 1
3/22 | 17:00:00 | 282.15 | 98815 | 8.2 | 260 | 5.9692 | 651.6 | 1281.6 | 267.568 | 0 | 1
3/22 | 18:00:00 | 281.15 | 98806 | 5.7 | 250 | 5.1861 | 180 | 216 | 266.163 | 0 | 1
3/22 | 19:00:00 | 279.15 | 98789 | 8.7 | 270 | 5.187 | 0 | 0 | 264.528 | 0 | 1
3/22 | 20:00:00 | 277.15 | 98771 | 3.1 | 250 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
3/22 | 21:00:00 | 277.15 | 98771 | 3.1 | 250 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/22 | 22:00:00 | 278.15 | 98780 | 6.2 | 260 | 4.4968 | 0 | 0 | 262.865 | 0 | 1
3/22 | 23:00:00 | 278.15 | 98780 | 6.2 | 260 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
3/22 | 24:00:00 | 278.75 | 98785 | 5.9 | 318 | 4.8655 | 0 | 0 | 264.299 | 0 | 1
3/23 | 01:00:00 | 278.15 | 98779 | 5 | 248 | 4.7626 | 0 | 0 | 263.662 | 0 | 1
3/23 | 02:00:00 | 277.55 | 98774 | 4.1 | 279 | 4.6283 | 0 | 0 | 263.112 | 0 | 1
3/23 | 03:00:00 | 276.95 | 98769 | 3.2 | 250 | 4.5298 | 0 | 0 | 262.474 | 0 | 1
3/23 | 04:00:00 | 276.35 | 98763 | 2.3 | 76 | 4.4014 | 0 | 0 | 261.813 | 0 | 1
3/23 | 05:00:00 | 275.75 | 98758 | 1.4 | 307 | 4.3073 | 0 | 0 | 261.176 | 0 | 1
3/23 | 06:00:00 | 275.15 | 98752 | 0.5 | 205 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
3/23 | 07:00:00 | 274.15 | 98743 | 2.1 | 170 | 4.185 | 64.8 | 0 | 258.857 | 0 | 1
3/23 | 08:00:00 | 275.15 | 98752 | 1.5 | 234 | 4.1846 | 187.2 | 0 | 260.622 | 0 | 1
3/23 | 09:00:00 | 277.15 | 98771 | 2.1 | 220 | 4.4973 | 583.2 | 255.6 | 262.64 | 0 | 1
3/23 | 10:00:00 | 279.15 | 98789 | 2.1 | 180 | 5.187 | 1440 | 1836 | 264.269 | 0 | 1
3/23 | 11:00:00 | 280.15 | 98798 | 3.6 | 160 | 5.1865 | 1810.8 | 2584.8 | 265.216 | 0 | 1
3/23 | 12:00:00 | 282.15 | 98815 | 6.2 | 180 | 4.4952 | 2034 | 2818.8 | 266.645 | 0 | 1
3/23 | 13:00:00 | 283.15 | 98824 | 5.1 | 160 | 4.4948 | 2077.2 | 2844 | 267.59 | 0 | 1
3/23 | 14:00:00 | 283.15 | 98824 | 5.1 | 170 | 3.8875 | 1944 | 2786.4 | 267.119 | 0 | 1
3/23 | 15:00:00 | 283.15 | 98824 | 5.7 | 150 | 4.829 | 1627.2 | 2476.8 | 267.824 | 0 | 1
3/23 | 16:00:00 | 283.15 | 98824 | 7.2 | 150 | 4.4948 | 1188 | 1666.8 | 267.59 | 0 | 1
3/23 | 17:00:00 | 282.15 | 98815 | 5.7 | 160 | 4.8294 | 352.8 | 25.2 | 267.612 | 0 | 1
3/23 | 18:00:00 | 281.15 | 98806 | 3.6 | 150 | 5.9698 | 100.8 | 0 | 267.353 | 0 | 1
3/23 | 19:00:00 | 281.15 | 98806 | 3.1 | 150 | 6.4 | 0 | 0 | 267.58 | 0 | 1
3/23 | 20:00:00 | 281.15 | 98806 | 4.6 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
3/23 | 21:00:00 | 281.15 | 98806 | 5.7 | 150 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
3/23 | 22:00:00 | 281.15 | 98806 | 4.6 | 160 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
3/23 | 23:00:00 | 282.15 | 98815 | 5.1 | 190 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
3/23 | 24:00:00 | 282.15 | 98815 | 5.1 | 210 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
3/24 | 01:00:00 | 281.15 | 98806 | 3.6 | 220 | 6.4 | 0 | 0 | 267.107 | 0 | 1
3/24 | 02:00:00 | 281.15 | 98806 | 4.6 | 220 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
3/24 | 03:00:00 | 281.15 | 98806 | 4.1 | 200 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
3/24 | 04:00:00 | 280.15 | 98798 | 3.1 | 180 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
3/24 | 05:00:00 | 280.15 | 98798 | 4.1 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
3/24 | 06:00:00 | 280.15 | 98798 | 4.6 | 120 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
3/24 | 07:00:00 | 280.15 | 98798 | 4.6 | 130 | 6.4005 | 39.6 | 0 | 266.628 | 0 | 1
3/24 | 08:00:00 | 280.15 | 98798 | 4.6 | 150 | 6.4005 | 241.2 | 0 | 266.628 | 0 | 1
3/24 | 09:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 507.6 | 39.6 | 267.805 | 0 | 1
3/24 | 10:00:00 | 281.15 | 98806 | 5.1 | 130 | 6.8577 | 759.6 | 68.4 | 267.805 | 0 | 1
3/24 | 11:00:00 | 282.15 | 98815 | 5.7 | 140 | 7.3438 | 954 | 154.8 | 268.983 | 0 | 1
3/24 | 12:00:00 | 282.15 | 98815 | 4.6 | 150 | 7.3438 | 1065.6 | 223.2 | 268.983 | 0 | 1
3/24 | 13:00:00 | 283.15 | 98824 | 4.6 | 160 | 7.3431 | 1083.6 | 226.8 | 269.936 | 0 | 1
3/24 | 14:00:00 | 284.15 | 98833 | 5.1 | 210 | 6.8558 | 1015.2 | 162 | 270.663 | 0 | 1
3/24 | 15:00:00 | 284.15 | 98833 | 5.1 | 210 | 6.8558 | 856.8 | 144 | 270.663 | 0 | 1
3/24 | 16:00:00 | 284.15 | 98833 | 4.1 | 210 | 6.8558 | 626.4 | 54 | 270.663 | 0 | 1
3/24 | 17:00:00 | 284.15 | 98833 | 3.1 | 200 | 6.8558 | 356.4 | 14.4 | 270.663 | 0 | 1
3/24 | 18:00:00 | 284.15 | 98833 | 3.6 | 190 | 6.8558 | 108 | 0 | 270.663 | 0 | 1
3/24 | 19:00:00 | 284.15 | 98833 | 2.6 | 220 | 6.8558 | 0 | 0 | 270.663 | 0 | 1
3/24 | 20:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
3/24 | 21:00:00 | 282.15 | 98815 | 0 | 311 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
3/24 | 22:00:00 | 282.15 | 98815 | 0 | 258 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
3/24 | 23:00:00 | 282.15 | 98815 | 0 | 257 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
3/24 | 24:00:00 | 281.95 | 98814 | 0.1 | 56 | 6.8571 | 0 | 0 | 268.676 | 0 | 1
3/25 | 01:00:00 | 281.85 | 98812 | 0.2 | 240 | 6.8573 | 0 | 0 | 268.581 | 0 | 1
3/25 | 02:00:00 | 281.65 | 98811 | 0.2 | 15 | 6.8574 | 0 | 0 | 268.39 | 0 | 1
3/25 | 03:00:00 | 281.45 | 98809 | 0.3 | 18 | 6.8575 | 0 | 0 | 268.2 | 0 | 1
3/25 | 04:00:00 | 281.35 | 98808 | 0.4 | 37 | 6.8576 | 0 | 0 | 268.105 | 0 | 1
3/25 | 05:00:00 | 281.15 | 98806 | 0.5 | 215 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
3/25 | 06:00:00 | 281.15 | 98806 | 0.5 | 65 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
3/25 | 07:00:00 | 281.15 | 98806 | 2.6 | 70 | 6.8577 | 43.2 | 0 | 267.805 | 0 | 1
3/25 | 08:00:00 | 281.15 | 98806 | 2.6 | 70 | 6.8577 | 151.2 | 0 | 267.914 | 0 | 1
3/25 | 09:00:00 | 282.15 | 98815 | 3.6 | 110 | 7 | 356.4 | 0 | 268.935 | 0 | 1
3/25 | 10:00:00 | 282.15 | 98815 | 4.6 | 140 | 6.9044 | 579.6 | 14.4 | 268.889 | 0 | 1
3/25 | 11:00:00 | 283.15 | 98824 | 3.6 | 150 | 7.2931 | 964.8 | 43.2 | 269.914 | 0 | 1
3/25 | 12:00:00 | 283.15 | 98824 | 2.6 | 170 | 6.9514 | 1076.4 | 194.4 | 269.756 | 0 | 1
3/25 | 13:00:00 | 285.15 | 98841 | 5.1 | 180 | 6.8552 | 1980 | 1886.4 | 271.136 | 0 | 1
3/25 | 14:00:00 | 285.15 | 98841 | 6.2 | 170 | 6.487 | 1850.4 | 2322 | 270.953 | 0 | 1
3/25 | 15:00:00 | 286.15 | 98850 | 4.6 | 200 | 6.3971 | 1562.4 | 1771.2 | 271.858 | 0 | 1
3/25 | 16:00:00 | 286.15 | 98850 | 4.1 | 180 | 6.5314 | 1216.8 | 2030.4 | 271.66 | 0 | 1
3/25 | 17:00:00 | 285.15 | 98841 | 3.1 | 170 | 6.6688 | 698.4 | 1332 | 270.78 | 0 | 1
3/25 | 18:00:00 | 284.15 | 98833 | 3.1 | 160 | 6.354 | 205.2 | 345.6 | 269.935 | 0 | 1
3/25 | 19:00:00 | 284.15 | 98833 | 2.6 | 110 | 6.052 | 0 | 0 | 269.774 | 0 | 1
3/25 | 20:00:00 | 283.15 | 98824 | 0.5 | 55 | 6.1804 | 0 | 0 | 269.369 | 0 | 1
3/25 | 21:00:00 | 283.15 | 98824 | 5.1 | 120 | 6.3988 | 0 | 0 | 269.483 | 0 | 1
3/25 | 22:00:00 | 283.15 | 98824 | 6.7 | 130 | 6.1804 | 0 | 0 | 269.369 | 0 | 1
3/25 | 23:00:00 | 281.15 | 98806 | 5.1 | 160 | 6.1815 | 0 | 0 | 267.467 | 0 | 1
3/25 | 24:00:00 | 281.15 | 98806 | 8.7 | 180 | 6.1815 | 0 | 0 | 267.467 | 0 | 1
3/26 | 01:00:00 | 280.15 | 98798 | 7.7 | 190 | 6.182 | 0 | 0 | 266.515 | 0 | 1
3/26 | 02:00:00 | 280.15 | 98798 | 5.7 | 190 | 6.182 | 0 | 0 | 266.515 | 0 | 1
3/26 | 03:00:00 | 279.15 | 98789 | 5.7 | 210 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
3/26 | 04:00:00 | 279.15 | 98789 | 7.7 | 210 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
3/26 | 05:00:00 | 278.15 | 98780 | 6.7 | 220 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
3/26 | 06:00:00 | 279.15 | 98789 | 6.7 | 210 | 5.9708 | 0 | 0 | 264.982 | 0 | 1
3/26 | 07:00:00 | 279.15 | 98789 | 7.2 | 220 | 5.9708 | 82.8 | 0 | 264.982 | 0 | 1
3/26 | 08:00:00 | 280.15 | 98798 | 7.2 | 210 | 6.182 | 471.6 | 806.4 | 266.045 | 0 | 1
3/26 | 09:00:00 | 281.15 | 98806 | 7.2 | 210 | 5.1861 | 968.4 | 1472.4 | 266.423 | 0 | 1
3/26 | 10:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.1856 | 1425.6 | 1936.8 | 267.371 | 0 | 1
3/26 | 11:00:00 | 283.15 | 98824 | 6.7 | 220 | 5.5646 | 1771.2 | 1911.6 | 268.55 | 0 | 1
3/26 | 12:00:00 | 282.15 | 98815 | 7.2 | 210 | 5.1856 | 1976.4 | 2361.6 | 267.371 | 0 | 1
3/26 | 13:00:00 | 283.15 | 98824 | 7.2 | 210 | 5.1851 | 2012.4 | 2379.6 | 268.319 | 0 | 1
3/26 | 14:00:00 | 283.15 | 98824 | 6.7 | 210 | 5.1851 | 1879.2 | 2314.8 | 268.319 | 0 | 1
3/26 | 15:00:00 | 283.15 | 98824 | 7.2 | 210 | 5.1851 | 1587.6 | 1692 | 268.319 | 0 | 1
3/26 | 16:00:00 | 283.15 | 98824 | 5.1 | 210 | 5.5646 | 648 | 230.4 | 269.025 | 0 | 1
3/26 | 17:00:00 | 282.15 | 98815 | 5.7 | 200 | 5.9692 | 676.8 | 903.6 | 267.83 | 0 | 1
3/26 | 18:00:00 | 282.15 | 98815 | 4.6 | 200 | 5.5651 | 118.8 | 0 | 268.075 | 0 | 1
3/26 | 19:00:00 | 281.15 | 98806 | 2.1 | 250 | 5.1861 | 0 | 0 | 266.423 | 0 | 1
3/26 | 20:00:00 | 280.15 | 98798 | 0 | 328 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
3/26 | 21:00:00 | 280.15 | 98798 | 1.5 | 127 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
3/26 | 22:00:00 | 280.15 | 98798 | 2.6 | 230 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
3/26 | 23:00:00 | 279.15 | 98789 | 3.1 | 220 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
3/26 | 24:00:00 | 279.15 | 98789 | 2.6 | 240 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
3/27 | 01:00:00 | 279.15 | 98789 | 1.5 | 250 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
3/27 | 02:00:00 | 279.15 | 98789 | 1.5 | 230 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
3/27 | 03:00:00 | 279.15 | 98789 | 3.1 | 230 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
3/27 | 04:00:00 | 279.15 | 98789 | 2.6 | 240 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
3/27 | 05:00:00 | 279.15 | 98789 | 3.1 | 260 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
3/27 | 06:00:00 | 279.15 | 98789 | 5.1 | 260 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
3/27 | 07:00:00 | 279.15 | 98789 | 4.1 | 260 | 5.9708 | 90 | 0 | 264.982 | 0 | 1
3/27 | 08:00:00 | 279.15 | 98789 | 4.6 | 270 | 5.5666 | 489.6 | 676.8 | 264.756 | 0 | 1
3/27 | 09:00:00 | 279.15 | 98789 | 4.6 | 290 | 5.187 | 550.8 | 183.6 | 264.996 | 0 | 1
3/27 | 10:00:00 | 280.15 | 98798 | 5.1 | 280 | 5.1865 | 1447.2 | 1584 | 265.476 | 0 | 1
3/27 | 11:00:00 | 281.15 | 98806 | 7.2 | 300 | 4.4957 | 1803.6 | 1947.6 | 265.96 | 0 | 1
3/27 | 12:00:00 | 281.15 | 98806 | 9.3 | 290 | 4.4957 | 2005.2 | 1868.4 | 265.96 | 0 | 1
3/27 | 13:00:00 | 281.15 | 98806 | 8.2 | 270 | 4.8299 | 1130.4 | 280.8 | 266.664 | 0 | 1
3/27 | 14:00:00 | 281.15 | 98806 | 9.8 | 270 | 4.4957 | 1904.4 | 1504.8 | 265.96 | 0 | 1
3/27 | 15:00:00 | 281.15 | 98806 | 9.8 | 270 | 4.4957 | 896.4 | 316.8 | 266.431 | 0 | 1
3/27 | 16:00:00 | 281.15 | 98806 | 8.7 | 270 | 4.4957 | 662.4 | 61.2 | 266.431 | 0 | 1
3/27 | 17:00:00 | 281.15 | 98806 | 9.8 | 270 | 4.4957 | 385.2 | 28.8 | 266.431 | 0 | 1
3/27 | 18:00:00 | 280.15 | 98798 | 8.2 | 260 | 4.1826 | 230.4 | 248.4 | 264.782 | 0 | 1
3/27 | 19:00:00 | 279.15 | 98789 | 6.7 | 250 | 4.183 | 0 | 0 | 263.837 | 0 | 1
3/27 | 20:00:00 | 279.15 | 98789 | 5.1 | 250 | 4.183 | 0 | 0 | 263.578 | 0 | 1
3/27 | 21:00:00 | 279.15 | 98789 | 6.2 | 260 | 4.4964 | 0 | 0 | 264.069 | 0 | 1
3/27 | 22:00:00 | 279.15 | 98789 | 5.7 | 250 | 4.4964 | 0 | 0 | 263.81 | 0 | 1
3/27 | 23:00:00 | 279.15 | 98789 | 7.2 | 250 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
3/27 | 24:00:00 | 279.15 | 98789 | 6.2 | 250 | 5.187 | 0 | 0 | 264.269 | 0 | 1
3/28 | 01:00:00 | 278.15 | 98780 | 1.5 | 106 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
3/28 | 02:00:00 | 278.15 | 98780 | 2.1 | 250 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
3/28 | 03:00:00 | 278.15 | 98780 | 5.1 | 260 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
3/28 | 04:00:00 | 278.15 | 98780 | 4.6 | 270 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
3/28 | 05:00:00 | 278.15 | 98780 | 5.1 | 260 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
3/28 | 06:00:00 | 278.15 | 98780 | 6.7 | 260 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
3/28 | 07:00:00 | 277.15 | 98771 | 8.2 | 270 | 4.8316 | 104.4 | 25.2 | 262.149 | 0 | 1
3/28 | 08:00:00 | 278.15 | 98780 | 9.8 | 260 | 4.8311 | 540 | 1069.2 | 263.095 | 0 | 1
3/28 | 09:00:00 | 279.15 | 98789 | 10.3 | 260 | 4.8307 | 1072.8 | 1810.8 | 264.041 | 0 | 1
3/28 | 10:00:00 | 280.15 | 98798 | 10.8 | 260 | 4.496 | 1562.4 | 2404.8 | 264.755 | 0 | 1
3/28 | 11:00:00 | 281.15 | 98806 | 9.8 | 270 | 4.4957 | 1933.2 | 2617.2 | 265.7 | 0 | 1
3/28 | 12:00:00 | 280.15 | 98798 | 9.8 | 270 | 4.1826 | 2026.8 | 2264.4 | 264.782 | 0 | 1
3/28 | 13:00:00 | 282.15 | 98815 | 10.8 | 260 | 4.4952 | 2059.2 | 2412 | 266.906 | 0 | 1
3/28 | 14:00:00 | 282.15 | 98815 | 10.8 | 260 | 4.1819 | 1926 | 2361.6 | 266.672 | 0 | 1
3/28 | 15:00:00 | 282.15 | 98815 | 8.7 | 260 | 4.1819 | 1634.4 | 1623.6 | 266.672 | 0 | 1
3/28 | 16:00:00 | 281.15 | 98806 | 10.3 | 260 | 3.8882 | 1213.2 | 1440 | 265.492 | 0 | 1
3/28 | 17:00:00 | 281.15 | 98806 | 7.2 | 260 | 4.4957 | 712.8 | 1220.4 | 265.96 | 0 | 1
3/28 | 18:00:00 | 280.15 | 98798 | 8.7 | 250 | 4.496 | 255.6 | 352.8 | 264.755 | 0 | 1
3/28 | 19:00:00 | 279.15 | 98789 | 1.5 | 261 | 4.4964 | 0 | 0 | 264.069 | 0 | 1
3/28 | 20:00:00 | 278.15 | 98780 | 6.7 | 270 | 4.4968 | 0 | 0 | 262.865 | 0 | 1
3/28 | 21:00:00 | 277.15 | 98771 | 2.1 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/28 | 22:00:00 | 277.15 | 98771 | 4.6 | 260 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/28 | 23:00:00 | 277.15 | 98771 | 3.1 | 250 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/28 | 24:00:00 | 277.15 | 98771 | 5.1 | 260 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/29 | 01:00:00 | 277.15 | 98771 | 4.6 | 260 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/29 | 02:00:00 | 277.15 | 98771 | 3.1 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
3/29 | 03:00:00 | 276.15 | 98762 | 0 | 132 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
3/29 | 04:00:00 | 276.15 | 98762 | 0 | 26 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
3/29 | 05:00:00 | 276.15 | 98762 | 0 | 173 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
3/29 | 06:00:00 | 276.15 | 98762 | 0 | 58 | 4.832 | 0 | 0 | 260.786 | 0 | 1
3/29 | 07:00:00 | 276.15 | 98762 | 0 | 216 | 4.4977 | 115.2 | 61.2 | 260.975 | 0 | 1
3/29 | 08:00:00 | 277.15 | 98771 | 0 | 8 | 4.8316 | 561.6 | 1101.6 | 262.149 | 0 | 1
3/29 | 09:00:00 | 277.15 | 98771 | 1 | 83 | 4.8316 | 1033.2 | 1288.8 | 262.405 | 0 | 1
3/29 | 10:00:00 | 277.15 | 98771 | 3.1 | 120 | 4.8316 | 828 | 140.4 | 262.87 | 0 | 1
3/29 | 11:00:00 | 277.15 | 98771 | 4.6 | 120 | 4.8316 | 1022.4 | 226.8 | 262.87 | 0 | 1
3/29 | 12:00:00 | 277.15 | 98771 | 4.6 | 120 | 5.1879 | 1130.4 | 234 | 263.098 | 0 | 1
3/29 | 13:00:00 | 277.15 | 98771 | 4.6 | 110 | 5.1879 | 1148.4 | 237.6 | 263.098 | 0 | 1
3/29 | 14:00:00 | 277.15 | 98771 | 5.7 | 110 | 5.1879 | 1072.8 | 230.4 | 263.098 | 0 | 1
3/29 | 15:00:00 | 277.15 | 98771 | 5.1 | 90 | 5.1879 | 910.8 | 151.2 | 263.098 | 0 | 1
3/29 | 16:00:00 | 277.15 | 98771 | 4.6 | 90 | 5.1879 | 414 | 0 | 263.204 | 0 | 1
3/29 | 17:00:00 | 278.15 | 98780 | 4.1 | 90 | 5.5671 | 244.8 | 0 | 264.381 | 0 | 1
3/29 | 18:00:00 | 278.15 | 98780 | 3.6 | 70 | 5.5671 | 140.4 | 0 | 264.274 | 0 | 1
3/29 | 19:00:00 | 278.15 | 98780 | 4.1 | 70 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
3/29 | 20:00:00 | 278.15 | 98780 | 3.1 | 70 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
3/29 | 21:00:00 | 278.15 | 98780 | 2.6 | 70 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
3/29 | 22:00:00 | 279.15 | 98789 | 2.6 | 130 | 5.9708 | 0 | 0 | 265.559 | 0 | 1
3/29 | 23:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
3/29 | 24:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
3/30 | 01:00:00 | 281.15 | 98806 | 2.6 | 150 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
3/30 | 02:00:00 | 281.15 | 98806 | 2.1 | 160 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
3/30 | 03:00:00 | 280.15 | 98798 | 1.5 | 170 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
3/30 | 04:00:00 | 280.15 | 98798 | 1 | 170 | 6.4005 | 0 | 0 | 265.897 | 0 | 1
3/30 | 05:00:00 | 280.15 | 98798 | 2.6 | 160 | 6.4005 | 0 | 0 | 265.897 | 0 | 1
3/30 | 06:00:00 | 280.15 | 98798 | 3.1 | 160 | 6.4005 | 0 | 0 | 266.157 | 0 | 1
3/30 | 07:00:00 | 280.15 | 98798 | 4.6 | 150 | 6.4005 | 118.8 | 25.2 | 266.157 | 0 | 1
3/30 | 08:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 302.4 | 0 | 267.805 | 0 | 1
3/30 | 09:00:00 | 281.15 | 98806 | 4.6 | 130 | 6.8577 | 579.6 | 46.8 | 267.805 | 0 | 1
3/30 | 10:00:00 | 281.15 | 98806 | 4.1 | 140 | 6.8577 | 835.2 | 140.4 | 267.805 | 0 | 1
3/30 | 11:00:00 | 282.15 | 98815 | 4.1 | 140 | 6.8571 | 1026 | 219.6 | 268.758 | 0 | 1
3/30 | 12:00:00 | 280.15 | 98798 | 5.1 | 170 | 5.9703 | 1137.6 | 198 | 266.402 | 0 | 1
3/30 | 13:00:00 | 280.15 | 98798 | 3.6 | 120 | 5.9703 | 2084.4 | 1364.4 | 265.931 | 0 | 1
3/30 | 14:00:00 | 281.15 | 98806 | 5.1 | 120 | 6.4 | 1080 | 194.4 | 267.58 | 0 | 1
3/30 | 15:00:00 | 281.15 | 98806 | 4.6 | 120 | 6.4 | 918 | 151.2 | 267.58 | 0 | 1
3/30 | 16:00:00 | 282.15 | 98815 | 5.7 | 110 | 6.3994 | 684 | 57.6 | 268.532 | 0 | 1
3/30 | 17:00:00 | 282.15 | 98815 | 5.7 | 140 | 5.9692 | 410.4 | 32.4 | 268.304 | 0 | 1
3/30 | 18:00:00 | 280.15 | 98798 | 4.6 | 110 | 5.5661 | 262.8 | 493.2 | 265.704 | 0 | 1
3/30 | 19:00:00 | 278.15 | 98780 | 2.1 | 120 | 5.5671 | 0 | 0 | 263.807 | 0 | 1
3/30 | 20:00:00 | 278.15 | 98780 | 1.5 | 109 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
3/30 | 21:00:00 | 279.15 | 98789 | 2.1 | 70 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
3/30 | 22:00:00 | 277.15 | 98771 | 3.6 | 230 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
3/30 | 23:00:00 | 274.15 | 98743 | 5.7 | 230 | 4.185 | 0 | 0 | 259.569 | 0 | 1
3/30 | 24:00:00 | 273.15 | 98734 | 3.1 | 210 | 3.891 | 0 | 0 | 258.394 | 0 | 1
3/31 | 01:00:00 | 274.15 | 98743 | 2.1 | 180 | 4.185 | 0 | 0 | 259.569 | 0 | 1
3/31 | 02:00:00 | 274.15 | 98743 | 1 | 160 | 4.185 | 0 | 0 | 259.569 | 0 | 1
3/31 | 03:00:00 | 274.15 | 98743 | 0.5 | 341 | 4.185 | 0 | 0 | 259.569 | 0 | 1
3/31 | 04:00:00 | 274.15 | 98743 | 0 | 226 | 4.185 | 0 | 0 | 259.569 | 0 | 1
3/31 | 05:00:00 | 274.15 | 98743 | 0 | 49 | 4.185 | 0 | 0 | 259.569 | 0 | 1
3/31 | 06:00:00 | 274.15 | 98743 | 0 | 356 | 4.185 | 0 | 0 | 259.569 | 0 | 1
3/31 | 07:00:00 | 274.15 | 98743 | 1 | 290 | 4.185 | 133.2 | 46.8 | 259.111 | 0 | 1
3/31 | 08:00:00 | 275.15 | 98752 | 0 | 241 | 4.4981 | 316.8 | 3.6 | 260.745 | 0 | 1
3/31 | 09:00:00 | 276.15 | 98762 | 3.6 | 310 | 4.4977 | 597.6 | 50.4 | 261.693 | 0 | 1
3/31 | 10:00:00 | 276.15 | 98762 | 3.6 | 310 | 4.4977 | 853.2 | 302.4 | 261.693 | 0 | 1
3/31 | 11:00:00 | 277.15 | 98771 | 5.7 | 280 | 4.8316 | 1886.4 | 2012.4 | 262.405 | 0 | 1
3/31 | 12:00:00 | 276.15 | 98762 | 4.1 | 300 | 4.832 | 2084.4 | 1886.4 | 261.459 | 0 | 1
3/31 | 13:00:00 | 277.15 | 98771 | 9.3 | 290 | 4.4973 | 1173.6 | 205.2 | 262.64 | 0 | 1
3/31 | 14:00:00 | 277.15 | 98771 | 10.8 | 300 | 4.4973 | 1098 | 234 | 262.64 | 0 | 1
3/31 | 15:00:00 | 276.15 | 98762 | 9.3 | 300 | 3.8899 | 936 | 158.4 | 261.231 | 0 | 1
3/31 | 16:00:00 | 277.15 | 98771 | 9.3 | 290 | 3.8896 | 1263.6 | 1422 | 261.714 | 0 | 1
3/31 | 17:00:00 | 276.15 | 98762 | 9.3 | 290 | 3.8899 | 759.6 | 1040.4 | 260.77 | 0 | 1
3/31 | 18:00:00 | 276.15 | 98762 | 8.7 | 280 | 4.1841 | 277.2 | 244.8 | 261.001 | 0 | 1
3/31 | 19:00:00 | 274.65 | 98748 | 6.3 | 275 | 3.8905 | 7.2 | 0 | 259.1 | 0 | 1
3/31 | 20:00:00 | 274.35 | 98745 | 6.2 | 272 | 3.8906 | 0 | 0 | 258.817 | 0 | 1
3/31 | 21:00:00 | 274.15 | 98743 | 5.4 | 272 | 3.8267 | 0 | 0 | 258.582 | 0 | 1
3/31 | 22:00:00 | 276.15 | 98761 | 4.7 | 250 | 4.4334 | 0 | 0 | 260.929 | 0 | 1
3/31 | 23:00:00 | 277.95 | 98777 | 3.5 | 237 | 5.0066 | 0 | 0 | 263.02 | 0 | 1
3/31 | 24:00:00 | 279.35 | 98791 | 2.6 | 205 | 5.5665 | 0 | 0 | 265.414 | 0 | 1
4/1 | 01:00:00 | 280.95 | 98804 | 2.4 | 170 | 6.3119 | 0 | 0 | 266.611 | 0 | 1
4/1 | 02:00:00 | 280.15 | 98798 | 2.3 | 160 | 6.0542 | 0 | 0 | 266.555 | 0 | 1
4/1 | 03:00:00 | 279.35 | 98791 | 2.6 | 135 | 5.8878 | 0 | 0 | 265.704 | 0 | 1
4/1 | 04:00:00 | 279.15 | 98789 | 2.6 | 132 | 5.8879 | 0 | 0 | 265.513 | 0 | 1
4/1 | 05:00:00 | 279.15 | 98789 | 2.2 | 184 | 5.9708 | 0 | 0 | 265.559 | 0 | 1
4/1 | 06:00:00 | 279.65 | 98793 | 1.9 | 148 | 6.0545 | 0 | 0 | 266.08 | 0 | 1
4/1 | 07:00:00 | 279.15 | 98789 | 3.1 | 130 | 5.9708 | 79.2 | 0 | 265.451 | 0 | 1
4/1 | 08:00:00 | 280.15 | 98798 | 1 | 348 | 6.4005 | 583.2 | 770.4 | 266.157 | 0 | 1
4/1 | 09:00:00 | 281.15 | 98806 | 1 | 6 | 6.4 | 1090.8 | 1299.6 | 267.107 | 0 | 1
4/1 | 10:00:00 | 282.15 | 98815 | 3.1 | 110 | 6.3994 | 860.4 | 140.4 | 268.532 | 0 | 1
4/1 | 11:00:00 | 281.15 | 98806 | 2.1 | 170 | 6.4 | 1051.2 | 190.8 | 267.58 | 0 | 1
4/1 | 12:00:00 | 283.15 | 98824 | 2.1 | 239 | 6.8564 | 2088 | 1911.6 | 269.234 | 0 | 1
4/1 | 13:00:00 | 283.15 | 98824 | 5.1 | 250 | 6.3988 | 2120.4 | 2358 | 269.007 | 0 | 1
4/1 | 14:00:00 | 283.15 | 98824 | 5.1 | 290 | 6.8564 | 1980 | 2336.4 | 269.234 | 0 | 1
4/1 | 15:00:00 | 283.15 | 98824 | 4.6 | 290 | 7.3431 | 1684.8 | 2077.2 | 269.46 | 0 | 1
4/1 | 16:00:00 | 283.15 | 98824 | 6.2 | 290 | 6.8564 | 1263.6 | 1742.4 | 269.234 | 0 | 1
4/1 | 17:00:00 | 284.15 | 98833 | 8.2 | 290 | 6.3982 | 813.6 | 1461.6 | 269.693 | 0 | 1
4/1 | 18:00:00 | 283.15 | 98824 | 5.1 | 280 | 6.3988 | 284.4 | 331.2 | 269.007 | 0 | 1
4/1 | 19:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.3988 | 14.4 | 0 | 268.744 | 0 | 1
4/1 | 20:00:00 | 281.15 | 98806 | 5.7 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
4/1 | 21:00:00 | 281.15 | 98806 | 5.7 | 280 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
4/1 | 22:00:00 | 280.15 | 98798 | 4.6 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
4/1 | 23:00:00 | 280.15 | 98798 | 6.7 | 280 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
4/1 | 24:00:00 | 280.15 | 98798 | 5.7 | 290 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
4/2 | 01:00:00 | 280.15 | 98798 | 3.6 | 290 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
4/2 | 02:00:00 | 279.15 | 98789 | 3.6 | 300 | 5.9708 | 0 | 0 | 264.723 | 0 | 1
4/2 | 03:00:00 | 279.15 | 98789 | 3.6 | 310 | 5.5666 | 0 | 0 | 264.497 | 0 | 1
4/2 | 04:00:00 | 278.15 | 98780 | 4.1 | 270 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
4/2 | 05:00:00 | 278.15 | 98780 | 4.1 | 270 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
4/2 | 06:00:00 | 278.15 | 98780 | 4.1 | 270 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
4/2 | 07:00:00 | 279.15 | 98789 | 3.6 | 290 | 5.5666 | 90 | 0 | 265.224 | 0 | 1
4/2 | 08:00:00 | 279.15 | 98789 | 3.6 | 320 | 5.5666 | 205.2 | 0 | 265.332 | 0 | 1
4/2 | 09:00:00 | 280.15 | 98798 | 3.1 | 310 | 5.5661 | 619.2 | 100.8 | 266.174 | 0 | 1
4/2 | 10:00:00 | 280.15 | 98798 | 1.5 | 95 | 6.4005 | 871.2 | 144 | 266.628 | 0 | 1
4/2 | 11:00:00 | 281.15 | 98806 | 2.1 | 20 | 6.4 | 1062 | 190.8 | 267.58 | 0 | 1
4/2 | 12:00:00 | 283.15 | 98824 | 1 | 124 | 5.9687 | 2113.2 | 1926 | 268.779 | 0 | 1
4/2 | 13:00:00 | 283.15 | 98824 | 1 | 120 | 5.9687 | 2145.6 | 2376 | 268.779 | 0 | 1
4/2 | 14:00:00 | 285.15 | 98841 | 1.5 | 137 | 5.9676 | 2005.2 | 1882.8 | 270.678 | 0 | 1
4/2 | 15:00:00 | 284.15 | 98833 | 1.5 | 6 | 5.5641 | 950.4 | 388.8 | 269.975 | 0 | 1
4/2 | 16:00:00 | 284.15 | 98833 | 1.5 | 202 | 5.5641 | 1288.8 | 1443.6 | 269.498 | 0 | 1
4/2 | 17:00:00 | 285.15 | 98841 | 2.1 | 230 | 5.5636 | 784.8 | 1281.6 | 270.447 | 0 | 1
4/2 | 18:00:00 | 285.15 | 98841 | 3.6 | 290 | 5.9676 | 316.8 | 446.4 | 270.413 | 0 | 1
4/2 | 19:00:00 | 283.15 | 98824 | 2.6 | 270 | 5.5646 | 18 | 0 | 268.55 | 0 | 1
4/2 | 20:00:00 | 281.15 | 98806 | 3.1 | 290 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
4/2 | 21:00:00 | 280.15 | 98798 | 2.6 | 270 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
4/2 | 22:00:00 | 279.15 | 98789 | 0 | 306 | 5.187 | 0 | 0 | 264.269 | 0 | 1
4/2 | 23:00:00 | 279.15 | 98789 | 1.5 | 220 | 5.187 | 0 | 0 | 264.269 | 0 | 1
4/2 | 24:00:00 | 278.15 | 98780 | 1.5 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
4/3 | 01:00:00 | 279.15 | 98789 | 0.5 | 166 | 5.187 | 0 | 0 | 264.996 | 0 | 1
4/3 | 02:00:00 | 277.15 | 98771 | 1 | 55 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
4/3 | 03:00:00 | 277.15 | 98771 | 1.5 | 189 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
4/3 | 04:00:00 | 277.15 | 98771 | 3.1 | 160 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
4/3 | 05:00:00 | 276.15 | 98762 | 2.1 | 140 | 4.832 | 0 | 0 | 262.027 | 0 | 1
4/3 | 06:00:00 | 276.15 | 98762 | 1 | 9 | 4.4977 | 0 | 0 | 260.558 | 0 | 1
4/3 | 07:00:00 | 276.15 | 98762 | 2.1 | 160 | 4.832 | 187.2 | 208.8 | 260.786 | 0 | 1
4/3 | 08:00:00 | 279.15 | 98789 | 2.6 | 180 | 5.5666 | 669.6 | 1285.2 | 264.075 | 0 | 1
4/3 | 09:00:00 | 281.15 | 98806 | 2.6 | 170 | 5.5656 | 1220.4 | 1980 | 265.967 | 0 | 1
4/3 | 10:00:00 | 283.15 | 98824 | 4.1 | 170 | 5.5646 | 1692 | 2451.6 | 268.287 | 0 | 1
4/3 | 11:00:00 | 286.15 | 98850 | 4.1 | 210 | 5.9671 | 2055.6 | 2732.4 | 271.361 | 0 | 1
4/3 | 12:00:00 | 286.15 | 98850 | 5.7 | 210 | 4.8277 | 2275.2 | 2887.2 | 270.662 | 0 | 1
4/3 | 13:00:00 | 287.15 | 98858 | 5.1 | 210 | 5.1833 | 2300.4 | 2887.2 | 271.843 | 0 | 1
4/3 | 14:00:00 | 288.15 | 98867 | 6.7 | 200 | 4.4929 | 2160 | 2840.4 | 272.316 | 0 | 1
4/3 | 15:00:00 | 288.15 | 98867 | 5.1 | 210 | 4.8269 | 1839.6 | 2541.6 | 272.553 | 0 | 1
4/3 | 16:00:00 | 287.15 | 98858 | 5.7 | 200 | 4.8273 | 1386 | 2041.2 | 271.608 | 0 | 1
4/3 | 17:00:00 | 286.15 | 98850 | 5.1 | 210 | 5.1837 | 849.6 | 1512 | 270.896 | 0 | 1
4/3 | 18:00:00 | 286.15 | 98850 | 4.6 | 210 | 5.1837 | 327.6 | 468 | 270.896 | 0 | 1
4/3 | 19:00:00 | 286.15 | 98850 | 5.7 | 220 | 5.5631 | 25.2 | 0 | 271.13 | 0 | 1
4/3 | 20:00:00 | 284.15 | 98833 | 4.6 | 220 | 5.5641 | 0 | 0 | 269.234 | 0 | 1
4/3 | 21:00:00 | 284.15 | 98833 | 3.1 | 210 | 5.5641 | 0 | 0 | 269.234 | 0 | 1
4/3 | 22:00:00 | 283.15 | 98824 | 3.1 | 210 | 5.5646 | 0 | 0 | 268.55 | 0 | 1
4/3 | 23:00:00 | 283.15 | 98824 | 5.1 | 230 | 5.5646 | 0 | 0 | 268.55 | 0 | 1
4/3 | 24:00:00 | 283.15 | 98824 | 6.7 | 230 | 5.9687 | 0 | 0 | 268.779 | 0 | 1
4/4 | 01:00:00 | 282.15 | 98815 | 4.6 | 230 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
4/4 | 02:00:00 | 282.15 | 98815 | 3.6 | 240 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
4/4 | 03:00:00 | 282.15 | 98815 | 4.1 | 240 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
4/4 | 04:00:00 | 282.15 | 98815 | 1.5 | 290 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
4/4 | 05:00:00 | 282.15 | 98815 | 2.6 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
4/4 | 06:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
4/4 | 07:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.8571 | 104.4 | 0 | 268.758 | 0 | 1
4/4 | 08:00:00 | 282.15 | 98815 | 6.2 | 290 | 6.8571 | 356.4 | 10.8 | 268.758 | 0 | 1
4/4 | 09:00:00 | 283.15 | 98824 | 3.6 | 310 | 7.3431 | 637.2 | 50.4 | 269.936 | 0 | 1
4/4 | 10:00:00 | 283.15 | 98824 | 2.6 | 350 | 6.3988 | 892.8 | 144 | 269.483 | 0 | 1
4/4 | 11:00:00 | 284.15 | 98833 | 4.1 | 310 | 6.3982 | 1083.6 | 223.2 | 270.435 | 0 | 1
4/4 | 12:00:00 | 283.15 | 98824 | 5.1 | 300 | 6.3988 | 1191.6 | 198 | 269.483 | 0 | 1
4/4 | 13:00:00 | 284.15 | 98833 | 4.1 | 320 | 5.9681 | 2181.6 | 1944 | 269.728 | 0 | 1
4/4 | 14:00:00 | 285.15 | 98841 | 4.6 | 290 | 5.5636 | 2044.8 | 2250 | 270.447 | 0 | 1
4/4 | 15:00:00 | 286.15 | 98850 | 5.1 | 310 | 4.8277 | 1857.6 | 2548.8 | 270.662 | 0 | 1
4/4 | 16:00:00 | 286.15 | 98850 | 5.1 | 300 | 5.1837 | 1404 | 2052 | 270.896 | 0 | 1
4/4 | 17:00:00 | 285.15 | 98841 | 5.7 | 280 | 5.1842 | 867.6 | 1530 | 269.95 | 0 | 1
4/4 | 18:00:00 | 284.15 | 98833 | 5.7 | 280 | 5.5641 | 342 | 504 | 269.234 | 0 | 1
4/4 | 19:00:00 | 282.15 | 98815 | 7.2 | 290 | 5.1856 | 28.8 | 0 | 267.11 | 0 | 1
4/4 | 20:00:00 | 281.15 | 98806 | 7.2 | 300 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
4/4 | 21:00:00 | 280.15 | 98798 | 5.7 | 290 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
4/4 | 22:00:00 | 279.15 | 98789 | 5.7 | 290 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
4/4 | 23:00:00 | 279.15 | 98789 | 3.6 | 290 | 4.4964 | 0 | 0 | 264.31 | 0 | 1
4/4 | 24:00:00 | 278.15 | 98780 | 1.5 | 292 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
4/5 | 01:00:00 | 278.15 | 98780 | 5.1 | 280 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
4/5 | 02:00:00 | 278.15 | 98780 | 4.1 | 290 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
4/5 | 03:00:00 | 278.15 | 98780 | 4.6 | 280 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
4/5 | 04:00:00 | 279.15 | 98789 | 11.3 | 280 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
4/5 | 05:00:00 | 279.15 | 98789 | 7.7 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
4/5 | 06:00:00 | 279.15 | 98789 | 7.2 | 290 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
4/5 | 07:00:00 | 279.15 | 98789 | 4.1 | 270 | 5.187 | 212.4 | 248.4 | 264.269 | 0 | 1
4/5 | 08:00:00 | 280.15 | 98798 | 7.2 | 290 | 5.1865 | 705.6 | 1296 | 265.216 | 0 | 1
4/5 | 09:00:00 | 281.15 | 98806 | 7.2 | 300 | 5.1861 | 1180.8 | 1681.2 | 266.423 | 0 | 1
4/5 | 10:00:00 | 282.15 | 98815 | 5.1 | 310 | 5.1856 | 1641.6 | 2073.6 | 267.371 | 0 | 1
4/5 | 11:00:00 | 283.15 | 98824 | 6.2 | 300 | 5.1851 | 1983.6 | 2322 | 268.319 | 0 | 1
4/5 | 12:00:00 | 284.15 | 98833 | 6.7 | 290 | 5.5641 | 2174.4 | 2386.8 | 269.498 | 0 | 1
4/5 | 13:00:00 | 285.15 | 98841 | 7.7 | 280 | 5.5636 | 2203.2 | 2397.6 | 270.447 | 0 | 1
4/5 | 14:00:00 | 284.15 | 98833 | 6.7 | 270 | 5.5641 | 2062.8 | 2343.6 | 269.498 | 0 | 1
4/5 | 15:00:00 | 284.15 | 98833 | 9.3 | 280 | 5.5641 | 1764 | 2149.2 | 269.498 | 0 | 1
4/5 | 16:00:00 | 283.15 | 98824 | 8.2 | 280 | 5.9687 | 1335.6 | 1717.2 | 268.779 | 0 | 1
4/5 | 17:00:00 | 283.15 | 98824 | 6.7 | 260 | 5.9687 | 828 | 1267.2 | 268.779 | 0 | 1
4/5 | 18:00:00 | 282.15 | 98815 | 5.1 | 280 | 5.9692 | 334.8 | 414 | 267.83 | 0 | 1
4/5 | 19:00:00 | 282.15 | 98815 | 6.2 | 280 | 5.5651 | 32.4 | 0 | 267.601 | 0 | 1
4/5 | 20:00:00 | 281.15 | 98806 | 5.7 | 280 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
4/5 | 21:00:00 | 280.15 | 98798 | 4.6 | 300 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
4/5 | 22:00:00 | 279.15 | 98789 | 3.6 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
4/5 | 23:00:00 | 278.15 | 98780 | 3.6 | 260 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
4/5 | 24:00:00 | 278.15 | 98780 | 3.1 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
4/6 | 01:00:00 | 277.15 | 98771 | 3.6 | 280 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
4/6 | 02:00:00 | 277.15 | 98771 | 3.1 | 280 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
4/6 | 03:00:00 | 277.15 | 98771 | 3.6 | 290 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
4/6 | 04:00:00 | 276.15 | 98762 | 3.6 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
4/6 | 05:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.832 | 0 | 0 | 262.027 | 0 | 1
4/6 | 06:00:00 | 276.15 | 98762 | 3.6 | 290 | 4.832 | 0 | 0 | 261.203 | 0 | 1
4/6 | 07:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.832 | 230.4 | 277.2 | 261.203 | 0 | 1
4/6 | 08:00:00 | 278.15 | 98780 | 4.6 | 260 | 5.1875 | 727.2 | 1321.2 | 263.323 | 0 | 1
4/6 | 09:00:00 | 279.15 | 98789 | 5.7 | 270 | 5.5666 | 1198.8 | 1684.8 | 264.756 | 0 | 1
4/6 | 10:00:00 | 281.15 | 98806 | 5.7 | 270 | 5.5656 | 1659.6 | 1681.2 | 266.653 | 0 | 1
4/6 | 11:00:00 | 282.15 | 98815 | 7.7 | 270 | 5.5651 | 1112.4 | 194.4 | 268.075 | 0 | 1
4/6 | 12:00:00 | 282.15 | 98815 | 7.2 | 280 | 5.5651 | 1216.8 | 237.6 | 268.075 | 0 | 1
4/6 | 13:00:00 | 282.15 | 98815 | 7.2 | 290 | 5.5651 | 1231.2 | 205.2 | 268.075 | 0 | 1
4/6 | 14:00:00 | 282.15 | 98815 | 7.2 | 280 | 5.5651 | 2080.8 | 1886.4 | 267.601 | 0 | 1
4/6 | 15:00:00 | 282.15 | 98815 | 9.3 | 280 | 5.1856 | 1782 | 2163.6 | 267.371 | 0 | 1
4/6 | 16:00:00 | 281.15 | 98806 | 9.8 | 280 | 5.1861 | 1353.6 | 1742.4 | 266.423 | 0 | 1
4/6 | 17:00:00 | 282.15 | 98815 | 9.8 | 280 | 5.1856 | 846 | 1296 | 267.371 | 0 | 1
4/6 | 18:00:00 | 281.15 | 98806 | 11.8 | 280 | 5.1861 | 349.2 | 435.6 | 266.423 | 0 | 1
4/6 | 19:00:00 | 280.15 | 98798 | 10.8 | 280 | 5.1865 | 39.6 | 0 | 265.476 | 0 | 1
4/6 | 20:00:00 | 280.15 | 98798 | 8.2 | 290 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
4/6 | 21:00:00 | 280.15 | 98798 | 6.2 | 280 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
4/6 | 22:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.5666 | 0 | 0 | 264.497 | 0 | 1
4/6 | 23:00:00 | 279.15 | 98789 | 5.7 | 280 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
4/6 | 24:00:00 | 279.15 | 98789 | 5.1 | 270 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
4/7 | 01:00:00 | 279.15 | 98789 | 4.1 | 280 | 5.5666 | 0 | 0 | 264.497 | 0 | 1
4/7 | 02:00:00 | 279.15 | 98789 | 3.6 | 270 | 5.5666 | 0 | 0 | 264.497 | 0 | 1
4/7 | 03:00:00 | 278.15 | 98780 | 4.1 | 270 | 5.5671 | 0 | 0 | 263.549 | 0 | 1
4/7 | 04:00:00 | 279.15 | 98789 | 4.6 | 280 | 5.9708 | 0 | 0 | 265.559 | 0 | 1
4/7 | 05:00:00 | 279.15 | 98789 | 5.1 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
4/7 | 06:00:00 | 280.15 | 98798 | 3.6 | 290 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/7 | 07:00:00 | 280.15 | 98798 | 4.6 | 290 | 5.1865 | 129.6 | 0 | 265.946 | 0 | 1
4/7 | 08:00:00 | 280.15 | 98798 | 4.6 | 290 | 5.1865 | 388.8 | 21.6 | 265.946 | 0 | 1
4/7 | 09:00:00 | 280.15 | 98798 | 4.6 | 310 | 5.1865 | 676.8 | 57.6 | 265.946 | 0 | 1
4/7 | 10:00:00 | 281.15 | 98806 | 5.1 | 310 | 4.8299 | 936 | 151.2 | 266.664 | 0 | 1
4/7 | 11:00:00 | 281.15 | 98806 | 4.1 | 290 | 5.1861 | 1123.2 | 230.4 | 266.895 | 0 | 1
4/7 | 12:00:00 | 281.15 | 98806 | 4.1 | 300 | 4.8299 | 1231.2 | 237.6 | 266.664 | 0 | 1
4/7 | 13:00:00 | 282.15 | 98815 | 4.1 | 290 | 5.1856 | 1245.6 | 90 | 267.844 | 0 | 1
4/7 | 14:00:00 | 282.15 | 98815 | 5.1 | 280 | 5.1856 | 709.2 | 7.2 | 267.953 | 0 | 1
4/7 | 15:00:00 | 282.15 | 98815 | 4.1 | 290 | 5.1856 | 997.2 | 324 | 267.844 | 0 | 1
4/7 | 16:00:00 | 284.15 | 98833 | 4.6 | 270 | 5.1847 | 1454.4 | 1789.2 | 269.003 | 0 | 1
4/7 | 17:00:00 | 283.15 | 98824 | 5.1 | 280 | 5.1851 | 914.4 | 1576.8 | 268.056 | 0 | 1
4/7 | 18:00:00 | 282.15 | 98815 | 4.6 | 280 | 5.1856 | 342 | 450 | 267.495 | 0 | 1
4/7 | 19:00:00 | 281.15 | 98806 | 3.1 | 270 | 4.8299 | 39.6 | 0 | 266.316 | 0 | 1
4/7 | 20:00:00 | 279.15 | 98789 | 2.6 | 260 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
4/7 | 21:00:00 | 278.15 | 98780 | 2.1 | 260 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
4/7 | 22:00:00 | 278.15 | 98780 | 2.1 | 270 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
4/7 | 23:00:00 | 277.15 | 98771 | 2.6 | 270 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
4/7 | 24:00:00 | 276.15 | 98762 | 1.5 | 290 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
4/8 | 01:00:00 | 275.15 | 98752 | 3.1 | 260 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
4/8 | 02:00:00 | 276.15 | 98762 | 2.6 | 260 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
4/8 | 03:00:00 | 276.15 | 98762 | 1.5 | 270 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
4/8 | 04:00:00 | 276.15 | 98762 | 1.5 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
4/8 | 05:00:00 | 275.15 | 98752 | 1.5 | 280 | 4.1846 | 0 | 0 | 259.387 | 0 | 1
4/8 | 06:00:00 | 276.15 | 98762 | 0 | 124 | 4.4977 | 0 | 0 | 260.558 | 0 | 1
4/8 | 07:00:00 | 277.15 | 98771 | 0.5 | 140 | 4.8316 | 262.8 | 349.2 | 261.73 | 0 | 1
4/8 | 08:00:00 | 279.15 | 98789 | 1 | 108 | 5.187 | 777.6 | 1429.2 | 263.847 | 0 | 1
4/8 | 09:00:00 | 281.15 | 98806 | 1 | 107 | 5.5656 | 1335.6 | 1893.6 | 265.967 | 0 | 1
4/8 | 10:00:00 | 283.15 | 98824 | 1.5 | 42 | 5.9687 | 1497.6 | 1220.4 | 269.025 | 0 | 1
4/8 | 11:00:00 | 285.15 | 98841 | 2.1 | 180 | 6.3977 | 2188.8 | 2520 | 270.21 | 0 | 1
4/8 | 12:00:00 | 287.15 | 98858 | 2.6 | 200 | 6.854 | 2386.8 | 2941.2 | 272.335 | 0 | 1
4/8 | 13:00:00 | 289.15 | 98875 | 3.1 | 160 | 6.8529 | 2347.2 | 2710.8 | 274.807 | 0 | 1
4/8 | 14:00:00 | 290.15 | 98883 | 2.6 | 150 | 6.8523 | 2228.4 | 2761.2 | 275.62 | 0 | 1
4/8 | 15:00:00 | 291.15 | 98892 | 3.1 | 170 | 6.3944 | 1936.8 | 2682 | 276.195 | 0 | 1
4/8 | 16:00:00 | 291.15 | 98892 | 3.1 | 180 | 6.3944 | 1479.6 | 2174.4 | 276.195 | 0 | 1
4/8 | 17:00:00 | 291.15 | 98892 | 3.1 | 210 | 5.9645 | 939.6 | 1634.4 | 275.961 | 0 | 1
4/8 | 18:00:00 | 291.15 | 98892 | 2.6 | 230 | 5.5607 | 399.6 | 759.6 | 275.578 | 0 | 1
4/8 | 19:00:00 | 288.15 | 98867 | 1.5 | 283 | 5.1829 | 50.4 | 0 | 272.649 | 0 | 1
4/8 | 20:00:00 | 287.15 | 98858 | 1.5 | 230 | 5.1833 | 0 | 0 | 271.843 | 0 | 1
4/8 | 21:00:00 | 287.15 | 98858 | 1 | 129 | 5.1833 | 0 | 0 | 271.843 | 0 | 1
4/8 | 22:00:00 | 283.15 | 98824 | 3.1 | 190 | 5.1851 | 0 | 0 | 268.319 | 0 | 1
4/8 | 23:00:00 | 285.15 | 98841 | 1 | 166 | 5.1842 | 0 | 0 | 270.084 | 0 | 1
4/8 | 24:00:00 | 285.15 | 98841 | 1.5 | 230 | 5.1842 | 0 | 0 | 270.084 | 0 | 1
4/9 | 01:00:00 | 283.15 | 98824 | 2.1 | 180 | 5.1851 | 0 | 0 | 268.319 | 0 | 1
4/9 | 02:00:00 | 282.15 | 98815 | 2.6 | 210 | 5.5651 | 0 | 0 | 267.846 | 0 | 1
4/9 | 03:00:00 | 285.15 | 98841 | 5.1 | 230 | 6.3977 | 0 | 0 | 271.033 | 0 | 1
4/9 | 04:00:00 | 284.15 | 98833 | 4.1 | 220 | 6.3982 | 0 | 0 | 270.204 | 0 | 1
4/9 | 05:00:00 | 283.15 | 98824 | 2.6 | 210 | 5.9687 | 0 | 0 | 269.025 | 0 | 1
4/9 | 06:00:00 | 282.15 | 98815 | 2.1 | 240 | 5.5651 | 3.6 | 0 | 267.846 | 0 | 1
4/9 | 07:00:00 | 282.15 | 98815 | 2.1 | 240 | 5.5651 | 230.4 | 133.2 | 267.846 | 0 | 1
4/9 | 08:00:00 | 284.15 | 98833 | 1 | 181 | 5.9681 | 702 | 957.6 | 269.854 | 0 | 1
4/9 | 09:00:00 | 286.15 | 98850 | 1.5 | 24 | 6.3971 | 1245.6 | 1591.2 | 271.858 | 0 | 1
4/9 | 10:00:00 | 288.15 | 98867 | 2.6 | 170 | 7.3399 | 1695.6 | 1911.6 | 274.218 | 0 | 1
4/9 | 11:00:00 | 291.15 | 98892 | 3.1 | 180 | 7.855 | 2134.8 | 2440.8 | 277.17 | 0 | 1
4/9 | 12:00:00 | 292.15 | 98900 | 5.1 | 220 | 7.3374 | 2383.2 | 2869.2 | 277.752 | 0 | 1
4/9 | 13:00:00 | 292.15 | 98900 | 5.7 | 220 | 6.8511 | 2422.8 | 2923.2 | 277.377 | 0 | 1
4/9 | 14:00:00 | 292.15 | 98900 | 6.2 | 240 | 7.3374 | 2246.4 | 2775.6 | 277.752 | 0 | 1
4/9 | 15:00:00 | 290.15 | 98883 | 7.7 | 270 | 7.8557 | 1951.2 | 2660.4 | 275.639 | 0 | 1
4/9 | 16:00:00 | 287.15 | 98858 | 9.3 | 280 | 7.8578 | 1472.4 | 2120.4 | 273.226 | 0 | 1
4/9 | 17:00:00 | 285.15 | 98841 | 11.8 | 270 | 6.8552 | 885.6 | 1245.6 | 271.136 | 0 | 1
4/9 | 18:00:00 | 284.15 | 98833 | 9.3 | 270 | 6.3982 | 406.8 | 759.6 | 269.693 | 0 | 1
4/9 | 19:00:00 | 283.15 | 98824 | 9.3 | 270 | 6.3988 | 50.4 | 0 | 269.007 | 0 | 1
4/9 | 20:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
4/9 | 21:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
4/9 | 22:00:00 | 282.15 | 98815 | 9.3 | 280 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
4/9 | 23:00:00 | 281.15 | 98806 | 9.8 | 290 | 5.1861 | 0 | 0 | 266.423 | 0 | 1
4/9 | 24:00:00 | 279.15 | 98789 | 9.3 | 290 | 5.187 | 0 | 0 | 264.269 | 0 | 1
4/10 | 01:00:00 | 278.15 | 98780 | 10.3 | 290 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
4/10 | 02:00:00 | 278.15 | 98780 | 7.7 | 300 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
4/10 | 03:00:00 | 278.15 | 98780 | 4.1 | 300 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
4/10 | 04:00:00 | 278.15 | 98780 | 5.1 | 290 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
4/10 | 05:00:00 | 278.15 | 98780 | 7.7 | 290 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
4/10 | 06:00:00 | 278.15 | 98780 | 7.2 | 290 | 4.8311 | 10.8 | 0 | 263.352 | 0 | 1
4/10 | 07:00:00 | 278.15 | 98780 | 7.2 | 290 | 4.8311 | 291.6 | 381.6 | 263.095 | 0 | 1
4/10 | 08:00:00 | 280.15 | 98798 | 7.2 | 280 | 4.8303 | 810 | 1422 | 264.986 | 0 | 1
4/10 | 09:00:00 | 281.15 | 98806 | 9.8 | 290 | 4.8299 | 1364.4 | 1976.4 | 265.932 | 0 | 1
4/10 | 10:00:00 | 282.15 | 98815 | 8.8 | 300 | 4.4952 | 1854 | 2512.8 | 266.645 | 0 | 1
4/10 | 11:00:00 | 284.15 | 98833 | 6.7 | 310 | 4.8285 | 2084.4 | 2228.4 | 269.033 | 0 | 1
4/10 | 12:00:00 | 283.15 | 98824 | 5.7 | 300 | 4.829 | 2275.2 | 2422.8 | 268.086 | 0 | 1
4/10 | 13:00:00 | 285.15 | 98841 | 6.2 | 290 | 5.1842 | 2296.8 | 2415.6 | 270.214 | 0 | 1
4/10 | 14:00:00 | 283.15 | 98824 | 6.2 | 300 | 5.1851 | 2149.2 | 2246.4 | 268.319 | 0 | 1
4/10 | 15:00:00 | 284.15 | 98833 | 7.2 | 270 | 5.1847 | 1962 | 2566.8 | 269.003 | 0 | 1
4/10 | 16:00:00 | 284.15 | 98833 | 7.2 | 270 | 5.1847 | 1504.8 | 2106 | 269.003 | 0 | 1
4/10 | 17:00:00 | 283.15 | 98824 | 7.7 | 280 | 5.1851 | 907.2 | 1281.6 | 268.319 | 0 | 1
4/10 | 18:00:00 | 282.15 | 98815 | 7.2 | 280 | 5.1856 | 396 | 496.8 | 267.371 | 0 | 1
4/10 | 19:00:00 | 282.15 | 98815 | 5.7 | 270 | 5.1856 | 61.2 | 0 | 267.11 | 0 | 1
4/10 | 20:00:00 | 281.15 | 98806 | 6.2 | 280 | 5.1861 | 0 | 0 | 266.163 | 0 | 1
4/10 | 21:00:00 | 280.15 | 98798 | 6.7 | 290 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
4/10 | 22:00:00 | 280.15 | 98798 | 5.1 | 280 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
4/10 | 23:00:00 | 279.15 | 98789 | 4.6 | 300 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
4/10 | 24:00:00 | 278.15 | 98780 | 5.7 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
4/11 | 01:00:00 | 278.15 | 98780 | 3.1 | 270 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
4/11 | 02:00:00 | 278.15 | 98780 | 6.2 | 290 | 4.4968 | 0 | 0 | 262.865 | 0 | 1
4/11 | 03:00:00 | 277.15 | 98771 | 5.7 | 270 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
4/11 | 04:00:00 | 277.15 | 98771 | 5.1 | 270 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
4/11 | 05:00:00 | 277.15 | 98771 | 3.6 | 280 | 4.8316 | 0 | 0 | 262.405 | 0 | 1
4/11 | 06:00:00 | 278.15 | 98780 | 5.7 | 260 | 4.8311 | 18 | 0 | 263.095 | 0 | 1
4/11 | 07:00:00 | 279.15 | 98789 | 4.6 | 250 | 5.187 | 309.6 | 403.2 | 264.269 | 0 | 1
4/11 | 08:00:00 | 280.15 | 98798 | 6.2 | 260 | 5.1865 | 781.2 | 1231.2 | 265.476 | 0 | 1
4/11 | 09:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.5656 | 1299.6 | 1674 | 266.653 | 0 | 1
4/11 | 10:00:00 | 282.15 | 98815 | 7.7 | 270 | 5.1856 | 1760.4 | 2127.6 | 267.371 | 0 | 1
4/11 | 11:00:00 | 282.15 | 98815 | 10.8 | 270 | 5.1856 | 2102.4 | 2347.2 | 267.371 | 0 | 1
4/11 | 12:00:00 | 282.15 | 98815 | 10.3 | 270 | 5.1856 | 2289.6 | 2408.4 | 267.371 | 0 | 1
4/11 | 13:00:00 | 284.15 | 98833 | 10.8 | 260 | 5.1847 | 2311.2 | 2415.6 | 269.266 | 0 | 1
4/11 | 14:00:00 | 283.15 | 98824 | 7.2 | 260 | 5.1851 | 2167.2 | 1890 | 268.319 | 0 | 1
4/11 | 15:00:00 | 282.15 | 98815 | 6.2 | 260 | 5.1856 | 1033.2 | 259.2 | 267.844 | 0 | 1
4/11 | 16:00:00 | 282.15 | 98815 | 10.3 | 260 | 5.1856 | 1432.8 | 1501.2 | 267.371 | 0 | 1
4/11 | 17:00:00 | 282.15 | 98815 | 12.4 | 260 | 5.1856 | 921.6 | 1339.2 | 267.371 | 0 | 1
4/11 | 18:00:00 | 281.15 | 98806 | 12.9 | 260 | 5.1861 | 410.4 | 511.2 | 266.423 | 0 | 1
4/11 | 19:00:00 | 281.15 | 98806 | 8.2 | 260 | 5.5656 | 61.2 | 0 | 266.653 | 0 | 1
4/11 | 20:00:00 | 281.15 | 98806 | 11.3 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
4/11 | 21:00:00 | 281.15 | 98806 | 10.8 | 280 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
4/11 | 22:00:00 | 281.15 | 98806 | 9.3 | 270 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
4/11 | 23:00:00 | 281.15 | 98806 | 10.8 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
4/11 | 24:00:00 | 281.15 | 98806 | 10.8 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
4/12 | 01:00:00 | 281.15 | 98806 | 10.8 | 280 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
4/12 | 02:00:00 | 280.65 | 98802 | 8.8 | 239 | 5.7648 | 0 | 0 | 266.764 | 0 | 1
4/12 | 03:00:00 | 280.15 | 98798 | 6.7 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/12 | 04:00:00 | 280.15 | 98798 | 6.2 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/12 | 05:00:00 | 280.15 | 98798 | 6.7 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/12 | 06:00:00 | 280.15 | 98798 | 7.7 | 260 | 5.9703 | 14.4 | 0 | 266.402 | 0 | 1
4/12 | 07:00:00 | 280.15 | 98798 | 6.7 | 250 | 5.9703 | 169.2 | 0 | 266.402 | 0 | 1
4/12 | 08:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.9703 | 442.8 | 32.4 | 266.402 | 0 | 1
4/12 | 09:00:00 | 281.15 | 98806 | 9.3 | 260 | 5.9698 | 730.8 | 61.2 | 267.353 | 0 | 1
4/12 | 10:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.4 | 982.8 | 151.2 | 267.58 | 0 | 1
4/12 | 11:00:00 | 282.15 | 98815 | 9.3 | 270 | 6.3994 | 1170 | 226.8 | 268.532 | 0 | 1
4/12 | 12:00:00 | 282.15 | 98815 | 9.3 | 270 | 6.3994 | 1274.4 | 234 | 268.532 | 0 | 1
4/12 | 13:00:00 | 282.15 | 98815 | 8.2 | 270 | 6.8571 | 1285.2 | 201.6 | 268.758 | 0 | 1
4/12 | 14:00:00 | 282.15 | 98815 | 6.7 | 270 | 6.8571 | 2170.8 | 1911.6 | 268.283 | 0 | 1
4/12 | 15:00:00 | 283.15 | 98824 | 13.4 | 280 | 5.9687 | 1875.6 | 2109.6 | 268.779 | 0 | 1
4/12 | 16:00:00 | 284.15 | 98833 | 14.4 | 280 | 4.8285 | 1540.8 | 2296.8 | 268.77 | 0 | 1
4/12 | 17:00:00 | 283.15 | 98824 | 12.9 | 280 | 4.4948 | 997.2 | 1645.2 | 267.59 | 0 | 1
4/12 | 18:00:00 | 282.15 | 98815 | 14.4 | 290 | 4.4952 | 450 | 820.8 | 266.645 | 0 | 1
4/12 | 19:00:00 | 281.15 | 98806 | 9.8 | 280 | 4.8299 | 72 | 0 | 265.932 | 0 | 1
4/12 | 20:00:00 | 280.15 | 98798 | 8.2 | 280 | 4.8303 | 0 | 0 | 264.986 | 0 | 1
4/12 | 21:00:00 | 279.15 | 98789 | 7.7 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
4/12 | 22:00:00 | 279.15 | 98789 | 6.2 | 290 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
4/12 | 23:00:00 | 279.15 | 98789 | 6.2 | 290 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
4/12 | 24:00:00 | 278.15 | 98780 | 6.7 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
4/13 | 01:00:00 | 278.15 | 98780 | 6.7 | 290 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
4/13 | 02:00:00 | 278.15 | 98780 | 7.7 | 300 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
4/13 | 03:00:00 | 278.15 | 98780 | 9.3 | 300 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
4/13 | 04:00:00 | 277.15 | 98771 | 6.2 | 280 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
4/13 | 05:00:00 | 278.15 | 98780 | 7.7 | 290 | 4.4968 | 0 | 0 | 262.865 | 0 | 1
4/13 | 06:00:00 | 278.15 | 98780 | 6.2 | 290 | 4.8311 | 32.4 | 0 | 263.095 | 0 | 1
4/13 | 07:00:00 | 278.15 | 98780 | 4.6 | 280 | 4.8311 | 342 | 396 | 263.095 | 0 | 1
4/13 | 08:00:00 | 279.15 | 98789 | 6.7 | 290 | 5.187 | 817.2 | 1270.8 | 264.528 | 0 | 1
4/13 | 09:00:00 | 281.15 | 98806 | 5.7 | 300 | 5.1861 | 1342.8 | 1702.8 | 266.423 | 0 | 1
4/13 | 10:00:00 | 281.15 | 98806 | 5.1 | 290 | 4.8299 | 1803.6 | 2095.2 | 266.193 | 0 | 1
4/13 | 11:00:00 | 282.15 | 98815 | 6.7 | 280 | 5.1856 | 2138.4 | 2354.4 | 267.371 | 0 | 1
4/13 | 12:00:00 | 283.15 | 98824 | 7.2 | 270 | 5.1851 | 2325.6 | 1936.8 | 268.319 | 0 | 1
4/13 | 13:00:00 | 281.15 | 98806 | 7.2 | 280 | 5.1861 | 1303.2 | 284.4 | 266.895 | 0 | 1
4/13 | 14:00:00 | 281.15 | 98806 | 6.7 | 280 | 5.1861 | 2199.6 | 1350 | 266.423 | 0 | 1
4/13 | 15:00:00 | 282.15 | 98815 | 7.2 | 280 | 4.8294 | 1054.8 | 190.8 | 267.612 | 0 | 1
4/13 | 16:00:00 | 282.15 | 98815 | 7.2 | 270 | 4.8294 | 813.6 | 68.4 | 267.612 | 0 | 1
4/13 | 17:00:00 | 281.15 | 98806 | 7.2 | 280 | 4.8299 | 529.2 | 21.6 | 266.664 | 0 | 1
4/13 | 18:00:00 | 281.15 | 98806 | 5.7 | 270 | 5.1861 | 241.2 | 0 | 266.895 | 0 | 1
4/13 | 19:00:00 | 280.15 | 98798 | 6.2 | 270 | 5.1865 | 39.6 | 0 | 265.946 | 0 | 1
4/13 | 20:00:00 | 280.15 | 98798 | 5.7 | 270 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
4/13 | 21:00:00 | 280.15 | 98798 | 4.6 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
4/13 | 22:00:00 | 280.15 | 98798 | 6.2 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
4/13 | 23:00:00 | 280.15 | 98798 | 5.7 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
4/13 | 24:00:00 | 280.15 | 98798 | 4.6 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
4/14 | 01:00:00 | 280.15 | 98798 | 6.2 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/14 | 02:00:00 | 280.15 | 98798 | 9.3 | 270 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
4/14 | 03:00:00 | 280.15 | 98798 | 5.1 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/14 | 04:00:00 | 280.15 | 98798 | 4.1 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/14 | 05:00:00 | 280.15 | 98798 | 2.1 | 210 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/14 | 06:00:00 | 279.15 | 98789 | 1.5 | 108 | 5.5666 | 21.6 | 0 | 265.224 | 0 | 1
4/14 | 07:00:00 | 279.15 | 98789 | 2.1 | 210 | 5.9708 | 187.2 | 0 | 265.451 | 0 | 1
4/14 | 08:00:00 | 280.15 | 98798 | 2.1 | 200 | 5.9703 | 464.4 | 36 | 266.402 | 0 | 1
4/14 | 09:00:00 | 281.15 | 98806 | 3.1 | 220 | 6.4 | 752.4 | 61.2 | 267.58 | 0 | 1
4/14 | 10:00:00 | 281.15 | 98806 | 3.1 | 220 | 6.4 | 1004.4 | 208.8 | 267.58 | 0 | 1
4/14 | 11:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.8577 | 1188 | 194.4 | 267.805 | 0 | 1
4/14 | 12:00:00 | 283.15 | 98824 | 5.1 | 250 | 6.8564 | 2329.2 | 1339.2 | 269.234 | 0 | 1
4/14 | 13:00:00 | 283.15 | 98824 | 5.1 | 260 | 7.3431 | 1299.6 | 273.6 | 269.936 | 0 | 1
4/14 | 14:00:00 | 283.15 | 98824 | 7.7 | 260 | 6.3988 | 2206.8 | 1267.2 | 269.007 | 0 | 1
4/14 | 15:00:00 | 283.15 | 98824 | 7.2 | 260 | 6.3988 | 1054.8 | 183.6 | 269.483 | 0 | 1
4/14 | 16:00:00 | 282.15 | 98815 | 6.7 | 270 | 5.9692 | 817.2 | 68.4 | 268.304 | 0 | 1
4/14 | 17:00:00 | 282.15 | 98815 | 5.1 | 270 | 5.9692 | 532.8 | 21.6 | 268.304 | 0 | 1
4/14 | 18:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.3994 | 248.4 | 0 | 268.532 | 0 | 1
4/14 | 19:00:00 | 281.15 | 98806 | 4.6 | 290 | 6.4 | 75.6 | 0 | 267.107 | 0 | 1
4/14 | 20:00:00 | 280.15 | 98798 | 5.1 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
4/14 | 21:00:00 | 280.15 | 98798 | 4.1 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
4/14 | 22:00:00 | 280.15 | 98798 | 4.6 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
4/14 | 23:00:00 | 280.15 | 98798 | 4.1 | 290 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
4/14 | 24:00:00 | 279.15 | 98789 | 2.6 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
4/15 | 01:00:00 | 279.15 | 98789 | 4.1 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
4/15 | 02:00:00 | 278.15 | 98780 | 3.6 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
4/15 | 03:00:00 | 278.15 | 98780 | 5.1 | 300 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
4/15 | 04:00:00 | 278.15 | 98780 | 6.2 | 280 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
4/15 | 05:00:00 | 277.15 | 98771 | 9.3 | 280 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
4/15 | 06:00:00 | 277.15 | 98771 | 9.8 | 270 | 4.4973 | 46.8 | 0 | 261.92 | 0 | 1
4/15 | 07:00:00 | 278.15 | 98780 | 9.8 | 270 | 4.4968 | 374.4 | 525.6 | 262.865 | 0 | 1
4/15 | 08:00:00 | 278.15 | 98780 | 8.2 | 270 | 4.8311 | 907.2 | 1576.8 | 263.095 | 0 | 1
4/15 | 09:00:00 | 279.15 | 98789 | 8.8 | 270 | 4.8307 | 1382.4 | 1796.4 | 264.299 | 0 | 1
4/15 | 10:00:00 | 280.15 | 98798 | 8.8 | 280 | 4.8303 | 1839.6 | 2102.4 | 265.246 | 0 | 1
4/15 | 11:00:00 | 282.15 | 98815 | 8.8 | 280 | 4.8294 | 2178 | 2372.4 | 267.139 | 0 | 1
4/15 | 12:00:00 | 282.15 | 98815 | 9.8 | 280 | 4.8294 | 2361.6 | 2422.8 | 267.139 | 0 | 1
4/15 | 13:00:00 | 282.15 | 98815 | 10.3 | 270 | 4.8294 | 2383.2 | 2426.4 | 267.139 | 0 | 1
4/15 | 14:00:00 | 283.15 | 98824 | 10.8 | 270 | 4.4948 | 2239.2 | 2404.8 | 267.852 | 0 | 1
4/15 | 15:00:00 | 282.15 | 98815 | 11.3 | 280 | 4.1819 | 1936.8 | 1846.8 | 266.672 | 0 | 1
4/15 | 16:00:00 | 282.15 | 98815 | 10.3 | 280 | 4.4952 | 1497.6 | 1659.6 | 266.906 | 0 | 1
4/15 | 17:00:00 | 282.15 | 98815 | 8.8 | 280 | 4.4952 | 1040.4 | 1677.6 | 266.645 | 0 | 1
4/15 | 18:00:00 | 281.15 | 98806 | 9.8 | 280 | 3.8882 | 489.6 | 748.8 | 265.232 | 0 | 1
4/15 | 19:00:00 | 280.15 | 98798 | 10.3 | 280 | 3.8885 | 86.4 | 0 | 264.289 | 0 | 1
4/15 | 20:00:00 | 279.15 | 98789 | 9.3 | 280 | 4.183 | 0 | 0 | 263.578 | 0 | 1
4/15 | 21:00:00 | 278.15 | 98780 | 5.7 | 280 | 4.1834 | 0 | 0 | 263.132 | 0 | 1
4/15 | 22:00:00 | 278.15 | 98780 | 4.1 | 280 | 3.8892 | 0 | 0 | 262.781 | 0 | 1
4/15 | 23:00:00 | 277.15 | 98771 | 5.1 | 270 | 3.5793 | 0 | 0 | 261.603 | 0 | 1
4/15 | 24:00:00 | 277.15 | 98771 | 5.7 | 300 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
4/16 | 01:00:00 | 277.15 | 98771 | 6.2 | 290 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
4/16 | 02:00:00 | 277.15 | 98771 | 6.2 | 280 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
4/16 | 03:00:00 | 278.15 | 98780 | 6.7 | 280 | 4.1834 | 0 | 0 | 263.132 | 0 | 1
4/16 | 04:00:00 | 277.15 | 98771 | 6.2 | 280 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
4/16 | 05:00:00 | 277.15 | 98771 | 4.6 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
4/16 | 06:00:00 | 277.15 | 98771 | 4.1 | 280 | 4.4973 | 50.4 | 0 | 261.92 | 0 | 1
4/16 | 07:00:00 | 277.15 | 98771 | 5.1 | 280 | 4.4973 | 388.8 | 457.2 | 261.92 | 0 | 1
4/16 | 08:00:00 | 279.15 | 98789 | 5.1 | 290 | 4.8307 | 874.8 | 1270.8 | 264.299 | 0 | 1
4/16 | 09:00:00 | 279.15 | 98789 | 4.6 | 300 | 5.187 | 1400.4 | 1728 | 264.528 | 0 | 1
4/16 | 10:00:00 | 280.15 | 98798 | 4.6 | 260 | 5.1865 | 1854 | 2098.8 | 265.476 | 0 | 1
4/16 | 11:00:00 | 280.15 | 98798 | 4.1 | 270 | 5.5661 | 2188.8 | 1893.6 | 265.704 | 0 | 1
4/16 | 12:00:00 | 280.15 | 98798 | 3.6 | 260 | 5.9703 | 1314 | 201.6 | 266.402 | 0 | 1
4/16 | 13:00:00 | 280.15 | 98798 | 4.1 | 250 | 6.4005 | 1321.2 | 234 | 266.628 | 0 | 1
4/16 | 14:00:00 | 281.15 | 98806 | 5.1 | 250 | 6.4 | 1242 | 230.4 | 267.58 | 0 | 1
4/16 | 15:00:00 | 281.15 | 98806 | 5.7 | 260 | 6.8577 | 1069.2 | 212.4 | 267.805 | 0 | 1
4/16 | 16:00:00 | 282.15 | 98815 | 5.7 | 260 | 6.8571 | 831.6 | 129.6 | 268.758 | 0 | 1
4/16 | 17:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.8564 | 986.4 | 1152 | 269.234 | 0 | 1
4/16 | 18:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.8571 | 468 | 568.8 | 268.283 | 0 | 1
4/16 | 19:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.8571 | 82.8 | 0 | 268.283 | 0 | 1
4/16 | 20:00:00 | 280.15 | 98798 | 3.1 | 360 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
4/16 | 21:00:00 | 279.15 | 98789 | 3.6 | 30 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
4/16 | 22:00:00 | 278.15 | 98780 | 3.6 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
4/16 | 23:00:00 | 277.15 | 98771 | 2.6 | 50 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
4/16 | 24:00:00 | 277.15 | 98771 | 2.6 | 60 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
4/17 | 01:00:00 | 277.15 | 98771 | 2.1 | 40 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
4/17 | 02:00:00 | 277.15 | 98771 | 1.5 | 349 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
4/17 | 03:00:00 | 277.15 | 98771 | 2.6 | 30 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
4/17 | 04:00:00 | 277.15 | 98771 | 1.5 | 101 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
4/17 | 05:00:00 | 277.15 | 98771 | 2.1 | 30 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
4/17 | 06:00:00 | 277.15 | 98771 | 1 | 299 | 5.1879 | 28.8 | 0 | 263.098 | 0 | 1
4/17 | 07:00:00 | 277.15 | 98771 | 2.1 | 40 | 5.1879 | 212.4 | 0 | 263.098 | 0 | 1
4/17 | 08:00:00 | 278.15 | 98780 | 2.1 | 30 | 4.8311 | 496.8 | 129.6 | 263.818 | 0 | 1
4/17 | 09:00:00 | 279.15 | 98789 | 3.1 | 40 | 4.8307 | 1418.4 | 1468.8 | 264.299 | 0 | 1
4/17 | 10:00:00 | 279.15 | 98789 | 3.1 | 40 | 4.183 | 1882.8 | 1818 | 263.837 | 0 | 1
4/17 | 11:00:00 | 279.15 | 98789 | 1.5 | 230 | 4.183 | 2217.6 | 1850.4 | 263.837 | 0 | 1
4/17 | 12:00:00 | 280.15 | 98798 | 2.1 | 60 | 4.496 | 1332 | 284.4 | 265.483 | 0 | 1
4/17 | 13:00:00 | 280.15 | 98798 | 1.5 | 93 | 4.1826 | 2422.8 | 1936.8 | 264.782 | 0 | 1
4/17 | 14:00:00 | 281.15 | 98806 | 1 | 76 | 4.4957 | 2268 | 2404.8 | 265.96 | 0 | 1
4/17 | 15:00:00 | 281.15 | 98806 | 2.1 | 10 | 4.4957 | 1962 | 2160 | 265.96 | 0 | 1
4/17 | 16:00:00 | 281.15 | 98806 | 0.5 | 206 | 4.4957 | 1530 | 1929.6 | 265.96 | 0 | 1
4/17 | 17:00:00 | 281.15 | 98806 | 2.1 | 10 | 4.1823 | 1011.6 | 1198.8 | 265.727 | 0 | 1
4/17 | 18:00:00 | 281.15 | 98806 | 1 | 163 | 4.1823 | 486 | 500.4 | 265.727 | 0 | 1
4/17 | 19:00:00 | 280.15 | 98798 | 1 | 360 | 4.496 | 93.6 | 0 | 264.755 | 0 | 1
4/17 | 20:00:00 | 279.15 | 98789 | 2.6 | 270 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
4/17 | 21:00:00 | 279.15 | 98789 | 2.6 | 280 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
4/17 | 22:00:00 | 279.15 | 98789 | 3.1 | 20 | 4.8307 | 0 | 0 | 264.299 | 0 | 1
4/17 | 23:00:00 | 277.15 | 98771 | 6.2 | 20 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
4/17 | 24:00:00 | 276.15 | 98762 | 3.1 | 20 | 3.8899 | 0 | 0 | 260.515 | 0 | 1
4/18 | 01:00:00 | 275.15 | 98752 | 3.6 | 30 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
4/18 | 02:00:00 | 275.15 | 98752 | 6.2 | 10 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
4/18 | 03:00:00 | 274.15 | 98743 | 3.1 | 350 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
4/18 | 04:00:00 | 274.15 | 98743 | 3.6 | 10 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
4/18 | 05:00:00 | 273.15 | 98734 | 2.6 | 310 | 3.293 | 0 | 0 | 257.823 | 0 | 1
4/18 | 06:00:00 | 272.15 | 98724 | 2.6 | 310 | 3.0271 | 43.2 | 0 | 256.647 | 0 | 1
4/18 | 07:00:00 | 275.15 | 98752 | 3.6 | 360 | 3.2924 | 370.8 | 295.2 | 259.482 | 0 | 1
4/18 | 08:00:00 | 276.15 | 98762 | 3.6 | 30 | 3.2921 | 900 | 1062 | 260.304 | 0 | 1
4/18 | 09:00:00 | 278.15 | 98780 | 4.6 | 30 | 3.5789 | 1533.6 | 2055.6 | 262.168 | 0 | 1
4/18 | 10:00:00 | 279.15 | 98789 | 4.6 | 40 | 3.5786 | 2019.6 | 2552.4 | 263.11 | 0 | 1
4/18 | 11:00:00 | 280.15 | 98798 | 4.1 | 30 | 3.8885 | 2239.2 | 2214 | 264.547 | 0 | 1
4/18 | 12:00:00 | 281.15 | 98806 | 3.6 | 40 | 4.1823 | 2419.2 | 2448 | 265.727 | 0 | 1
4/18 | 13:00:00 | 281.15 | 98806 | 3.1 | 22 | 4.1823 | 2437.2 | 2451.6 | 265.727 | 0 | 1
4/18 | 14:00:00 | 281.15 | 98806 | 3.6 | 50 | 3.578 | 2293.2 | 2444.4 | 265.255 | 0 | 1
4/18 | 15:00:00 | 282.15 | 98815 | 1.5 | 221 | 3.2903 | 1990.8 | 2163.6 | 265.959 | 0 | 1
4/18 | 16:00:00 | 282.15 | 98815 | 2.6 | 50 | 3.5777 | 1551.6 | 1501.2 | 266.199 | 0 | 1
4/18 | 17:00:00 | 282.15 | 98815 | 2.6 | 90 | 3.5777 | 1090.8 | 1468.8 | 265.938 | 0 | 1
4/18 | 18:00:00 | 281.15 | 98806 | 3.1 | 90 | 3.8882 | 529.2 | 799.2 | 265.232 | 0 | 1
4/18 | 19:00:00 | 280.15 | 98798 | 3.1 | 100 | 4.1826 | 100.8 | 0 | 264.523 | 0 | 1
4/18 | 20:00:00 | 279.15 | 98789 | 2.6 | 110 | 4.183 | 0 | 0 | 263.959 | 0 | 1
4/18 | 21:00:00 | 279.15 | 98789 | 4.1 | 120 | 4.4964 | 0 | 0 | 264.31 | 0 | 1
4/18 | 22:00:00 | 278.15 | 98780 | 4.1 | 120 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
4/18 | 23:00:00 | 278.15 | 98780 | 2.6 | 130 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
4/18 | 24:00:00 | 277.15 | 98771 | 2.6 | 150 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
4/19 | 01:00:00 | 276.15 | 98762 | 2.1 | 160 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
4/19 | 02:00:00 | 276.15 | 98762 | 2.1 | 150 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
4/19 | 03:00:00 | 277.15 | 98771 | 2.6 | 160 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
4/19 | 04:00:00 | 277.15 | 98771 | 2.6 | 160 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
4/19 | 05:00:00 | 276.15 | 98762 | 2.6 | 160 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
4/19 | 06:00:00 | 276.15 | 98762 | 2.6 | 170 | 4.4977 | 28.8 | 0 | 261.799 | 0 | 1
4/19 | 07:00:00 | 277.15 | 98771 | 2.6 | 180 | 4.8316 | 187.2 | 0 | 262.976 | 0 | 1
4/19 | 08:00:00 | 278.15 | 98780 | 2.1 | 190 | 4.8311 | 597.6 | 208.8 | 263.818 | 0 | 1
4/19 | 09:00:00 | 279.15 | 98789 | 2.6 | 190 | 4.8307 | 1152 | 716.4 | 264.656 | 0 | 1
4/19 | 10:00:00 | 281.15 | 98806 | 3.6 | 200 | 4.8299 | 1818 | 1677.6 | 266.316 | 0 | 1
4/19 | 11:00:00 | 281.15 | 98806 | 3.6 | 210 | 4.4957 | 2386.8 | 2246.4 | 265.7 | 0 | 1
4/19 | 12:00:00 | 282.15 | 98815 | 3.1 | 210 | 4.4952 | 1350 | 208.8 | 267.379 | 0 | 1
4/19 | 13:00:00 | 283.15 | 98824 | 2.6 | 250 | 4.4948 | 1357.2 | 90 | 268.326 | 0 | 1
4/19 | 14:00:00 | 283.15 | 98824 | 4.1 | 260 | 4.4948 | 777.6 | 10.8 | 268.435 | 0 | 1
4/19 | 15:00:00 | 283.15 | 98824 | 3.6 | 240 | 4.4948 | 673.2 | 14.4 | 268.435 | 0 | 1
4/19 | 16:00:00 | 283.15 | 98824 | 3.6 | 230 | 4.4948 | 864 | 288 | 268.326 | 0 | 1
4/19 | 17:00:00 | 284.15 | 98833 | 3.6 | 230 | 4.4944 | 1036.8 | 1213.2 | 268.798 | 0 | 1
4/19 | 18:00:00 | 283.15 | 98824 | 4.6 | 260 | 4.829 | 284.4 | 0 | 268.561 | 0 | 1
4/19 | 19:00:00 | 283.15 | 98824 | 4.6 | 260 | 4.829 | 100.8 | 0 | 268.086 | 0 | 1
4/19 | 20:00:00 | 282.15 | 98815 | 4.6 | 260 | 5.1856 | 0 | 0 | 267.844 | 0 | 1
4/19 | 21:00:00 | 282.15 | 98815 | 4.6 | 270 | 5.5651 | 0 | 0 | 268.075 | 0 | 1
4/19 | 22:00:00 | 281.15 | 98806 | 4.6 | 260 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
4/19 | 23:00:00 | 281.15 | 98806 | 4.1 | 250 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
4/19 | 24:00:00 | 281.15 | 98806 | 4.6 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1
4/20 | 01:00:00 | 281.15 | 98806 | 5.1 | 260 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
4/20 | 02:00:00 | 281.15 | 98806 | 4.1 | 260 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
4/20 | 03:00:00 | 281.15 | 98806 | 5.1 | 260 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
4/20 | 04:00:00 | 281.15 | 98806 | 4.6 | 270 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
4/20 | 05:00:00 | 282.15 | 98815 | 4.1 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
4/20 | 06:00:00 | 282.15 | 98815 | 5.7 | 280 | 7.3438 | 39.6 | 0 | 268.983 | 0 | 1
4/20 | 07:00:00 | 282.15 | 98815 | 3.1 | 280 | 7.3438 | 234 | 0 | 268.983 | 0 | 1
4/20 | 08:00:00 | 283.15 | 98824 | 5.1 | 280 | 7.3431 | 936 | 1087.2 | 269.46 | 0 | 1
4/20 | 09:00:00 | 283.15 | 98824 | 4.1 | 270 | 7.3431 | 810 | 122.4 | 269.936 | 0 | 1
4/20 | 10:00:00 | 284.15 | 98833 | 5.1 | 290 | 7.3425 | 1062 | 208.8 | 270.89 | 0 | 1
4/20 | 11:00:00 | 284.15 | 98833 | 4.1 | 280 | 7.3425 | 1242 | 226.8 | 270.89 | 0 | 1
4/20 | 12:00:00 | 284.15 | 98833 | 5.1 | 280 | 6.8558 | 1346.4 | 201.6 | 270.663 | 0 | 1
4/20 | 13:00:00 | 285.15 | 98841 | 7.2 | 290 | 6.3977 | 2444.4 | 1976.4 | 270.907 | 0 | 1
4/20 | 14:00:00 | 286.15 | 98850 | 7.7 | 280 | 6.8546 | 2293.2 | 2329.2 | 272.087 | 0 | 1
4/20 | 15:00:00 | 285.15 | 98841 | 8.2 | 280 | 6.8552 | 1987.2 | 2106 | 271.136 | 0 | 1
4/20 | 16:00:00 | 286.15 | 98850 | 7.7 | 290 | 6.8546 | 1555.2 | 1530 | 272.087 | 0 | 1
4/20 | 17:00:00 | 285.15 | 98841 | 7.7 | 280 | 6.8552 | 579.6 | 169.2 | 271.616 | 0 | 1
4/20 | 18:00:00 | 285.15 | 98841 | 7.2 | 270 | 6.8552 | 518.4 | 759.6 | 271.136 | 0 | 1
4/20 | 19:00:00 | 284.15 | 98833 | 7.2 | 290 | 6.8558 | 108 | 0 | 270.185 | 0 | 1
4/20 | 20:00:00 | 282.15 | 98815 | 5.7 | 280 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
4/20 | 21:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
4/20 | 22:00:00 | 281.15 | 98806 | 4.6 | 260 | 6.4 | 0 | 0 | 266.846 | 0 | 1
4/20 | 23:00:00 | 281.15 | 98806 | 7.2 | 280 | 6.4 | 0 | 0 | 266.846 | 0 | 1
4/20 | 24:00:00 | 281.15 | 98806 | 3.6 | 290 | 6.4 | 0 | 0 | 266.846 | 0 | 1
4/21 | 01:00:00 | 280.15 | 98798 | 3.1 | 290 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
4/21 | 02:00:00 | 279.15 | 98789 | 1.5 | 270 | 5.9708 | 0 | 0 | 264.723 | 0 | 1
4/21 | 03:00:00 | 278.15 | 98780 | 2.6 | 280 | 5.5671 | 0 | 0 | 263.549 | 0 | 1
4/21 | 04:00:00 | 280.15 | 98798 | 3.1 | 280 | 6.4005 | 0 | 0 | 266.157 | 0 | 1
4/21 | 05:00:00 | 281.15 | 98806 | 2.1 | 280 | 6.4 | 0 | 0 | 267.107 | 0 | 1
4/21 | 06:00:00 | 281.15 | 98806 | 4.1 | 270 | 6.4 | 75.6 | 0 | 267.107 | 0 | 1
4/21 | 07:00:00 | 282.15 | 98815 | 3.1 | 260 | 6.3994 | 439.2 | 518.4 | 268.057 | 0 | 1
4/21 | 08:00:00 | 282.15 | 98815 | 5.1 | 280 | 6.3994 | 957.6 | 1314 | 268.057 | 0 | 1
4/21 | 09:00:00 | 283.15 | 98824 | 6.7 | 270 | 6.8564 | 1479.6 | 1731.6 | 269.234 | 0 | 1
4/21 | 10:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.3988 | 1933.2 | 1918.8 | 269.007 | 0 | 1
4/21 | 11:00:00 | 284.15 | 98833 | 6.2 | 280 | 6.3982 | 1256.4 | 198 | 270.435 | 0 | 1
4/21 | 12:00:00 | 282.15 | 98815 | 6.2 | 280 | 6.8571 | 1353.6 | 201.6 | 268.758 | 0 | 1
4/21 | 13:00:00 | 284.15 | 98833 | 7.2 | 280 | 6.8558 | 2455.2 | 1962 | 270.185 | 0 | 1
4/21 | 14:00:00 | 286.15 | 98850 | 8.8 | 290 | 6.3971 | 2311.2 | 2336.4 | 271.858 | 0 | 1
4/21 | 15:00:00 | 285.15 | 98841 | 9.8 | 280 | 6.3977 | 2005.2 | 2116.8 | 270.907 | 0 | 1
4/21 | 16:00:00 | 285.15 | 98841 | 6.7 | 280 | 6.3977 | 1573.2 | 1904.4 | 270.907 | 0 | 1
4/21 | 17:00:00 | 285.15 | 98841 | 9.3 | 280 | 6.3977 | 1058.4 | 1411.2 | 270.907 | 0 | 1
4/21 | 18:00:00 | 284.15 | 98833 | 8.8 | 290 | 6.3982 | 529.2 | 633.6 | 269.957 | 0 | 1
4/21 | 19:00:00 | 284.15 | 98833 | 7.2 | 280 | 6.3982 | 115.2 | 0 | 269.957 | 0 | 1
4/21 | 20:00:00 | 283.15 | 98824 | 7.2 | 280 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
4/21 | 21:00:00 | 282.15 | 98815 | 6.7 | 290 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
4/21 | 22:00:00 | 281.15 | 98806 | 6.7 | 300 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
4/21 | 23:00:00 | 280.15 | 98798 | 2.1 | 60 | 6.4005 | 0 | 0 | 266.157 | 0 | 1
4/21 | 24:00:00 | 280.15 | 98798 | 1.5 | 122 | 6.4005 | 0 | 0 | 266.157 | 0 | 1
4/22 | 01:00:00 | 279.15 | 98789 | 1 | 150 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
4/22 | 02:00:00 | 280.15 | 98798 | 1 | 240 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
4/22 | 03:00:00 | 280.15 | 98798 | 1.5 | 96 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
4/22 | 04:00:00 | 279.15 | 98789 | 2.1 | 260 | 5.9708 | 0 | 0 | 264.982 | 0 | 1
4/22 | 05:00:00 | 278.15 | 98780 | 2.6 | 290 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
4/22 | 06:00:00 | 277.15 | 98771 | 2.1 | 280 | 4.8316 | 82.8 | 0 | 262.405 | 0 | 1
4/22 | 07:00:00 | 279.15 | 98789 | 2.1 | 320 | 5.187 | 457.2 | 543.6 | 264.528 | 0 | 1
4/22 | 08:00:00 | 279.15 | 98789 | 2.6 | 10 | 4.8307 | 979.2 | 1353.6 | 264.299 | 0 | 1
4/22 | 09:00:00 | 279.15 | 98789 | 3.1 | 20 | 4.8307 | 1508.4 | 1875.6 | 264.299 | 0 | 1
4/22 | 10:00:00 | 280.15 | 98798 | 2.1 | 40 | 5.1865 | 1958.4 | 2120.4 | 265.476 | 0 | 1
4/22 | 11:00:00 | 281.15 | 98806 | 2.1 | 60 | 5.1861 | 2289.6 | 2365.2 | 266.423 | 0 | 1
4/22 | 12:00:00 | 281.15 | 98806 | 2.1 | 60 | 5.1861 | 2469.6 | 2404.8 | 266.423 | 0 | 1
4/22 | 13:00:00 | 283.15 | 98824 | 1 | 190 | 5.1851 | 2487.6 | 2408.4 | 268.319 | 0 | 1
4/22 | 14:00:00 | 284.15 | 98833 | 1.5 | 15 | 4.8285 | 2336.4 | 2390.4 | 269.033 | 0 | 1
4/22 | 15:00:00 | 284.15 | 98833 | 2.1 | 40 | 4.8285 | 2030.4 | 2156.4 | 269.033 | 0 | 1
4/22 | 16:00:00 | 284.15 | 98833 | 2.1 | 56 | 5.1847 | 1594.8 | 1947.6 | 269.266 | 0 | 1
4/22 | 17:00:00 | 283.15 | 98824 | 4.1 | 40 | 4.4948 | 1080 | 1454.4 | 267.852 | 0 | 1
4/22 | 18:00:00 | 283.15 | 98824 | 2.6 | 30 | 4.4948 | 579.6 | 1011.6 | 267.59 | 0 | 1
4/22 | 19:00:00 | 282.15 | 98815 | 4.1 | 70 | 4.8294 | 126 | 21.6 | 267.139 | 0 | 1
4/22 | 20:00:00 | 280.15 | 98798 | 2.6 | 80 | 4.496 | 0 | 0 | 265.483 | 0 | 1
4/22 | 21:00:00 | 280.15 | 98798 | 3.1 | 130 | 4.8303 | 0 | 0 | 265.715 | 0 | 1
4/22 | 22:00:00 | 279.15 | 98789 | 2.6 | 140 | 4.183 | 0 | 0 | 264.303 | 0 | 1
4/22 | 23:00:00 | 278.15 | 98780 | 2.1 | 160 | 4.1834 | 0 | 0 | 262.891 | 0 | 1
4/22 | 24:00:00 | 276.15 | 98762 | 2.1 | 210 | 3.8899 | 0 | 0 | 260.515 | 0 | 1
4/23 | 01:00:00 | 277.15 | 98771 | 2.6 | 210 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
4/23 | 02:00:00 | 277.15 | 98771 | 3.1 | 240 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
4/23 | 03:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
4/23 | 04:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
4/23 | 05:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
4/23 | 06:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.8316 | 39.6 | 0 | 262.976 | 0 | 1
4/23 | 07:00:00 | 278.15 | 98780 | 5.1 | 270 | 5.1875 | 500.4 | 864 | 263.323 | 0 | 1
4/23 | 08:00:00 | 280.15 | 98798 | 3.6 | 290 | 5.5661 | 1054.8 | 1634.4 | 265.444 | 0 | 1
4/23 | 09:00:00 | 281.15 | 98806 | 4.6 | 280 | 5.1861 | 1616.4 | 2127.6 | 266.163 | 0 | 1
4/23 | 10:00:00 | 283.15 | 98824 | 4.1 | 270 | 4.829 | 2098.8 | 2566.8 | 267.824 | 0 | 1
4/23 | 11:00:00 | 283.15 | 98824 | 3.1 | 250 | 4.4948 | 2314.8 | 2221.2 | 267.852 | 0 | 1
4/23 | 12:00:00 | 284.15 | 98833 | 3.6 | 270 | 4.8285 | 2491.2 | 2419.2 | 269.033 | 0 | 1
4/23 | 13:00:00 | 285.15 | 98841 | 3.6 | 280 | 4.8281 | 2505.6 | 2268 | 269.98 | 0 | 1
4/23 | 14:00:00 | 285.15 | 98841 | 5.7 | 280 | 4.8281 | 2494.8 | 2710.8 | 269.716 | 0 | 1
4/23 | 15:00:00 | 285.15 | 98841 | 5.7 | 280 | 4.8281 | 2170.8 | 2595.6 | 269.716 | 0 | 1
4/23 | 16:00:00 | 285.15 | 98841 | 7.7 | 280 | 4.8281 | 1710 | 2178 | 269.716 | 0 | 1
4/23 | 17:00:00 | 283.15 | 98824 | 7.2 | 270 | 4.4948 | 1148.4 | 1717.2 | 267.724 | 0 | 1
4/23 | 18:00:00 | 283.15 | 98824 | 7.2 | 270 | 4.1815 | 594 | 871.2 | 267.355 | 0 | 1
4/23 | 19:00:00 | 282.15 | 98815 | 6.2 | 280 | 4.1819 | 140.4 | 64.8 | 266.544 | 0 | 1
4/23 | 20:00:00 | 280.15 | 98798 | 6.7 | 280 | 4.8303 | 0 | 0 | 264.986 | 0 | 1
4/23 | 21:00:00 | 280.15 | 98798 | 5.7 | 280 | 4.8303 | 0 | 0 | 264.986 | 0 | 1
4/23 | 22:00:00 | 280.15 | 98798 | 2.6 | 250 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
4/23 | 23:00:00 | 280.15 | 98798 | 6.2 | 250 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
4/23 | 24:00:00 | 281.15 | 98806 | 6.2 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
4/24 | 01:00:00 | 281.15 | 98806 | 6.2 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1
4/24 | 02:00:00 | 281.15 | 98806 | 7.2 | 260 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
4/24 | 03:00:00 | 281.15 | 98806 | 7.7 | 260 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
4/24 | 04:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
4/24 | 05:00:00 | 281.15 | 98806 | 7.2 | 290 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
4/24 | 06:00:00 | 281.15 | 98806 | 5.1 | 280 | 5.9698 | 93.6 | 0 | 266.881 | 0 | 1
4/24 | 07:00:00 | 281.15 | 98806 | 4.6 | 260 | 5.5656 | 486 | 576 | 266.653 | 0 | 1
4/24 | 08:00:00 | 281.15 | 98806 | 5.1 | 280 | 5.9698 | 1011.6 | 1360.8 | 266.881 | 0 | 1
4/24 | 09:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.3994 | 1533.6 | 1504.8 | 268.057 | 0 | 1
4/24 | 10:00:00 | 281.15 | 98806 | 7.7 | 300 | 5.9698 | 1101.6 | 255.6 | 267.353 | 0 | 1
4/24 | 11:00:00 | 280.15 | 98798 | 3.1 | 290 | 5.5661 | 2318.4 | 1915.2 | 265.704 | 0 | 1
4/24 | 12:00:00 | 281.15 | 98806 | 5.1 | 330 | 4.4957 | 2509.2 | 2430 | 265.96 | 0 | 1
4/24 | 13:00:00 | 283.15 | 98824 | 8.8 | 310 | 3.8875 | 2527.2 | 2455.2 | 267.38 | 0 | 1
4/24 | 14:00:00 | 283.15 | 98824 | 7.7 | 290 | 3.5773 | 2379.6 | 2440.8 | 267.142 | 0 | 1
4/24 | 15:00:00 | 283.15 | 98824 | 10.8 | 280 | 3.8875 | 2066.4 | 2160 | 267.38 | 0 | 1
4/24 | 16:00:00 | 282.15 | 98815 | 12.9 | 290 | 2.7781 | 1738.8 | 2149.2 | 265.217 | 0 | 1
4/24 | 17:00:00 | 278.15 | 98780 | 10.8 | 310 | 3.5789 | 1108.8 | 1260 | 262.425 | 0 | 1
4/24 | 18:00:00 | 279.15 | 98789 | 10.8 | 300 | 3.0251 | 612 | 900 | 262.637 | 0 | 1
4/24 | 19:00:00 | 278.15 | 98780 | 9.8 | 290 | 3.0253 | 151.2 | 90 | 261.696 | 0 | 1
4/24 | 20:00:00 | 276.15 | 98762 | 9.3 | 320 | 3.0259 | 0 | 0 | 259.814 | 0 | 1
4/24 | 21:00:00 | 275.15 | 98752 | 7.7 | 310 | 3.2924 | 0 | 0 | 259.107 | 0 | 1
4/24 | 22:00:00 | 274.15 | 98743 | 5.7 | 290 | 3.5803 | 0 | 0 | 258.398 | 0 | 1
4/24 | 23:00:00 | 273.15 | 98734 | 6.7 | 300 | 3.293 | 0 | 0 | 257.224 | 0 | 1
4/24 | 24:00:00 | 273.15 | 98734 | 6.2 | 290 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
4/25 | 01:00:00 | 273.15 | 98734 | 5.1 | 290 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
4/25 | 02:00:00 | 272.15 | 98724 | 6.2 | 310 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
4/25 | 03:00:00 | 273.15 | 98734 | 6.2 | 310 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
4/25 | 04:00:00 | 272.15 | 98724 | 5.7 | 310 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
4/25 | 05:00:00 | 272.15 | 98724 | 6.7 | 330 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
4/25 | 06:00:00 | 272.15 | 98724 | 5.7 | 310 | 2.7806 | 86.4 | 0 | 256.302 | 0 | 1
4/25 | 07:00:00 | 273.15 | 98734 | 5.1 | 290 | 3.0267 | 428.4 | 302.4 | 257.478 | 0 | 1
4/25 | 08:00:00 | 275.15 | 98752 | 6.2 | 300 | 3.0262 | 1101.6 | 1454.4 | 258.873 | 0 | 1
4/25 | 09:00:00 | 277.15 | 98771 | 7.2 | 300 | 3.2918 | 1569.6 | 1591.2 | 261.246 | 0 | 1
4/25 | 10:00:00 | 278.15 | 98780 | 7.7 | 320 | 3.0253 | 1123.2 | 28.8 | 262.415 | 0 | 1
4/25 | 11:00:00 | 278.15 | 98780 | 8.2 | 330 | 3.0253 | 1310.4 | 93.6 | 262.415 | 0 | 1
4/25 | 12:00:00 | 278.15 | 98780 | 6.2 | 320 | 3.2915 | 1407.6 | 198 | 262.653 | 0 | 1
4/25 | 13:00:00 | 279.15 | 98789 | 6.7 | 340 | 3.2912 | 2548.8 | 1969.2 | 263.132 | 0 | 1
4/25 | 14:00:00 | 281.15 | 98806 | 6.7 | 350 | 3.2906 | 2394 | 2448 | 265.017 | 0 | 1
4/25 | 15:00:00 | 276.15 | 98762 | 4.1 | 350 | 4.1841 | 2077.2 | 2152.8 | 261.001 | 0 | 1
4/25 | 16:00:00 | 277.15 | 98771 | 5.1 | 30 | 4.1838 | 1641.6 | 1519.2 | 261.946 | 0 | 1
4/25 | 17:00:00 | 279.15 | 98789 | 4.6 | 360 | 4.183 | 1119.6 | 1252.8 | 263.837 | 0 | 1
4/25 | 18:00:00 | 279.15 | 98789 | 5.7 | 20 | 3.8889 | 583.2 | 734.4 | 263.603 | 0 | 1
4/25 | 19:00:00 | 278.15 | 98780 | 6.2 | 350 | 3.5789 | 151.2 | 46.8 | 262.425 | 0 | 1
4/25 | 20:00:00 | 276.15 | 98762 | 5.1 | 340 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
4/25 | 21:00:00 | 276.15 | 98762 | 7.2 | 360 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
4/25 | 22:00:00 | 276.15 | 98762 | 4.1 | 330 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
4/25 | 23:00:00 | 275.15 | 98752 | 5.7 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
4/25 | 24:00:00 | 275.15 | 98752 | 5.7 | 320 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
4/26 | 01:00:00 | 275.15 | 98752 | 6.2 | 350 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
4/26 | 02:00:00 | 275.15 | 98752 | 6.2 | 350 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
4/26 | 03:00:00 | 275.15 | 98752 | 6.2 | 340 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
4/26 | 04:00:00 | 275.15 | 98752 | 4.6 | 340 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
4/26 | 05:00:00 | 274.15 | 98743 | 4.6 | 320 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
4/26 | 06:00:00 | 275.15 | 98752 | 5.7 | 320 | 3.5799 | 111.6 | 0 | 259.594 | 0 | 1
4/26 | 07:00:00 | 275.15 | 98752 | 7.2 | 340 | 3.2924 | 522 | 518.4 | 259.361 | 0 | 1
4/26 | 08:00:00 | 276.15 | 98762 | 6.2 | 350 | 3.2921 | 1054.8 | 1209.6 | 260.304 | 0 | 1
4/26 | 09:00:00 | 277.15 | 98771 | 7.2 | 360 | 3.2918 | 1587.6 | 1497.6 | 261.246 | 0 | 1
4/26 | 10:00:00 | 279.15 | 98789 | 6.2 | 10 | 3.5786 | 2037.6 | 2138.4 | 263.368 | 0 | 1
4/26 | 11:00:00 | 279.15 | 98789 | 6.2 | 350 | 3.0251 | 2372.4 | 2451.6 | 262.894 | 0 | 1
4/26 | 12:00:00 | 280.15 | 98798 | 5.1 | 30 | 3.5783 | 2545.2 | 2462.4 | 264.312 | 0 | 1
4/26 | 13:00:00 | 279.15 | 98789 | 5.1 | 10 | 3.0251 | 2566.8 | 2487.6 | 262.894 | 0 | 1
4/26 | 14:00:00 | 281.15 | 98806 | 5.1 | 20 | 3.2906 | 2408.4 | 2448 | 265.017 | 0 | 1
4/26 | 15:00:00 | 280.15 | 98798 | 5.1 | 20 | 2.7786 | 2106 | 2163.6 | 263.595 | 0 | 1
4/26 | 16:00:00 | 280.15 | 98798 | 4.6 | 30 | 3.5783 | 1659.6 | 1540.8 | 264.312 | 0 | 1
4/26 | 17:00:00 | 279.15 | 98789 | 4.6 | 40 | 3.5786 | 1137.6 | 1270.8 | 263.368 | 0 | 1
4/26 | 18:00:00 | 279.15 | 98789 | 3.1 | 20 | 3.5786 | 633.6 | 918 | 263.11 | 0 | 1
4/26 | 19:00:00 | 277.15 | 98771 | 1.5 | 328 | 4.1838 | 158.4 | 72 | 261.946 | 0 | 1
4/26 | 20:00:00 | 277.15 | 98771 | 1 | 147 | 3.8896 | 0 | 0 | 261.458 | 0 | 1
4/26 | 21:00:00 | 276.15 | 98762 | 1.5 | 270 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
4/26 | 22:00:00 | 276.15 | 98762 | 1.5 | 260 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
4/26 | 23:00:00 | 276.15 | 98762 | 2.6 | 250 | 3.8899 | 0 | 0 | 260.515 | 0 | 1
4/26 | 24:00:00 | 276.15 | 98762 | 3.1 | 260 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
4/27 | 01:00:00 | 276.15 | 98762 | 3.6 | 260 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
4/27 | 02:00:00 | 276.15 | 98762 | 4.1 | 260 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
4/27 | 03:00:00 | 276.15 | 98762 | 4.1 | 270 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
4/27 | 04:00:00 | 276.15 | 98762 | 4.6 | 270 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
4/27 | 05:00:00 | 276.15 | 98762 | 3.6 | 260 | 3.5796 | 0 | 0 | 260.283 | 0 | 1
4/27 | 06:00:00 | 277.15 | 98771 | 4.6 | 280 | 4.1838 | 68.4 | 0 | 262.41 | 0 | 1
4/27 | 07:00:00 | 277.15 | 98771 | 6.7 | 280 | 4.4973 | 295.2 | 0 | 262.64 | 0 | 1
4/27 | 08:00:00 | 278.15 | 98780 | 6.2 | 270 | 5.1875 | 1062 | 1188 | 263.581 | 0 | 1
4/27 | 09:00:00 | 280.15 | 98798 | 5.7 | 280 | 5.1865 | 1587.6 | 1918.8 | 265.476 | 0 | 1
4/27 | 10:00:00 | 281.15 | 98806 | 7.7 | 300 | 5.1861 | 2037.6 | 2131.2 | 266.423 | 0 | 1
4/27 | 11:00:00 | 282.15 | 98815 | 6.7 | 290 | 5.1856 | 2365.2 | 2365.2 | 267.371 | 0 | 1
4/27 | 12:00:00 | 283.15 | 98824 | 6.2 | 300 | 5.1851 | 2541.6 | 2397.6 | 268.319 | 0 | 1
4/27 | 13:00:00 | 284.15 | 98833 | 7.2 | 300 | 5.1847 | 2556 | 2401.2 | 269.266 | 0 | 1
4/27 | 14:00:00 | 284.15 | 98833 | 6.7 | 290 | 5.1847 | 2401.2 | 2372.4 | 269.266 | 0 | 1
4/27 | 15:00:00 | 282.15 | 98815 | 3.6 | 330 | 5.5651 | 2091.6 | 2142 | 267.601 | 0 | 1
4/27 | 16:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.3994 | 1652.4 | 1947.6 | 268.057 | 0 | 1
4/27 | 17:00:00 | 283.15 | 98824 | 5.1 | 270 | 6.3988 | 1137.6 | 1454.4 | 269.007 | 0 | 1
4/27 | 18:00:00 | 283.15 | 98824 | 5.7 | 280 | 6.3988 | 601.2 | 698.4 | 269.007 | 0 | 1
4/27 | 19:00:00 | 280.15 | 98798 | 4.1 | 10 | 6.4005 | 93.6 | 0 | 266.628 | 0 | 1
4/27 | 20:00:00 | 279.15 | 98789 | 4.6 | 20 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
4/27 | 21:00:00 | 279.15 | 98789 | 2.1 | 30 | 5.9708 | 0 | 0 | 264.982 | 0 | 1
4/27 | 22:00:00 | 279.15 | 98789 | 3.1 | 30 | 5.187 | 0 | 0 | 264.528 | 0 | 1
4/27 | 23:00:00 | 279.15 | 98789 | 1.5 | 214 | 5.187 | 0 | 0 | 264.528 | 0 | 1
4/27 | 24:00:00 | 278.15 | 98780 | 2.1 | 20 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
4/28 | 01:00:00 | 278.15 | 98780 | 3.1 | 350 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
4/28 | 02:00:00 | 278.15 | 98780 | 2.6 | 340 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
4/28 | 03:00:00 | 278.15 | 98780 | 3.1 | 360 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
4/28 | 04:00:00 | 276.15 | 98762 | 3.1 | 320 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
4/28 | 05:00:00 | 275.15 | 98752 | 3.6 | 310 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
4/28 | 06:00:00 | 276.15 | 98762 | 2.6 | 310 | 4.1841 | 82.8 | 0 | 261.463 | 0 | 1
4/28 | 07:00:00 | 277.15 | 98771 | 2.6 | 290 | 4.4973 | 302.4 | 0 | 262.64 | 0 | 1
4/28 | 08:00:00 | 279.15 | 98789 | 3.6 | 320 | 4.4964 | 597.6 | 180 | 264.536 | 0 | 1
4/28 | 09:00:00 | 279.15 | 98789 | 2.1 | 360 | 4.4964 | 1609.2 | 1580.4 | 264.069 | 0 | 1
4/28 | 10:00:00 | 281.15 | 98806 | 3.1 | 10 | 4.4957 | 2059.2 | 1976.4 | 265.96 | 0 | 1
4/28 | 11:00:00 | 281.15 | 98806 | 2.6 | 326 | 4.1823 | 1324.8 | 190.8 | 266.197 | 0 | 1
4/28 | 12:00:00 | 282.15 | 98815 | 3.1 | 14 | 4.1819 | 1422 | 194.4 | 267.144 | 0 | 1
4/28 | 13:00:00 | 283.15 | 98824 | 1 | 194 | 4.4948 | 2574 | 1443.6 | 267.852 | 0 | 1
4/28 | 14:00:00 | 284.15 | 98833 | 2.1 | 42 | 4.4944 | 1342.8 | 205.2 | 269.274 | 0 | 1
4/28 | 15:00:00 | 283.15 | 98824 | 1.5 | 26 | 4.829 | 1170 | 223.2 | 268.561 | 0 | 1
4/28 | 16:00:00 | 283.15 | 98824 | 2.1 | 258 | 4.4948 | 932.4 | 72 | 268.326 | 0 | 1
4/28 | 17:00:00 | 283.15 | 98824 | 3.1 | 280 | 4.829 | 640.8 | 93.6 | 268.561 | 0 | 1
4/28 | 18:00:00 | 282.15 | 98815 | 2.1 | 280 | 5.1856 | 619.2 | 720 | 267.371 | 0 | 1
4/28 | 19:00:00 | 282.15 | 98815 | 2.6 | 270 | 5.1856 | 176.4 | 100.8 | 267.371 | 0 | 1
4/28 | 20:00:00 | 281.15 | 98806 | 2.1 | 300 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
4/28 | 21:00:00 | 281.15 | 98806 | 2.1 | 300 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
4/28 | 22:00:00 | 280.15 | 98798 | 3.1 | 290 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
4/28 | 23:00:00 | 280.15 | 98798 | 3.6 | 280 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
4/28 | 24:00:00 | 280.15 | 98798 | 2.6 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/29 | 01:00:00 | 280.15 | 98798 | 1 | 210 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/29 | 02:00:00 | 279.15 | 98789 | 1 | 230 | 5.5666 | 0 | 0 | 264.075 | 0 | 1
4/29 | 03:00:00 | 279.15 | 98789 | 1 | 290 | 5.5666 | 0 | 0 | 264.075 | 0 | 1
4/29 | 04:00:00 | 279.15 | 98789 | 1.5 | 250 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
4/29 | 05:00:00 | 279.15 | 98789 | 0.5 | 312 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
4/29 | 06:00:00 | 279.15 | 98789 | 0 | 246 | 5.5666 | 79.2 | 0 | 265.224 | 0 | 1
4/29 | 07:00:00 | 280.15 | 98798 | 0.5 | 273 | 5.5661 | 309.6 | 0 | 266.174 | 0 | 1
4/29 | 08:00:00 | 280.15 | 98798 | 1 | 82 | 5.5661 | 604.8 | 176.4 | 266.174 | 0 | 1
4/29 | 09:00:00 | 281.15 | 98806 | 1 | 168 | 5.5656 | 1616.4 | 1562.4 | 266.653 | 0 | 1
4/29 | 10:00:00 | 281.15 | 98806 | 0.5 | 164 | 5.5656 | 2062.8 | 2124 | 266.653 | 0 | 1
4/29 | 11:00:00 | 282.15 | 98815 | 1.5 | 161 | 5.1856 | 2394 | 2361.6 | 267.371 | 0 | 1
4/29 | 12:00:00 | 283.15 | 98824 | 1 | 11 | 5.1851 | 2570.4 | 2397.6 | 268.319 | 0 | 1
4/29 | 13:00:00 | 283.15 | 98824 | 3.1 | 210 | 5.1851 | 2581.2 | 2397.6 | 268.319 | 0 | 1
4/29 | 14:00:00 | 284.15 | 98833 | 3.1 | 160 | 5.1847 | 2426.4 | 1929.6 | 269.266 | 0 | 1
4/29 | 15:00:00 | 284.15 | 98833 | 3.6 | 170 | 5.1847 | 1177.2 | 190.8 | 269.743 | 0 | 1
4/29 | 16:00:00 | 284.15 | 98833 | 4.6 | 150 | 4.4944 | 939.6 | 72 | 269.274 | 0 | 1
4/29 | 17:00:00 | 283.15 | 98824 | 5.1 | 160 | 4.4948 | 648 | 50.4 | 268.326 | 0 | 1
4/29 | 18:00:00 | 283.15 | 98824 | 3.1 | 160 | 4.4948 | 349.2 | 7.2 | 268.326 | 0 | 1
4/29 | 19:00:00 | 283.15 | 98824 | 3.1 | 140 | 4.829 | 61.2 | 0 | 268.669 | 0 | 1
4/29 | 20:00:00 | 283.15 | 98824 | 3.6 | 130 | 4.829 | 0 | 0 | 268.561 | 0 | 1
4/29 | 21:00:00 | 282.15 | 98815 | 3.1 | 120 | 5.1856 | 0 | 0 | 267.844 | 0 | 1
4/29 | 22:00:00 | 282.15 | 98815 | 5.1 | 120 | 5.5651 | 0 | 0 | 268.075 | 0 | 1
4/29 | 23:00:00 | 282.15 | 98815 | 4.6 | 120 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
4/29 | 24:00:00 | 281.15 | 98806 | 5.1 | 130 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
4/30 | 01:00:00 | 280.15 | 98798 | 4.6 | 130 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
4/30 | 02:00:00 | 279.15 | 98789 | 5.1 | 120 | 5.187 | 0 | 0 | 264.996 | 0 | 1
4/30 | 03:00:00 | 279.15 | 98789 | 5.1 | 110 | 5.187 | 0 | 0 | 264.996 | 0 | 1
4/30 | 04:00:00 | 279.15 | 98789 | 6.2 | 110 | 5.187 | 0 | 0 | 264.996 | 0 | 1
4/30 | 05:00:00 | 279.15 | 98789 | 5.7 | 100 | 5.187 | 0 | 0 | 264.269 | 0 | 1
4/30 | 06:00:00 | 279.15 | 98789 | 6.2 | 110 | 5.187 | 162 | 172.8 | 263.847 | 0 | 1
4/30 | 07:00:00 | 280.15 | 98798 | 6.7 | 110 | 5.1865 | 615.6 | 1062 | 264.793 | 0 | 1
4/30 | 08:00:00 | 281.15 | 98806 | 7.7 | 110 | 5.1861 | 1191.6 | 1803.6 | 265.738 | 0 | 1
4/30 | 09:00:00 | 283.15 | 98824 | 6.7 | 110 | 5.5646 | 1731.6 | 2188.8 | 268.287 | 0 | 1
4/30 | 10:00:00 | 284.15 | 98833 | 6.2 | 80 | 5.9681 | 1972.8 | 1778.4 | 269.854 | 0 | 1
4/30 | 11:00:00 | 285.15 | 98841 | 8.2 | 90 | 5.9676 | 2401.2 | 2127.6 | 270.678 | 0 | 1
4/30 | 12:00:00 | 285.15 | 98841 | 6.7 | 100 | 5.9676 | 2732.4 | 2793.6 | 270.413 | 0 | 1
4/30 | 13:00:00 | 286.15 | 98850 | 7.7 | 80 | 6.3971 | 2739.6 | 2887.2 | 271.592 | 0 | 1
4/30 | 14:00:00 | 286.15 | 98850 | 9.3 | 90 | 5.5631 | 2584.8 | 2869.2 | 271.13 | 0 | 1
4/30 | 15:00:00 | 286.15 | 98850 | 9.8 | 100 | 5.1837 | 2264.4 | 2602.8 | 270.896 | 0 | 1
4/30 | 16:00:00 | 285.15 | 98841 | 9.3 | 90 | 5.9676 | 1796.4 | 2386.8 | 270.413 | 0 | 1
4/30 | 17:00:00 | 284.15 | 98833 | 8.2 | 90 | 6.3982 | 1245.6 | 1782 | 269.693 | 0 | 1
4/30 | 18:00:00 | 284.15 | 98833 | 6.7 | 90 | 7.8598 | 673.2 | 878.4 | 270.371 | 0 | 1
4/30 | 19:00:00 | 282.35 | 98817 | 4.2 | 67 | 7.0966 | 64.8 | 0 | 269.17 | 0 | 1
4/30 | 20:00:00 | 281.95 | 98813 | 4 | 57 | 6.4888 | 0 | 0 | 268.495 | 0 | 1
4/30 | 21:00:00 | 281.35 | 98808 | 3.6 | 52 | 6.0536 | 0 | 0 | 267.697 | 0 | 1
4/30 | 22:00:00 | 281.75 | 98812 | 3 | 79 | 6.1383 | 0 | 0 | 267.902 | 0 | 1
4/30 | 23:00:00 | 282.35 | 98817 | 2.6 | 143 | 6.6246 | 0 | 0 | 268.723 | 0 | 1
4/30 | 24:00:00 | 282.95 | 98822 | 2.3 | 165 | 7.145 | 0 | 0 | 269.656 | 0 | 1
5/1 | 01:00:00 | 283.45 | 98827 | 2.3 | 192 | 7.4948 | 0 | 0 | 270.399 | 0 | 1
5/1 | 02:00:00 | 283.25 | 98825 | 2.3 | 188 | 7.3934 | 0 | 0 | 270.164 | 0 | 1
5/1 | 03:00:00 | 283.45 | 98827 | 2.5 | 154 | 7.3932 | 0 | 0 | 270.354 | 0 | 1
5/1 | 04:00:00 | 283.65 | 98829 | 2.7 | 170 | 7.3427 | 0 | 0 | 269.671 | 0 | 1
5/1 | 05:00:00 | 284.15 | 98833 | 3.2 | 182 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
5/1 | 06:00:00 | 284.65 | 98837 | 3.8 | 192 | 7.3422 | 169.2 | 108 | 270.622 | 0 | 1
5/1 | 07:00:00 | 284.15 | 98833 | 3.1 | 190 | 7.3425 | 583.2 | 658.8 | 270.411 | 0 | 1
5/1 | 08:00:00 | 285.15 | 98841 | 4.6 | 210 | 7.3418 | 1112.4 | 1407.6 | 271.363 | 0 | 1
5/1 | 09:00:00 | 285.15 | 98841 | 4.6 | 200 | 7.3418 | 1634.4 | 1818 | 271.363 | 0 | 1
5/1 | 10:00:00 | 286.15 | 98850 | 4.6 | 210 | 7.3412 | 2206.8 | 2480.4 | 272.048 | 0 | 1
5/1 | 11:00:00 | 288.15 | 98867 | 6.2 | 200 | 6.8534 | 2404.8 | 2250 | 273.988 | 0 | 1
5/1 | 12:00:00 | 289.15 | 98875 | 6.2 | 200 | 6.3955 | 2581.2 | 2289.6 | 274.708 | 0 | 1
5/1 | 13:00:00 | 289.15 | 98875 | 6.7 | 210 | 5.1824 | 2797.2 | 2750.4 | 273.596 | 0 | 1
5/1 | 14:00:00 | 287.15 | 98858 | 5.1 | 230 | 4.4933 | 2458.8 | 2084.4 | 271.636 | 0 | 1
5/1 | 15:00:00 | 284.15 | 98833 | 5.1 | 240 | 5.5641 | 2271.6 | 2440.8 | 269.234 | 0 | 1
5/1 | 16:00:00 | 284.15 | 98833 | 4.1 | 210 | 6.8558 | 1699.2 | 1879.2 | 270.185 | 0 | 1
5/1 | 17:00:00 | 285.15 | 98841 | 6.2 | 220 | 6.3977 | 1184.4 | 1479.6 | 270.907 | 0 | 1
5/1 | 18:00:00 | 285.15 | 98841 | 5.1 | 240 | 6.3977 | 648 | 918 | 270.907 | 0 | 1
5/1 | 19:00:00 | 285.15 | 98841 | 5.1 | 220 | 6.8552 | 212.4 | 187.2 | 270.871 | 0 | 1
5/1 | 20:00:00 | 284.15 | 98833 | 2.1 | 240 | 6.8558 | 0 | 0 | 269.921 | 0 | 1
5/1 | 21:00:00 | 283.15 | 98824 | 3.1 | 250 | 6.3988 | 0 | 0 | 268.744 | 0 | 1
5/1 | 22:00:00 | 282.15 | 98815 | 2.6 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/1 | 23:00:00 | 280.15 | 98798 | 1.5 | 209 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
5/1 | 24:00:00 | 281.15 | 98806 | 2.1 | 240 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
5/2 | 01:00:00 | 281.15 | 98806 | 2.6 | 220 | 6.4 | 0 | 0 | 267.688 | 0 | 1
5/2 | 02:00:00 | 281.15 | 98806 | 2.6 | 230 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/2 | 03:00:00 | 280.15 | 98798 | 1 | 229 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
5/2 | 04:00:00 | 279.15 | 98789 | 1 | 282 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
5/2 | 05:00:00 | 279.15 | 98789 | 1.5 | 111 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
5/2 | 06:00:00 | 278.15 | 98780 | 1.5 | 240 | 5.5671 | 180 | 126 | 263.549 | 0 | 1
5/2 | 07:00:00 | 281.15 | 98806 | 1.5 | 95 | 5.9698 | 637.2 | 1040.4 | 266.62 | 0 | 1
5/2 | 08:00:00 | 282.15 | 98815 | 4.1 | 270 | 5.9692 | 1202.4 | 1735.2 | 267.568 | 0 | 1
5/2 | 09:00:00 | 284.15 | 98833 | 3.6 | 270 | 5.5641 | 1659.6 | 1947.6 | 269.498 | 0 | 1
5/2 | 10:00:00 | 283.15 | 98824 | 3.6 | 300 | 5.5646 | 2235.6 | 2422.8 | 268.287 | 0 | 1
5/2 | 11:00:00 | 284.15 | 98833 | 3.1 | 250 | 4.8285 | 2584.8 | 2883.6 | 268.77 | 0 | 1
5/2 | 12:00:00 | 286.15 | 98850 | 5.1 | 250 | 4.8277 | 2768.4 | 2937.6 | 270.662 | 0 | 1
5/2 | 13:00:00 | 285.15 | 98841 | 5.7 | 260 | 4.494 | 2782.8 | 2952 | 269.481 | 0 | 1
5/2 | 14:00:00 | 287.15 | 98858 | 5.1 | 230 | 4.8273 | 2617.2 | 2894.4 | 271.608 | 0 | 1
5/2 | 15:00:00 | 287.15 | 98858 | 5.7 | 260 | 4.4933 | 2293.2 | 2592 | 271.371 | 0 | 1
5/2 | 16:00:00 | 285.15 | 98841 | 4.6 | 280 | 4.494 | 1832.4 | 2394 | 269.481 | 0 | 1
5/2 | 17:00:00 | 285.15 | 98841 | 4.6 | 280 | 4.8281 | 1278 | 1828.8 | 269.716 | 0 | 1
5/2 | 18:00:00 | 285.15 | 98841 | 5.1 | 270 | 4.8281 | 705.6 | 1159.2 | 269.716 | 0 | 1
5/2 | 19:00:00 | 285.15 | 98841 | 5.1 | 270 | 4.8281 | 223.2 | 208.8 | 269.716 | 0 | 1
5/2 | 20:00:00 | 283.15 | 98824 | 3.6 | 260 | 4.4948 | 3.6 | 0 | 267.724 | 0 | 1
5/2 | 21:00:00 | 281.15 | 98806 | 4.1 | 270 | 4.4957 | 0 | 0 | 265.96 | 0 | 1
5/2 | 22:00:00 | 281.15 | 98806 | 2.1 | 260 | 4.8299 | 0 | 0 | 266.316 | 0 | 1
5/2 | 23:00:00 | 280.15 | 98798 | 3.1 | 260 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
5/2 | 24:00:00 | 281.15 | 98806 | 3.6 | 270 | 4.8299 | 0 | 0 | 266.316 | 0 | 1
5/3 | 01:00:00 | 280.15 | 98798 | 2.6 | 250 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
5/3 | 02:00:00 | 281.15 | 98806 | 4.6 | 230 | 4.8299 | 0 | 0 | 266.316 | 0 | 1
5/3 | 03:00:00 | 281.15 | 98806 | 2.1 | 230 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
5/3 | 04:00:00 | 281.15 | 98806 | 5.1 | 230 | 4.8299 | 0 | 0 | 266.664 | 0 | 1
5/3 | 05:00:00 | 279.15 | 98789 | 4.1 | 290 | 5.187 | 0 | 0 | 264.528 | 0 | 1
5/3 | 06:00:00 | 278.15 | 98780 | 5.1 | 260 | 5.1875 | 180 | 93.6 | 263.581 | 0 | 1
5/3 | 07:00:00 | 280.15 | 98798 | 7.2 | 280 | 5.5661 | 612 | 867.6 | 265.704 | 0 | 1
5/3 | 08:00:00 | 280.15 | 98798 | 8.2 | 290 | 5.5661 | 1148.4 | 1404 | 265.704 | 0 | 1
5/3 | 09:00:00 | 282.15 | 98815 | 9.3 | 300 | 4.8294 | 1782 | 2178 | 266.878 | 0 | 1
5/3 | 10:00:00 | 282.15 | 98815 | 9.8 | 300 | 4.4952 | 2257.2 | 2574 | 266.645 | 0 | 1
5/3 | 11:00:00 | 283.15 | 98824 | 8.7 | 290 | 4.1815 | 2606.4 | 2912.4 | 267.355 | 0 | 1
5/3 | 12:00:00 | 283.15 | 98824 | 9.3 | 300 | 4.1815 | 2790 | 2962.8 | 267.355 | 0 | 1
5/3 | 13:00:00 | 284.15 | 98833 | 9.8 | 300 | 4.1811 | 2800.8 | 2750.4 | 268.3 | 0 | 1
5/3 | 14:00:00 | 282.15 | 98815 | 8.7 | 310 | 4.4952 | 2480.4 | 2221.2 | 266.906 | 0 | 1
5/3 | 15:00:00 | 283.15 | 98824 | 8.7 | 290 | 4.1815 | 2178 | 2149.2 | 267.617 | 0 | 1
5/3 | 16:00:00 | 283.15 | 98824 | 8.2 | 290 | 4.4948 | 1738.8 | 1767.6 | 267.852 | 0 | 1
5/3 | 17:00:00 | 284.15 | 98833 | 8.7 | 290 | 4.1811 | 1296 | 1569.6 | 268.3 | 0 | 1
5/3 | 18:00:00 | 283.15 | 98824 | 8.2 | 290 | 4.1815 | 720 | 997.2 | 267.355 | 0 | 1
5/3 | 19:00:00 | 282.15 | 98815 | 7.7 | 270 | 4.1819 | 234 | 172.8 | 266.411 | 0 | 1
5/3 | 20:00:00 | 280.15 | 98798 | 7.7 | 280 | 4.1826 | 7.2 | 0 | 264.523 | 0 | 1
5/3 | 21:00:00 | 279.15 | 98789 | 5.1 | 280 | 4.4964 | 0 | 0 | 264.31 | 0 | 1
5/3 | 22:00:00 | 278.15 | 98780 | 3.6 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
5/3 | 23:00:00 | 278.15 | 98780 | 3.6 | 260 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
5/3 | 24:00:00 | 278.15 | 98780 | 4.1 | 260 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
5/4 | 01:00:00 | 279.15 | 98789 | 6.2 | 270 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/4 | 02:00:00 | 279.15 | 98789 | 5.1 | 250 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/4 | 03:00:00 | 279.15 | 98789 | 7.2 | 260 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
5/4 | 04:00:00 | 279.15 | 98789 | 7.7 | 260 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/4 | 05:00:00 | 280.15 | 98798 | 4.6 | 250 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
5/4 | 06:00:00 | 280.15 | 98798 | 4.6 | 260 | 5.5661 | 187.2 | 108 | 265.704 | 0 | 1
5/4 | 07:00:00 | 280.15 | 98798 | 3.6 | 240 | 5.5661 | 626.4 | 885.6 | 265.704 | 0 | 1
5/4 | 08:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.5661 | 1162.8 | 1461.6 | 265.704 | 0 | 1
5/4 | 09:00:00 | 280.15 | 98798 | 5.7 | 250 | 5.5661 | 1688.4 | 1591.2 | 265.704 | 0 | 1
5/4 | 10:00:00 | 280.15 | 98798 | 6.7 | 250 | 5.1865 | 1184.4 | 82.8 | 265.946 | 0 | 1
5/4 | 11:00:00 | 281.15 | 98806 | 9.3 | 250 | 5.1861 | 1364.4 | 234 | 266.895 | 0 | 1
5/4 | 12:00:00 | 282.15 | 98815 | 9.3 | 250 | 5.5651 | 1458 | 72 | 268.075 | 0 | 1
5/4 | 13:00:00 | 281.15 | 98806 | 6.7 | 230 | 5.5656 | 1461.6 | 72 | 267.125 | 0 | 1
5/4 | 14:00:00 | 282.15 | 98815 | 6.7 | 240 | 5.9692 | 1375.2 | 230.4 | 268.304 | 0 | 1
5/4 | 15:00:00 | 283.15 | 98824 | 5.7 | 240 | 6.3988 | 1202.4 | 219.6 | 269.483 | 0 | 1
5/4 | 16:00:00 | 283.15 | 98824 | 8.7 | 260 | 6.8564 | 964.8 | 72 | 269.71 | 0 | 1
5/4 | 17:00:00 | 282.15 | 98815 | 6.2 | 240 | 7.3438 | 676.8 | 50.4 | 268.983 | 0 | 1
5/4 | 18:00:00 | 282.15 | 98815 | 5.1 | 230 | 7.3438 | 378 | 10.8 | 268.983 | 0 | 1
5/4 | 19:00:00 | 282.15 | 98815 | 3.6 | 250 | 7.3438 | 126 | 0 | 268.983 | 0 | 1
5/4 | 20:00:00 | 283.15 | 98824 | 11.3 | 270 | 7.3431 | 3.6 | 0 | 269.936 | 0 | 1
5/4 | 21:00:00 | 283.15 | 98824 | 9.8 | 270 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
5/4 | 22:00:00 | 283.15 | 98824 | 6.7 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
5/4 | 23:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
5/4 | 24:00:00 | 283.15 | 98824 | 5.7 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
5/5 | 01:00:00 | 282.15 | 98815 | 5.7 | 290 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
5/5 | 02:00:00 | 282.15 | 98815 | 6.7 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
5/5 | 03:00:00 | 282.15 | 98815 | 5.7 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
5/5 | 04:00:00 | 282.15 | 98815 | 5.7 | 260 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
5/5 | 05:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
5/5 | 06:00:00 | 282.15 | 98815 | 5.1 | 260 | 6.3994 | 108 | 0 | 268.532 | 0 | 1
5/5 | 07:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.8577 | 352.8 | 3.6 | 267.805 | 0 | 1
5/5 | 08:00:00 | 282.15 | 98815 | 5.1 | 260 | 7.3438 | 648 | 46.8 | 268.983 | 0 | 1
5/5 | 09:00:00 | 283.15 | 98824 | 4.1 | 260 | 7.3431 | 939.6 | 68.4 | 269.936 | 0 | 1
5/5 | 10:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.8605 | 1180.8 | 212.4 | 270.161 | 0 | 1
5/5 | 11:00:00 | 284.15 | 98833 | 7.2 | 270 | 7.3425 | 1360.8 | 226.8 | 270.89 | 0 | 1
5/5 | 12:00:00 | 283.15 | 98824 | 7.7 | 260 | 7.3431 | 1454.4 | 72 | 269.936 | 0 | 1
5/5 | 13:00:00 | 284.15 | 98833 | 8.7 | 260 | 7.3425 | 1458 | 72 | 270.89 | 0 | 1
5/5 | 14:00:00 | 284.15 | 98833 | 9.3 | 260 | 6.8558 | 1375.2 | 226.8 | 270.663 | 0 | 1
5/5 | 15:00:00 | 284.15 | 98833 | 8.2 | 250 | 6.8558 | 1209.6 | 219.6 | 270.663 | 0 | 1
5/5 | 16:00:00 | 284.15 | 98833 | 8.2 | 250 | 6.8558 | 968.4 | 50.4 | 270.663 | 0 | 1
5/5 | 17:00:00 | 284.15 | 98833 | 8.2 | 250 | 6.8558 | 684 | 50.4 | 270.663 | 0 | 1
5/5 | 18:00:00 | 284.15 | 98833 | 8.2 | 250 | 6.8558 | 385.2 | 10.8 | 270.663 | 0 | 1
5/5 | 19:00:00 | 284.15 | 98833 | 8.7 | 250 | 6.8558 | 133.2 | 0 | 270.663 | 0 | 1
5/5 | 20:00:00 | 284.15 | 98833 | 9.3 | 250 | 6.3982 | 14.4 | 0 | 269.957 | 0 | 1
5/5 | 21:00:00 | 284.15 | 98833 | 8.7 | 250 | 6.8558 | 0 | 0 | 270.663 | 0 | 1
5/5 | 22:00:00 | 284.15 | 98833 | 10.8 | 250 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
5/5 | 23:00:00 | 284.15 | 98833 | 11.8 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
5/5 | 24:00:00 | 284.15 | 98833 | 12.9 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
5/6 | 01:00:00 | 284.15 | 98833 | 12.3 | 260 | 6.8558 | 0 | 0 | 270.663 | 0 | 1
5/6 | 02:00:00 | 283.15 | 98824 | 10.3 | 260 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
5/6 | 03:00:00 | 283.15 | 98824 | 8.2 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
5/6 | 04:00:00 | 283.15 | 98824 | 7.7 | 260 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
5/6 | 05:00:00 | 283.15 | 98824 | 5.7 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
5/6 | 06:00:00 | 283.15 | 98824 | 4.6 | 280 | 7.3431 | 115.2 | 0 | 269.936 | 0 | 1
5/6 | 07:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.8605 | 648 | 709.2 | 269.684 | 0 | 1
5/6 | 08:00:00 | 284.15 | 98833 | 7.7 | 280 | 7.3425 | 655.2 | 90 | 270.89 | 0 | 1
5/6 | 09:00:00 | 284.15 | 98833 | 6.7 | 270 | 7.3425 | 943.2 | 68.4 | 270.89 | 0 | 1
5/6 | 10:00:00 | 285.15 | 98841 | 8.2 | 260 | 7.8591 | 1188 | 212.4 | 272.069 | 0 | 1
5/6 | 11:00:00 | 285.15 | 98841 | 9.3 | 250 | 7.8591 | 1364.4 | 223.2 | 272.069 | 0 | 1
5/6 | 12:00:00 | 285.15 | 98841 | 8.2 | 260 | 7.8591 | 1458 | 72 | 272.069 | 0 | 1
5/6 | 13:00:00 | 285.15 | 98841 | 7.7 | 250 | 7.3418 | 1465.2 | 223.2 | 271.843 | 0 | 1
5/6 | 14:00:00 | 285.15 | 98841 | 6.7 | 250 | 7.8591 | 2484 | 1897.2 | 271.588 | 0 | 1
5/6 | 15:00:00 | 287.15 | 98858 | 7.7 | 250 | 7.3406 | 2185.2 | 2102.4 | 273.266 | 0 | 1
5/6 | 16:00:00 | 287.15 | 98858 | 6.2 | 240 | 6.854 | 1864.8 | 2278.8 | 272.77 | 0 | 1
5/6 | 17:00:00 | 286.15 | 98850 | 8.7 | 240 | 6.8546 | 1242 | 1501.2 | 272.087 | 0 | 1
5/6 | 18:00:00 | 286.15 | 98850 | 9.3 | 240 | 6.3971 | 748.8 | 1188 | 271.592 | 0 | 1
5/6 | 19:00:00 | 286.15 | 98850 | 7.7 | 240 | 5.9671 | 244.8 | 313.2 | 271.627 | 0 | 1
5/6 | 20:00:00 | 285.15 | 98841 | 7.2 | 230 | 6.3977 | 18 | 0 | 270.907 | 0 | 1
5/6 | 21:00:00 | 285.15 | 98841 | 7.7 | 240 | 5.5636 | 0 | 0 | 270.447 | 0 | 1
5/6 | 22:00:00 | 284.15 | 98833 | 7.2 | 230 | 6.3982 | 0 | 0 | 269.957 | 0 | 1
5/6 | 23:00:00 | 284.15 | 98833 | 8.7 | 230 | 6.3982 | 0 | 0 | 269.957 | 0 | 1
5/6 | 24:00:00 | 283.15 | 98824 | 8.7 | 230 | 6.3988 | 0 | 0 | 269.483 | 0 | 1
5/7 | 01:00:00 | 282.15 | 98815 | 7.7 | 230 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
5/7 | 02:00:00 | 282.15 | 98815 | 9.3 | 250 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
5/7 | 03:00:00 | 281.15 | 98806 | 7.2 | 260 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/7 | 04:00:00 | 280.15 | 98798 | 8.2 | 260 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
5/7 | 05:00:00 | 280.15 | 98798 | 9.3 | 260 | 5.5661 | 3.6 | 0 | 266.174 | 0 | 1
5/7 | 06:00:00 | 280.15 | 98798 | 9.8 | 260 | 5.1865 | 230.4 | 208.8 | 265.216 | 0 | 1
5/7 | 07:00:00 | 280.15 | 98798 | 9.3 | 250 | 4.8303 | 705.6 | 1137.6 | 264.986 | 0 | 1
5/7 | 08:00:00 | 281.15 | 98806 | 11.3 | 260 | 4.8299 | 1278 | 1803.6 | 265.932 | 0 | 1
5/7 | 09:00:00 | 282.15 | 98815 | 11.3 | 250 | 4.4952 | 1731.6 | 1746 | 266.906 | 0 | 1
5/7 | 10:00:00 | 283.15 | 98824 | 8.7 | 260 | 4.4948 | 2178 | 2134.8 | 267.852 | 0 | 1
5/7 | 11:00:00 | 283.15 | 98824 | 7.7 | 260 | 4.4948 | 2498.4 | 2376 | 267.852 | 0 | 1
5/7 | 12:00:00 | 285.15 | 98841 | 7.2 | 240 | 4.1808 | 2674.8 | 2415.6 | 269.507 | 0 | 1
5/7 | 13:00:00 | 285.15 | 98841 | 7.2 | 240 | 4.1808 | 2682 | 2235.6 | 269.507 | 0 | 1
5/7 | 14:00:00 | 286.15 | 98850 | 7.2 | 250 | 4.4936 | 2678.4 | 2710.8 | 270.426 | 0 | 1
5/7 | 15:00:00 | 287.15 | 98858 | 6.7 | 230 | 4.4933 | 2354.4 | 2592 | 271.371 | 0 | 1
5/7 | 16:00:00 | 287.15 | 98858 | 7.2 | 220 | 4.4933 | 1893.6 | 2404.8 | 271.371 | 0 | 1
5/7 | 17:00:00 | 287.15 | 98858 | 7.7 | 230 | 4.1801 | 1342.8 | 1602 | 271.132 | 0 | 1
5/7 | 18:00:00 | 286.15 | 98850 | 8.2 | 220 | 4.4936 | 766.8 | 1231.2 | 270.426 | 0 | 1
5/7 | 19:00:00 | 285.15 | 98841 | 6.7 | 220 | 4.494 | 270 | 277.2 | 269.481 | 0 | 1
5/7 | 20:00:00 | 284.15 | 98833 | 8.7 | 230 | 4.1811 | 21.6 | 0 | 268.3 | 0 | 1
5/7 | 21:00:00 | 283.15 | 98824 | 6.7 | 230 | 4.4948 | 0 | 0 | 267.852 | 0 | 1
5/7 | 22:00:00 | 283.15 | 98824 | 9.3 | 230 | 4.4948 | 0 | 0 | 267.852 | 0 | 1
5/7 | 23:00:00 | 282.15 | 98815 | 7.2 | 230 | 3.8878 | 0 | 0 | 266.436 | 0 | 1
5/7 | 24:00:00 | 282.15 | 98815 | 7.7 | 210 | 4.4952 | 0 | 0 | 266.906 | 0 | 1
5/8 | 01:00:00 | 281.15 | 98806 | 8.7 | 210 | 4.4957 | 0 | 0 | 265.96 | 0 | 1
5/8 | 02:00:00 | 280.15 | 98798 | 7.7 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
5/8 | 03:00:00 | 280.15 | 98798 | 6.7 | 230 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
5/8 | 04:00:00 | 279.15 | 98789 | 6.2 | 230 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
5/8 | 05:00:00 | 279.15 | 98789 | 7.2 | 220 | 4.4964 | 10.8 | 0 | 263.81 | 0 | 1
5/8 | 06:00:00 | 279.15 | 98789 | 7.2 | 230 | 4.4964 | 241.2 | 223.2 | 263.81 | 0 | 1
5/8 | 07:00:00 | 280.15 | 98798 | 7.7 | 230 | 4.496 | 680.4 | 950.4 | 265.014 | 0 | 1
5/8 | 08:00:00 | 281.15 | 98806 | 8.2 | 230 | 4.1823 | 1296 | 1548 | 265.467 | 0 | 1
5/8 | 09:00:00 | 282.15 | 98815 | 8.2 | 240 | 4.4952 | 1746 | 1753.2 | 266.906 | 0 | 1
5/8 | 10:00:00 | 284.15 | 98833 | 14.4 | 240 | 3.577 | 2199.6 | 2127.6 | 268.085 | 0 | 1
5/8 | 11:00:00 | 283.15 | 98824 | 12.9 | 250 | 4.4948 | 2509.2 | 1926 | 267.852 | 0 | 1
5/8 | 12:00:00 | 281.15 | 98806 | 11.3 | 250 | 5.5656 | 1479.6 | 226.8 | 267.125 | 0 | 1
5/8 | 13:00:00 | 283.15 | 98824 | 9.8 | 250 | 5.1851 | 1486.8 | 72 | 268.793 | 0 | 1
5/8 | 14:00:00 | 284.15 | 98833 | 10.8 | 250 | 4.8285 | 1404 | 201.6 | 269.509 | 0 | 1
5/8 | 15:00:00 | 283.15 | 98824 | 10.8 | 260 | 5.5646 | 2221.2 | 1843.2 | 268.55 | 0 | 1
5/8 | 16:00:00 | 284.15 | 98833 | 9.8 | 250 | 4.8285 | 1904.4 | 2404.8 | 268.77 | 0 | 1
5/8 | 17:00:00 | 283.15 | 98824 | 8.7 | 260 | 5.9687 | 1346.4 | 1854 | 268.516 | 0 | 1
5/8 | 18:00:00 | 284.15 | 98833 | 10.3 | 260 | 4.8285 | 777.6 | 1234.8 | 268.77 | 0 | 1
5/8 | 19:00:00 | 284.15 | 98833 | 7.7 | 250 | 5.1847 | 280.8 | 288 | 269.003 | 0 | 1
5/8 | 20:00:00 | 282.15 | 98815 | 9.3 | 260 | 4.8294 | 25.2 | 0 | 266.878 | 0 | 1
5/8 | 21:00:00 | 281.15 | 98806 | 5.1 | 240 | 5.1861 | 0 | 0 | 266.163 | 0 | 1
5/8 | 22:00:00 | 281.15 | 98806 | 5.7 | 240 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
5/8 | 23:00:00 | 280.15 | 98798 | 3.6 | 240 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
5/8 | 24:00:00 | 280.15 | 98798 | 4.6 | 230 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
5/9 | 01:00:00 | 279.15 | 98789 | 4.1 | 210 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/9 | 02:00:00 | 279.15 | 98789 | 4.1 | 210 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/9 | 03:00:00 | 279.15 | 98789 | 3.1 | 210 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/9 | 04:00:00 | 279.15 | 98789 | 2.6 | 220 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/9 | 05:00:00 | 279.15 | 98789 | 1.5 | 69 | 5.187 | 14.4 | 0 | 264.269 | 0 | 1
5/9 | 06:00:00 | 279.15 | 98789 | 3.6 | 210 | 5.187 | 248.4 | 237.6 | 264.269 | 0 | 1
5/9 | 07:00:00 | 281.15 | 98806 | 5.7 | 220 | 5.5656 | 730.8 | 1155.6 | 266.392 | 0 | 1
5/9 | 08:00:00 | 282.15 | 98815 | 5.1 | 230 | 5.1856 | 1303.2 | 1814.4 | 267.11 | 0 | 1
5/9 | 09:00:00 | 283.15 | 98824 | 7.7 | 220 | 4.829 | 1861.2 | 2379.6 | 267.824 | 0 | 1
5/9 | 10:00:00 | 284.15 | 98833 | 7.2 | 230 | 4.1811 | 2340 | 2574 | 268.3 | 0 | 1
5/9 | 11:00:00 | 285.15 | 98841 | 8.2 | 230 | 4.494 | 2520 | 2210.4 | 269.744 | 0 | 1
5/9 | 12:00:00 | 284.15 | 98833 | 7.2 | 230 | 4.4944 | 2692.8 | 2401.2 | 268.798 | 0 | 1
5/9 | 13:00:00 | 285.15 | 98841 | 9.3 | 230 | 4.494 | 2700 | 2401.2 | 269.744 | 0 | 1
5/9 | 14:00:00 | 285.15 | 98841 | 7.7 | 210 | 4.494 | 2545.2 | 2379.6 | 269.744 | 0 | 1
5/9 | 15:00:00 | 285.15 | 98841 | 5.7 | 220 | 5.1842 | 2232 | 2156.4 | 270.214 | 0 | 1
5/9 | 16:00:00 | 281.15 | 98806 | 9.8 | 270 | 5.9698 | 1796.4 | 2098.8 | 266.881 | 0 | 1
5/9 | 17:00:00 | 282.15 | 98815 | 8.2 | 260 | 5.9692 | 1357.2 | 1944 | 267.568 | 0 | 1
5/9 | 18:00:00 | 283.15 | 98824 | 7.2 | 280 | 4.829 | 788.4 | 1249.2 | 267.824 | 0 | 1
5/9 | 19:00:00 | 282.15 | 98815 | 6.7 | 270 | 4.4952 | 291.6 | 306 | 266.645 | 0 | 1
5/9 | 20:00:00 | 281.15 | 98806 | 3.1 | 260 | 4.8299 | 28.8 | 0 | 265.932 | 0 | 1
5/9 | 21:00:00 | 280.15 | 98798 | 6.2 | 250 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
5/9 | 22:00:00 | 280.15 | 98798 | 5.1 | 260 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
5/9 | 23:00:00 | 280.15 | 98798 | 5.7 | 250 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
5/9 | 24:00:00 | 279.15 | 98789 | 4.1 | 250 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
5/10 | 01:00:00 | 280.15 | 98798 | 3.1 | 250 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
5/10 | 02:00:00 | 279.15 | 98789 | 0.5 | 90 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/10 | 03:00:00 | 279.15 | 98789 | 0.5 | 190 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/10 | 04:00:00 | 279.15 | 98789 | 1.5 | 160 | 5.187 | 0 | 0 | 264.269 | 0 | 1
5/10 | 05:00:00 | 279.15 | 98789 | 1.5 | 230 | 5.187 | 21.6 | 0 | 264.269 | 0 | 1
5/10 | 06:00:00 | 280.15 | 98798 | 1 | 230 | 5.5661 | 259.2 | 248.4 | 265.444 | 0 | 1
5/10 | 07:00:00 | 280.15 | 98798 | 1.5 | 214 | 5.5661 | 741.6 | 1170 | 265.444 | 0 | 1
5/10 | 08:00:00 | 281.15 | 98806 | 1.5 | 249 | 5.9698 | 1314 | 1807.2 | 266.62 | 0 | 1
5/10 | 09:00:00 | 282.15 | 98815 | 2.1 | 310 | 5.9692 | 1864.8 | 2383.2 | 267.568 | 0 | 1
5/10 | 10:00:00 | 283.15 | 98824 | 2.6 | 300 | 5.9687 | 2332.8 | 2610 | 268.516 | 0 | 1
5/10 | 11:00:00 | 284.15 | 98833 | 2.6 | 310 | 5.5641 | 2674.8 | 2725.2 | 269.234 | 0 | 1
5/10 | 12:00:00 | 283.15 | 98824 | 3.1 | 290 | 4.4948 | 2703.6 | 2138.4 | 267.852 | 0 | 1
5/10 | 13:00:00 | 283.15 | 98824 | 0.5 | 190 | 5.1851 | 2865.6 | 2768.4 | 268.056 | 0 | 1
5/10 | 14:00:00 | 283.15 | 98824 | 2.1 | 10 | 5.1851 | 2703.6 | 2876.4 | 268.056 | 0 | 1
5/10 | 15:00:00 | 284.15 | 98833 | 1.5 | 170 | 4.8285 | 2383.2 | 2602.8 | 268.77 | 0 | 1
5/10 | 16:00:00 | 283.15 | 98824 | 2.1 | 20 | 5.1851 | 1922.4 | 1987.2 | 268.056 | 0 | 1
5/10 | 17:00:00 | 283.15 | 98824 | 3.1 | 70 | 6.3988 | 716.4 | 212.4 | 269.483 | 0 | 1
5/10 | 18:00:00 | 283.15 | 98824 | 3.1 | 80 | 6.3988 | 414 | 18 | 269.483 | 0 | 1
5/10 | 19:00:00 | 282.15 | 98815 | 3.1 | 80 | 5.9692 | 154.8 | 0 | 268.304 | 0 | 1
5/10 | 20:00:00 | 282.15 | 98815 | 2.1 | 70 | 5.9692 | 25.2 | 0 | 268.191 | 0 | 1
5/10 | 21:00:00 | 281.15 | 98806 | 1.5 | 90 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
5/10 | 22:00:00 | 280.15 | 98798 | 2.1 | 70 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
5/10 | 23:00:00 | 279.15 | 98789 | 2.6 | 70 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/10 | 24:00:00 | 278.15 | 98780 | 2.6 | 50 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
5/11 | 01:00:00 | 278.15 | 98780 | 2.6 | 60 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
5/11 | 02:00:00 | 277.15 | 98771 | 3.1 | 20 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
5/11 | 03:00:00 | 277.15 | 98771 | 2.6 | 20 | 5.1879 | 0 | 0 | 262.633 | 0 | 1
5/11 | 04:00:00 | 277.15 | 98771 | 3.1 | 20 | 5.1879 | 0 | 0 | 262.633 | 0 | 1
5/11 | 05:00:00 | 277.15 | 98771 | 3.6 | 30 | 4.8316 | 25.2 | 0 | 262.149 | 0 | 1
5/11 | 06:00:00 | 278.15 | 98780 | 4.1 | 30 | 5.1875 | 266.4 | 262.8 | 263.323 | 0 | 1
5/11 | 07:00:00 | 279.15 | 98789 | 4.6 | 40 | 5.5666 | 752.4 | 1177.2 | 264.497 | 0 | 1
5/11 | 08:00:00 | 280.15 | 98798 | 5.1 | 50 | 5.1865 | 1328.4 | 1828.8 | 265.216 | 0 | 1
5/11 | 09:00:00 | 281.15 | 98806 | 5.1 | 70 | 5.5656 | 1879.2 | 2383.2 | 266.392 | 0 | 1
5/11 | 10:00:00 | 283.15 | 98824 | 5.7 | 60 | 4.829 | 2354.4 | 2584.8 | 267.824 | 0 | 1
5/11 | 11:00:00 | 284.15 | 98833 | 6.2 | 50 | 4.8285 | 2692.8 | 2883.6 | 268.77 | 0 | 1
5/11 | 12:00:00 | 285.15 | 98841 | 7.2 | 50 | 4.494 | 2876.4 | 2944.8 | 269.481 | 0 | 1
5/11 | 13:00:00 | 285.15 | 98841 | 6.7 | 60 | 4.1808 | 2887.2 | 2959.2 | 269.244 | 0 | 1
5/11 | 14:00:00 | 285.15 | 98841 | 7.7 | 60 | 4.8281 | 2718 | 2890.8 | 269.716 | 0 | 1
5/11 | 15:00:00 | 285.15 | 98841 | 7.7 | 70 | 4.494 | 2397.6 | 2595.6 | 269.481 | 0 | 1
5/11 | 16:00:00 | 284.15 | 98833 | 7.7 | 70 | 4.4944 | 1940.4 | 2408.4 | 268.535 | 0 | 1
5/11 | 17:00:00 | 283.15 | 98824 | 7.7 | 70 | 4.4948 | 1389.6 | 1922.4 | 267.59 | 0 | 1
5/11 | 18:00:00 | 283.15 | 98824 | 7.2 | 60 | 4.829 | 810 | 1267.2 | 267.824 | 0 | 1
5/11 | 19:00:00 | 282.15 | 98815 | 6.7 | 60 | 4.4952 | 309.6 | 342 | 266.645 | 0 | 1
5/11 | 20:00:00 | 280.15 | 98798 | 6.2 | 70 | 4.496 | 39.6 | 0 | 264.755 | 0 | 1
5/11 | 21:00:00 | 279.15 | 98789 | 5.1 | 60 | 4.4964 | 0 | 0 | 264.069 | 0 | 1
5/11 | 22:00:00 | 278.15 | 98780 | 4.1 | 60 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
5/11 | 23:00:00 | 278.15 | 98780 | 4.1 | 60 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
5/11 | 24:00:00 | 278.15 | 98780 | 4.6 | 60 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
5/12 | 01:00:00 | 277.15 | 98771 | 4.6 | 60 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
5/12 | 02:00:00 | 277.15 | 98771 | 4.6 | 50 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
5/12 | 03:00:00 | 277.15 | 98771 | 5.1 | 50 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
5/12 | 04:00:00 | 277.15 | 98771 | 4.6 | 50 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
5/12 | 05:00:00 | 278.15 | 98780 | 3.6 | 60 | 4.8311 | 14.4 | 0 | 263.818 | 0 | 1
5/12 | 06:00:00 | 278.15 | 98780 | 4.6 | 60 | 4.8311 | 144 | 0 | 263.818 | 0 | 1
5/12 | 07:00:00 | 279.15 | 98789 | 4.6 | 70 | 4.8307 | 399.6 | 14.4 | 264.767 | 0 | 1
5/12 | 08:00:00 | 280.15 | 98798 | 4.6 | 60 | 5.1865 | 702 | 208.8 | 265.946 | 0 | 1
5/12 | 09:00:00 | 281.15 | 98806 | 7.2 | 60 | 4.8299 | 1789.2 | 1803.6 | 266.193 | 0 | 1
5/12 | 10:00:00 | 282.15 | 98815 | 7.7 | 60 | 4.8294 | 2228.4 | 2138.4 | 267.139 | 0 | 1
5/12 | 11:00:00 | 284.15 | 98833 | 7.2 | 60 | 5.1847 | 2545.2 | 2343.6 | 269.266 | 0 | 1
5/12 | 12:00:00 | 285.15 | 98841 | 7.2 | 70 | 5.5636 | 2710.8 | 2361.6 | 270.447 | 0 | 1
5/12 | 13:00:00 | 285.15 | 98841 | 8.2 | 80 | 5.1842 | 2721.6 | 2246.4 | 270.214 | 0 | 1
5/12 | 14:00:00 | 285.15 | 98841 | 8.2 | 70 | 5.1842 | 2721.6 | 2721.6 | 269.95 | 0 | 1
5/12 | 15:00:00 | 286.15 | 98850 | 8.7 | 80 | 5.1837 | 2401.2 | 2610 | 270.896 | 0 | 1
5/12 | 16:00:00 | 286.15 | 98850 | 8.7 | 80 | 5.5631 | 1940.4 | 2412 | 271.13 | 0 | 1
5/12 | 17:00:00 | 286.15 | 98850 | 9.3 | 80 | 4.8277 | 1396.8 | 1922.4 | 270.662 | 0 | 1
5/12 | 18:00:00 | 285.15 | 98841 | 8.7 | 80 | 4.8281 | 820.8 | 1278 | 269.716 | 0 | 1
5/12 | 19:00:00 | 284.15 | 98833 | 8.2 | 80 | 5.1847 | 306 | 306 | 269.137 | 0 | 1
5/12 | 20:00:00 | 282.15 | 98815 | 5.7 | 70 | 7.3438 | 14.4 | 0 | 269.092 | 0 | 1
5/12 | 21:00:00 | 280.15 | 98798 | 5.7 | 60 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
5/12 | 22:00:00 | 279.15 | 98789 | 4.6 | 60 | 5.9708 | 0 | 0 | 265.559 | 0 | 1
5/12 | 23:00:00 | 279.15 | 98789 | 4.1 | 60 | 5.187 | 0 | 0 | 264.996 | 0 | 1
5/12 | 24:00:00 | 278.15 | 98780 | 4.1 | 60 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
5/13 | 01:00:00 | 278.15 | 98780 | 4.6 | 50 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
5/13 | 02:00:00 | 278.15 | 98780 | 5.1 | 50 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
5/13 | 03:00:00 | 278.15 | 98780 | 5.1 | 50 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
5/13 | 04:00:00 | 278.15 | 98780 | 5.1 | 50 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
5/13 | 05:00:00 | 278.15 | 98780 | 5.1 | 40 | 4.8311 | 18 | 0 | 263.818 | 0 | 1
5/13 | 06:00:00 | 279.15 | 98789 | 5.1 | 50 | 5.187 | 172.8 | 0 | 264.996 | 0 | 1
5/13 | 07:00:00 | 280.15 | 98798 | 6.2 | 50 | 5.5661 | 471.6 | 104.4 | 266.174 | 0 | 1
5/13 | 08:00:00 | 282.15 | 98815 | 5.7 | 60 | 5.9692 | 1346.4 | 1548 | 267.568 | 0 | 1
5/13 | 09:00:00 | 285.15 | 98841 | 7.7 | 80 | 5.9676 | 1900.8 | 2390.4 | 270.413 | 0 | 1
5/13 | 10:00:00 | 286.15 | 98850 | 7.2 | 70 | 6.3971 | 2361.6 | 2620.8 | 271.592 | 0 | 1
5/13 | 11:00:00 | 287.15 | 98858 | 8.7 | 90 | 5.9666 | 2545.2 | 2232 | 272.576 | 0 | 1
5/13 | 12:00:00 | 287.15 | 98858 | 10.3 | 90 | 5.5627 | 2718 | 2250 | 272.343 | 0 | 1
5/13 | 13:00:00 | 286.15 | 98850 | 10.8 | 90 | 5.1837 | 2894.4 | 2768.4 | 270.896 | 0 | 1
5/13 | 14:00:00 | 285.15 | 98841 | 10.8 | 90 | 5.1842 | 2732.4 | 2876.4 | 269.95 | 0 | 1
5/13 | 15:00:00 | 285.15 | 98841 | 9.8 | 80 | 4.8281 | 2415.6 | 2214 | 269.716 | 0 | 1
5/13 | 16:00:00 | 284.15 | 98833 | 8.2 | 90 | 4.4944 | 1026 | 172.8 | 269.274 | 0 | 1
5/13 | 17:00:00 | 283.15 | 98824 | 7.7 | 80 | 5.1851 | 734.4 | 54 | 268.793 | 0 | 1
5/13 | 18:00:00 | 282.15 | 98815 | 6.7 | 80 | 5.5651 | 435.6 | 21.6 | 268.075 | 0 | 1
5/13 | 19:00:00 | 282.15 | 98815 | 5.1 | 70 | 5.5651 | 169.2 | 0 | 268.075 | 0 | 1
5/13 | 20:00:00 | 282.15 | 98815 | 5.1 | 60 | 5.5651 | 25.2 | 0 | 268.075 | 0 | 1
5/13 | 21:00:00 | 281.15 | 98806 | 5.1 | 60 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/13 | 22:00:00 | 281.15 | 98806 | 5.1 | 60 | 6.4 | 0 | 0 | 267.58 | 0 | 1
5/13 | 23:00:00 | 281.15 | 98806 | 4.6 | 60 | 6.4 | 0 | 0 | 267.58 | 0 | 1
5/13 | 24:00:00 | 280.15 | 98798 | 5.7 | 50 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
5/14 | 01:00:00 | 280.15 | 98798 | 4.6 | 50 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
5/14 | 02:00:00 | 280.15 | 98798 | 4.6 | 50 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
5/14 | 03:00:00 | 281.15 | 98806 | 4.6 | 50 | 6.4 | 0 | 0 | 267.107 | 0 | 1
5/14 | 04:00:00 | 280.15 | 98798 | 4.1 | 40 | 6.4005 | 0 | 0 | 265.897 | 0 | 1
5/14 | 05:00:00 | 281.15 | 98806 | 3.6 | 50 | 6.4 | 32.4 | 0 | 267.107 | 0 | 1
5/14 | 06:00:00 | 281.15 | 98806 | 4.6 | 50 | 6.4 | 154.8 | 0 | 267.58 | 0 | 1
5/14 | 07:00:00 | 281.15 | 98806 | 4.1 | 50 | 6.8577 | 410.4 | 14.4 | 267.805 | 0 | 1
5/14 | 08:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.8577 | 709.2 | 50.4 | 267.805 | 0 | 1
5/14 | 09:00:00 | 282.15 | 98815 | 5.1 | 60 | 6.8571 | 997.2 | 50.4 | 268.758 | 0 | 1
5/14 | 10:00:00 | 283.15 | 98824 | 5.1 | 60 | 7.3431 | 1234.8 | 183.6 | 269.936 | 0 | 1
5/14 | 11:00:00 | 283.15 | 98824 | 5.7 | 60 | 7.3431 | 2545.2 | 1904.4 | 269.46 | 0 | 1
5/14 | 12:00:00 | 284.15 | 98833 | 6.7 | 60 | 6.8558 | 2880 | 2793.6 | 269.921 | 0 | 1
5/14 | 13:00:00 | 285.15 | 98841 | 6.2 | 60 | 6.8552 | 2887.2 | 2397.6 | 270.871 | 0 | 1
5/14 | 14:00:00 | 285.15 | 98841 | 6.7 | 70 | 6.3977 | 1429.2 | 939.6 | 271.387 | 0 | 1
5/14 | 15:00:00 | 286.15 | 98850 | 6.7 | 70 | 5.9671 | 2275.2 | 1861.2 | 271.627 | 0 | 1
5/14 | 16:00:00 | 286.15 | 98850 | 7.2 | 80 | 5.5631 | 1962 | 2415.6 | 271.13 | 0 | 1
5/14 | 17:00:00 | 285.15 | 98841 | 6.7 | 80 | 5.5636 | 1414.8 | 1915.2 | 270.182 | 0 | 1
5/14 | 18:00:00 | 284.15 | 98833 | 5.1 | 60 | 6.3982 | 838.8 | 1274.4 | 269.693 | 0 | 1
5/14 | 19:00:00 | 283.15 | 98824 | 6.7 | 60 | 5.9687 | 334.8 | 374.4 | 268.516 | 0 | 1
5/14 | 20:00:00 | 282.15 | 98815 | 4.1 | 60 | 6.3994 | 46.8 | 0 | 268.057 | 0 | 1
5/14 | 21:00:00 | 282.15 | 98815 | 5.1 | 60 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
5/14 | 22:00:00 | 281.15 | 98806 | 4.6 | 50 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
5/14 | 23:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
5/14 | 24:00:00 | 281.15 | 98806 | 4.1 | 60 | 6.4 | 0 | 0 | 267.58 | 0 | 1
5/15 | 01:00:00 | 281.15 | 98806 | 5.7 | 40 | 6.4 | 0 | 0 | 267.58 | 0 | 1
5/15 | 02:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.4 | 0 | 0 | 267.58 | 0 | 1
5/15 | 03:00:00 | 281.15 | 98806 | 5.7 | 40 | 6.4 | 0 | 0 | 267.58 | 0 | 1
5/15 | 04:00:00 | 281.15 | 98806 | 5.1 | 40 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
5/15 | 05:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.8577 | 21.6 | 0 | 267.805 | 0 | 1
5/15 | 06:00:00 | 281.15 | 98806 | 5.1 | 50 | 6.8577 | 158.4 | 0 | 267.805 | 0 | 1
5/15 | 07:00:00 | 281.15 | 98806 | 3.6 | 60 | 6.8577 | 414 | 21.6 | 267.805 | 0 | 1
5/15 | 08:00:00 | 281.15 | 98806 | 5.1 | 40 | 6.8577 | 435.6 | 0 | 267.914 | 0 | 1
5/15 | 09:00:00 | 281.15 | 98806 | 4.1 | 40 | 6.8577 | 612 | 3.6 | 267.914 | 0 | 1
5/15 | 10:00:00 | 281.15 | 98806 | 4.6 | 50 | 6.8577 | 1242 | 82.8 | 267.805 | 0 | 1
5/15 | 11:00:00 | 282.15 | 98815 | 4.6 | 40 | 6.8571 | 1418.4 | 68.4 | 268.758 | 0 | 1
5/15 | 12:00:00 | 282.15 | 98815 | 4.1 | 50 | 7.3438 | 1508.4 | 72 | 268.983 | 0 | 1
5/15 | 13:00:00 | 282.15 | 98815 | 2.6 | 50 | 7.3438 | 1512 | 72 | 268.983 | 0 | 1
5/15 | 14:00:00 | 282.15 | 98815 | 2.1 | 50 | 7.3438 | 1429.2 | 68.4 | 268.983 | 0 | 1
5/15 | 15:00:00 | 283.15 | 98824 | 1.5 | 7 | 7.3431 | 1260 | 216 | 269.936 | 0 | 1
5/15 | 16:00:00 | 283.15 | 98824 | 1.5 | 281 | 7.3431 | 1026 | 194.4 | 269.936 | 0 | 1
5/15 | 17:00:00 | 284.15 | 98833 | 1.5 | 130 | 7.8598 | 741.6 | 100.8 | 271.115 | 0 | 1
5/15 | 18:00:00 | 284.15 | 98833 | 2.1 | 100 | 7.8598 | 846 | 1015.2 | 270.371 | 0 | 1
5/15 | 19:00:00 | 284.15 | 98833 | 2.6 | 100 | 7.8598 | 342 | 378 | 270.371 | 0 | 1
5/15 | 20:00:00 | 284.15 | 98833 | 2.1 | 41 | 7.8598 | 50.4 | 0 | 270.636 | 0 | 1
5/15 | 21:00:00 | 283.15 | 98824 | 1.5 | 276 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
5/15 | 22:00:00 | 282.15 | 98815 | 0.5 | 111 | 6.8571 | 0 | 0 | 267.593 | 0 | 1
5/15 | 23:00:00 | 282.15 | 98815 | 1 | 204 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
5/15 | 24:00:00 | 282.15 | 98815 | 0.5 | 90 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
5/16 | 01:00:00 | 282.15 | 98815 | 1.5 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
5/16 | 02:00:00 | 282.15 | 98815 | 5.1 | 230 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
5/16 | 03:00:00 | 281.15 | 98806 | 5.1 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1
5/16 | 04:00:00 | 280.15 | 98798 | 5.1 | 250 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
5/16 | 05:00:00 | 279.15 | 98789 | 3.1 | 240 | 5.187 | 39.6 | 0 | 264.528 | 0 | 1
5/16 | 06:00:00 | 279.15 | 98789 | 1 | 304 | 5.5666 | 313.2 | 414 | 264.497 | 0 | 1
5/16 | 07:00:00 | 280.15 | 98798 | 3.1 | 140 | 5.9703 | 345.6 | 0 | 266.51 | 0 | 1
5/16 | 08:00:00 | 281.15 | 98806 | 5.1 | 150 | 6.4 | 720 | 28.8 | 267.58 | 0 | 1
5/16 | 09:00:00 | 281.15 | 98806 | 5.1 | 140 | 6.4 | 1008 | 54 | 267.58 | 0 | 1
5/16 | 10:00:00 | 281.15 | 98806 | 4.1 | 140 | 6.8577 | 1249.2 | 187.2 | 267.805 | 0 | 1
5/16 | 11:00:00 | 284.15 | 98833 | 5.1 | 150 | 7.3425 | 2559.6 | 1904.4 | 270.411 | 0 | 1
5/16 | 12:00:00 | 286.15 | 98850 | 6.2 | 170 | 8.408 | 2721.6 | 2311.2 | 272.766 | 0 | 1
5/16 | 13:00:00 | 285.15 | 98841 | 8.2 | 180 | 7.3418 | 2736 | 2257.2 | 271.363 | 0 | 1
5/16 | 14:00:00 | 286.15 | 98850 | 5.7 | 160 | 7.3412 | 2739.6 | 2750.4 | 272.048 | 0 | 1
5/16 | 15:00:00 | 286.15 | 98850 | 6.2 | 180 | 7.3412 | 2422.8 | 2512.8 | 272.048 | 0 | 1
5/16 | 16:00:00 | 286.15 | 98850 | 6.2 | 170 | 6.3971 | 1864.8 | 1962 | 271.858 | 0 | 1
5/16 | 17:00:00 | 286.15 | 98850 | 5.1 | 180 | 6.3971 | 1432.8 | 1990.8 | 271.592 | 0 | 1
5/16 | 18:00:00 | 286.15 | 98850 | 5.7 | 200 | 5.9671 | 860.4 | 1303.2 | 271.361 | 0 | 1
5/16 | 19:00:00 | 284.15 | 98833 | 4.1 | 160 | 5.5641 | 352.8 | 399.6 | 269.234 | 0 | 1
5/16 | 20:00:00 | 284.15 | 98833 | 5.7 | 180 | 5.5641 | 54 | 0 | 269.234 | 0 | 1
5/16 | 21:00:00 | 284.15 | 98833 | 7.2 | 210 | 5.5641 | 0 | 0 | 269.234 | 0 | 1
5/16 | 22:00:00 | 280.15 | 98798 | 5.1 | 180 | 4.8303 | 0 | 0 | 265.246 | 0 | 1
5/16 | 23:00:00 | 279.15 | 98789 | 3.6 | 180 | 5.187 | 0 | 0 | 264.269 | 0 | 1
5/16 | 24:00:00 | 278.65 | 98784 | 3.1 | 236 | 5.1872 | 0 | 0 | 264.522 | 0 | 1
5/17 | 01:00:00 | 278.15 | 98780 | 2.6 | 160 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
5/17 | 02:00:00 | 276.15 | 98762 | 3.1 | 150 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
5/17 | 03:00:00 | 277.15 | 98771 | 4.1 | 160 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
5/17 | 04:00:00 | 278.15 | 98780 | 3.6 | 160 | 4.4968 | 0 | 0 | 262.445 | 0 | 1
5/17 | 05:00:00 | 277.15 | 98771 | 2.6 | 110 | 4.8316 | 46.8 | 0 | 261.73 | 0 | 1
5/17 | 06:00:00 | 276.15 | 98762 | 2.6 | 90 | 4.1841 | 320.4 | 295.2 | 260.746 | 0 | 1
5/17 | 07:00:00 | 277.15 | 98771 | 3.1 | 100 | 4.8316 | 774 | 1033.2 | 262.405 | 0 | 1
5/17 | 08:00:00 | 279.15 | 98789 | 3.1 | 110 | 5.187 | 1314 | 1537.2 | 264.528 | 0 | 1
5/17 | 09:00:00 | 282.15 | 98815 | 5.1 | 120 | 6.8571 | 1825.2 | 1929.6 | 268.283 | 0 | 1
5/17 | 10:00:00 | 282.15 | 98815 | 7.2 | 120 | 6.8571 | 2260.8 | 2095.2 | 268.283 | 0 | 1
5/17 | 11:00:00 | 283.15 | 98824 | 6.7 | 120 | 6.8564 | 2574 | 2296.8 | 269.234 | 0 | 1
5/17 | 12:00:00 | 285.15 | 98841 | 6.7 | 120 | 6.3977 | 2743.2 | 1958.4 | 270.907 | 0 | 1
5/17 | 13:00:00 | 284.15 | 98833 | 7.7 | 120 | 5.9681 | 1530 | 223.2 | 270.206 | 0 | 1
5/17 | 14:00:00 | 283.15 | 98824 | 6.7 | 110 | 6.3988 | 1443.6 | 219.6 | 269.483 | 0 | 1
5/17 | 15:00:00 | 283.15 | 98824 | 6.2 | 120 | 6.8564 | 2296.8 | 1929.6 | 269.234 | 0 | 1
5/17 | 16:00:00 | 284.15 | 98833 | 6.2 | 130 | 6.8558 | 1872 | 1796.4 | 270.185 | 0 | 1
5/17 | 17:00:00 | 282.15 | 98815 | 4.6 | 160 | 6.8571 | 752.4 | 219.6 | 268.758 | 0 | 1
5/17 | 18:00:00 | 282.15 | 98815 | 4.6 | 110 | 6.8571 | 453.6 | 36 | 268.758 | 0 | 1
5/17 | 19:00:00 | 282.15 | 98815 | 4.6 | 160 | 7.3438 | 360 | 496.8 | 268.245 | 0 | 1
5/17 | 20:00:00 | 283.15 | 98824 | 3.6 | 200 | 7.3431 | 54 | 0 | 269.46 | 0 | 1
5/17 | 21:00:00 | 282.15 | 98815 | 4.1 | 190 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
5/17 | 22:00:00 | 282.15 | 98815 | 4.1 | 190 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/17 | 23:00:00 | 282.15 | 98815 | 4.6 | 180 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/17 | 24:00:00 | 281.15 | 98806 | 4.6 | 180 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
5/18 | 01:00:00 | 281.15 | 98806 | 4.6 | 180 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/18 | 02:00:00 | 280.15 | 98798 | 3.6 | 170 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
5/18 | 03:00:00 | 281.15 | 98806 | 3.1 | 170 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
5/18 | 04:00:00 | 281.15 | 98806 | 2.6 | 160 | 6.4 | 0 | 0 | 267.107 | 0 | 1
5/18 | 05:00:00 | 280.15 | 98798 | 3.1 | 140 | 5.9703 | 46.8 | 0 | 265.931 | 0 | 1
5/18 | 06:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.4 | 309.6 | 270 | 267.107 | 0 | 1
5/18 | 07:00:00 | 282.15 | 98815 | 6.7 | 170 | 5.9692 | 781.2 | 824.4 | 267.83 | 0 | 1
5/18 | 08:00:00 | 282.15 | 98815 | 6.7 | 170 | 6.3994 | 730.8 | 212.4 | 268.532 | 0 | 1
5/18 | 09:00:00 | 282.15 | 98815 | 4.1 | 180 | 6.8571 | 1832.4 | 1760.4 | 268.283 | 0 | 1
5/18 | 10:00:00 | 283.15 | 98824 | 4.6 | 190 | 6.8564 | 1256.4 | 82.8 | 269.71 | 0 | 1
5/18 | 11:00:00 | 285.15 | 98841 | 6.7 | 200 | 6.3977 | 1432.8 | 219.6 | 271.387 | 0 | 1
5/18 | 12:00:00 | 285.15 | 98841 | 7.7 | 210 | 6.3977 | 2754 | 1958.4 | 270.907 | 0 | 1
5/18 | 13:00:00 | 286.15 | 98850 | 6.7 | 210 | 6.8546 | 2757.6 | 2325.6 | 272.087 | 0 | 1
5/18 | 14:00:00 | 286.15 | 98850 | 8.7 | 200 | 6.3971 | 2610 | 2307.6 | 271.858 | 0 | 1
5/18 | 15:00:00 | 285.15 | 98841 | 8.7 | 220 | 6.3977 | 2307.6 | 2174.4 | 270.907 | 0 | 1
5/18 | 16:00:00 | 285.15 | 98841 | 8.2 | 210 | 6.8552 | 1879.2 | 1958.4 | 271.136 | 0 | 1
5/18 | 17:00:00 | 285.15 | 98841 | 7.7 | 230 | 6.8552 | 1368 | 1551.6 | 271.136 | 0 | 1
5/18 | 18:00:00 | 284.15 | 98833 | 5.1 | 220 | 7.3425 | 828 | 1022.4 | 270.411 | 0 | 1
5/18 | 19:00:00 | 284.15 | 98833 | 5.1 | 210 | 7.3425 | 349.2 | 320.4 | 270.411 | 0 | 1
5/18 | 20:00:00 | 283.15 | 98824 | 6.2 | 220 | 6.8564 | 57.6 | 0 | 269.234 | 0 | 1
5/18 | 21:00:00 | 283.15 | 98824 | 5.1 | 210 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
5/18 | 22:00:00 | 282.15 | 98815 | 4.6 | 210 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
5/18 | 23:00:00 | 282.15 | 98815 | 5.1 | 210 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/18 | 24:00:00 | 282.15 | 98815 | 5.1 | 200 | 5.9692 | 0 | 0 | 268.191 | 0 | 1
5/19 | 01:00:00 | 281.15 | 98806 | 5.1 | 200 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
5/19 | 02:00:00 | 281.15 | 98806 | 4.1 | 200 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/19 | 03:00:00 | 281.15 | 98806 | 4.1 | 210 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/19 | 04:00:00 | 281.15 | 98806 | 4.1 | 210 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/19 | 05:00:00 | 281.15 | 98806 | 5.1 | 200 | 5.5656 | 39.6 | 0 | 267.013 | 0 | 1
5/19 | 06:00:00 | 281.15 | 98806 | 3.6 | 160 | 5.9698 | 334.8 | 367.2 | 266.62 | 0 | 1
5/19 | 07:00:00 | 282.15 | 98815 | 3.1 | 170 | 5.9692 | 788.4 | 828 | 267.83 | 0 | 1
5/19 | 08:00:00 | 282.15 | 98815 | 3.6 | 170 | 6.3994 | 734.4 | 216 | 268.532 | 0 | 1
5/19 | 09:00:00 | 283.15 | 98824 | 4.1 | 190 | 6.3988 | 1843.2 | 1785.6 | 269.007 | 0 | 1
5/19 | 10:00:00 | 284.15 | 98833 | 4.6 | 200 | 5.9681 | 2282.4 | 2113.2 | 269.728 | 0 | 1
5/19 | 11:00:00 | 284.15 | 98833 | 6.2 | 180 | 6.3982 | 2592 | 2300.4 | 269.957 | 0 | 1
5/19 | 12:00:00 | 285.15 | 98841 | 6.2 | 180 | 6.8552 | 2754 | 2257.2 | 271.136 | 0 | 1
5/19 | 13:00:00 | 285.15 | 98841 | 6.7 | 200 | 6.3977 | 2937.6 | 2797.2 | 270.643 | 0 | 1
5/19 | 14:00:00 | 285.15 | 98841 | 5.1 | 170 | 6.3977 | 2775.6 | 2754 | 270.643 | 0 | 1
5/19 | 15:00:00 | 285.15 | 98841 | 4.6 | 160 | 6.8552 | 2311.2 | 2088 | 271.136 | 0 | 1
5/19 | 16:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.8564 | 2001.6 | 2307.6 | 268.971 | 0 | 1
5/19 | 17:00:00 | 284.15 | 98833 | 3.6 | 220 | 6.8558 | 1378.8 | 1555.2 | 270.185 | 0 | 1
5/19 | 18:00:00 | 285.15 | 98841 | 2.6 | 230 | 7.3418 | 835.2 | 1029.6 | 271.363 | 0 | 1
5/19 | 19:00:00 | 283.15 | 98824 | 5.1 | 230 | 6.8564 | 356.4 | 331.2 | 269.234 | 0 | 1
5/19 | 20:00:00 | 283.15 | 98824 | 1.5 | 48 | 6.8564 | 61.2 | 0 | 269.234 | 0 | 1
5/19 | 21:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
5/19 | 22:00:00 | 282.15 | 98815 | 4.1 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/19 | 23:00:00 | 281.15 | 98806 | 1.5 | 230 | 6.4 | 0 | 0 | 266.846 | 0 | 1
5/19 | 24:00:00 | 282.15 | 98815 | 5.1 | 220 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/20 | 01:00:00 | 282.15 | 98815 | 2.6 | 210 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
5/20 | 02:00:00 | 281.15 | 98806 | 2.1 | 210 | 6.4 | 0 | 0 | 267.107 | 0 | 1
5/20 | 03:00:00 | 280.65 | 98802 | 1.8 | 39 | 6.1818 | 0 | 0 | 267.099 | 0 | 1
5/20 | 04:00:00 | 280.15 | 98798 | 1.5 | 98 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
5/20 | 05:00:00 | 280.15 | 98798 | 1.5 | 59 | 5.9703 | 54 | 0 | 265.671 | 0 | 1
5/20 | 06:00:00 | 281.15 | 98806 | 4.6 | 210 | 6.4 | 342 | 374.4 | 266.846 | 0 | 1
5/20 | 07:00:00 | 282.15 | 98815 | 5.1 | 220 | 6.3994 | 842.4 | 1260 | 267.795 | 0 | 1
5/20 | 08:00:00 | 283.15 | 98824 | 4.6 | 230 | 6.3988 | 1418.4 | 1875.6 | 268.744 | 0 | 1
5/20 | 09:00:00 | 284.15 | 98833 | 7.7 | 230 | 6.3982 | 1965.6 | 2404.8 | 269.693 | 0 | 1
5/20 | 10:00:00 | 285.15 | 98841 | 6.7 | 230 | 6.3977 | 2426.4 | 2624.4 | 270.643 | 0 | 1
5/20 | 11:00:00 | 287.15 | 98858 | 6.7 | 230 | 6.3966 | 2599.2 | 2232 | 272.808 | 0 | 1
5/20 | 12:00:00 | 286.15 | 98850 | 5.7 | 240 | 5.9671 | 2772 | 2250 | 271.627 | 0 | 1
5/20 | 13:00:00 | 286.15 | 98850 | 3.6 | 250 | 6.3971 | 2944.8 | 2797.2 | 271.592 | 0 | 1
5/20 | 14:00:00 | 285.15 | 98841 | 4.1 | 240 | 7.3418 | 2775.6 | 2347.2 | 271.097 | 0 | 1
5/20 | 15:00:00 | 286.15 | 98850 | 4.1 | 260 | 6.8546 | 1288.8 | 259.2 | 272.568 | 0 | 1
5/20 | 16:00:00 | 285.15 | 98841 | 3.6 | 230 | 7.3418 | 1893.6 | 1792.8 | 271.363 | 0 | 1
5/20 | 17:00:00 | 285.15 | 98841 | 5.7 | 250 | 7.3418 | 1386 | 1551.6 | 271.363 | 0 | 1
5/20 | 18:00:00 | 284.15 | 98833 | 2.1 | 270 | 7.3425 | 846 | 1036.8 | 270.411 | 0 | 1
5/20 | 19:00:00 | 284.15 | 98833 | 1.5 | 230 | 7.3425 | 363.6 | 338.4 | 270.411 | 0 | 1
5/20 | 20:00:00 | 284.15 | 98833 | 1 | 221 | 7.3425 | 64.8 | 0 | 270.411 | 0 | 1
5/20 | 21:00:00 | 284.15 | 98833 | 0.5 | 100 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
5/20 | 22:00:00 | 282.15 | 98815 | 1.5 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
5/20 | 23:00:00 | 282.15 | 98815 | 1.5 | 124 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
5/20 | 24:00:00 | 282.15 | 98815 | 1.5 | 160 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
5/21 | 01:00:00 | 281.15 | 98806 | 1 | 210 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
5/21 | 02:00:00 | 282.15 | 98815 | 1 | 74 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
5/21 | 03:00:00 | 282.15 | 98815 | 0.5 | 301 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
5/21 | 04:00:00 | 281.15 | 98806 | 1.5 | 220 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
5/21 | 05:00:00 | 281.15 | 98806 | 0 | 7 | 6.8577 | 54 | 0 | 267.332 | 0 | 1
5/21 | 06:00:00 | 282.15 | 98815 | 2.6 | 230 | 6.8571 | 331.2 | 295.2 | 268.283 | 0 | 1
5/21 | 07:00:00 | 282.15 | 98815 | 3.6 | 230 | 7.3438 | 849.6 | 1256.4 | 268.245 | 0 | 1
5/21 | 08:00:00 | 283.15 | 98824 | 3.6 | 240 | 7.3431 | 1422 | 1936.8 | 269.196 | 0 | 1
5/21 | 09:00:00 | 283.15 | 98824 | 4.6 | 270 | 7.3431 | 1854 | 2066.4 | 269.46 | 0 | 1
5/21 | 10:00:00 | 280.15 | 98798 | 2.6 | 270 | 5.9703 | 2296.8 | 2037.6 | 265.931 | 0 | 1
5/21 | 11:00:00 | 283.15 | 98824 | 2.6 | 250 | 6.8564 | 2761.2 | 2743.2 | 268.971 | 0 | 1
5/21 | 12:00:00 | 285.15 | 98841 | 3.1 | 250 | 7.8591 | 2930.4 | 2858.4 | 271.323 | 0 | 1
5/21 | 13:00:00 | 286.15 | 98850 | 6.7 | 280 | 7.3412 | 2941.2 | 2865.6 | 272.048 | 0 | 1
5/21 | 14:00:00 | 287.15 | 98858 | 6.7 | 270 | 6.854 | 2786.4 | 2750.4 | 272.77 | 0 | 1
5/21 | 15:00:00 | 286.15 | 98850 | 7.7 | 280 | 5.9671 | 2336.4 | 2167.2 | 271.627 | 0 | 1
5/21 | 16:00:00 | 287.15 | 98858 | 8.2 | 280 | 5.9666 | 1911.6 | 2127.6 | 272.576 | 0 | 1
5/21 | 17:00:00 | 286.15 | 98850 | 6.7 | 270 | 5.1837 | 1490.4 | 2062.8 | 270.896 | 0 | 1
5/21 | 18:00:00 | 285.15 | 98841 | 6.7 | 280 | 5.1842 | 914.4 | 1303.2 | 269.95 | 0 | 1
5/21 | 19:00:00 | 285.15 | 98841 | 6.7 | 270 | 4.8281 | 396 | 460.8 | 269.716 | 0 | 1
5/21 | 20:00:00 | 284.15 | 98833 | 6.7 | 280 | 5.1847 | 72 | 0 | 269.003 | 0 | 1
5/21 | 21:00:00 | 283.15 | 98824 | 6.2 | 270 | 5.9687 | 0 | 0 | 268.516 | 0 | 1
5/21 | 22:00:00 | 282.15 | 98815 | 3.1 | 270 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
5/21 | 23:00:00 | 282.15 | 98815 | 2.6 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/21 | 24:00:00 | 282.15 | 98815 | 3.6 | 250 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
5/22 | 01:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/22 | 02:00:00 | 282.15 | 98815 | 3.6 | 250 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/22 | 03:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/22 | 04:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.4 | 0 | 0 | 266.846 | 0 | 1
5/22 | 05:00:00 | 281.15 | 98806 | 2.1 | 270 | 5.9698 | 61.2 | 0 | 266.62 | 0 | 1
5/22 | 06:00:00 | 281.15 | 98806 | 3.1 | 260 | 5.9698 | 360 | 392.4 | 266.62 | 0 | 1
5/22 | 07:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.3994 | 860.4 | 1263.6 | 267.795 | 0 | 1
5/22 | 08:00:00 | 282.15 | 98815 | 5.1 | 260 | 6.8571 | 1350 | 1591.2 | 268.283 | 0 | 1
5/22 | 09:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.8564 | 1864.8 | 1936.8 | 269.234 | 0 | 1
5/22 | 10:00:00 | 284.15 | 98833 | 5.7 | 270 | 6.8558 | 2296.8 | 2091.6 | 270.185 | 0 | 1
5/22 | 11:00:00 | 284.15 | 98833 | 6.2 | 250 | 5.9681 | 2617.2 | 1929.6 | 269.728 | 0 | 1
5/22 | 12:00:00 | 285.15 | 98841 | 6.2 | 270 | 6.8552 | 1540.8 | 219.6 | 271.616 | 0 | 1
5/22 | 13:00:00 | 285.15 | 98841 | 5.7 | 260 | 6.8552 | 1544.4 | 72 | 271.616 | 0 | 1
5/22 | 14:00:00 | 286.15 | 98850 | 6.7 | 270 | 7.3412 | 1458 | 216 | 272.796 | 0 | 1
5/22 | 15:00:00 | 287.15 | 98858 | 7.7 | 260 | 7.3406 | 2332.8 | 1918.8 | 273.266 | 0 | 1
5/22 | 16:00:00 | 286.15 | 98850 | 6.2 | 280 | 7.3412 | 1911.6 | 1954.8 | 272.314 | 0 | 1
5/22 | 17:00:00 | 285.15 | 98841 | 4.6 | 240 | 7.3418 | 1404 | 1558.8 | 271.363 | 0 | 1
5/22 | 18:00:00 | 286.15 | 98850 | 4.6 | 260 | 7.3412 | 864 | 921.6 | 272.314 | 0 | 1
5/22 | 19:00:00 | 286.15 | 98850 | 3.6 | 250 | 7.3412 | 208.8 | 0 | 272.796 | 0 | 1
5/22 | 20:00:00 | 285.15 | 98841 | 3.1 | 250 | 7.3418 | 39.6 | 0 | 271.843 | 0 | 1
5/22 | 21:00:00 | 285.15 | 98841 | 3.1 | 240 | 7.3418 | 0 | 0 | 271.843 | 0 | 1
5/22 | 22:00:00 | 284.15 | 98833 | 1.5 | 210 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
5/22 | 23:00:00 | 284.15 | 98833 | 2.6 | 200 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
5/22 | 24:00:00 | 284.15 | 98833 | 2.1 | 210 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
5/23 | 01:00:00 | 284.15 | 98833 | 3.1 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
5/23 | 02:00:00 | 284.15 | 98833 | 1.5 | 210 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
5/23 | 03:00:00 | 282.15 | 98815 | 1 | 220 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
5/23 | 04:00:00 | 283.15 | 98824 | 3.1 | 220 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
5/23 | 05:00:00 | 282.15 | 98815 | 2.1 | 190 | 6.8571 | 61.2 | 0 | 268.021 | 0 | 1
5/23 | 06:00:00 | 283.15 | 98824 | 2.1 | 170 | 7.3431 | 363.6 | 399.6 | 269.196 | 0 | 1
5/23 | 07:00:00 | 284.15 | 98833 | 2.6 | 180 | 7.8598 | 867.6 | 1256.4 | 270.371 | 0 | 1
5/23 | 08:00:00 | 286.15 | 98850 | 3.1 | 210 | 7.8584 | 1353.6 | 1465.2 | 272.541 | 0 | 1
5/23 | 09:00:00 | 286.15 | 98850 | 2.6 | 180 | 7.8584 | 1036.8 | 72 | 273.023 | 0 | 1
5/23 | 10:00:00 | 287.15 | 98858 | 4.1 | 190 | 8.4073 | 1274.4 | 277.2 | 274.203 | 0 | 1
5/23 | 11:00:00 | 286.15 | 98850 | 3.1 | 130 | 8.408 | 2606.4 | 1875.6 | 272.766 | 0 | 1
5/23 | 12:00:00 | 289.15 | 98875 | 3.6 | 180 | 8.9895 | 2768.4 | 2300.4 | 275.852 | 0 | 1
5/23 | 13:00:00 | 290.15 | 98883 | 5.1 | 170 | 7.8557 | 2782.8 | 2311.2 | 276.351 | 0 | 1
5/23 | 14:00:00 | 289.15 | 98875 | 5.7 | 190 | 7.3393 | 2638.8 | 2293.2 | 275.169 | 0 | 1
5/23 | 15:00:00 | 290.15 | 98883 | 6.2 | 210 | 7.3387 | 2340 | 2091.6 | 276.121 | 0 | 1
5/23 | 16:00:00 | 288.15 | 98867 | 4.1 | 280 | 7.3399 | 2037.6 | 2437.2 | 273.95 | 0 | 1
5/23 | 17:00:00 | 289.15 | 98875 | 6.7 | 270 | 7.8564 | 1497.6 | 1933.2 | 275.129 | 0 | 1
5/23 | 18:00:00 | 288.15 | 98867 | 6.2 | 260 | 5.9661 | 932.4 | 1310.4 | 273.258 | 0 | 1
5/23 | 19:00:00 | 287.15 | 98858 | 5.7 | 270 | 5.1833 | 417.6 | 489.6 | 271.843 | 0 | 1
5/23 | 20:00:00 | 285.15 | 98841 | 5.1 | 270 | 5.9676 | 72 | 0 | 270.678 | 0 | 1
5/23 | 21:00:00 | 284.15 | 98833 | 5.7 | 270 | 6.8558 | 0 | 0 | 270.185 | 0 | 1
5/23 | 22:00:00 | 283.15 | 98824 | 5.7 | 270 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
5/23 | 23:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
5/23 | 24:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.4 | 0 | 0 | 267.688 | 0 | 1
5/24 | 01:00:00 | 282.15 | 98815 | 3.1 | 300 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
5/24 | 02:00:00 | 281.15 | 98806 | 3.6 | 250 | 6.4 | 0 | 0 | 266.846 | 0 | 1
5/24 | 03:00:00 | 281.15 | 98806 | 5.7 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1
5/24 | 04:00:00 | 280.15 | 98798 | 5.7 | 290 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
5/24 | 05:00:00 | 280.15 | 98798 | 5.1 | 300 | 5.5661 | 39.6 | 0 | 266.174 | 0 | 1
5/24 | 06:00:00 | 280.15 | 98798 | 5.7 | 310 | 5.9703 | 158.4 | 0 | 266.51 | 0 | 1
5/24 | 07:00:00 | 281.15 | 98806 | 5.7 | 300 | 6.4 | 878.4 | 1083.6 | 266.846 | 0 | 1
5/24 | 08:00:00 | 283.15 | 98824 | 5.7 | 300 | 5.9687 | 1206 | 972 | 269.025 | 0 | 1
5/24 | 09:00:00 | 285.15 | 98841 | 6.2 | 290 | 5.9676 | 1868.4 | 1803.6 | 270.678 | 0 | 1
5/24 | 10:00:00 | 287.15 | 98858 | 4.1 | 250 | 5.9666 | 2419.2 | 2347.2 | 272.445 | 0 | 1
5/24 | 11:00:00 | 288.15 | 98867 | 3.1 | 250 | 6.396 | 2786.4 | 2829.6 | 273.49 | 0 | 1
5/24 | 12:00:00 | 289.15 | 98875 | 3.6 | 240 | 5.9656 | 2970 | 2883.6 | 274.206 | 0 | 1
5/24 | 13:00:00 | 289.15 | 98875 | 5.1 | 280 | 5.9656 | 2977.2 | 2887.2 | 274.206 | 0 | 1
5/24 | 14:00:00 | 290.15 | 98883 | 4.1 | 260 | 5.9651 | 2818.8 | 2847.6 | 275.155 | 0 | 1
5/24 | 15:00:00 | 291.15 | 98892 | 4.6 | 270 | 5.9645 | 2530.8 | 2844 | 275.961 | 0 | 1
5/24 | 16:00:00 | 291.15 | 98892 | 3.1 | 250 | 5.9645 | 2077.2 | 2527.2 | 275.961 | 0 | 1
5/24 | 17:00:00 | 291.15 | 98892 | 4.6 | 300 | 5.5607 | 1537.2 | 2012.4 | 275.578 | 0 | 1
5/24 | 18:00:00 | 290.15 | 98883 | 3.6 | 300 | 5.5612 | 950.4 | 1371.6 | 274.778 | 0 | 1
5/24 | 19:00:00 | 290.15 | 98883 | 2.6 | 310 | 5.5612 | 424.8 | 511.2 | 274.778 | 0 | 1
5/24 | 20:00:00 | 289.15 | 98875 | 3.1 | 310 | 5.9656 | 79.2 | 0 | 274.206 | 0 | 1
5/24 | 21:00:00 | 287.15 | 98858 | 0.5 | 10 | 6.854 | 0 | 0 | 273.038 | 0 | 1
5/24 | 22:00:00 | 286.15 | 98850 | 0.5 | 340 | 6.3971 | 0 | 0 | 271.858 | 0 | 1
5/24 | 23:00:00 | 285.15 | 98841 | 1 | 320 | 6.3977 | 0 | 0 | 271.033 | 0 | 1
5/24 | 24:00:00 | 284.15 | 98833 | 2.1 | 270 | 6.3982 | 0 | 0 | 270.204 | 0 | 1
5/25 | 01:00:00 | 283.15 | 98824 | 2.1 | 310 | 5.9687 | 0 | 0 | 269.025 | 0 | 1
5/25 | 02:00:00 | 283.15 | 98824 | 1 | 300 | 5.9687 | 0 | 0 | 269.025 | 0 | 1
5/25 | 03:00:00 | 281.15 | 98806 | 1 | 310 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/25 | 04:00:00 | 282.15 | 98815 | 0 | 101 | 5.9692 | 0 | 0 | 268.191 | 0 | 1
5/25 | 05:00:00 | 281.15 | 98806 | 1 | 40 | 5.9698 | 39.6 | 0 | 267.353 | 0 | 1
5/25 | 06:00:00 | 282.15 | 98815 | 0.5 | 63 | 6.3994 | 230.4 | 0 | 268.532 | 0 | 1
5/25 | 07:00:00 | 283.15 | 98824 | 2.6 | 90 | 6.8564 | 536.4 | 115.2 | 269.71 | 0 | 1
5/25 | 08:00:00 | 286.15 | 98850 | 1.5 | 76 | 7.3412 | 1184.4 | 853.2 | 272.563 | 0 | 1
5/25 | 09:00:00 | 288.15 | 98867 | 2.1 | 120 | 7.3399 | 1868.4 | 1778.4 | 274.218 | 0 | 1
5/25 | 10:00:00 | 290.15 | 98883 | 3.6 | 130 | 7.8557 | 2361.6 | 2311.2 | 276.351 | 0 | 1
5/25 | 11:00:00 | 291.15 | 98892 | 3.1 | 140 | 8.4044 | 2656.8 | 2340 | 277.532 | 0 | 1
5/25 | 12:00:00 | 292.15 | 98900 | 3.6 | 160 | 8.4037 | 2952 | 2779.2 | 278.213 | 0 | 1
5/25 | 13:00:00 | 294.15 | 98916 | 3.6 | 170 | 8.4023 | 2962.8 | 2858.4 | 280.117 | 0 | 1
5/25 | 14:00:00 | 293.15 | 98908 | 2.6 | 180 | 7.8537 | 2808 | 2746.8 | 278.935 | 0 | 1
5/25 | 15:00:00 | 293.15 | 98908 | 4.6 | 150 | 7.8537 | 2354.4 | 2066.4 | 279.208 | 0 | 1
5/25 | 16:00:00 | 291.15 | 98892 | 4.1 | 160 | 7.855 | 2052 | 2437.2 | 277.032 | 0 | 1
5/25 | 17:00:00 | 291.15 | 98892 | 4.1 | 150 | 7.855 | 1515.6 | 1944 | 277.032 | 0 | 1
5/25 | 18:00:00 | 289.15 | 98875 | 3.6 | 160 | 8.4059 | 889.2 | 1054.8 | 275.626 | 0 | 1
5/25 | 19:00:00 | 288.15 | 98867 | 3.6 | 150 | 8.4065 | 424.8 | 547.2 | 274.404 | 0 | 1
5/25 | 20:00:00 | 287.15 | 98858 | 1.5 | 244 | 8.4073 | 82.8 | 0 | 273.451 | 0 | 1
5/25 | 21:00:00 | 287.15 | 98858 | 0.5 | 298 | 8.991 | 0 | 0 | 273.944 | 0 | 1
5/25 | 22:00:00 | 285.15 | 98841 | 3.1 | 290 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
5/25 | 23:00:00 | 284.15 | 98833 | 2.6 | 300 | 6.3982 | 0 | 0 | 270.435 | 0 | 1
5/25 | 24:00:00 | 284.15 | 98833 | 3.6 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
5/26 | 01:00:00 | 283.15 | 98824 | 3.1 | 280 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
5/26 | 02:00:00 | 283.15 | 98824 | 4.1 | 280 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
5/26 | 03:00:00 | 283.15 | 98824 | 4.6 | 280 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
5/26 | 04:00:00 | 283.15 | 98824 | 7.7 | 270 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
5/26 | 05:00:00 | 283.15 | 98824 | 6.2 | 280 | 7.8605 | 36 | 0 | 270.161 | 0 | 1
5/26 | 06:00:00 | 282.15 | 98815 | 8.2 | 290 | 6.8571 | 201.6 | 0 | 268.758 | 0 | 1
5/26 | 07:00:00 | 282.15 | 98815 | 7.2 | 290 | 6.8571 | 464.4 | 79.2 | 268.758 | 0 | 1
5/26 | 08:00:00 | 282.15 | 98815 | 9.8 | 300 | 5.9692 | 1465.2 | 1623.6 | 267.568 | 0 | 1
5/26 | 09:00:00 | 283.15 | 98824 | 9.3 | 300 | 5.5646 | 2016 | 2404.8 | 268.287 | 0 | 1
5/26 | 10:00:00 | 284.15 | 98833 | 10.3 | 290 | 6.3982 | 2469.6 | 2624.4 | 269.693 | 0 | 1
5/26 | 11:00:00 | 285.15 | 98841 | 10.3 | 300 | 7.3418 | 2631.6 | 2221.2 | 271.363 | 0 | 1
5/26 | 12:00:00 | 285.15 | 98841 | 11.3 | 290 | 7.8591 | 2793.6 | 2304 | 271.588 | 0 | 1
5/26 | 13:00:00 | 286.15 | 98850 | 10.8 | 280 | 8.408 | 2797.2 | 2300.4 | 272.766 | 0 | 1
5/26 | 14:00:00 | 286.15 | 98850 | 10.8 | 280 | 8.408 | 2649.6 | 2275.2 | 272.766 | 0 | 1
5/26 | 15:00:00 | 285.15 | 98841 | 11.8 | 270 | 8.4088 | 2354.4 | 2145.6 | 271.813 | 0 | 1
5/26 | 16:00:00 | 285.15 | 98841 | 11.3 | 280 | 8.4088 | 2055.6 | 2433.6 | 271.547 | 0 | 1
5/26 | 17:00:00 | 285.15 | 98841 | 10.3 | 270 | 8.4088 | 1519.2 | 2070 | 271.547 | 0 | 1
5/26 | 18:00:00 | 285.15 | 98841 | 9.8 | 270 | 4.8281 | 961.2 | 1346.4 | 269.716 | 0 | 1
5/26 | 19:00:00 | 284.15 | 98833 | 8.2 | 260 | 4.8285 | 439.2 | 511.2 | 268.77 | 0 | 1
5/26 | 20:00:00 | 283.15 | 98824 | 6.7 | 260 | 5.1851 | 86.4 | 0 | 268.056 | 0 | 1
5/26 | 21:00:00 | 282.15 | 98815 | 4.6 | 260 | 5.1856 | 0 | 0 | 267.11 | 0 | 1
5/26 | 22:00:00 | 281.15 | 98806 | 3.6 | 240 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
5/26 | 23:00:00 | 281.15 | 98806 | 2.6 | 250 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
5/26 | 24:00:00 | 282.15 | 98815 | 3.6 | 230 | 5.5651 | 0 | 0 | 267.846 | 0 | 1
5/27 | 01:00:00 | 282.15 | 98815 | 3.1 | 230 | 5.9692 | 0 | 0 | 268.191 | 0 | 1
5/27 | 02:00:00 | 282.15 | 98815 | 4.6 | 240 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
5/27 | 03:00:00 | 281.15 | 98806 | 6.2 | 250 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
5/27 | 04:00:00 | 281.15 | 98806 | 4.1 | 240 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
5/27 | 05:00:00 | 281.15 | 98806 | 4.6 | 220 | 5.5656 | 72 | 0 | 266.392 | 0 | 1
5/27 | 06:00:00 | 281.15 | 98806 | 3.6 | 210 | 5.5656 | 392.4 | 540 | 266.392 | 0 | 1
5/27 | 07:00:00 | 282.15 | 98815 | 5.1 | 210 | 5.9692 | 471.6 | 39.6 | 268.304 | 0 | 1
5/27 | 08:00:00 | 282.15 | 98815 | 5.7 | 210 | 6.3994 | 770.4 | 223.2 | 268.532 | 0 | 1
5/27 | 09:00:00 | 282.15 | 98815 | 6.2 | 210 | 6.3994 | 1900.8 | 1782 | 268.057 | 0 | 1
5/27 | 10:00:00 | 282.15 | 98815 | 5.7 | 200 | 6.8571 | 1292.4 | 82.8 | 268.758 | 0 | 1
5/27 | 11:00:00 | 283.15 | 98824 | 6.7 | 210 | 6.8564 | 1465.2 | 68.4 | 269.71 | 0 | 1
5/27 | 12:00:00 | 283.15 | 98824 | 4.6 | 220 | 7.3431 | 1555.2 | 68.4 | 269.936 | 0 | 1
5/27 | 13:00:00 | 284.15 | 98833 | 4.1 | 240 | 7.8598 | 1558.8 | 68.4 | 271.115 | 0 | 1
5/27 | 14:00:00 | 286.15 | 98850 | 6.2 | 260 | 8.408 | 1472.4 | 158.4 | 273.248 | 0 | 1
5/27 | 15:00:00 | 287.15 | 98858 | 7.2 | 260 | 8.4073 | 1310.4 | 111.6 | 274.203 | 0 | 1
5/27 | 16:00:00 | 286.15 | 98850 | 8.7 | 270 | 8.408 | 1080 | 111.6 | 273.248 | 0 | 1
5/27 | 17:00:00 | 287.15 | 98858 | 6.7 | 260 | 8.4073 | 1440 | 1314 | 273.719 | 0 | 1
5/27 | 18:00:00 | 288.15 | 98867 | 7.2 | 270 | 8.4065 | 903.6 | 1065.6 | 274.672 | 0 | 1
5/27 | 19:00:00 | 287.15 | 98858 | 8.7 | 270 | 7.8578 | 417.6 | 396 | 273.493 | 0 | 1
5/27 | 20:00:00 | 287.15 | 98858 | 8.7 | 270 | 7.8578 | 90 | 0 | 273.226 | 0 | 1
5/27 | 21:00:00 | 286.15 | 98850 | 4.6 | 280 | 8.408 | 0 | 0 | 272.499 | 0 | 1
5/27 | 22:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
5/27 | 23:00:00 | 285.15 | 98841 | 5.1 | 270 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
5/27 | 24:00:00 | 285.15 | 98841 | 6.7 | 260 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
5/28 | 01:00:00 | 285.15 | 98841 | 7.2 | 270 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
5/28 | 02:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
5/28 | 03:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
5/28 | 04:00:00 | 285.15 | 98841 | 8.7 | 280 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
5/28 | 05:00:00 | 285.15 | 98841 | 7.2 | 270 | 8.4088 | 39.6 | 0 | 272.294 | 0 | 1
5/28 | 06:00:00 | 286.15 | 98850 | 6.7 | 280 | 8.9918 | 205.2 | 0 | 273.473 | 0 | 1
5/28 | 07:00:00 | 286.15 | 98850 | 3.1 | 290 | 8.9918 | 468 | 25.2 | 273.473 | 0 | 1
5/28 | 08:00:00 | 286.15 | 98850 | 5.7 | 280 | 8.9918 | 766.8 | 72 | 273.473 | 0 | 1
5/28 | 09:00:00 | 287.15 | 98858 | 6.2 | 290 | 8.991 | 1047.6 | 97.2 | 274.428 | 0 | 1
5/28 | 10:00:00 | 287.15 | 98858 | 7.2 | 280 | 8.991 | 1288.8 | 108 | 274.428 | 0 | 1
5/28 | 11:00:00 | 288.15 | 98867 | 7.2 | 270 | 8.9902 | 1458 | 370.8 | 275.384 | 0 | 1
5/28 | 12:00:00 | 289.15 | 98875 | 10.3 | 270 | 8.9895 | 2793.6 | 1904.4 | 275.852 | 0 | 1
5/28 | 13:00:00 | 290.15 | 98883 | 10.3 | 270 | 8.9887 | 2804.4 | 2296.8 | 276.806 | 0 | 1
5/28 | 14:00:00 | 289.15 | 98875 | 10.8 | 270 | 8.9895 | 2656.8 | 2217.6 | 275.852 | 0 | 1
5/28 | 15:00:00 | 290.15 | 98883 | 10.8 | 280 | 8.9887 | 2509.2 | 2534.4 | 276.535 | 0 | 1
5/28 | 16:00:00 | 290.15 | 98883 | 10.3 | 270 | 8.9887 | 1947.6 | 1911.6 | 276.806 | 0 | 1
5/28 | 17:00:00 | 288.15 | 98867 | 6.2 | 270 | 8.9902 | 1447.2 | 1659.6 | 274.898 | 0 | 1
5/28 | 18:00:00 | 289.15 | 98875 | 4.6 | 260 | 8.9895 | 910.8 | 1065.6 | 275.852 | 0 | 1
5/28 | 19:00:00 | 288.15 | 98867 | 5.7 | 270 | 8.4065 | 421.2 | 482.4 | 274.672 | 0 | 1
5/28 | 20:00:00 | 288.15 | 98867 | 3.6 | 280 | 8.9902 | 86.4 | 0 | 274.898 | 0 | 1
5/28 | 21:00:00 | 287.15 | 98858 | 2.1 | 270 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
5/28 | 22:00:00 | 285.15 | 98841 | 2.1 | 300 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
5/28 | 23:00:00 | 285.15 | 98841 | 1 | 355 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
5/28 | 24:00:00 | 285.15 | 98841 | 0.5 | 34 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
5/29 | 01:00:00 | 286.15 | 98850 | 3.1 | 260 | 8.408 | 0 | 0 | 272.499 | 0 | 1
5/29 | 02:00:00 | 285.15 | 98841 | 6.2 | 300 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
5/29 | 03:00:00 | 285.15 | 98841 | 4.1 | 290 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
5/29 | 04:00:00 | 283.15 | 98824 | 2.1 | 250 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
5/29 | 05:00:00 | 282.15 | 98815 | 2.1 | 290 | 6.8571 | 32.4 | 0 | 268.867 | 0 | 1
5/29 | 06:00:00 | 285.15 | 98841 | 1 | 92 | 7.8591 | 230.4 | 0 | 272.069 | 0 | 1
5/29 | 07:00:00 | 285.15 | 98841 | 1.5 | 246 | 8.4088 | 903.6 | 1080 | 271.547 | 0 | 1
5/29 | 08:00:00 | 287.15 | 98858 | 2.1 | 120 | 8.4073 | 1389.6 | 1623.6 | 273.719 | 0 | 1
5/29 | 09:00:00 | 289.15 | 98875 | 1.5 | 167 | 8.9895 | 2012.4 | 2318.4 | 275.582 | 0 | 1
5/29 | 10:00:00 | 290.15 | 98883 | 2.6 | 140 | 9.6084 | 2462.4 | 2610 | 276.76 | 0 | 1
5/29 | 11:00:00 | 292.15 | 98900 | 3.6 | 140 | 9.6067 | 2790 | 2797.2 | 278.668 | 0 | 1
5/29 | 12:00:00 | 293.15 | 98908 | 4.1 | 130 | 10.2634 | 2962.8 | 2851.2 | 279.848 | 0 | 1
5/29 | 13:00:00 | 294.15 | 98916 | 4.1 | 140 | 10.2625 | 2973.6 | 2854.8 | 280.803 | 0 | 1
5/29 | 14:00:00 | 295.15 | 98924 | 3.6 | 140 | 9.6043 | 2822.4 | 2808 | 281.529 | 0 | 1
5/29 | 15:00:00 | 295.15 | 98924 | 4.6 | 140 | 9.6043 | 2512.8 | 2631.6 | 281.529 | 0 | 1
5/29 | 16:00:00 | 295.15 | 98924 | 5.1 | 110 | 10.2617 | 2070 | 2437.2 | 281.757 | 0 | 1
5/29 | 17:00:00 | 294.15 | 98916 | 5.7 | 100 | 10.2625 | 1537.2 | 2052 | 280.803 | 0 | 1
5/29 | 18:00:00 | 293.15 | 98908 | 5.7 | 110 | 9.6059 | 972 | 1296 | 279.622 | 0 | 1
5/29 | 19:00:00 | 292.15 | 98900 | 6.2 | 110 | 9.6067 | 453.6 | 612 | 278.668 | 0 | 1
5/29 | 20:00:00 | 290.15 | 98883 | 5.1 | 100 | 8.9887 | 97.2 | 0 | 276.535 | 0 | 1
5/29 | 21:00:00 | 287.15 | 98858 | 4.6 | 90 | 8.4073 | 0 | 0 | 274.088 | 0 | 1
5/29 | 22:00:00 | 285.15 | 98841 | 4.1 | 80 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
5/29 | 23:00:00 | 283.15 | 98824 | 3.6 | 80 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
5/29 | 24:00:00 | 282.15 | 98815 | 3.6 | 70 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
5/30 | 01:00:00 | 281.15 | 98806 | 3.6 | 80 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
5/30 | 02:00:00 | 280.15 | 98798 | 3.1 | 70 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
5/30 | 03:00:00 | 279.15 | 98789 | 3.6 | 70 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
5/30 | 04:00:00 | 279.15 | 98789 | 3.6 | 60 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
5/30 | 05:00:00 | 280.15 | 98798 | 3.1 | 60 | 5.9703 | 32.4 | 0 | 266.51 | 0 | 1
5/30 | 06:00:00 | 281.15 | 98806 | 2.1 | 40 | 5.9698 | 248.4 | 0 | 267.353 | 0 | 1
5/30 | 07:00:00 | 283.15 | 98824 | 2.1 | 70 | 6.3988 | 662.4 | 360 | 269.37 | 0 | 1
5/30 | 08:00:00 | 284.15 | 98833 | 2.1 | 80 | 6.8558 | 1076.4 | 550.8 | 270.549 | 0 | 1
5/30 | 09:00:00 | 286.15 | 98850 | 3.1 | 70 | 7.3412 | 2026.8 | 2170.8 | 272.048 | 0 | 1
5/30 | 10:00:00 | 288.15 | 98867 | 3.1 | 70 | 7.857 | 2476.8 | 2613.6 | 274.177 | 0 | 1
5/30 | 11:00:00 | 289.15 | 98875 | 3.6 | 90 | 7.8564 | 2808 | 2808 | 275.129 | 0 | 1
5/30 | 12:00:00 | 291.15 | 98892 | 4.6 | 110 | 7.338 | 2988 | 2858.4 | 276.802 | 0 | 1
5/30 | 13:00:00 | 292.15 | 98900 | 6.2 | 100 | 6.8511 | 3006 | 2865.6 | 277.52 | 0 | 1
5/30 | 14:00:00 | 292.15 | 98900 | 6.2 | 90 | 6.3938 | 2883.6 | 2923.2 | 277.144 | 0 | 1
5/30 | 15:00:00 | 292.15 | 98900 | 6.2 | 100 | 4.8252 | 2588.4 | 2718 | 275.896 | 0 | 1
5/30 | 16:00:00 | 291.15 | 98892 | 5.7 | 110 | 4.8256 | 2109.6 | 2426.4 | 275.391 | 0 | 1
5/30 | 17:00:00 | 291.15 | 98892 | 5.1 | 90 | 6.8517 | 1558.8 | 1987.2 | 276.57 | 0 | 1
5/30 | 18:00:00 | 290.15 | 98883 | 5.7 | 90 | 6.3949 | 986.4 | 1346.4 | 275.388 | 0 | 1
5/30 | 19:00:00 | 288.15 | 98867 | 5.7 | 90 | 5.9661 | 464.4 | 529.2 | 273.258 | 0 | 1
5/30 | 20:00:00 | 286.15 | 98850 | 6.2 | 90 | 5.9671 | 97.2 | 0 | 271.496 | 0 | 1
5/30 | 21:00:00 | 285.15 | 98841 | 3.6 | 80 | 6.8552 | 0 | 0 | 271.384 | 0 | 1
5/30 | 22:00:00 | 283.15 | 98824 | 2.1 | 60 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
5/30 | 23:00:00 | 283.15 | 98824 | 3.1 | 70 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
5/30 | 24:00:00 | 282.15 | 98815 | 3.6 | 70 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
5/31 | 01:00:00 | 282.15 | 98815 | 3.1 | 40 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
5/31 | 02:00:00 | 282.15 | 98815 | 2.1 | 30 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
5/31 | 03:00:00 | 281.15 | 98806 | 3.1 | 60 | 6.4 | 0 | 0 | 267.688 | 0 | 1
5/31 | 04:00:00 | 281.15 | 98806 | 2.6 | 30 | 6.4 | 0 | 0 | 267.688 | 0 | 1
5/31 | 05:00:00 | 282.15 | 98815 | 2.6 | 20 | 6.3994 | 46.8 | 0 | 268.532 | 0 | 1
5/31 | 06:00:00 | 283.15 | 98824 | 2.6 | 10 | 6.8564 | 248.4 | 0 | 269.71 | 0 | 1
5/31 | 07:00:00 | 285.15 | 98841 | 3.1 | 40 | 6.8552 | 763.2 | 626.4 | 271.384 | 0 | 1
5/31 | 08:00:00 | 286.15 | 98850 | 4.1 | 40 | 7.3412 | 1213.2 | 856.8 | 272.563 | 0 | 1
5/31 | 09:00:00 | 288.15 | 98867 | 4.1 | 50 | 7.3399 | 1897.2 | 1778.4 | 274.218 | 0 | 1
5/31 | 10:00:00 | 290.15 | 98883 | 4.6 | 60 | 7.3387 | 2448 | 2476.8 | 275.988 | 0 | 1
5/31 | 11:00:00 | 291.15 | 98892 | 7.2 | 80 | 7.855 | 2768.4 | 2581.2 | 277.17 | 0 | 1
5/31 | 12:00:00 | 293.15 | 98908 | 6.7 | 80 | 7.3368 | 3020.4 | 2923.2 | 278.56 | 0 | 1
5/31 | 13:00:00 | 294.15 | 98916 | 6.7 | 70 | 7.8531 | 3027.6 | 2923.2 | 279.742 | 0 | 1
5/31 | 14:00:00 | 294.15 | 98916 | 6.7 | 70 | 7.3362 | 2880 | 2908.8 | 279.51 | 0 | 1
5/31 | 15:00:00 | 294.15 | 98916 | 6.2 | 70 | 6.85 | 2574 | 2826 | 279.127 | 0 | 1
5/31 | 16:00:00 | 294.15 | 98916 | 6.7 | 90 | 6.3928 | 2131.2 | 2545.2 | 278.892 | 0 | 1
5/31 | 17:00:00 | 293.15 | 98908 | 5.7 | 70 | 5.9636 | 1591.2 | 2048.4 | 277.708 | 0 | 1
5/31 | 18:00:00 | 293.15 | 98908 | 6.2 | 80 | 5.5598 | 1011.6 | 1422 | 277.319 | 0 | 1
5/31 | 19:00:00 | 288.95 | 98873 | 3.5 | 75 | 5.6406 | 478.8 | 572.4 | 273.543 | 0 | 1
5/31 | 20:00:00 | 287.65 | 98863 | 2.6 | 65 | 5.8835 | 108 | 0 | 272.597 | 0 | 1
5/31 | 21:00:00 | 286.35 | 98852 | 2.1 | 132 | 5.8841 | 0 | 0 | 271.505 | 0 | 1
5/31 | 22:00:00 | 285.65 | 98846 | 1.8 | 117 | 5.7622 | 0 | 0 | 270.906 | 0 | 1
5/31 | 23:00:00 | 285.15 | 98841 | 1.9 | 107 | 5.6424 | 0 | 0 | 270.363 | 0 | 1
5/31 | 24:00:00 | 284.65 | 98837 | 1.8 | 104 | 5.5639 | 0 | 0 | 269.842 | 0 | 1
6/1 | 01:00:00 | 284.35 | 98835 | 1.9 | 17 | 5.6428 | 0 | 0 | 269.604 | 0 | 1
6/1 | 02:00:00 | 284.15 | 98833 | 2.3 | 105 | 5.7629 | 0 | 0 | 269.613 | 0 | 1
6/1 | 03:00:00 | 284.35 | 98835 | 2.3 | 105 | 5.8852 | 0 | 0 | 269.872 | 0 | 1
6/1 | 04:00:00 | 284.95 | 98839 | 2.6 | 102 | 5.9678 | 0 | 0 | 270.614 | 0 | 1
6/1 | 05:00:00 | 285.95 | 98848 | 2.8 | 110 | 5.9672 | 72 | 0 | 271.563 | 0 | 1
6/1 | 06:00:00 | 287.35 | 98860 | 3 | 30 | 5.9665 | 388.8 | 349.2 | 272.766 | 0 | 1
6/1 | 07:00:00 | 286.15 | 98850 | 2.6 | 20 | 5.9671 | 900 | 1152 | 271.496 | 0 | 1
6/1 | 08:00:00 | 288.15 | 98867 | 3.1 | 40 | 5.9661 | 1497.6 | 1918.8 | 273.258 | 0 | 1
6/1 | 09:00:00 | 290.15 | 98883 | 3.6 | 40 | 5.9651 | 2062.8 | 2480.4 | 275.013 | 0 | 1
6/1 | 10:00:00 | 291.15 | 98892 | 3.6 | 60 | 5.5607 | 2538 | 2844 | 275.578 | 0 | 1
6/1 | 11:00:00 | 292.15 | 98900 | 4.1 | 60 | 6.8511 | 2851.2 | 2887.2 | 277.377 | 0 | 1
6/1 | 12:00:00 | 293.15 | 98908 | 4.6 | 70 | 6.8506 | 3034.8 | 2952 | 278.327 | 0 | 1
6/1 | 13:00:00 | 294.15 | 98916 | 3.6 | 70 | 6.85 | 3052.8 | 2966.4 | 279.127 | 0 | 1
6/1 | 14:00:00 | 294.15 | 98916 | 4.6 | 90 | 5.9631 | 2905.2 | 2952 | 278.502 | 0 | 1
6/1 | 15:00:00 | 295.15 | 98924 | 3.1 | 70 | 6.3923 | 2588.4 | 2757.6 | 279.686 | 0 | 1
6/1 | 16:00:00 | 295.15 | 98924 | 3.6 | 80 | 6.3923 | 2138.4 | 2548.8 | 279.686 | 0 | 1
6/1 | 17:00:00 | 295.15 | 98924 | 3.1 | 80 | 6.3923 | 1598.4 | 2070 | 279.686 | 0 | 1
6/1 | 18:00:00 | 294.15 | 98916 | 4.1 | 100 | 5.9631 | 1018.8 | 1425.6 | 278.502 | 0 | 1
6/1 | 19:00:00 | 293.15 | 98908 | 3.6 | 80 | 6.3933 | 486 | 576 | 277.944 | 0 | 1
6/1 | 20:00:00 | 291.15 | 98892 | 2.6 | 110 | 6.3944 | 111.6 | 0 | 276.195 | 0 | 1
6/1 | 21:00:00 | 289.15 | 98875 | 2.1 | 110 | 5.9656 | 0 | 0 | 274.206 | 0 | 1
6/1 | 22:00:00 | 286.15 | 98850 | 3.1 | 130 | 5.9671 | 0 | 0 | 271.496 | 0 | 1
6/1 | 23:00:00 | 287.15 | 98858 | 1 | 13 | 5.9666 | 0 | 0 | 272.445 | 0 | 1
6/1 | 24:00:00 | 286.15 | 98850 | 1.5 | 200 | 5.5631 | 0 | 0 | 271.264 | 0 | 1
6/2 | 01:00:00 | 285.15 | 98841 | 1 | 180 | 5.1842 | 0 | 0 | 270.084 | 0 | 1
6/2 | 02:00:00 | 285.15 | 98841 | 1 | 190 | 5.5636 | 0 | 0 | 270.316 | 0 | 1
6/2 | 03:00:00 | 284.15 | 98833 | 1.5 | 220 | 5.5641 | 0 | 0 | 269.498 | 0 | 1
6/2 | 04:00:00 | 284.15 | 98833 | 1 | 260 | 5.9681 | 0 | 0 | 269.854 | 0 | 1
6/2 | 05:00:00 | 284.15 | 98833 | 2.1 | 290 | 5.9681 | 72 | 0 | 269.854 | 0 | 1
6/2 | 06:00:00 | 285.15 | 98841 | 2.1 | 280 | 6.8552 | 349.2 | 244.8 | 271.384 | 0 | 1
6/2 | 07:00:00 | 288.15 | 98867 | 3.1 | 300 | 6.8534 | 896.4 | 1119.6 | 273.988 | 0 | 1
6/2 | 08:00:00 | 290.15 | 98883 | 1.5 | 188 | 7.3387 | 1472.4 | 1789.2 | 275.988 | 0 | 1
6/2 | 09:00:00 | 292.15 | 98900 | 1.5 | 324 | 7.8544 | 2026.8 | 2268 | 277.983 | 0 | 1
6/2 | 10:00:00 | 293.15 | 98908 | 1.5 | 122 | 7.3368 | 2516.4 | 2692.8 | 278.56 | 0 | 1
6/2 | 11:00:00 | 294.15 | 98916 | 1.5 | 181 | 7.8531 | 2844 | 2876.4 | 279.742 | 0 | 1
6/2 | 12:00:00 | 295.15 | 98924 | 1.5 | 85 | 7.8525 | 2998.8 | 2851.2 | 280.838 | 0 | 1
6/2 | 13:00:00 | 296.15 | 98932 | 2.1 | 330 | 7.335 | 3013.2 | 2862 | 281.555 | 0 | 1
6/2 | 14:00:00 | 296.15 | 98932 | 2.1 | 60 | 7.8518 | 2854.8 | 2818.8 | 281.789 | 0 | 1
6/2 | 15:00:00 | 296.15 | 98932 | 1.5 | 195 | 8.4009 | 2545.2 | 2635.2 | 282.022 | 0 | 1
6/2 | 16:00:00 | 295.15 | 98924 | 1.5 | 268 | 8.4016 | 2106 | 2440.8 | 281.07 | 0 | 1
6/2 | 17:00:00 | 294.15 | 98916 | 1 | 154 | 8.9857 | 1569.6 | 2095.2 | 280.347 | 0 | 1
6/2 | 18:00:00 | 291.15 | 98892 | 5.1 | 10 | 8.9879 | 1004.4 | 1324.8 | 277.488 | 0 | 1
6/2 | 19:00:00 | 289.15 | 98875 | 5.1 | 20 | 7.8564 | 482.4 | 547.2 | 275.129 | 0 | 1
6/2 | 20:00:00 | 288.15 | 98867 | 2.6 | 30 | 7.3399 | 115.2 | 0 | 273.95 | 0 | 1
6/2 | 21:00:00 | 286.15 | 98850 | 4.1 | 30 | 8.408 | 0 | 0 | 273.248 | 0 | 1
6/2 | 22:00:00 | 284.15 | 98833 | 3.6 | 30 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/2 | 23:00:00 | 283.15 | 98824 | 3.1 | 30 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
6/2 | 24:00:00 | 283.15 | 98824 | 3.1 | 30 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
6/3 | 01:00:00 | 283.15 | 98824 | 2.6 | 30 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
6/3 | 02:00:00 | 284.15 | 98833 | 3.6 | 20 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
6/3 | 03:00:00 | 284.15 | 98833 | 3.1 | 30 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/3 | 04:00:00 | 283.15 | 98824 | 3.6 | 30 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
6/3 | 05:00:00 | 283.15 | 98824 | 3.1 | 30 | 7.3431 | 79.2 | 0 | 269.46 | 0 | 1
6/3 | 06:00:00 | 283.15 | 98824 | 3.1 | 30 | 7.3431 | 219.6 | 0 | 269.936 | 0 | 1
6/3 | 07:00:00 | 283.15 | 98824 | 4.1 | 20 | 6.8564 | 486 | 10.8 | 269.71 | 0 | 1
6/3 | 08:00:00 | 283.15 | 98824 | 4.1 | 30 | 6.3988 | 788.4 | 223.2 | 269.483 | 0 | 1
6/3 | 09:00:00 | 283.15 | 98824 | 4.6 | 30 | 5.9687 | 1933.2 | 1800 | 268.779 | 0 | 1
6/3 | 10:00:00 | 284.15 | 98833 | 3.6 | 40 | 5.5641 | 2368.8 | 1839.6 | 269.498 | 0 | 1
6/3 | 11:00:00 | 285.15 | 98841 | 3.6 | 30 | 5.1842 | 1490.4 | 943.2 | 270.692 | 0 | 1
6/3 | 12:00:00 | 286.15 | 98850 | 3.1 | 60 | 5.5631 | 3024 | 2440.8 | 271.13 | 0 | 1
6/3 | 13:00:00 | 287.15 | 98858 | 3.6 | 30 | 5.1833 | 3038.4 | 2754 | 271.843 | 0 | 1
6/3 | 14:00:00 | 287.15 | 98858 | 4.1 | 30 | 5.1833 | 2718 | 2098.8 | 272.109 | 0 | 1
6/3 | 15:00:00 | 287.15 | 98858 | 3.6 | 50 | 5.1833 | 2574 | 2613.6 | 271.843 | 0 | 1
6/3 | 16:00:00 | 287.15 | 98858 | 4.1 | 50 | 4.8273 | 2134.8 | 2242.8 | 271.608 | 0 | 1
6/3 | 17:00:00 | 287.15 | 98858 | 3.6 | 60 | 4.8273 | 1508.4 | 1630.8 | 271.873 | 0 | 1
6/3 | 18:00:00 | 286.15 | 98850 | 4.1 | 30 | 5.5631 | 1018.8 | 1429.2 | 271.13 | 0 | 1
6/3 | 19:00:00 | 285.15 | 98841 | 4.1 | 30 | 5.1842 | 493.2 | 568.8 | 269.95 | 0 | 1
6/3 | 20:00:00 | 284.15 | 98833 | 4.1 | 40 | 5.1847 | 118.8 | 0 | 269.003 | 0 | 1
6/3 | 21:00:00 | 282.15 | 98815 | 3.1 | 40 | 4.8294 | 0 | 0 | 267.139 | 0 | 1
6/3 | 22:00:00 | 281.15 | 98806 | 3.6 | 30 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
6/3 | 23:00:00 | 280.15 | 98798 | 3.1 | 20 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
6/3 | 24:00:00 | 280.15 | 98798 | 1.5 | 340 | 4.8303 | 0 | 0 | 264.986 | 0 | 1
6/4 | 01:00:00 | 279.15 | 98789 | 2.6 | 330 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
6/4 | 02:00:00 | 278.15 | 98780 | 2.6 | 290 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
6/4 | 03:00:00 | 279.15 | 98789 | 2.6 | 350 | 4.8307 | 0 | 0 | 264.767 | 0 | 1
6/4 | 04:00:00 | 280.15 | 98798 | 2.1 | 340 | 4.8303 | 0 | 0 | 265.715 | 0 | 1
6/4 | 05:00:00 | 279.15 | 98789 | 0.5 | 37 | 4.8307 | 28.8 | 0 | 264.874 | 0 | 1
6/4 | 06:00:00 | 280.15 | 98798 | 2.1 | 300 | 5.1865 | 428.4 | 529.2 | 265.216 | 0 | 1
6/4 | 07:00:00 | 281.15 | 98806 | 1 | 154 | 4.8299 | 493.2 | 46.8 | 266.664 | 0 | 1
6/4 | 08:00:00 | 281.15 | 98806 | 1 | 35 | 5.1861 | 792 | 57.6 | 266.895 | 0 | 1
6/4 | 09:00:00 | 282.15 | 98815 | 1.5 | 329 | 4.8294 | 1080 | 201.6 | 267.612 | 0 | 1
6/4 | 10:00:00 | 283.15 | 98824 | 1 | 138 | 4.829 | 1317.6 | 223.2 | 268.561 | 0 | 1
6/4 | 11:00:00 | 283.15 | 98824 | 1.5 | 78 | 5.1851 | 1490.4 | 72 | 268.793 | 0 | 1
6/4 | 12:00:00 | 284.15 | 98833 | 3.6 | 260 | 5.1847 | 1584 | 223.2 | 269.743 | 0 | 1
6/4 | 13:00:00 | 285.15 | 98841 | 1 | 36 | 5.9676 | 2862 | 1958.4 | 270.678 | 0 | 1
6/4 | 14:00:00 | 286.15 | 98850 | 3.6 | 320 | 5.5631 | 2721.6 | 2304 | 271.395 | 0 | 1
6/4 | 15:00:00 | 284.15 | 98833 | 3.1 | 50 | 5.9681 | 2426.4 | 2242.8 | 269.728 | 0 | 1
6/4 | 16:00:00 | 285.15 | 98841 | 2.6 | 70 | 5.9676 | 2008.8 | 1990.8 | 270.678 | 0 | 1
6/4 | 17:00:00 | 284.15 | 98833 | 3.1 | 50 | 5.9681 | 1504.8 | 1612.8 | 269.728 | 0 | 1
6/4 | 18:00:00 | 284.15 | 98833 | 4.1 | 60 | 5.9681 | 964.8 | 993.6 | 269.728 | 0 | 1
6/4 | 19:00:00 | 282.15 | 98815 | 4.6 | 60 | 5.5651 | 259.2 | 0 | 268.075 | 0 | 1
6/4 | 20:00:00 | 280.15 | 98798 | 3.1 | 50 | 5.9703 | 115.2 | 0 | 265.931 | 0 | 1
6/4 | 21:00:00 | 280.15 | 98798 | 1.5 | 124 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
6/4 | 22:00:00 | 280.15 | 98798 | 0 | 269 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
6/4 | 23:00:00 | 280.15 | 98798 | 0.5 | 172 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
6/4 | 24:00:00 | 280.15 | 98798 | 1 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
6/5 | 01:00:00 | 280.15 | 98798 | 1 | 220 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
6/5 | 02:00:00 | 280.15 | 98798 | 1 | 210 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
6/5 | 03:00:00 | 279.15 | 98789 | 1.5 | 200 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
6/5 | 04:00:00 | 279.15 | 98789 | 0.5 | 230 | 5.187 | 0 | 0 | 264.996 | 0 | 1
6/5 | 05:00:00 | 279.15 | 98789 | 0 | 271 | 5.187 | 54 | 0 | 264.996 | 0 | 1
6/5 | 06:00:00 | 280.15 | 98798 | 0.5 | 339 | 5.5661 | 262.8 | 0 | 266.174 | 0 | 1
6/5 | 07:00:00 | 281.15 | 98806 | 2.1 | 170 | 5.1861 | 784.8 | 702 | 266.667 | 0 | 1
6/5 | 08:00:00 | 282.15 | 98815 | 0.5 | 238 | 4.4952 | 1483.2 | 1728 | 266.778 | 0 | 1
6/5 | 09:00:00 | 283.15 | 98824 | 2.6 | 120 | 4.4948 | 2052 | 2134.8 | 267.724 | 0 | 1
6/5 | 10:00:00 | 285.15 | 98841 | 1 | 38 | 4.494 | 2530.8 | 2574 | 269.481 | 0 | 1
6/5 | 11:00:00 | 286.15 | 98850 | 1.5 | 98 | 4.8277 | 2692.8 | 2174.4 | 270.927 | 0 | 1
6/5 | 12:00:00 | 287.15 | 98858 | 2.6 | 70 | 4.8273 | 2865.6 | 2343.6 | 271.873 | 0 | 1
6/5 | 13:00:00 | 285.15 | 98841 | 4.1 | 80 | 4.494 | 2880 | 2354.4 | 269.744 | 0 | 1
6/5 | 14:00:00 | 282.15 | 98815 | 4.6 | 20 | 5.9692 | 2718 | 2289.6 | 267.83 | 0 | 1
6/5 | 15:00:00 | 282.15 | 98815 | 5.7 | 30 | 5.9692 | 2430 | 2239.2 | 267.83 | 0 | 1
6/5 | 16:00:00 | 280.15 | 98798 | 6.7 | 30 | 6.4005 | 2012.4 | 1821.6 | 266.157 | 0 | 1
6/5 | 17:00:00 | 279.15 | 98789 | 6.2 | 30 | 5.5666 | 838.8 | 241.2 | 265.224 | 0 | 1
6/5 | 18:00:00 | 279.15 | 98789 | 5.1 | 30 | 5.9708 | 540 | 14.4 | 265.451 | 0 | 1
6/5 | 19:00:00 | 278.15 | 98780 | 5.7 | 30 | 5.5671 | 262.8 | 0 | 264.274 | 0 | 1
6/5 | 20:00:00 | 278.15 | 98780 | 4.6 | 30 | 5.5671 | 64.8 | 0 | 264.274 | 0 | 1
6/5 | 21:00:00 | 278.15 | 98780 | 5.7 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
6/5 | 22:00:00 | 278.15 | 98780 | 5.7 | 30 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
6/5 | 23:00:00 | 278.15 | 98780 | 6.2 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
6/5 | 24:00:00 | 278.15 | 98780 | 5.7 | 30 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
6/6 | 01:00:00 | 278.15 | 98780 | 6.7 | 30 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
6/6 | 02:00:00 | 278.15 | 98780 | 5.1 | 40 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
6/6 | 03:00:00 | 279.15 | 98789 | 4.1 | 80 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
6/6 | 04:00:00 | 279.15 | 98789 | 3.6 | 60 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
6/6 | 05:00:00 | 279.15 | 98789 | 3.1 | 70 | 5.9708 | 46.8 | 0 | 265.451 | 0 | 1
6/6 | 06:00:00 | 279.15 | 98789 | 3.1 | 70 | 5.9708 | 226.8 | 0 | 265.451 | 0 | 1
6/6 | 07:00:00 | 279.15 | 98789 | 4.1 | 70 | 5.9708 | 493.2 | 10.8 | 265.451 | 0 | 1
6/6 | 08:00:00 | 280.15 | 98798 | 3.6 | 80 | 6.4005 | 792 | 54 | 266.628 | 0 | 1
6/6 | 09:00:00 | 281.15 | 98806 | 6.2 | 70 | 6.4 | 1076.4 | 169.2 | 267.58 | 0 | 1
6/6 | 10:00:00 | 282.15 | 98815 | 6.2 | 70 | 6.3994 | 2368.8 | 1911.6 | 268.057 | 0 | 1
6/6 | 11:00:00 | 282.15 | 98815 | 9.3 | 80 | 5.9692 | 2685.6 | 2199.6 | 267.83 | 0 | 1
6/6 | 12:00:00 | 283.15 | 98824 | 6.7 | 70 | 5.5646 | 3031.2 | 2757.6 | 268.287 | 0 | 1
6/6 | 13:00:00 | 283.15 | 98824 | 6.2 | 60 | 5.9687 | 3042 | 2779.2 | 268.516 | 0 | 1
6/6 | 14:00:00 | 283.15 | 98824 | 6.7 | 70 | 5.5646 | 2728.8 | 2196 | 268.55 | 0 | 1
6/6 | 15:00:00 | 284.15 | 98833 | 6.2 | 70 | 5.5641 | 2437.2 | 2250 | 269.498 | 0 | 1
6/6 | 16:00:00 | 283.15 | 98824 | 7.2 | 80 | 5.1851 | 2026.8 | 2008.8 | 268.319 | 0 | 1
6/6 | 17:00:00 | 283.15 | 98824 | 7.2 | 60 | 5.5646 | 1519.2 | 1612.8 | 268.55 | 0 | 1
6/6 | 18:00:00 | 283.15 | 98824 | 5.7 | 70 | 5.5646 | 979.2 | 1144.8 | 268.55 | 0 | 1
6/6 | 19:00:00 | 283.15 | 98824 | 5.1 | 60 | 5.5646 | 478.8 | 464.4 | 268.55 | 0 | 1
6/6 | 20:00:00 | 282.15 | 98815 | 4.6 | 60 | 5.1856 | 122.4 | 0 | 267.371 | 0 | 1
6/6 | 21:00:00 | 281.15 | 98806 | 4.1 | 60 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
6/6 | 22:00:00 | 281.15 | 98806 | 4.1 | 50 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
6/6 | 23:00:00 | 281.15 | 98806 | 4.1 | 50 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
6/6 | 24:00:00 | 281.15 | 98806 | 4.6 | 50 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
6/7 | 01:00:00 | 280.15 | 98798 | 5.1 | 40 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
6/7 | 02:00:00 | 280.15 | 98798 | 5.1 | 40 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
6/7 | 03:00:00 | 280.15 | 98798 | 5.7 | 50 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
6/7 | 04:00:00 | 280.15 | 98798 | 5.7 | 50 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
6/7 | 05:00:00 | 280.15 | 98798 | 5.1 | 50 | 5.9703 | 86.4 | 0 | 265.931 | 0 | 1
6/7 | 06:00:00 | 280.15 | 98798 | 5.1 | 50 | 6.4005 | 410.4 | 374.4 | 266.157 | 0 | 1
6/7 | 07:00:00 | 281.15 | 98806 | 6.2 | 40 | 6.4 | 946.8 | 1116 | 266.846 | 0 | 1
6/7 | 08:00:00 | 282.15 | 98815 | 6.7 | 50 | 6.3994 | 792 | 108 | 268.532 | 0 | 1
6/7 | 09:00:00 | 284.15 | 98833 | 7.7 | 60 | 5.9681 | 1080 | 169.2 | 270.206 | 0 | 1
6/7 | 10:00:00 | 284.15 | 98833 | 7.2 | 60 | 5.9681 | 2376 | 1839.6 | 269.728 | 0 | 1
6/7 | 11:00:00 | 284.15 | 98833 | 7.2 | 60 | 5.5641 | 2692.8 | 2293.2 | 269.498 | 0 | 1
6/7 | 12:00:00 | 285.15 | 98841 | 7.7 | 50 | 5.1842 | 2865.6 | 2329.2 | 270.214 | 0 | 1
6/7 | 13:00:00 | 285.15 | 98841 | 8.2 | 60 | 5.5636 | 2872.8 | 2322 | 270.447 | 0 | 1
6/7 | 14:00:00 | 286.15 | 98850 | 7.7 | 50 | 5.5631 | 2732.4 | 2300.4 | 271.395 | 0 | 1
6/7 | 15:00:00 | 285.15 | 98841 | 7.7 | 50 | 5.1842 | 2444.4 | 2260.8 | 270.214 | 0 | 1
6/7 | 16:00:00 | 285.15 | 98841 | 7.7 | 60 | 5.1842 | 2030.4 | 2008.8 | 270.214 | 0 | 1
6/7 | 17:00:00 | 285.15 | 98841 | 7.2 | 50 | 5.1842 | 1526.4 | 1627.2 | 270.214 | 0 | 1
6/7 | 18:00:00 | 284.15 | 98833 | 6.7 | 50 | 5.5641 | 986.4 | 1148.4 | 269.498 | 0 | 1
6/7 | 19:00:00 | 284.15 | 98833 | 7.2 | 60 | 5.5641 | 486 | 468 | 269.498 | 0 | 1
6/7 | 20:00:00 | 283.15 | 98824 | 5.7 | 50 | 5.5646 | 126 | 0 | 268.55 | 0 | 1
6/7 | 21:00:00 | 282.15 | 98815 | 4.6 | 50 | 5.5651 | 0 | 0 | 267.601 | 0 | 1
6/7 | 22:00:00 | 282.15 | 98815 | 4.1 | 40 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
6/7 | 23:00:00 | 281.15 | 98806 | 4.1 | 20 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
6/7 | 24:00:00 | 280.15 | 98798 | 4.1 | 20 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
6/8 | 01:00:00 | 280.15 | 98798 | 4.1 | 20 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
6/8 | 02:00:00 | 280.15 | 98798 | 3.6 | 20 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
6/8 | 03:00:00 | 280.15 | 98798 | 2.6 | 30 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
6/8 | 04:00:00 | 280.15 | 98798 | 3.1 | 20 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
6/8 | 05:00:00 | 280.15 | 98798 | 3.1 | 20 | 5.9703 | 93.6 | 0 | 265.671 | 0 | 1
6/8 | 06:00:00 | 280.15 | 98798 | 3.1 | 30 | 5.9703 | 410.4 | 374.4 | 265.931 | 0 | 1
6/8 | 07:00:00 | 281.15 | 98806 | 3.6 | 30 | 5.9698 | 892.8 | 1051.2 | 266.881 | 0 | 1
6/8 | 08:00:00 | 283.15 | 98824 | 4.1 | 50 | 6.3988 | 1429.2 | 1544.4 | 269.007 | 0 | 1
6/8 | 09:00:00 | 283.15 | 98824 | 3.6 | 70 | 5.9687 | 2062.8 | 2257.2 | 268.516 | 0 | 1
6/8 | 10:00:00 | 284.15 | 98833 | 4.1 | 60 | 5.9681 | 2376 | 2134.8 | 269.728 | 0 | 1
6/8 | 11:00:00 | 285.15 | 98841 | 4.1 | 50 | 5.5636 | 2692.8 | 2289.6 | 270.447 | 0 | 1
6/8 | 12:00:00 | 286.15 | 98850 | 4.6 | 60 | 5.5631 | 2862 | 2318.4 | 271.395 | 0 | 1
6/8 | 13:00:00 | 286.15 | 98850 | 5.7 | 80 | 5.9671 | 2872.8 | 2311.2 | 271.627 | 0 | 1
6/8 | 14:00:00 | 287.15 | 98858 | 4.6 | 70 | 5.5627 | 2736 | 2296.8 | 272.343 | 0 | 1
6/8 | 15:00:00 | 287.15 | 98858 | 6.2 | 50 | 5.5627 | 2444.4 | 2246.4 | 272.343 | 0 | 1
6/8 | 16:00:00 | 286.15 | 98850 | 5.7 | 70 | 5.5631 | 2030.4 | 2145.6 | 271.395 | 0 | 1
6/8 | 17:00:00 | 285.15 | 98841 | 5.7 | 70 | 5.5636 | 1623.6 | 2124 | 270.182 | 0 | 1
6/8 | 18:00:00 | 285.15 | 98841 | 5.7 | 80 | 5.5636 | 1051.2 | 1396.8 | 270.182 | 0 | 1
6/8 | 19:00:00 | 284.15 | 98833 | 4.6 | 70 | 5.5641 | 518.4 | 590.4 | 269.234 | 0 | 1
6/8 | 20:00:00 | 283.15 | 98824 | 4.6 | 50 | 5.5646 | 136.8 | 18 | 268.287 | 0 | 1
6/8 | 21:00:00 | 283.15 | 98824 | 2.6 | 60 | 5.9687 | 0 | 0 | 268.779 | 0 | 1
6/8 | 22:00:00 | 282.15 | 98815 | 3.1 | 70 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
6/8 | 23:00:00 | 281.15 | 98806 | 2.6 | 60 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
6/8 | 24:00:00 | 280.15 | 98798 | 3.1 | 40 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
6/9 | 01:00:00 | 280.15 | 98798 | 3.6 | 20 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
6/9 | 02:00:00 | 280.15 | 98798 | 4.1 | 20 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
6/9 | 03:00:00 | 280.15 | 98798 | 4.6 | 20 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
6/9 | 04:00:00 | 279.15 | 98789 | 4.1 | 20 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
6/9 | 05:00:00 | 280.15 | 98798 | 4.6 | 10 | 5.9703 | 93.6 | 0 | 265.671 | 0 | 1
6/9 | 06:00:00 | 281.15 | 98806 | 4.6 | 20 | 5.9698 | 439.2 | 482.4 | 266.62 | 0 | 1
6/9 | 07:00:00 | 282.15 | 98815 | 4.6 | 30 | 6.3994 | 896.4 | 1047.6 | 268.057 | 0 | 1
6/9 | 08:00:00 | 282.15 | 98815 | 5.7 | 10 | 6.3994 | 795.6 | 223.2 | 268.532 | 0 | 1
6/9 | 09:00:00 | 283.15 | 98824 | 6.2 | 20 | 6.3988 | 1944 | 1785.6 | 269.007 | 0 | 1
6/9 | 10:00:00 | 283.15 | 98824 | 6.7 | 20 | 6.8564 | 2372.4 | 2217.6 | 269.234 | 0 | 1
6/9 | 11:00:00 | 285.15 | 98841 | 6.7 | 20 | 6.8552 | 2685.6 | 1897.2 | 271.136 | 0 | 1
6/9 | 12:00:00 | 285.15 | 98841 | 7.7 | 20 | 6.8552 | 1584 | 932.4 | 271.616 | 0 | 1
6/9 | 13:00:00 | 284.15 | 98833 | 5.7 | 20 | 6.8558 | 2869.2 | 1929.6 | 270.185 | 0 | 1
6/9 | 14:00:00 | 285.15 | 98841 | 7.7 | 10 | 6.3977 | 2728.8 | 2278.8 | 270.907 | 0 | 1
6/9 | 15:00:00 | 285.15 | 98841 | 7.7 | 20 | 6.8552 | 2437.2 | 2156.4 | 271.136 | 0 | 1
6/9 | 16:00:00 | 285.15 | 98841 | 6.7 | 20 | 6.3977 | 2152.8 | 2448 | 270.643 | 0 | 1
6/9 | 17:00:00 | 285.15 | 98841 | 6.7 | 20 | 6.3977 | 1623.6 | 2026.8 | 270.643 | 0 | 1
6/9 | 18:00:00 | 284.15 | 98833 | 5.7 | 20 | 6.3982 | 1054.8 | 1389.6 | 269.693 | 0 | 1
6/9 | 19:00:00 | 283.15 | 98824 | 5.7 | 30 | 6.8564 | 522 | 590.4 | 268.971 | 0 | 1
6/9 | 20:00:00 | 283.15 | 98824 | 4.6 | 30 | 6.3988 | 140.4 | 25.2 | 268.744 | 0 | 1
6/9 | 21:00:00 | 282.15 | 98815 | 4.6 | 20 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
6/9 | 22:00:00 | 282.15 | 98815 | 3.6 | 20 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
6/9 | 23:00:00 | 282.15 | 98815 | 3.1 | 10 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
6/9 | 24:00:00 | 282.15 | 98815 | 3.1 | 360 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
6/10 | 01:00:00 | 281.15 | 98806 | 2.1 | 340 | 6.4 | 0 | 0 | 266.846 | 0 | 1
6/10 | 02:00:00 | 281.15 | 98806 | 1 | 285 | 6.4 | 0 | 0 | 266.846 | 0 | 1
6/10 | 03:00:00 | 281.15 | 98806 | 1.5 | 350 | 6.4 | 0 | 0 | 266.846 | 0 | 1
6/10 | 04:00:00 | 281.15 | 98806 | 1.5 | 12 | 6.4 | 0 | 0 | 266.846 | 0 | 1
6/10 | 05:00:00 | 281.15 | 98806 | 2.1 | 30 | 6.4 | 97.2 | 0 | 266.846 | 0 | 1
6/10 | 06:00:00 | 281.15 | 98806 | 2.1 | 30 | 6.4 | 230.4 | 0 | 267.58 | 0 | 1
6/10 | 07:00:00 | 282.15 | 98815 | 2.1 | 40 | 6.3994 | 496.8 | 10.8 | 268.532 | 0 | 1
6/10 | 08:00:00 | 282.15 | 98815 | 2.1 | 50 | 6.3994 | 795.6 | 54 | 268.532 | 0 | 1
6/10 | 09:00:00 | 284.15 | 98833 | 2.1 | 80 | 6.8558 | 1076.4 | 194.4 | 270.663 | 0 | 1
6/10 | 10:00:00 | 284.15 | 98833 | 2.1 | 70 | 6.8558 | 1317.6 | 216 | 270.663 | 0 | 1
6/10 | 11:00:00 | 285.15 | 98841 | 2.1 | 100 | 6.8552 | 1490.4 | 216 | 271.616 | 0 | 1
6/10 | 12:00:00 | 286.15 | 98850 | 3.1 | 140 | 6.3971 | 2858.4 | 1936.8 | 271.858 | 0 | 1
6/10 | 13:00:00 | 287.15 | 98858 | 3.1 | 120 | 6.3966 | 2872.8 | 2304 | 272.808 | 0 | 1
6/10 | 14:00:00 | 287.15 | 98858 | 2.1 | 110 | 6.3966 | 2732.4 | 2275.2 | 272.808 | 0 | 1
6/10 | 15:00:00 | 287.15 | 98858 | 2.1 | 120 | 6.3966 | 2444.4 | 2224.8 | 272.808 | 0 | 1
6/10 | 16:00:00 | 285.15 | 98841 | 5.1 | 80 | 7.3418 | 2030.4 | 1962 | 271.363 | 0 | 1
6/10 | 17:00:00 | 285.15 | 98841 | 4.6 | 80 | 7.8591 | 1526.4 | 1587.6 | 271.588 | 0 | 1
6/10 | 18:00:00 | 284.15 | 98833 | 5.1 | 90 | 7.3425 | 993.6 | 993.6 | 270.411 | 0 | 1
6/10 | 19:00:00 | 283.15 | 98824 | 3.6 | 80 | 7.3431 | 273.6 | 0 | 269.936 | 0 | 1
6/10 | 20:00:00 | 283.15 | 98824 | 3.1 | 80 | 7.8605 | 75.6 | 0 | 270.161 | 0 | 1
6/10 | 21:00:00 | 283.15 | 98824 | 3.1 | 70 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
6/10 | 22:00:00 | 282.15 | 98815 | 2.1 | 70 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
6/10 | 23:00:00 | 282.15 | 98815 | 1 | 195 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
6/10 | 24:00:00 | 282.15 | 98815 | 2.1 | 70 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
6/11 | 01:00:00 | 282.15 | 98815 | 2.6 | 40 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
6/11 | 02:00:00 | 282.15 | 98815 | 1.5 | 58 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
6/11 | 03:00:00 | 281.15 | 98806 | 1 | 115 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
6/11 | 04:00:00 | 281.15 | 98806 | 1 | 310 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
6/11 | 05:00:00 | 281.15 | 98806 | 1 | 83 | 6.4 | 97.2 | 0 | 266.846 | 0 | 1
6/11 | 06:00:00 | 282.15 | 98815 | 2.6 | 260 | 6.8571 | 442.8 | 475.2 | 268.021 | 0 | 1
6/11 | 07:00:00 | 282.15 | 98815 | 4.1 | 270 | 6.8571 | 950.4 | 1267.2 | 268.021 | 0 | 1
6/11 | 08:00:00 | 282.15 | 98815 | 3.6 | 260 | 7.3438 | 1515.6 | 1897.2 | 268.245 | 0 | 1
6/11 | 09:00:00 | 284.15 | 98833 | 5.1 | 270 | 6.8558 | 2062.8 | 2394 | 269.921 | 0 | 1
6/11 | 10:00:00 | 285.15 | 98841 | 7.2 | 280 | 5.9676 | 2379.6 | 2131.2 | 270.678 | 0 | 1
6/11 | 11:00:00 | 286.15 | 98850 | 7.2 | 250 | 5.5631 | 2700 | 2286 | 271.395 | 0 | 1
6/11 | 12:00:00 | 286.15 | 98850 | 7.7 | 270 | 5.5631 | 2869.2 | 2214 | 271.395 | 0 | 1
6/11 | 13:00:00 | 287.15 | 98858 | 8.2 | 270 | 5.5627 | 3060 | 2764.8 | 272.077 | 0 | 1
6/11 | 14:00:00 | 288.15 | 98867 | 8.7 | 280 | 4.8269 | 2919.6 | 2865.6 | 272.553 | 0 | 1
6/11 | 15:00:00 | 287.15 | 98858 | 8.2 | 280 | 4.8273 | 2613.6 | 2599.2 | 271.608 | 0 | 1
6/11 | 16:00:00 | 287.15 | 98858 | 9.8 | 290 | 5.9666 | 2167.2 | 2300.4 | 272.31 | 0 | 1
6/11 | 17:00:00 | 287.15 | 98858 | 7.2 | 280 | 5.5627 | 1544.4 | 1623.6 | 272.343 | 0 | 1
6/11 | 18:00:00 | 286.15 | 98850 | 7.7 | 280 | 5.5631 | 1065.6 | 1458 | 271.13 | 0 | 1
6/11 | 19:00:00 | 286.15 | 98850 | 6.2 | 270 | 5.1837 | 532.8 | 608.4 | 270.896 | 0 | 1
6/11 | 20:00:00 | 285.15 | 98841 | 4.1 | 270 | 5.5636 | 147.6 | 54 | 270.182 | 0 | 1
6/11 | 21:00:00 | 283.15 | 98824 | 3.6 | 270 | 5.1851 | 0 | 0 | 268.056 | 0 | 1
6/11 | 22:00:00 | 282.15 | 98815 | 4.1 | 260 | 5.1856 | 0 | 0 | 267.11 | 0 | 1
6/11 | 23:00:00 | 281.15 | 98806 | 5.7 | 280 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
6/11 | 24:00:00 | 281.15 | 98806 | 5.7 | 260 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
6/12 | 01:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
6/12 | 02:00:00 | 280.15 | 98798 | 5.7 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
6/12 | 03:00:00 | 280.15 | 98798 | 4.6 | 270 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
6/12 | 04:00:00 | 279.15 | 98789 | 5.7 | 300 | 5.9708 | 0 | 0 | 265.559 | 0 | 1
6/12 | 05:00:00 | 280.15 | 98798 | 4.1 | 280 | 5.9703 | 43.2 | 0 | 266.51 | 0 | 1
6/12 | 06:00:00 | 281.15 | 98806 | 5.1 | 300 | 6.4 | 190.8 | 0 | 267.688 | 0 | 1
6/12 | 07:00:00 | 283.15 | 98824 | 3.6 | 270 | 6.3988 | 954 | 1116 | 268.744 | 0 | 1
6/12 | 08:00:00 | 283.15 | 98824 | 2.1 | 270 | 6.3988 | 1436.4 | 1609.2 | 269.007 | 0 | 1
6/12 | 09:00:00 | 285.15 | 98841 | 2.1 | 360 | 5.9676 | 1951.2 | 1951.2 | 270.678 | 0 | 1
6/12 | 10:00:00 | 286.15 | 98850 | 1.5 | 293 | 5.9671 | 2383.2 | 2131.2 | 271.627 | 0 | 1
6/12 | 11:00:00 | 287.15 | 98858 | 1 | 141 | 5.1833 | 2703.6 | 2296.8 | 272.109 | 0 | 1
6/12 | 12:00:00 | 288.15 | 98867 | 1.5 | 158 | 5.5621 | 2872.8 | 2217.6 | 273.292 | 0 | 1
6/12 | 13:00:00 | 288.15 | 98867 | 2.6 | 90 | 5.5621 | 3063.6 | 2768.4 | 273.025 | 0 | 1
6/12 | 14:00:00 | 289.15 | 98875 | 1.5 | 279 | 5.5617 | 2912.4 | 2840.4 | 273.972 | 0 | 1
6/12 | 15:00:00 | 290.15 | 98883 | 2.1 | 170 | 5.182 | 2613.6 | 2761.2 | 274.683 | 0 | 1
6/12 | 16:00:00 | 290.15 | 98883 | 3.6 | 160 | 5.5612 | 2174.4 | 2433.6 | 274.92 | 0 | 1
6/12 | 17:00:00 | 290.15 | 98883 | 2.6 | 160 | 5.5612 | 1663.2 | 2055.6 | 274.778 | 0 | 1
6/12 | 18:00:00 | 290.15 | 98883 | 3.1 | 150 | 5.5612 | 1083.6 | 1465.2 | 274.778 | 0 | 1
6/12 | 19:00:00 | 289.15 | 98875 | 3.6 | 120 | 5.9656 | 536.4 | 608.4 | 274.206 | 0 | 1
6/12 | 20:00:00 | 288.15 | 98867 | 5.1 | 100 | 6.8534 | 151.2 | 36 | 273.72 | 0 | 1
6/12 | 21:00:00 | 286.15 | 98850 | 5.1 | 110 | 6.8546 | 0 | 0 | 272.087 | 0 | 1
6/12 | 22:00:00 | 285.15 | 98841 | 4.6 | 110 | 6.8552 | 0 | 0 | 271.136 | 0 | 1
6/12 | 23:00:00 | 284.15 | 98833 | 4.6 | 120 | 6.3982 | 0 | 0 | 270.435 | 0 | 1
6/12 | 24:00:00 | 284.15 | 98833 | 4.1 | 130 | 6.3982 | 0 | 0 | 270.435 | 0 | 1
6/13 | 01:00:00 | 283.15 | 98824 | 2.6 | 110 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
6/13 | 02:00:00 | 283.15 | 98824 | 2.1 | 110 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
6/13 | 03:00:00 | 283.15 | 98824 | 0 | 224 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
6/13 | 04:00:00 | 283.15 | 98824 | 1 | 185 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
6/13 | 05:00:00 | 283.15 | 98824 | 0.5 | 162 | 7.3431 | 93.6 | 0 | 269.46 | 0 | 1
6/13 | 06:00:00 | 285.15 | 98841 | 0.5 | 224 | 7.8591 | 230.4 | 0 | 272.069 | 0 | 1
6/13 | 07:00:00 | 286.15 | 98850 | 2.1 | 270 | 7.8584 | 896.4 | 900 | 272.541 | 0 | 1
6/13 | 08:00:00 | 287.15 | 98858 | 3.6 | 270 | 7.8578 | 1429.2 | 1281.6 | 273.493 | 0 | 1
6/13 | 09:00:00 | 287.15 | 98858 | 2.6 | 260 | 7.3406 | 1076.4 | 165.6 | 273.75 | 0 | 1
6/13 | 10:00:00 | 288.15 | 98867 | 2.1 | 240 | 7.3399 | 2372.4 | 1886.4 | 274.218 | 0 | 1
6/13 | 11:00:00 | 290.15 | 98883 | 3.6 | 210 | 6.8523 | 2689.2 | 2260.8 | 275.89 | 0 | 1
6/13 | 12:00:00 | 290.15 | 98883 | 2.6 | 260 | 6.3949 | 2865.6 | 2296.8 | 275.658 | 0 | 1
6/13 | 13:00:00 | 291.15 | 98892 | 3.6 | 260 | 6.3944 | 2880 | 2239.2 | 276.608 | 0 | 1
6/13 | 14:00:00 | 292.15 | 98900 | 4.1 | 240 | 6.3938 | 2908.8 | 2739.6 | 277.286 | 0 | 1
6/13 | 15:00:00 | 291.15 | 98892 | 3.6 | 270 | 6.3944 | 2606.4 | 2721.6 | 276.337 | 0 | 1
6/13 | 16:00:00 | 292.15 | 98900 | 3.6 | 260 | 6.3938 | 2170.8 | 2448 | 277.286 | 0 | 1
6/13 | 17:00:00 | 292.15 | 98900 | 4.1 | 280 | 7.3374 | 1638 | 2012.4 | 277.752 | 0 | 1
6/13 | 18:00:00 | 291.15 | 98892 | 2.6 | 260 | 6.8517 | 1069.2 | 1393.2 | 276.57 | 0 | 1
6/13 | 19:00:00 | 291.15 | 98892 | 3.6 | 310 | 6.8517 | 540 | 604.8 | 276.57 | 0 | 1
6/13 | 20:00:00 | 289.15 | 98875 | 4.6 | 310 | 7.3393 | 151.2 | 39.6 | 274.9 | 0 | 1
6/13 | 21:00:00 | 288.15 | 98867 | 3.6 | 320 | 7.3399 | 0 | 0 | 274.218 | 0 | 1
6/13 | 22:00:00 | 287.15 | 98858 | 4.6 | 310 | 7.3406 | 0 | 0 | 273.393 | 0 | 1
6/13 | 23:00:00 | 286.15 | 98850 | 3.6 | 290 | 7.3412 | 0 | 0 | 272.563 | 0 | 1
6/13 | 24:00:00 | 285.15 | 98841 | 3.6 | 290 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
6/14 | 01:00:00 | 285.15 | 98841 | 3.1 | 270 | 7.3418 | 0 | 0 | 271.729 | 0 | 1
6/14 | 02:00:00 | 284.15 | 98833 | 1.5 | 310 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/14 | 03:00:00 | 284.15 | 98833 | 1 | 350 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/14 | 04:00:00 | 282.15 | 98815 | 2.6 | 250 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
6/14 | 05:00:00 | 282.15 | 98815 | 3.6 | 300 | 6.8571 | 100.8 | 0 | 268.021 | 0 | 1
6/14 | 06:00:00 | 284.15 | 98833 | 1.5 | 209 | 7.3425 | 442.8 | 475.2 | 270.147 | 0 | 1
6/14 | 07:00:00 | 285.15 | 98841 | 3.1 | 270 | 7.8591 | 950.4 | 1256.4 | 271.323 | 0 | 1
6/14 | 08:00:00 | 287.15 | 98858 | 5.7 | 270 | 7.8578 | 1515.6 | 1886.4 | 273.226 | 0 | 1
6/14 | 09:00:00 | 288.15 | 98867 | 6.7 | 260 | 7.3399 | 2059.2 | 2390.4 | 273.95 | 0 | 1
6/14 | 10:00:00 | 289.15 | 98875 | 5.7 | 280 | 6.8529 | 2520 | 2602.8 | 274.67 | 0 | 1
6/14 | 11:00:00 | 290.15 | 98883 | 4.1 | 270 | 7.3387 | 2685.6 | 2196 | 276.121 | 0 | 1
6/14 | 12:00:00 | 289.15 | 98875 | 5.7 | 310 | 6.8529 | 2862 | 2289.6 | 274.939 | 0 | 1
6/14 | 13:00:00 | 290.15 | 98883 | 5.1 | 320 | 7.3387 | 2872.8 | 2228.4 | 276.121 | 0 | 1
6/14 | 14:00:00 | 290.15 | 98883 | 5.7 | 320 | 6.8523 | 2905.2 | 2736 | 275.62 | 0 | 1
6/14 | 15:00:00 | 292.15 | 98900 | 4.6 | 280 | 7.3374 | 2602.8 | 2635.2 | 277.752 | 0 | 1
6/14 | 16:00:00 | 292.15 | 98900 | 4.6 | 270 | 6.8511 | 2048.4 | 1976.4 | 277.792 | 0 | 1
6/14 | 17:00:00 | 292.15 | 98900 | 4.6 | 280 | 6.8511 | 1645.2 | 2109.6 | 277.52 | 0 | 1
6/14 | 18:00:00 | 292.15 | 98900 | 5.1 | 270 | 6.3938 | 1076.4 | 1404 | 277.286 | 0 | 1
6/14 | 19:00:00 | 291.15 | 98892 | 5.1 | 290 | 6.8517 | 543.6 | 612 | 276.57 | 0 | 1
6/14 | 20:00:00 | 290.15 | 98883 | 3.6 | 320 | 6.3949 | 154.8 | 50.4 | 275.388 | 0 | 1
6/14 | 21:00:00 | 288.15 | 98867 | 2.6 | 330 | 6.8534 | 0 | 0 | 273.988 | 0 | 1
6/14 | 22:00:00 | 287.15 | 98858 | 3.6 | 330 | 6.3966 | 0 | 0 | 272.808 | 0 | 1
6/14 | 23:00:00 | 286.15 | 98850 | 2.6 | 350 | 7.3412 | 0 | 0 | 272.563 | 0 | 1
6/14 | 24:00:00 | 285.15 | 98841 | 3.1 | 310 | 7.3418 | 0 | 0 | 271.729 | 0 | 1
6/15 | 01:00:00 | 285.15 | 98841 | 3.6 | 230 | 7.3418 | 0 | 0 | 271.363 | 0 | 1
6/15 | 02:00:00 | 284.15 | 98833 | 2.1 | 310 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
6/15 | 03:00:00 | 284.15 | 98833 | 1.5 | 200 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
6/15 | 04:00:00 | 284.15 | 98833 | 1 | 125 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
6/15 | 05:00:00 | 284.15 | 98833 | 2.1 | 220 | 7.8598 | 39.6 | 0 | 271.225 | 0 | 1
6/15 | 06:00:00 | 284.15 | 98833 | 0 | 176 | 8.4095 | 442.8 | 687.6 | 270.595 | 0 | 1
6/15 | 07:00:00 | 285.15 | 98841 | 1.5 | 300 | 8.4088 | 950.4 | 1242 | 271.547 | 0 | 1
6/15 | 08:00:00 | 286.15 | 98850 | 2.1 | 310 | 8.408 | 1515.6 | 2005.2 | 272.499 | 0 | 1
6/15 | 09:00:00 | 287.15 | 98858 | 3.6 | 320 | 7.8578 | 2059.2 | 2386.8 | 273.226 | 0 | 1
6/15 | 10:00:00 | 289.15 | 98875 | 2.1 | 360 | 7.8564 | 2512.8 | 2595.6 | 275.129 | 0 | 1
6/15 | 11:00:00 | 290.15 | 98883 | 3.1 | 100 | 7.8557 | 2847.6 | 2790 | 276.08 | 0 | 1
6/15 | 12:00:00 | 290.15 | 98883 | 2.6 | 90 | 7.3387 | 3031.2 | 2768.4 | 275.851 | 0 | 1
6/15 | 13:00:00 | 285.15 | 98841 | 4.6 | 270 | 7.8591 | 2872.8 | 2221.2 | 271.588 | 0 | 1
6/15 | 14:00:00 | 286.15 | 98850 | 1.5 | 29 | 8.408 | 2728.8 | 2196 | 272.766 | 0 | 1
6/15 | 15:00:00 | 288.15 | 98867 | 3.1 | 60 | 7.857 | 2599.2 | 2631.6 | 274.177 | 0 | 1
6/15 | 16:00:00 | 289.15 | 98875 | 1.5 | 170 | 6.8529 | 2174.4 | 2448 | 274.67 | 0 | 1
6/15 | 17:00:00 | 288.15 | 98867 | 2.1 | 50 | 6.8534 | 1648.8 | 2026.8 | 273.72 | 0 | 1
6/15 | 18:00:00 | 287.15 | 98858 | 3.6 | 70 | 7.8578 | 1076.4 | 1389.6 | 273.226 | 0 | 1
6/15 | 19:00:00 | 286.15 | 98850 | 3.6 | 20 | 7.3412 | 514.8 | 489.6 | 272.314 | 0 | 1
6/15 | 20:00:00 | 285.15 | 98841 | 1.5 | 249 | 7.8591 | 147.6 | 7.2 | 271.588 | 0 | 1
6/15 | 21:00:00 | 285.15 | 98841 | 3.1 | 30 | 7.8591 | 3.6 | 0 | 271.323 | 0 | 1
6/15 | 22:00:00 | 284.15 | 98833 | 3.1 | 360 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
6/15 | 23:00:00 | 284.15 | 98833 | 2.6 | 340 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
6/15 | 24:00:00 | 284.15 | 98833 | 3.1 | 10 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
6/16 | 01:00:00 | 284.15 | 98833 | 2.6 | 350 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
6/16 | 02:00:00 | 284.15 | 98833 | 3.1 | 330 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
6/16 | 03:00:00 | 283.15 | 98824 | 2.6 | 330 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
6/16 | 04:00:00 | 281.15 | 98806 | 2.6 | 300 | 6.8577 | 0 | 0 | 266.644 | 0 | 1
6/16 | 05:00:00 | 283.15 | 98824 | 2.6 | 330 | 7.3431 | 100.8 | 0 | 268.766 | 0 | 1
6/16 | 06:00:00 | 283.15 | 98824 | 1.5 | 320 | 7.3431 | 450 | 500.4 | 268.766 | 0 | 1
6/16 | 07:00:00 | 284.15 | 98833 | 2.1 | 10 | 7.8598 | 950.4 | 1299.6 | 270.371 | 0 | 1
6/16 | 08:00:00 | 286.15 | 98850 | 1.5 | 108 | 7.8584 | 1429.2 | 1580.4 | 272.541 | 0 | 1
6/16 | 09:00:00 | 286.15 | 98850 | 1 | 120 | 7.8584 | 1940.4 | 1911.6 | 272.541 | 0 | 1
6/16 | 10:00:00 | 288.15 | 98867 | 0.5 | 64 | 7.857 | 2368.8 | 2030.4 | 274.446 | 0 | 1
6/16 | 11:00:00 | 290.15 | 98883 | 1 | 165 | 7.3387 | 2851.2 | 2718 | 275.851 | 0 | 1
6/16 | 12:00:00 | 289.15 | 98875 | 0.5 | 202 | 7.3393 | 3031.2 | 2844 | 274.9 | 0 | 1
6/16 | 13:00:00 | 290.15 | 98883 | 2.6 | 130 | 7.3387 | 3052.8 | 2851.2 | 275.851 | 0 | 1
6/16 | 14:00:00 | 290.15 | 98883 | 1.5 | 213 | 6.8523 | 2912.4 | 2815.2 | 275.62 | 0 | 1
6/16 | 15:00:00 | 291.15 | 98892 | 2.1 | 170 | 7.338 | 2606.4 | 2710.8 | 276.802 | 0 | 1
6/16 | 16:00:00 | 292.15 | 98900 | 3.1 | 160 | 6.8511 | 2178 | 2448 | 277.52 | 0 | 1
6/16 | 17:00:00 | 291.15 | 98892 | 3.1 | 160 | 6.8517 | 1652.4 | 2034 | 276.57 | 0 | 1
6/16 | 18:00:00 | 292.15 | 98900 | 3.6 | 170 | 6.8511 | 1022.4 | 1159.2 | 277.792 | 0 | 1
6/16 | 19:00:00 | 292.15 | 98900 | 4.6 | 160 | 6.8511 | 550.8 | 622.8 | 277.52 | 0 | 1
6/16 | 20:00:00 | 290.15 | 98883 | 2.6 | 160 | 7.3387 | 158.4 | 54 | 275.851 | 0 | 1
6/16 | 21:00:00 | 290.15 | 98883 | 2.6 | 140 | 7.8557 | 3.6 | 0 | 276.08 | 0 | 1
6/16 | 22:00:00 | 287.15 | 98858 | 3.1 | 120 | 8.4073 | 0 | 0 | 273.451 | 0 | 1
6/16 | 23:00:00 | 287.15 | 98858 | 4.1 | 130 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
6/16 | 24:00:00 | 286.15 | 98850 | 2.6 | 140 | 8.408 | 0 | 0 | 272.766 | 0 | 1
6/17 | 01:00:00 | 286.15 | 98850 | 2.6 | 150 | 8.408 | 0 | 0 | 273.248 | 0 | 1
6/17 | 02:00:00 | 286.15 | 98850 | 2.1 | 160 | 7.8584 | 0 | 0 | 272.909 | 0 | 1
6/17 | 03:00:00 | 285.15 | 98841 | 2.1 | 170 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
6/17 | 04:00:00 | 285.15 | 98841 | 2.1 | 170 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
6/17 | 05:00:00 | 285.15 | 98841 | 2.1 | 190 | 7.8591 | 93.6 | 0 | 271.588 | 0 | 1
6/17 | 06:00:00 | 285.15 | 98841 | 3.1 | 150 | 8.4088 | 442.8 | 568.8 | 271.547 | 0 | 1
6/17 | 07:00:00 | 286.15 | 98850 | 3.6 | 190 | 8.408 | 950.4 | 1242 | 272.499 | 0 | 1
6/17 | 08:00:00 | 286.15 | 98850 | 5.1 | 180 | 7.8584 | 1515.6 | 1965.6 | 272.274 | 0 | 1
6/17 | 09:00:00 | 286.15 | 98850 | 5.7 | 180 | 7.3412 | 1944 | 2059.2 | 272.314 | 0 | 1
6/17 | 10:00:00 | 286.15 | 98850 | 6.7 | 190 | 7.3412 | 2372.4 | 1882.8 | 272.314 | 0 | 1
6/17 | 11:00:00 | 286.15 | 98850 | 5.7 | 210 | 7.8584 | 1486.8 | 212.4 | 273.023 | 0 | 1
6/17 | 12:00:00 | 285.15 | 98841 | 4.1 | 180 | 8.4088 | 1580.4 | 158.4 | 272.294 | 0 | 1
6/17 | 13:00:00 | 285.15 | 98841 | 7.2 | 180 | 7.8591 | 1594.8 | 68.4 | 272.069 | 0 | 1
6/17 | 14:00:00 | 285.15 | 98841 | 7.2 | 190 | 8.4088 | 1515.6 | 158.4 | 272.294 | 0 | 1
6/17 | 15:00:00 | 286.15 | 98850 | 5.7 | 190 | 8.9918 | 1357.2 | 108 | 273.473 | 0 | 1
6/17 | 16:00:00 | 287.15 | 98858 | 6.7 | 210 | 8.991 | 1134 | 100.8 | 274.428 | 0 | 1
6/17 | 17:00:00 | 287.15 | 98858 | 7.2 | 210 | 8.991 | 860.4 | 104.4 | 274.428 | 0 | 1
6/17 | 18:00:00 | 286.15 | 98850 | 7.7 | 270 | 8.9918 | 1018.8 | 1130.4 | 272.99 | 0 | 1
6/17 | 19:00:00 | 286.15 | 98850 | 7.7 | 270 | 7.8584 | 554.4 | 619.2 | 272.274 | 0 | 1
6/17 | 20:00:00 | 286.15 | 98850 | 5.7 | 270 | 7.8584 | 162 | 54 | 272.274 | 0 | 1
6/17 | 21:00:00 | 285.15 | 98841 | 6.7 | 260 | 7.8591 | 3.6 | 0 | 271.323 | 0 | 1
6/17 | 22:00:00 | 285.15 | 98841 | 5.1 | 260 | 7.3418 | 0 | 0 | 271.363 | 0 | 1
6/17 | 23:00:00 | 284.15 | 98833 | 3.1 | 230 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
6/17 | 24:00:00 | 283.15 | 98824 | 3.1 | 250 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
6/18 | 01:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
6/18 | 02:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
6/18 | 03:00:00 | 283.15 | 98824 | 4.1 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
6/18 | 04:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
6/18 | 05:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.3994 | 93.6 | 0 | 268.057 | 0 | 1
6/18 | 06:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.3988 | 421.2 | 378 | 269.007 | 0 | 1
6/18 | 07:00:00 | 284.15 | 98833 | 5.1 | 250 | 6.3982 | 900 | 1044 | 269.957 | 0 | 1
6/18 | 08:00:00 | 284.15 | 98833 | 5.7 | 240 | 6.3982 | 1436.4 | 1540.8 | 269.957 | 0 | 1
6/18 | 09:00:00 | 284.15 | 98833 | 5.1 | 240 | 6.3982 | 1947.6 | 1936.8 | 269.957 | 0 | 1
6/18 | 10:00:00 | 285.15 | 98841 | 7.2 | 250 | 6.3977 | 2379.6 | 2070 | 270.907 | 0 | 1
6/18 | 11:00:00 | 286.15 | 98850 | 6.2 | 240 | 5.9671 | 2700 | 2271.6 | 271.627 | 0 | 1
6/18 | 12:00:00 | 286.15 | 98850 | 7.7 | 250 | 6.3971 | 2869.2 | 2296.8 | 271.858 | 0 | 1
6/18 | 13:00:00 | 287.15 | 98858 | 8.7 | 250 | 5.9666 | 2890.8 | 2311.2 | 272.576 | 0 | 1
6/18 | 14:00:00 | 289.15 | 98875 | 8.2 | 250 | 5.9656 | 2754 | 2282.4 | 274.475 | 0 | 1
6/18 | 15:00:00 | 288.15 | 98867 | 8.7 | 250 | 5.9661 | 2473.2 | 2232 | 273.525 | 0 | 1
6/18 | 16:00:00 | 289.15 | 98875 | 7.2 | 240 | 6.3955 | 2062.8 | 1987.2 | 274.708 | 0 | 1
6/18 | 17:00:00 | 288.15 | 98867 | 8.2 | 250 | 5.9661 | 1569.6 | 1638 | 273.525 | 0 | 1
6/18 | 18:00:00 | 287.15 | 98858 | 7.2 | 250 | 6.3966 | 1029.6 | 1213.2 | 272.808 | 0 | 1
6/18 | 19:00:00 | 287.15 | 98858 | 7.7 | 250 | 6.3966 | 525.6 | 507.6 | 272.808 | 0 | 1
6/18 | 20:00:00 | 286.15 | 98850 | 9.3 | 250 | 6.3971 | 154.8 | 18 | 271.858 | 0 | 1
6/18 | 21:00:00 | 284.15 | 98833 | 8.7 | 280 | 6.3982 | 3.6 | 0 | 269.693 | 0 | 1
6/18 | 22:00:00 | 284.15 | 98833 | 5.7 | 260 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
6/18 | 23:00:00 | 283.15 | 98824 | 5.1 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
6/18 | 24:00:00 | 283.15 | 98824 | 4.6 | 266 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
6/19 | 01:00:00 | 284.15 | 98833 | 6.7 | 260 | 6.3982 | 0 | 0 | 269.957 | 0 | 1
6/19 | 02:00:00 | 283.15 | 98824 | 8.2 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
6/19 | 03:00:00 | 283.15 | 98824 | 7.2 | 260 | 6.3988 | 0 | 0 | 269.483 | 0 | 1
6/19 | 04:00:00 | 283.15 | 98824 | 7.7 | 280 | 6.3988 | 0 | 0 | 269.483 | 0 | 1
6/19 | 05:00:00 | 283.15 | 98824 | 7.2 | 280 | 6.8564 | 54 | 0 | 269.71 | 0 | 1
6/19 | 06:00:00 | 283.15 | 98824 | 7.2 | 280 | 6.8564 | 417.6 | 460.8 | 269.234 | 0 | 1
6/19 | 07:00:00 | 283.15 | 98824 | 5.7 | 270 | 6.8564 | 896.4 | 1033.2 | 269.234 | 0 | 1
6/19 | 08:00:00 | 284.15 | 98833 | 7.7 | 270 | 6.3982 | 1432.8 | 1537.2 | 269.957 | 0 | 1
6/19 | 09:00:00 | 285.15 | 98841 | 9.8 | 280 | 6.3977 | 1944 | 1933.2 | 270.907 | 0 | 1
6/19 | 10:00:00 | 286.15 | 98850 | 8.7 | 280 | 6.3971 | 2379.6 | 2066.4 | 271.858 | 0 | 1
6/19 | 11:00:00 | 287.15 | 98858 | 11.3 | 270 | 6.3966 | 2692.8 | 2260.8 | 272.808 | 0 | 1
6/19 | 12:00:00 | 288.15 | 98867 | 11.8 | 270 | 6.8534 | 2865.6 | 2289.6 | 273.988 | 0 | 1
6/19 | 13:00:00 | 286.15 | 98850 | 10.3 | 270 | 8.9918 | 2865.6 | 2271.6 | 272.99 | 0 | 1
6/19 | 14:00:00 | 287.15 | 98858 | 11.3 | 280 | 10.2686 | 2721.6 | 2246.4 | 274.389 | 0 | 1
6/19 | 15:00:00 | 288.15 | 98867 | 11.3 | 280 | 6.8534 | 2466 | 2214 | 273.988 | 0 | 1
6/19 | 16:00:00 | 287.15 | 98858 | 10.8 | 280 | 6.3966 | 2062.8 | 1983.6 | 272.808 | 0 | 1
6/19 | 17:00:00 | 286.15 | 98850 | 11.8 | 280 | 6.8546 | 1566 | 1681.2 | 272.087 | 0 | 1
6/19 | 18:00:00 | 286.15 | 98850 | 11.8 | 280 | 6.3971 | 1094.4 | 1468.8 | 271.592 | 0 | 1
6/19 | 19:00:00 | 286.15 | 98850 | 11.8 | 280 | 5.9671 | 561.6 | 633.6 | 271.361 | 0 | 1
6/19 | 20:00:00 | 285.15 | 98841 | 8.2 | 270 | 5.9676 | 165.6 | 61.2 | 270.413 | 0 | 1
6/19 | 21:00:00 | 284.15 | 98833 | 7.2 | 290 | 6.3982 | 7.2 | 0 | 269.693 | 0 | 1
6/19 | 22:00:00 | 284.15 | 98833 | 6.7 | 280 | 5.9681 | 0 | 0 | 269.465 | 0 | 1
6/19 | 23:00:00 | 284.15 | 98833 | 6.7 | 280 | 5.9681 | 0 | 0 | 269.465 | 0 | 1
6/19 | 24:00:00 | 283.15 | 98824 | 4.1 | 300 | 5.9687 | 0 | 0 | 268.088 | 0 | 1
6/20 | 01:00:00 | 283.15 | 98824 | 5.7 | 300 | 6.3988 | 0 | 0 | 268.744 | 0 | 1
6/20 | 02:00:00 | 283.15 | 98824 | 5.1 | 290 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
6/20 | 03:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
6/20 | 04:00:00 | 282.15 | 98815 | 5.1 | 270 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
6/20 | 05:00:00 | 283.15 | 98824 | 4.6 | 280 | 7.3431 | 93.6 | 0 | 269.46 | 0 | 1
6/20 | 06:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.3431 | 417.6 | 370.8 | 269.46 | 0 | 1
6/20 | 07:00:00 | 284.15 | 98833 | 6.2 | 260 | 7.3425 | 892.8 | 1029.6 | 270.411 | 0 | 1
6/20 | 08:00:00 | 285.15 | 98841 | 5.7 | 280 | 7.3418 | 1429.2 | 1519.2 | 271.363 | 0 | 1
6/20 | 09:00:00 | 285.15 | 98841 | 6.7 | 270 | 7.3418 | 1936.8 | 1900.8 | 271.363 | 0 | 1
6/20 | 10:00:00 | 286.15 | 98850 | 7.2 | 270 | 7.8584 | 2509.2 | 2480.4 | 272.274 | 0 | 1
6/20 | 11:00:00 | 287.15 | 98858 | 8.7 | 280 | 7.3406 | 2685.6 | 2188.8 | 273.266 | 0 | 1
6/20 | 12:00:00 | 286.15 | 98850 | 5.7 | 270 | 8.408 | 2851.2 | 2271.6 | 272.766 | 0 | 1
6/20 | 13:00:00 | 289.15 | 98875 | 8.2 | 280 | 7.8564 | 2876.4 | 2282.4 | 275.398 | 0 | 1
6/20 | 14:00:00 | 288.15 | 98867 | 8.2 | 280 | 7.3399 | 2743.2 | 2260.8 | 274.218 | 0 | 1
6/20 | 15:00:00 | 289.15 | 98875 | 7.7 | 290 | 7.3393 | 2466 | 2210.4 | 275.169 | 0 | 1
6/20 | 16:00:00 | 288.15 | 98867 | 7.7 | 290 | 7.3399 | 2059.2 | 2109.6 | 274.218 | 0 | 1
6/20 | 17:00:00 | 288.15 | 98867 | 8.7 | 290 | 6.8534 | 1663.2 | 2124 | 273.72 | 0 | 1
6/20 | 18:00:00 | 287.15 | 98858 | 8.7 | 280 | 7.3406 | 1094.4 | 1407.6 | 272.999 | 0 | 1
6/20 | 19:00:00 | 286.15 | 98850 | 8.2 | 280 | 7.3412 | 561.6 | 630 | 272.048 | 0 | 1
6/20 | 20:00:00 | 286.15 | 98850 | 8.2 | 280 | 7.3412 | 165.6 | 64.8 | 272.048 | 0 | 1
6/20 | 21:00:00 | 285.15 | 98841 | 5.7 | 280 | 7.3418 | 7.2 | 0 | 271.097 | 0 | 1
6/20 | 22:00:00 | 284.15 | 98833 | 5.7 | 280 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/20 | 23:00:00 | 284.15 | 98833 | 5.7 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/20 | 24:00:00 | 284.15 | 98833 | 5.1 | 290 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
6/21 | 01:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
6/21 | 02:00:00 | 284.15 | 98833 | 5.7 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/21 | 03:00:00 | 284.15 | 98833 | 6.2 | 280 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/21 | 04:00:00 | 284.15 | 98833 | 4.6 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/21 | 05:00:00 | 283.15 | 98824 | 4.1 | 290 | 7.3431 | 97.2 | 0 | 269.196 | 0 | 1
6/21 | 06:00:00 | 283.15 | 98824 | 4.6 | 280 | 7.3431 | 439.2 | 468 | 269.196 | 0 | 1
6/21 | 07:00:00 | 285.15 | 98841 | 6.2 | 300 | 7.3418 | 946.8 | 1252.8 | 271.097 | 0 | 1
6/21 | 08:00:00 | 286.15 | 98850 | 4.6 | 310 | 7.3412 | 1512 | 1965.6 | 272.048 | 0 | 1
6/21 | 09:00:00 | 287.15 | 98858 | 3.6 | 320 | 6.854 | 1940.4 | 2062.8 | 273.038 | 0 | 1
6/21 | 10:00:00 | 288.15 | 98867 | 3.6 | 320 | 6.8534 | 2372.4 | 2059.2 | 273.988 | 0 | 1
6/21 | 11:00:00 | 289.15 | 98875 | 3.1 | 187 | 6.8529 | 2689.2 | 2257.2 | 274.939 | 0 | 1
6/21 | 12:00:00 | 290.15 | 98883 | 3.1 | 290 | 6.3949 | 2869.2 | 2293.2 | 275.658 | 0 | 1
6/21 | 13:00:00 | 290.15 | 98883 | 3.1 | 270 | 6.8523 | 2883.6 | 2293.2 | 275.89 | 0 | 1
6/21 | 14:00:00 | 290.15 | 98883 | 3.6 | 280 | 6.8523 | 2750.4 | 2268 | 275.89 | 0 | 1
6/21 | 15:00:00 | 290.15 | 98883 | 3.1 | 280 | 7.3387 | 2466 | 2149.2 | 276.121 | 0 | 1
6/21 | 16:00:00 | 290.15 | 98883 | 4.1 | 270 | 7.3387 | 2188.8 | 2448 | 275.851 | 0 | 1
6/21 | 17:00:00 | 290.15 | 98883 | 5.7 | 290 | 7.8557 | 1659.6 | 2019.6 | 276.08 | 0 | 1
6/21 | 18:00:00 | 290.15 | 98883 | 6.7 | 280 | 7.8557 | 1094.4 | 1404 | 276.08 | 0 | 1
6/21 | 19:00:00 | 289.15 | 98875 | 5.7 | 280 | 7.8564 | 561.6 | 630 | 275.129 | 0 | 1
6/21 | 20:00:00 | 288.15 | 98867 | 4.1 | 280 | 7.857 | 169.2 | 64.8 | 274.177 | 0 | 1
6/21 | 21:00:00 | 286.15 | 98850 | 4.1 | 280 | 7.8584 | 7.2 | 0 | 272.274 | 0 | 1
6/21 | 22:00:00 | 286.15 | 98850 | 3.6 | 270 | 7.8584 | 0 | 0 | 272.541 | 0 | 1
6/21 | 23:00:00 | 286.15 | 98850 | 3.1 | 290 | 7.8584 | 0 | 0 | 273.023 | 0 | 1
6/21 | 24:00:00 | 285.15 | 98841 | 4.1 | 280 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
6/22 | 01:00:00 | 285.15 | 98841 | 3.1 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
6/22 | 02:00:00 | 285.15 | 98841 | 3.6 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
6/22 | 03:00:00 | 285.15 | 98841 | 3.1 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
6/22 | 04:00:00 | 285.15 | 98841 | 4.1 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
6/22 | 05:00:00 | 285.15 | 98841 | 4.1 | 270 | 8.4088 | 50.4 | 0 | 272.294 | 0 | 1
6/22 | 06:00:00 | 285.15 | 98841 | 4.1 | 260 | 8.4088 | 230.4 | 0 | 272.294 | 0 | 1
6/22 | 07:00:00 | 286.15 | 98850 | 4.1 | 270 | 8.9918 | 493.2 | 28.8 | 273.473 | 0 | 1
6/22 | 08:00:00 | 287.15 | 98858 | 4.1 | 290 | 9.6108 | 784.8 | 72 | 274.652 | 0 | 1
6/22 | 09:00:00 | 289.15 | 98875 | 6.2 | 280 | 9.6091 | 1065.6 | 241.2 | 276.565 | 0 | 1
6/22 | 10:00:00 | 290.15 | 98883 | 4.6 | 270 | 9.6084 | 2354.4 | 1836 | 277.031 | 0 | 1
6/22 | 11:00:00 | 291.15 | 98892 | 4.6 | 280 | 10.265 | 2664 | 2235.6 | 278.211 | 0 | 1
6/22 | 12:00:00 | 293.15 | 98908 | 5.7 | 290 | 10.2634 | 2836.8 | 2264.4 | 280.122 | 0 | 1
6/22 | 13:00:00 | 293.15 | 98908 | 3.6 | 300 | 10.2634 | 2858.4 | 2264.4 | 280.122 | 0 | 1
6/22 | 14:00:00 | 294.15 | 98916 | 5.1 | 310 | 10.2625 | 2725.2 | 2246.4 | 281.078 | 0 | 1
6/22 | 15:00:00 | 294.15 | 98916 | 4.6 | 310 | 10.96 | 2444.4 | 2084.4 | 281.303 | 0 | 1
6/22 | 16:00:00 | 294.15 | 98916 | 4.6 | 280 | 10.96 | 2170.8 | 2458.8 | 281.028 | 0 | 1
6/22 | 17:00:00 | 294.15 | 98916 | 2.6 | 300 | 10.96 | 1648.8 | 2106 | 281.028 | 0 | 1
6/22 | 18:00:00 | 291.15 | 98892 | 4.1 | 330 | 11.7026 | 1087.2 | 1357.2 | 278.384 | 0 | 1
6/22 | 19:00:00 | 290.15 | 98883 | 2.6 | 310 | 10.9637 | 529.2 | 594 | 277.478 | 0 | 1
6/22 | 20:00:00 | 289.15 | 98875 | 3.6 | 290 | 10.9646 | 158.4 | 14.4 | 276.522 | 0 | 1
6/22 | 21:00:00 | 290.15 | 98883 | 4.1 | 300 | 11.7037 | 7.2 | 0 | 277.428 | 0 | 1
6/22 | 22:00:00 | 290.15 | 98883 | 4.1 | 300 | 10.9637 | 0 | 0 | 277.207 | 0 | 1
6/22 | 23:00:00 | 289.15 | 98875 | 4.6 | 300 | 10.9646 | 0 | 0 | 276.251 | 0 | 1
6/22 | 24:00:00 | 289.15 | 98875 | 3.6 | 300 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
6/23 | 01:00:00 | 289.15 | 98875 | 3.6 | 290 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
6/23 | 02:00:00 | 288.15 | 98867 | 2.1 | 310 | 10.2677 | 0 | 0 | 275.344 | 0 | 1
6/23 | 03:00:00 | 288.15 | 98867 | 3.1 | 290 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
6/23 | 04:00:00 | 288.15 | 98867 | 2.1 | 310 | 10.2677 | 0 | 0 | 275.344 | 0 | 1
6/23 | 05:00:00 | 287.15 | 98858 | 2.6 | 290 | 10.2686 | 50.4 | 0 | 274.874 | 0 | 1
6/23 | 06:00:00 | 288.15 | 98867 | 1 | 129 | 10.9655 | 226.8 | 0 | 276.053 | 0 | 1
6/23 | 07:00:00 | 289.15 | 98875 | 1 | 199 | 10.9646 | 489.6 | 25.2 | 277.011 | 0 | 1
6/23 | 08:00:00 | 290.15 | 98883 | 1 | 212 | 11.7037 | 781.2 | 72 | 278.191 | 0 | 1
6/23 | 09:00:00 | 291.15 | 98892 | 1.5 | 322 | 11.7026 | 1062 | 93.6 | 279.15 | 0 | 1
6/23 | 10:00:00 | 291.15 | 98892 | 1.5 | 49 | 12.4871 | 1296 | 316.8 | 279.371 | 0 | 1
6/23 | 11:00:00 | 292.15 | 98900 | 1.5 | 201 | 12.4861 | 2649.6 | 2109.6 | 279.836 | 0 | 1
6/23 | 12:00:00 | 294.15 | 98916 | 1.5 | 205 | 12.484 | 2826 | 2314.8 | 281.751 | 0 | 1
6/23 | 13:00:00 | 294.15 | 98916 | 2.6 | 70 | 12.484 | 2847.6 | 2314.8 | 281.751 | 0 | 1
6/23 | 14:00:00 | 296.15 | 98932 | 3.1 | 100 | 11.6978 | 2718 | 2278.8 | 283.442 | 0 | 1
6/23 | 15:00:00 | 295.15 | 98924 | 6.2 | 90 | 11.6988 | 2440.8 | 2001.6 | 282.485 | 0 | 1
6/23 | 16:00:00 | 295.15 | 98924 | 5.7 | 90 | 11.6988 | 2044.8 | 1976.4 | 282.485 | 0 | 1
6/23 | 17:00:00 | 294.15 | 98916 | 5.7 | 80 | 11.6997 | 1555.2 | 1666.8 | 281.528 | 0 | 1
6/23 | 18:00:00 | 293.15 | 98908 | 4.1 | 70 | 11.7007 | 1087.2 | 1515.6 | 280.296 | 0 | 1
6/23 | 19:00:00 | 292.15 | 98900 | 3.1 | 80 | 10.9618 | 561.6 | 745.2 | 279.117 | 0 | 1
6/23 | 20:00:00 | 292.15 | 98900 | 3.6 | 80 | 10.2642 | 169.2 | 86.4 | 278.893 | 0 | 1
6/23 | 21:00:00 | 290.15 | 98883 | 3.6 | 100 | 9.6084 | 7.2 | 0 | 276.76 | 0 | 1
6/23 | 22:00:00 | 288.15 | 98867 | 2.6 | 80 | 8.9902 | 0 | 0 | 275.269 | 0 | 1
6/23 | 23:00:00 | 287.15 | 98858 | 4.1 | 90 | 7.8578 | 0 | 0 | 273.743 | 0 | 1
6/23 | 24:00:00 | 285.15 | 98841 | 3.1 | 70 | 6.8552 | 0 | 0 | 271.384 | 0 | 1
6/24 | 01:00:00 | 284.15 | 98833 | 2.6 | 70 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
6/24 | 02:00:00 | 283.15 | 98824 | 2.6 | 70 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
6/24 | 03:00:00 | 283.15 | 98824 | 2.6 | 60 | 7.3431 | 0 | 0 | 268.766 | 0 | 1
6/24 | 04:00:00 | 282.15 | 98815 | 2.1 | 50 | 7.3438 | 0 | 0 | 267.817 | 0 | 1
6/24 | 05:00:00 | 283.15 | 98824 | 2.1 | 70 | 7.3431 | 39.6 | 0 | 270.046 | 0 | 1
6/24 | 06:00:00 | 283.15 | 98824 | 2.1 | 60 | 7.8605 | 136.8 | 0 | 270.27 | 0 | 1
6/24 | 07:00:00 | 283.15 | 98824 | 2.1 | 60 | 7.8605 | 298.8 | 0 | 270.27 | 0 | 1
6/24 | 08:00:00 | 283.15 | 98824 | 2.1 | 80 | 7.8605 | 784.8 | 216 | 270.161 | 0 | 1
6/24 | 09:00:00 | 285.15 | 98841 | 3.6 | 80 | 8.4088 | 1926 | 1724.4 | 271.813 | 0 | 1
6/24 | 10:00:00 | 288.15 | 98867 | 3.6 | 90 | 8.4065 | 2358 | 2106 | 274.672 | 0 | 1
6/24 | 11:00:00 | 290.15 | 98883 | 3.6 | 70 | 8.4052 | 2671.2 | 2242.8 | 276.579 | 0 | 1
6/24 | 12:00:00 | 291.15 | 98892 | 5.1 | 100 | 8.4044 | 2847.6 | 2271.6 | 277.532 | 0 | 1
6/24 | 13:00:00 | 292.15 | 98900 | 6.2 | 90 | 8.4037 | 2872.8 | 2275.2 | 278.485 | 0 | 1
6/24 | 14:00:00 | 292.15 | 98900 | 6.2 | 80 | 8.4037 | 2739.6 | 2253.6 | 278.485 | 0 | 1
6/24 | 15:00:00 | 293.15 | 98908 | 6.2 | 90 | 8.403 | 2462.4 | 2124 | 279.439 | 0 | 1
6/24 | 16:00:00 | 292.15 | 98900 | 6.7 | 80 | 8.4037 | 2185.2 | 2444.4 | 278.213 | 0 | 1
6/24 | 17:00:00 | 292.15 | 98900 | 6.2 | 80 | 8.4037 | 1663.2 | 2152.8 | 278.213 | 0 | 1
6/24 | 18:00:00 | 291.15 | 98892 | 5.7 | 90 | 8.9879 | 1098 | 1386 | 277.488 | 0 | 1
6/24 | 19:00:00 | 290.15 | 98883 | 6.7 | 90 | 8.9887 | 532.8 | 734.4 | 276.806 | 0 | 1
6/24 | 20:00:00 | 287.15 | 98858 | 6.2 | 90 | 8.991 | 90 | 0 | 274.428 | 0 | 1
6/24 | 21:00:00 | 286.15 | 98850 | 6.2 | 90 | 8.408 | 3.6 | 0 | 273.248 | 0 | 1
6/24 | 22:00:00 | 286.15 | 98850 | 4.6 | 80 | 8.408 | 0 | 0 | 273.248 | 0 | 1
6/24 | 23:00:00 | 285.15 | 98841 | 5.1 | 90 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
6/24 | 24:00:00 | 285.15 | 98841 | 3.6 | 80 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
6/25 | 01:00:00 | 285.15 | 98841 | 4.1 | 80 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
6/25 | 02:00:00 | 285.15 | 98841 | 3.1 | 80 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
6/25 | 03:00:00 | 285.15 | 98841 | 2.6 | 50 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
6/25 | 04:00:00 | 284.15 | 98833 | 4.1 | 60 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
6/25 | 05:00:00 | 284.15 | 98833 | 3.6 | 70 | 8.4095 | 50.4 | 0 | 271.339 | 0 | 1
6/25 | 06:00:00 | 284.15 | 98833 | 4.1 | 60 | 7.8598 | 406.8 | 439.2 | 270.636 | 0 | 1
6/25 | 07:00:00 | 284.15 | 98833 | 5.1 | 50 | 7.8598 | 489.6 | 39.6 | 271.115 | 0 | 1
6/25 | 08:00:00 | 284.15 | 98833 | 3.6 | 50 | 7.8598 | 784.8 | 54 | 271.115 | 0 | 1
6/25 | 09:00:00 | 286.15 | 98850 | 4.6 | 50 | 8.408 | 1065.6 | 244.8 | 273.248 | 0 | 1
6/25 | 10:00:00 | 288.15 | 98867 | 4.6 | 40 | 8.9902 | 2350.8 | 1839.6 | 274.898 | 0 | 1
6/25 | 11:00:00 | 290.15 | 98883 | 5.7 | 50 | 8.4052 | 2833.2 | 2707.2 | 276.308 | 0 | 1
6/25 | 12:00:00 | 291.15 | 98892 | 6.2 | 50 | 8.9879 | 3016.8 | 2829.6 | 277.488 | 0 | 1
6/25 | 13:00:00 | 293.15 | 98908 | 6.2 | 70 | 9.6059 | 3034.8 | 2833.2 | 279.622 | 0 | 1
6/25 | 14:00:00 | 293.15 | 98908 | 5.7 | 90 | 8.9864 | 2901.6 | 2800.8 | 279.394 | 0 | 1
6/25 | 15:00:00 | 293.15 | 98908 | 6.2 | 90 | 8.9864 | 2606.4 | 2685.6 | 279.394 | 0 | 1
6/25 | 16:00:00 | 292.15 | 98900 | 6.2 | 80 | 9.6067 | 2178 | 2440.8 | 278.668 | 0 | 1
6/25 | 17:00:00 | 293.15 | 98908 | 7.2 | 90 | 7.8537 | 1666.8 | 2019.6 | 278.935 | 0 | 1
6/25 | 18:00:00 | 293.15 | 98908 | 6.7 | 80 | 7.8537 | 1101.6 | 1458 | 278.935 | 0 | 1
6/25 | 19:00:00 | 292.15 | 98900 | 5.7 | 80 | 6.8511 | 572.4 | 658.8 | 277.377 | 0 | 1
6/25 | 20:00:00 | 291.15 | 98892 | 5.7 | 80 | 7.338 | 169.2 | 64.8 | 276.802 | 0 | 1
6/25 | 21:00:00 | 289.15 | 98875 | 3.6 | 70 | 7.8564 | 7.2 | 0 | 275.398 | 0 | 1
6/25 | 22:00:00 | 287.15 | 98858 | 4.1 | 60 | 8.4073 | 0 | 0 | 274.088 | 0 | 1
6/25 | 23:00:00 | 285.15 | 98841 | 3.6 | 50 | 8.9926 | 0 | 0 | 272.627 | 0 | 1
6/25 | 24:00:00 | 285.15 | 98841 | 3.6 | 40 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
6/26 | 01:00:00 | 285.15 | 98841 | 3.6 | 30 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
6/26 | 02:00:00 | 285.15 | 98841 | 3.6 | 40 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
6/26 | 03:00:00 | 285.15 | 98841 | 3.6 | 40 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
6/26 | 04:00:00 | 284.15 | 98833 | 3.6 | 40 | 8.4095 | 0 | 0 | 270.859 | 0 | 1
6/26 | 05:00:00 | 285.15 | 98841 | 4.1 | 40 | 8.9926 | 50.4 | 0 | 272.517 | 0 | 1
6/26 | 06:00:00 | 286.15 | 98850 | 3.6 | 50 | 8.9918 | 223.2 | 0 | 273.473 | 0 | 1
6/26 | 07:00:00 | 287.15 | 98858 | 3.6 | 40 | 9.6108 | 486 | 36 | 274.652 | 0 | 1
6/26 | 08:00:00 | 288.15 | 98867 | 3.6 | 50 | 9.6099 | 1404 | 1245.6 | 275.122 | 0 | 1
6/26 | 09:00:00 | 289.15 | 98875 | 4.6 | 50 | 10.2668 | 2026.8 | 2307.6 | 276.029 | 0 | 1
6/26 | 10:00:00 | 291.15 | 98892 | 4.6 | 50 | 10.9627 | 2480.4 | 2595.6 | 278.162 | 0 | 1
6/26 | 11:00:00 | 293.15 | 98908 | 6.2 | 50 | 10.2634 | 2656.8 | 2181.6 | 280.122 | 0 | 1
6/26 | 12:00:00 | 292.15 | 98900 | 4.6 | 20 | 10.9618 | 2829.6 | 1882.8 | 279.391 | 0 | 1
6/26 | 13:00:00 | 291.15 | 98892 | 4.6 | 30 | 10.265 | 1584 | 370.8 | 278.703 | 0 | 1
6/26 | 14:00:00 | 291.15 | 98892 | 5.1 | 50 | 10.9627 | 1508.4 | 154.8 | 278.927 | 0 | 1
6/26 | 15:00:00 | 290.15 | 98883 | 3.6 | 60 | 10.9637 | 1357.2 | 108 | 277.969 | 0 | 1
6/26 | 16:00:00 | 289.15 | 98875 | 3.6 | 50 | 10.9646 | 1134 | 97.2 | 277.011 | 0 | 1
6/26 | 17:00:00 | 289.15 | 98875 | 2.1 | 70 | 10.9646 | 864 | 79.2 | 277.011 | 0 | 1
6/26 | 18:00:00 | 289.15 | 98875 | 2.6 | 60 | 10.9646 | 572.4 | 39.6 | 277.011 | 0 | 1
6/26 | 19:00:00 | 289.15 | 98875 | 3.1 | 60 | 10.9646 | 295.2 | 0 | 277.011 | 0 | 1
6/26 | 20:00:00 | 289.15 | 98875 | 2.6 | 50 | 10.9646 | 90 | 0 | 277.011 | 0 | 1
6/26 | 21:00:00 | 288.15 | 98867 | 2.1 | 60 | 10.9655 | 3.6 | 0 | 276.053 | 0 | 1
6/26 | 22:00:00 | 288.15 | 98867 | 2.1 | 60 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
6/26 | 23:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.9655 | 0 | 0 | 276.165 | 0 | 1
6/26 | 24:00:00 | 288.15 | 98867 | 1.5 | 208 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
6/27 | 01:00:00 | 287.15 | 98858 | 2.1 | 80 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/27 | 02:00:00 | 287.15 | 98858 | 2.1 | 70 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/27 | 03:00:00 | 287.15 | 98858 | 2.1 | 70 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/27 | 04:00:00 | 287.15 | 98858 | 2.1 | 30 | 10.2686 | 0 | 0 | 274.985 | 0 | 1
6/27 | 05:00:00 | 287.15 | 98858 | 1.5 | 171 | 10.2686 | 46.8 | 0 | 274.874 | 0 | 1
6/27 | 06:00:00 | 287.15 | 98858 | 2.1 | 40 | 10.2686 | 223.2 | 0 | 274.874 | 0 | 1
6/27 | 07:00:00 | 288.15 | 98867 | 2.6 | 50 | 10.2677 | 482.4 | 25.2 | 275.831 | 0 | 1
6/27 | 08:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.9655 | 774 | 93.6 | 276.053 | 0 | 1
6/27 | 09:00:00 | 289.15 | 98875 | 3.1 | 60 | 10.9646 | 1904.4 | 1684.8 | 276.522 | 0 | 1
6/27 | 10:00:00 | 290.15 | 98883 | 2.1 | 40 | 10.9637 | 2332.8 | 1814.4 | 277.478 | 0 | 1
6/27 | 11:00:00 | 291.15 | 98892 | 3.1 | 20 | 10.9627 | 1468.8 | 280.8 | 278.927 | 0 | 1
6/27 | 12:00:00 | 292.15 | 98900 | 2.6 | 60 | 10.9618 | 2826 | 1882.8 | 279.391 | 0 | 1
6/27 | 13:00:00 | 293.15 | 98908 | 3.1 | 60 | 11.7007 | 2847.6 | 2293.2 | 280.571 | 0 | 1
6/27 | 14:00:00 | 293.15 | 98908 | 5.1 | 10 | 11.7007 | 2718 | 2275.2 | 280.571 | 0 | 1
6/27 | 15:00:00 | 293.15 | 98908 | 4.1 | 40 | 11.7007 | 2440.8 | 1998 | 280.571 | 0 | 1
6/27 | 16:00:00 | 292.15 | 98900 | 4.6 | 50 | 11.7017 | 2044.8 | 1976.4 | 279.614 | 0 | 1
6/27 | 17:00:00 | 291.15 | 98892 | 4.1 | 50 | 11.7026 | 1555.2 | 1310.4 | 278.657 | 0 | 1
6/27 | 18:00:00 | 290.15 | 98883 | 3.6 | 20 | 10.9637 | 572.4 | 57.6 | 277.969 | 0 | 1
6/27 | 19:00:00 | 289.15 | 98875 | 3.6 | 20 | 10.9646 | 295.2 | 0 | 277.011 | 0 | 1
6/27 | 20:00:00 | 288.15 | 98867 | 2.6 | 20 | 10.9655 | 54 | 0 | 276.165 | 0 | 1
6/27 | 21:00:00 | 288.15 | 98867 | 3.1 | 20 | 10.9655 | 3.6 | 0 | 276.165 | 0 | 1
6/27 | 22:00:00 | 288.15 | 98867 | 2.6 | 10 | 10.9655 | 0 | 0 | 276.165 | 0 | 1
6/27 | 23:00:00 | 287.15 | 98858 | 2.6 | 10 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/27 | 24:00:00 | 287.15 | 98858 | 2.1 | 30 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/28 | 01:00:00 | 287.15 | 98858 | 2.1 | 30 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/28 | 02:00:00 | 287.15 | 98858 | 2.1 | 20 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/28 | 03:00:00 | 287.15 | 98858 | 2.6 | 40 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/28 | 04:00:00 | 287.15 | 98858 | 2.6 | 332 | 10.2686 | 0 | 0 | 274.985 | 0 | 1
6/28 | 05:00:00 | 287.15 | 98858 | 2.6 | 179 | 10.2686 | 28.8 | 0 | 274.985 | 0 | 1
6/28 | 06:00:00 | 287.15 | 98858 | 2.6 | 10 | 10.2686 | 133.2 | 0 | 274.985 | 0 | 1
6/28 | 07:00:00 | 287.15 | 98858 | 2.6 | 30 | 10.2686 | 291.6 | 0 | 274.985 | 0 | 1
6/28 | 08:00:00 | 287.15 | 98858 | 2.6 | 50 | 10.2686 | 471.6 | 0 | 274.985 | 0 | 1
6/28 | 09:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.9655 | 644.4 | 3.6 | 276.165 | 0 | 1
6/28 | 10:00:00 | 288.15 | 98867 | 1 | 246 | 10.9655 | 788.4 | 25.2 | 276.165 | 0 | 1
6/28 | 11:00:00 | 288.15 | 98867 | 1.5 | 156 | 10.9655 | 1468.8 | 104.4 | 276.053 | 0 | 1
6/28 | 12:00:00 | 288.15 | 98867 | 1 | 17 | 10.9655 | 1566 | 154.8 | 276.053 | 0 | 1
6/28 | 13:00:00 | 289.15 | 98875 | 2.1 | 70 | 11.7047 | 1576.8 | 363.6 | 277.232 | 0 | 1
6/28 | 14:00:00 | 291.15 | 98892 | 2.1 | 60 | 11.7026 | 2714.4 | 1897.2 | 278.657 | 0 | 1
6/28 | 15:00:00 | 292.15 | 98900 | 2.1 | 80 | 11.7017 | 2440.8 | 1998 | 279.614 | 0 | 1
6/28 | 16:00:00 | 294.15 | 98916 | 1.5 | 52 | 11.6997 | 2044.8 | 1976.4 | 281.528 | 0 | 1
6/28 | 17:00:00 | 294.15 | 98916 | 4.1 | 70 | 10.96 | 1558.8 | 1674 | 281.303 | 0 | 1
6/28 | 18:00:00 | 294.15 | 98916 | 3.6 | 50 | 10.96 | 1094.4 | 1522.8 | 281.028 | 0 | 1
6/28 | 19:00:00 | 293.15 | 98908 | 3.6 | 70 | 10.9609 | 565.2 | 745.2 | 280.073 | 0 | 1
6/28 | 20:00:00 | 291.15 | 98892 | 2.6 | 50 | 10.9627 | 169.2 | 86.4 | 278.162 | 0 | 1
6/28 | 21:00:00 | 289.15 | 98875 | 2.6 | 70 | 10.2668 | 7.2 | 0 | 276.029 | 0 | 1
6/28 | 22:00:00 | 289.15 | 98875 | 2.1 | 60 | 10.9646 | 0 | 0 | 276.251 | 0 | 1
6/28 | 23:00:00 | 288.15 | 98867 | 2.1 | 60 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
6/28 | 24:00:00 | 288.15 | 98867 | 2.1 | 80 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
6/29 | 01:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.9655 | 0 | 0 | 276.165 | 0 | 1
6/29 | 02:00:00 | 288.15 | 98867 | 2.1 | 50 | 10.9655 | 0 | 0 | 276.165 | 0 | 1
6/29 | 03:00:00 | 288.15 | 98867 | 1.5 | 30 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
6/29 | 04:00:00 | 288.15 | 98867 | 1 | 127 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
6/29 | 05:00:00 | 288.15 | 98867 | 2.1 | 60 | 10.9655 | 46.8 | 0 | 276.053 | 0 | 1
6/29 | 06:00:00 | 288.15 | 98867 | 1.5 | 233 | 10.9655 | 216 | 0 | 276.053 | 0 | 1
6/29 | 07:00:00 | 288.15 | 98867 | 2.1 | 100 | 10.9655 | 291.6 | 0 | 276.165 | 0 | 1
6/29 | 08:00:00 | 288.15 | 98867 | 2.6 | 90 | 10.9655 | 471.6 | 0 | 276.165 | 0 | 1
6/29 | 09:00:00 | 288.15 | 98867 | 2.6 | 100 | 10.9655 | 1051.2 | 104.4 | 276.053 | 0 | 1
6/29 | 10:00:00 | 289.15 | 98875 | 1.5 | 209 | 11.7047 | 1288.8 | 104.4 | 277.232 | 0 | 1
6/29 | 11:00:00 | 290.15 | 98883 | 2.1 | 90 | 11.7037 | 1465.2 | 151.2 | 278.191 | 0 | 1
6/29 | 12:00:00 | 291.15 | 98892 | 2.1 | 80 | 11.7026 | 1562.4 | 363.6 | 279.15 | 0 | 1
6/29 | 13:00:00 | 293.15 | 98908 | 2.6 | 100 | 11.7007 | 2844 | 1911.6 | 280.571 | 0 | 1
6/29 | 14:00:00 | 294.15 | 98916 | 2.6 | 80 | 12.484 | 2876.4 | 2768.4 | 281.476 | 0 | 1
6/29 | 15:00:00 | 295.15 | 98924 | 3.6 | 90 | 12.483 | 2584.8 | 2721.6 | 282.433 | 0 | 1
6/29 | 16:00:00 | 295.15 | 98924 | 4.1 | 70 | 12.483 | 2163.6 | 2505.6 | 282.433 | 0 | 1
6/29 | 17:00:00 | 295.15 | 98924 | 4.1 | 80 | 12.483 | 1648.8 | 2246.4 | 282.433 | 0 | 1
6/29 | 18:00:00 | 295.15 | 98924 | 4.1 | 110 | 11.6988 | 1090.8 | 1515.6 | 282.209 | 0 | 1
6/29 | 19:00:00 | 294.15 | 98916 | 5.1 | 100 | 11.6997 | 561.6 | 741.6 | 281.253 | 0 | 1
6/29 | 20:00:00 | 293.15 | 98908 | 4.1 | 100 | 12.485 | 169.2 | 79.2 | 280.519 | 0 | 1
6/29 | 21:00:00 | 291.15 | 98892 | 3.6 | 80 | 11.7026 | 3.6 | 0 | 279.15 | 0 | 1
6/29 | 22:00:00 | 290.15 | 98883 | 4.1 | 90 | 10.9637 | 0 | 0 | 276.764 | 0 | 1
6/29 | 23:00:00 | 289.15 | 98875 | 3.1 | 90 | 10.9646 | 0 | 0 | 275.81 | 0 | 1
6/29 | 24:00:00 | 289.15 | 98875 | 3.1 | 80 | 10.9646 | 0 | 0 | 275.81 | 0 | 1
6/30 | 01:00:00 | 288.15 | 98867 | 2.1 | 80 | 10.2677 | 0 | 0 | 274.636 | 0 | 1
6/30 | 02:00:00 | 287.15 | 98858 | 2.6 | 60 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
6/30 | 03:00:00 | 286.15 | 98850 | 2.6 | 80 | 9.6116 | 0 | 0 | 272.509 | 0 | 1
6/30 | 04:00:00 | 286.15 | 98850 | 2.6 | 70 | 9.6116 | 0 | 0 | 272.509 | 0 | 1
6/30 | 05:00:00 | 286.15 | 98850 | 2.1 | 70 | 9.6116 | 86.4 | 0 | 272.509 | 0 | 1
6/30 | 06:00:00 | 286.15 | 98850 | 1 | 60 | 9.6116 | 133.2 | 0 | 273.806 | 0 | 1
6/30 | 07:00:00 | 286.15 | 98850 | 0.5 | 111 | 9.6116 | 291.6 | 0 | 273.806 | 0 | 1
6/30 | 08:00:00 | 287.15 | 98858 | 0.5 | 249 | 10.2686 | 770.4 | 93.6 | 274.874 | 0 | 1
6/30 | 09:00:00 | 287.15 | 98858 | 0.5 | 83 | 10.2686 | 1051.2 | 237.6 | 274.874 | 0 | 1
6/30 | 10:00:00 | 288.15 | 98867 | 0.5 | 216 | 10.9655 | 2325.6 | 1810.8 | 275.565 | 0 | 1
6/30 | 11:00:00 | 289.15 | 98875 | 1.5 | 245 | 11.7047 | 2797.2 | 2728.8 | 276.472 | 0 | 1
6/30 | 12:00:00 | 291.15 | 98892 | 1.5 | 290 | 11.7026 | 2988 | 2865.6 | 278.384 | 0 | 1
6/30 | 13:00:00 | 292.15 | 98900 | 2.1 | 90 | 13.3174 | 3042 | 2746.8 | 279.335 | 0 | 1
6/30 | 14:00:00 | 295.15 | 98924 | 2.1 | 70 | 13.3141 | 2905.2 | 2998.8 | 282.204 | 0 | 1
6/30 | 15:00:00 | 296.15 | 98932 | 2.6 | 150 | 12.482 | 2617.2 | 2847.6 | 282.937 | 0 | 1
6/30 | 16:00:00 | 296.15 | 98932 | 3.1 | 130 | 12.482 | 2192.4 | 2610 | 282.937 | 0 | 1
6/30 | 17:00:00 | 296.15 | 98932 | 2.1 | 160 | 13.313 | 1645.2 | 2232 | 283.613 | 0 | 1
6/30 | 18:00:00 | 295.15 | 98924 | 1 | 276 | 14.1948 | 1083.6 | 1605.6 | 282.876 | 0 | 1
6/30 | 19:00:00 | 292.95 | 98906 | 1.6 | 225 | 13.1465 | 558 | 777.6 | 280.504 | 0 | 1
6/30 | 20:00:00 | 292.15 | 98900 | 1.6 | 178 | 12.4861 | 169.2 | 75.6 | 279.562 | 0 | 1
6/30 | 21:00:00 | 291.35 | 98894 | 2.2 | 118 | 11.8556 | 3.6 | 0 | 279.386 | 0 | 1
6/30 | 22:00:00 | 289.15 | 98875 | 2.7 | 167 | 10.6106 | 0 | 0 | 276.9 | 0 | 1
6/30 | 23:00:00 | 287.15 | 98858 | 3.2 | 175 | 9.4839 | 0 | 0 | 274.607 | 0 | 1
6/30 | 24:00:00 | 285.15 | 98841 | 3.6 | 215 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
7/1 | 01:00:00 | 283.35 | 98826 | 3.8 | 252 | 7.5977 | 0 | 0 | 269.762 | 0 | 1
7/1 | 02:00:00 | 283.15 | 98824 | 3.6 | 252 | 7.4441 | 0 | 0 | 269.504 | 0 | 1
7/1 | 03:00:00 | 283.15 | 98824 | 3.5 | 255 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
7/1 | 04:00:00 | 283.65 | 98828 | 3.2 | 255 | 7.4438 | 0 | 0 | 269.716 | 0 | 1
7/1 | 05:00:00 | 284.35 | 98835 | 3.5 | 255 | 7.4433 | 86.4 | 0 | 270.382 | 0 | 1
7/1 | 06:00:00 | 285.65 | 98846 | 4 | 255 | 7.3415 | 417.6 | 435.6 | 271.573 | 0 | 1
7/1 | 07:00:00 | 285.15 | 98841 | 3.6 | 250 | 7.8591 | 864 | 1026 | 271.588 | 0 | 1
7/1 | 08:00:00 | 286.15 | 98850 | 4.6 | 260 | 7.3412 | 1396.8 | 1494 | 272.314 | 0 | 1
7/1 | 09:00:00 | 287.15 | 98858 | 4.6 | 250 | 6.854 | 1911.6 | 1908 | 273.038 | 0 | 1
7/1 | 10:00:00 | 286.15 | 98850 | 4.6 | 270 | 6.3971 | 2350.8 | 2059.2 | 271.858 | 0 | 1
7/1 | 11:00:00 | 287.15 | 98858 | 3.6 | 240 | 6.854 | 2667.6 | 2250 | 273.038 | 0 | 1
7/1 | 12:00:00 | 286.15 | 98850 | 3.6 | 260 | 7.3412 | 2844 | 2275.2 | 272.314 | 0 | 1
7/1 | 13:00:00 | 288.15 | 98867 | 4.1 | 220 | 6.8534 | 2876.4 | 2286 | 273.988 | 0 | 1
7/1 | 14:00:00 | 289.15 | 98875 | 5.1 | 250 | 6.8529 | 2746.8 | 2260.8 | 274.939 | 0 | 1
7/1 | 15:00:00 | 289.15 | 98875 | 5.1 | 260 | 6.8529 | 2469.6 | 2210.4 | 274.939 | 0 | 1
7/1 | 16:00:00 | 287.15 | 98858 | 3.6 | 240 | 7.3406 | 2062.8 | 1965.6 | 273.266 | 0 | 1
7/1 | 17:00:00 | 288.15 | 98867 | 5.7 | 230 | 7.3399 | 1573.2 | 1609.2 | 274.218 | 0 | 1
7/1 | 18:00:00 | 287.15 | 98858 | 3.1 | 230 | 6.854 | 1040.4 | 1209.6 | 273.038 | 0 | 1
7/1 | 19:00:00 | 286.15 | 98850 | 3.6 | 230 | 6.8546 | 568.8 | 637.2 | 271.821 | 0 | 1
7/1 | 20:00:00 | 286.15 | 98850 | 4.1 | 220 | 7.3412 | 169.2 | 68.4 | 272.048 | 0 | 1
7/1 | 21:00:00 | 285.15 | 98841 | 3.6 | 190 | 7.8591 | 7.2 | 0 | 271.588 | 0 | 1
7/1 | 22:00:00 | 285.15 | 98841 | 3.6 | 180 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
7/1 | 23:00:00 | 285.15 | 98841 | 4.1 | 190 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
7/1 | 24:00:00 | 285.15 | 98841 | 5.1 | 230 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
7/2 | 01:00:00 | 285.15 | 98841 | 5.7 | 250 | 8.9926 | 0 | 0 | 272.036 | 0 | 1
7/2 | 02:00:00 | 285.15 | 98841 | 5.1 | 250 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
7/2 | 03:00:00 | 285.15 | 98841 | 6.2 | 270 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
7/2 | 04:00:00 | 284.15 | 98833 | 5.7 | 280 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
7/2 | 05:00:00 | 284.15 | 98833 | 4.1 | 260 | 7.3425 | 82.8 | 0 | 270.147 | 0 | 1
7/2 | 06:00:00 | 284.15 | 98833 | 4.6 | 250 | 7.8598 | 388.8 | 406.8 | 270.636 | 0 | 1
7/2 | 07:00:00 | 284.15 | 98833 | 4.6 | 260 | 7.8598 | 475.2 | 75.6 | 271.115 | 0 | 1
7/2 | 08:00:00 | 285.15 | 98841 | 4.6 | 240 | 7.8591 | 1389.6 | 1252.8 | 271.588 | 0 | 1
7/2 | 09:00:00 | 286.15 | 98850 | 6.2 | 250 | 7.8584 | 1900.8 | 1882.8 | 272.541 | 0 | 1
7/2 | 10:00:00 | 285.15 | 98841 | 5.1 | 250 | 7.3418 | 2340 | 2037.6 | 271.363 | 0 | 1
7/2 | 11:00:00 | 287.15 | 98858 | 5.7 | 270 | 6.854 | 2664 | 2246.4 | 273.038 | 0 | 1
7/2 | 12:00:00 | 287.15 | 98858 | 7.2 | 250 | 6.3966 | 2851.2 | 2282.4 | 272.808 | 0 | 1
7/2 | 13:00:00 | 288.15 | 98867 | 5.7 | 260 | 6.396 | 2876.4 | 2289.6 | 273.758 | 0 | 1
7/2 | 14:00:00 | 289.15 | 98875 | 5.1 | 230 | 6.8529 | 2743.2 | 2260.8 | 274.939 | 0 | 1
7/2 | 15:00:00 | 288.15 | 98867 | 5.7 | 230 | 6.396 | 2469.6 | 2214 | 273.758 | 0 | 1
7/2 | 16:00:00 | 285.15 | 98841 | 3.6 | 240 | 7.3418 | 2062.8 | 1962 | 271.363 | 0 | 1
7/2 | 17:00:00 | 286.15 | 98850 | 6.2 | 260 | 6.8546 | 1573.2 | 1612.8 | 272.087 | 0 | 1
7/2 | 18:00:00 | 283.15 | 98824 | 6.2 | 270 | 6.8564 | 1036.8 | 1206 | 269.234 | 0 | 1
7/2 | 19:00:00 | 285.15 | 98841 | 5.1 | 250 | 7.3418 | 532.8 | 504 | 271.363 | 0 | 1
7/2 | 20:00:00 | 284.15 | 98833 | 6.7 | 250 | 6.8558 | 158.4 | 21.6 | 270.185 | 0 | 1
7/2 | 21:00:00 | 282.15 | 98815 | 4.6 | 270 | 5.9692 | 7.2 | 0 | 267.83 | 0 | 1
7/2 | 22:00:00 | 281.15 | 98806 | 3.1 | 260 | 6.4 | 0 | 0 | 266.846 | 0 | 1
7/2 | 23:00:00 | 281.15 | 98806 | 5.1 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
7/2 | 24:00:00 | 281.15 | 98806 | 2.6 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1
7/3 | 01:00:00 | 281.15 | 98806 | 3.1 | 230 | 6.4 | 0 | 0 | 266.846 | 0 | 1
7/3 | 02:00:00 | 282.15 | 98815 | 4.1 | 260 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
7/3 | 03:00:00 | 281.15 | 98806 | 3.1 | 260 | 6.4 | 0 | 0 | 266.846 | 0 | 1
7/3 | 04:00:00 | 281.15 | 98806 | 3.6 | 260 | 6.4 | 0 | 0 | 266.846 | 0 | 1
7/3 | 05:00:00 | 281.15 | 98806 | 4.1 | 230 | 6.4 | 75.6 | 0 | 267.107 | 0 | 1
7/3 | 06:00:00 | 282.15 | 98815 | 5.7 | 250 | 6.8571 | 385.2 | 327.6 | 268.283 | 0 | 1
7/3 | 07:00:00 | 283.15 | 98824 | 7.2 | 250 | 6.8564 | 907.2 | 1202.4 | 268.971 | 0 | 1
7/3 | 08:00:00 | 283.15 | 98824 | 5.7 | 230 | 6.8564 | 1389.6 | 1440 | 269.234 | 0 | 1
7/3 | 09:00:00 | 283.15 | 98824 | 5.1 | 230 | 7.3431 | 1054.8 | 72 | 269.936 | 0 | 1
7/3 | 10:00:00 | 284.15 | 98833 | 7.2 | 260 | 7.3425 | 1296 | 180 | 270.89 | 0 | 1
7/3 | 11:00:00 | 285.15 | 98841 | 7.7 | 250 | 7.8591 | 2653.2 | 1857.6 | 271.588 | 0 | 1
7/3 | 12:00:00 | 285.15 | 98841 | 6.2 | 250 | 7.8591 | 2833.2 | 2268 | 271.588 | 0 | 1
7/3 | 13:00:00 | 286.15 | 98850 | 5.7 | 260 | 7.8584 | 2862 | 2271.6 | 272.541 | 0 | 1
7/3 | 14:00:00 | 287.15 | 98858 | 8.8 | 250 | 7.3406 | 2736 | 2253.6 | 273.266 | 0 | 1
7/3 | 15:00:00 | 287.15 | 98858 | 8.8 | 250 | 6.854 | 2466 | 2210.4 | 273.038 | 0 | 1
7/3 | 16:00:00 | 288.15 | 98867 | 10.8 | 260 | 6.8534 | 2062.8 | 1972.8 | 273.988 | 0 | 1
7/3 | 17:00:00 | 287.15 | 98858 | 9.3 | 260 | 6.3966 | 1573.2 | 1623.6 | 272.808 | 0 | 1
7/3 | 18:00:00 | 288.15 | 98867 | 10.3 | 270 | 6.396 | 1036.8 | 1209.6 | 273.758 | 0 | 1
7/3 | 19:00:00 | 287.15 | 98858 | 10.8 | 270 | 6.3966 | 532.8 | 507.6 | 272.808 | 0 | 1
7/3 | 20:00:00 | 286.15 | 98850 | 7.2 | 260 | 6.8546 | 158.4 | 18 | 272.087 | 0 | 1
7/3 | 21:00:00 | 284.15 | 98833 | 6.2 | 270 | 7.3425 | 7.2 | 0 | 270.411 | 0 | 1
7/3 | 22:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
7/3 | 23:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
7/3 | 24:00:00 | 283.15 | 98824 | 5.1 | 250 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
7/4 | 01:00:00 | 283.15 | 98824 | 3.1 | 260 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
7/4 | 02:00:00 | 282.15 | 98815 | 3.1 | 240 | 7.3438 | 0 | 0 | 268.245 | 0 | 1
7/4 | 03:00:00 | 282.15 | 98815 | 2.6 | 230 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
7/4 | 04:00:00 | 282.15 | 98815 | 3.1 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
7/4 | 05:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.8571 | 79.2 | 0 | 268.021 | 0 | 1
7/4 | 06:00:00 | 283.15 | 98824 | 2.6 | 240 | 7.3431 | 378 | 320.4 | 269.46 | 0 | 1
7/4 | 07:00:00 | 285.15 | 98841 | 3.1 | 240 | 7.8591 | 849.6 | 972 | 271.588 | 0 | 1
7/4 | 08:00:00 | 286.15 | 98850 | 5.7 | 260 | 7.8584 | 1378.8 | 1476 | 272.541 | 0 | 1
7/4 | 09:00:00 | 286.15 | 98850 | 5.7 | 250 | 6.8546 | 1897.2 | 1897.2 | 272.087 | 0 | 1
7/4 | 10:00:00 | 287.15 | 98858 | 6.7 | 260 | 6.854 | 2336.4 | 2044.8 | 273.038 | 0 | 1
7/4 | 11:00:00 | 287.15 | 98858 | 6.7 | 250 | 5.9666 | 2667.6 | 2260.8 | 272.576 | 0 | 1
7/4 | 12:00:00 | 288.15 | 98867 | 6.7 | 260 | 5.9661 | 2847.6 | 2289.6 | 273.525 | 0 | 1
7/4 | 13:00:00 | 289.15 | 98875 | 8.2 | 270 | 5.1824 | 2883.6 | 2318.4 | 274.004 | 0 | 1
7/4 | 14:00:00 | 289.15 | 98875 | 8.8 | 270 | 5.5617 | 2750.4 | 2282.4 | 274.24 | 0 | 1
7/4 | 15:00:00 | 289.15 | 98875 | 8.2 | 270 | 5.9656 | 2469.6 | 2224.8 | 274.475 | 0 | 1
7/4 | 16:00:00 | 290.15 | 98883 | 8.2 | 270 | 5.9651 | 2070 | 2134.8 | 275.424 | 0 | 1
7/4 | 17:00:00 | 289.15 | 98875 | 8.2 | 270 | 5.5617 | 1674 | 2145.6 | 273.972 | 0 | 1
7/4 | 18:00:00 | 288.15 | 98867 | 8.8 | 290 | 5.1829 | 1116 | 1483.2 | 272.649 | 0 | 1
7/4 | 19:00:00 | 288.15 | 98867 | 6.7 | 280 | 5.9661 | 561.6 | 630 | 273.258 | 0 | 1
7/4 | 20:00:00 | 287.15 | 98858 | 5.1 | 290 | 6.3966 | 162 | 36 | 272.808 | 0 | 1
7/4 | 21:00:00 | 285.15 | 98841 | 2.6 | 280 | 6.3977 | 3.6 | 0 | 271.033 | 0 | 1
7/4 | 22:00:00 | 284.15 | 98833 | 2.1 | 270 | 6.3982 | 0 | 0 | 270.204 | 0 | 1
7/4 | 23:00:00 | 283.15 | 98824 | 1.5 | 270 | 6.3988 | 0 | 0 | 269.37 | 0 | 1
7/4 | 24:00:00 | 284.15 | 98833 | 1.5 | 310 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
7/5 | 01:00:00 | 284.15 | 98833 | 1.5 | 260 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
7/5 | 02:00:00 | 284.15 | 98833 | 0 | 262 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
7/5 | 03:00:00 | 283.15 | 98824 | 1.5 | 190 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
7/5 | 04:00:00 | 284.15 | 98833 | 1.5 | 200 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
7/5 | 05:00:00 | 284.15 | 98833 | 2.1 | 190 | 6.8558 | 57.6 | 0 | 270.549 | 0 | 1
7/5 | 06:00:00 | 284.15 | 98833 | 2.1 | 170 | 7.3425 | 241.2 | 0 | 270.89 | 0 | 1
7/5 | 07:00:00 | 286.15 | 98850 | 2.1 | 180 | 7.3412 | 730.8 | 543.6 | 272.563 | 0 | 1
7/5 | 08:00:00 | 287.15 | 98858 | 2.1 | 180 | 7.3406 | 1292.4 | 1152 | 273.393 | 0 | 1
7/5 | 09:00:00 | 289.15 | 98875 | 3.6 | 190 | 6.8529 | 2008.8 | 2235.6 | 274.67 | 0 | 1
7/5 | 10:00:00 | 290.15 | 98883 | 4.1 | 190 | 6.8523 | 2473.2 | 2574 | 275.62 | 0 | 1
7/5 | 11:00:00 | 291.15 | 98892 | 4.1 | 190 | 6.3944 | 2660.4 | 2185.2 | 276.608 | 0 | 1
7/5 | 12:00:00 | 292.15 | 98900 | 4.6 | 200 | 6.8511 | 2836.8 | 2278.8 | 277.792 | 0 | 1
7/5 | 13:00:00 | 293.15 | 98908 | 4.6 | 200 | 6.8506 | 2865.6 | 2286 | 278.743 | 0 | 1
7/5 | 14:00:00 | 293.15 | 98908 | 4.6 | 190 | 6.8506 | 2736 | 1897.2 | 278.743 | 0 | 1
7/5 | 15:00:00 | 291.15 | 98892 | 3.6 | 220 | 7.338 | 1364.4 | 183.6 | 277.563 | 0 | 1
7/5 | 16:00:00 | 290.15 | 98883 | 3.1 | 220 | 8.4052 | 1137.6 | 100.8 | 277.068 | 0 | 1
7/5 | 17:00:00 | 290.15 | 98883 | 4.6 | 190 | 8.4052 | 867.6 | 108 | 277.068 | 0 | 1
7/5 | 18:00:00 | 288.15 | 98867 | 3.1 | 200 | 10.2677 | 1022.4 | 982.8 | 275.344 | 0 | 1
7/5 | 19:00:00 | 288.15 | 98867 | 3.6 | 200 | 10.2677 | 525.6 | 709.2 | 275.344 | 0 | 1
7/5 | 20:00:00 | 288.15 | 98867 | 3.1 | 210 | 10.9655 | 86.4 | 0 | 276.053 | 0 | 1
7/5 | 21:00:00 | 288.15 | 98867 | 2.6 | 220 | 10.2677 | 3.6 | 0 | 275.344 | 0 | 1
7/5 | 22:00:00 | 288.15 | 98867 | 6.2 | 220 | 9.6099 | 0 | 0 | 275.122 | 0 | 1
7/5 | 23:00:00 | 287.15 | 98858 | 5.7 | 240 | 9.6108 | 0 | 0 | 274.167 | 0 | 1
7/5 | 24:00:00 | 287.15 | 98858 | 5.1 | 240 | 8.991 | 0 | 0 | 273.944 | 0 | 1
7/6 | 01:00:00 | 286.15 | 98850 | 4.1 | 260 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
7/6 | 02:00:00 | 286.15 | 98850 | 4.6 | 250 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
7/6 | 03:00:00 | 286.15 | 98850 | 8.2 | 270 | 9.6116 | 0 | 0 | 273.695 | 0 | 1
7/6 | 04:00:00 | 286.15 | 98850 | 4.6 | 290 | 9.6116 | 0 | 0 | 273.695 | 0 | 1
7/6 | 05:00:00 | 285.15 | 98841 | 5.7 | 320 | 8.4088 | 72 | 0 | 271.813 | 0 | 1
7/6 | 06:00:00 | 285.15 | 98841 | 4.6 | 330 | 7.8591 | 370.8 | 309.6 | 271.588 | 0 | 1
7/6 | 07:00:00 | 285.15 | 98841 | 6.7 | 310 | 7.3418 | 838.8 | 964.8 | 271.363 | 0 | 1
7/6 | 08:00:00 | 286.15 | 98850 | 8.8 | 310 | 7.3412 | 1454.4 | 1814.4 | 272.048 | 0 | 1
7/6 | 09:00:00 | 287.15 | 98858 | 7.2 | 300 | 7.3406 | 1886.4 | 2016 | 273.266 | 0 | 1
7/6 | 10:00:00 | 287.15 | 98858 | 6.7 | 310 | 7.3406 | 2322 | 2034 | 273.266 | 0 | 1
7/6 | 11:00:00 | 289.15 | 98875 | 7.2 | 300 | 6.8529 | 2649.6 | 2246.4 | 274.939 | 0 | 1
7/6 | 12:00:00 | 290.15 | 98883 | 7.2 | 300 | 7.3387 | 2829.6 | 2271.6 | 276.121 | 0 | 1
7/6 | 13:00:00 | 289.15 | 98875 | 7.2 | 290 | 7.3393 | 2858.4 | 2275.2 | 275.169 | 0 | 1
7/6 | 14:00:00 | 290.15 | 98883 | 7.2 | 280 | 7.3387 | 2728.8 | 2253.6 | 276.121 | 0 | 1
7/6 | 15:00:00 | 291.15 | 98892 | 7.7 | 270 | 7.338 | 2455.2 | 2142 | 277.073 | 0 | 1
7/6 | 16:00:00 | 289.15 | 98875 | 8.8 | 280 | 6.8529 | 2185.2 | 2440.8 | 274.67 | 0 | 1
7/6 | 17:00:00 | 288.15 | 98867 | 9.8 | 270 | 6.396 | 1663.2 | 2037.6 | 273.49 | 0 | 1
7/6 | 18:00:00 | 288.15 | 98867 | 8.2 | 280 | 6.8534 | 1094.4 | 1407.6 | 273.72 | 0 | 1
7/6 | 19:00:00 | 288.15 | 98867 | 10.8 | 280 | 6.396 | 558 | 626.4 | 273.49 | 0 | 1
7/6 | 20:00:00 | 287.15 | 98858 | 6.2 | 280 | 6.854 | 162 | 57.6 | 272.77 | 0 | 1
7/6 | 21:00:00 | 285.15 | 98841 | 6.2 | 280 | 6.8552 | 3.6 | 0 | 270.871 | 0 | 1
7/6 | 22:00:00 | 284.15 | 98833 | 6.7 | 290 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
7/6 | 23:00:00 | 283.15 | 98824 | 5.7 | 290 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
7/6 | 24:00:00 | 283.15 | 98824 | 3.1 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
7/7 | 01:00:00 | 282.15 | 98815 | 4.6 | 290 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
7/7 | 02:00:00 | 282.15 | 98815 | 6.2 | 290 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
7/7 | 03:00:00 | 281.15 | 98806 | 4.6 | 270 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
7/7 | 04:00:00 | 282.15 | 98815 | 5.1 | 280 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
7/7 | 05:00:00 | 282.15 | 98815 | 5.1 | 280 | 6.8571 | 32.4 | 0 | 268.867 | 0 | 1
7/7 | 06:00:00 | 282.15 | 98815 | 4.1 | 290 | 6.8571 | 165.6 | 0 | 268.867 | 0 | 1
7/7 | 07:00:00 | 283.15 | 98824 | 3.6 | 270 | 7.3431 | 378 | 0 | 270.046 | 0 | 1
7/7 | 08:00:00 | 285.15 | 98841 | 3.1 | 280 | 7.3418 | 1047.6 | 568.8 | 271.729 | 0 | 1
7/7 | 09:00:00 | 286.15 | 98850 | 2.6 | 280 | 6.8546 | 1882.8 | 1789.2 | 272.087 | 0 | 1
7/7 | 10:00:00 | 287.15 | 98858 | 3.6 | 280 | 6.3966 | 2325.6 | 2052 | 272.808 | 0 | 1
7/7 | 11:00:00 | 288.15 | 98867 | 3.1 | 260 | 6.8534 | 2646 | 2242.8 | 273.988 | 0 | 1
7/7 | 12:00:00 | 289.15 | 98875 | 4.1 | 260 | 7.3393 | 2826 | 2268 | 275.169 | 0 | 1
7/7 | 13:00:00 | 289.15 | 98875 | 5.7 | 250 | 7.8564 | 2851.2 | 2271.6 | 275.398 | 0 | 1
7/7 | 14:00:00 | 289.15 | 98875 | 5.1 | 260 | 7.8564 | 2721.6 | 2250 | 275.398 | 0 | 1
7/7 | 15:00:00 | 289.15 | 98875 | 6.2 | 270 | 7.3393 | 2451.6 | 2206.8 | 275.169 | 0 | 1
7/7 | 16:00:00 | 289.15 | 98875 | 4.6 | 250 | 7.3393 | 2052 | 2102.4 | 275.169 | 0 | 1
7/7 | 17:00:00 | 289.15 | 98875 | 3.6 | 260 | 7.8564 | 1652.4 | 2091.6 | 275.129 | 0 | 1
7/7 | 18:00:00 | 289.15 | 98875 | 2.1 | 260 | 8.4059 | 1083.6 | 1375.2 | 275.356 | 0 | 1
7/7 | 19:00:00 | 289.15 | 98875 | 1 | 102 | 8.4059 | 522 | 590.4 | 275.626 | 0 | 1
7/7 | 20:00:00 | 288.15 | 98867 | 1.5 | 117 | 8.9902 | 151.2 | 7.2 | 274.898 | 0 | 1
7/7 | 21:00:00 | 288.15 | 98867 | 1.5 | 280 | 8.9902 | 3.6 | 0 | 274.629 | 0 | 1
7/7 | 22:00:00 | 288.15 | 98867 | 2.1 | 210 | 8.9902 | 0 | 0 | 274.629 | 0 | 1
7/7 | 23:00:00 | 288.15 | 98867 | 3.6 | 230 | 8.4065 | 0 | 0 | 274.404 | 0 | 1
7/7 | 24:00:00 | 288.15 | 98867 | 4.1 | 240 | 8.4065 | 0 | 0 | 274.404 | 0 | 1
7/8 | 01:00:00 | 287.15 | 98858 | 4.1 | 230 | 8.4073 | 0 | 0 | 274.203 | 0 | 1
7/8 | 02:00:00 | 287.15 | 98858 | 4.6 | 230 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
7/8 | 03:00:00 | 287.15 | 98858 | 4.1 | 240 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
7/8 | 04:00:00 | 286.15 | 98850 | 4.6 | 250 | 8.9918 | 0 | 0 | 272.99 | 0 | 1
7/8 | 05:00:00 | 286.15 | 98850 | 4.1 | 250 | 8.9918 | 68.4 | 0 | 272.99 | 0 | 1
7/8 | 06:00:00 | 287.15 | 98858 | 4.1 | 250 | 8.991 | 360 | 349.2 | 273.944 | 0 | 1
7/8 | 07:00:00 | 287.15 | 98858 | 4.6 | 240 | 9.6108 | 820.8 | 925.2 | 274.167 | 0 | 1
7/8 | 08:00:00 | 288.15 | 98867 | 4.6 | 230 | 9.6099 | 1350 | 1533.6 | 275.122 | 0 | 1
7/8 | 09:00:00 | 288.15 | 98867 | 5.7 | 240 | 9.6099 | 1861.2 | 1670.4 | 275.122 | 0 | 1
7/8 | 10:00:00 | 290.15 | 98883 | 5.7 | 240 | 10.266 | 1274.4 | 115.2 | 277.746 | 0 | 1
7/8 | 11:00:00 | 290.15 | 98883 | 6.7 | 230 | 10.266 | 1450.8 | 154.8 | 277.746 | 0 | 1
7/8 | 12:00:00 | 289.15 | 98875 | 5.7 | 270 | 10.2668 | 1551.6 | 367.2 | 276.789 | 0 | 1
7/8 | 13:00:00 | 290.15 | 98883 | 5.1 | 260 | 10.9637 | 2826 | 1526.4 | 277.478 | 0 | 1
7/8 | 14:00:00 | 292.15 | 98900 | 5.7 | 260 | 10.2642 | 1501.2 | 280.8 | 279.66 | 0 | 1
7/8 | 15:00:00 | 292.15 | 98900 | 5.7 | 260 | 9.6067 | 2433.6 | 1843.2 | 278.941 | 0 | 1
7/8 | 16:00:00 | 292.15 | 98900 | 5.7 | 280 | 10.2642 | 2034 | 1983.6 | 279.166 | 0 | 1
7/8 | 17:00:00 | 292.15 | 98900 | 3.6 | 260 | 10.2642 | 1544.4 | 1663.2 | 279.166 | 0 | 1
7/8 | 18:00:00 | 292.15 | 98900 | 5.7 | 260 | 9.6067 | 1015.2 | 1242 | 278.941 | 0 | 1
7/8 | 19:00:00 | 291.15 | 98892 | 5.1 | 270 | 9.6075 | 518.4 | 576 | 277.986 | 0 | 1
7/8 | 20:00:00 | 291.15 | 98892 | 4.6 | 270 | 9.6075 | 147.6 | 3.6 | 277.986 | 0 | 1
7/8 | 21:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.2668 | 0 | 0 | 276.3 | 0 | 1
7/8 | 22:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
7/8 | 23:00:00 | 288.15 | 98867 | 4.6 | 220 | 10.2677 | 0 | 0 | 275.831 | 0 | 1
7/8 | 24:00:00 | 288.15 | 98867 | 4.6 | 220 | 10.2677 | 0 | 0 | 275.344 | 0 | 1
7/9 | 01:00:00 | 288.15 | 98867 | 2.1 | 220 | 9.6099 | 0 | 0 | 274.852 | 0 | 1
7/9 | 02:00:00 | 287.15 | 98858 | 3.6 | 220 | 9.6108 | 0 | 0 | 274.167 | 0 | 1
7/9 | 03:00:00 | 288.15 | 98867 | 2.6 | 210 | 10.2677 | 0 | 0 | 275.831 | 0 | 1
7/9 | 04:00:00 | 288.15 | 98867 | 3.6 | 210 | 10.2677 | 0 | 0 | 275.831 | 0 | 1
7/9 | 05:00:00 | 287.15 | 98858 | 3.6 | 220 | 10.2686 | 36 | 0 | 274.874 | 0 | 1
7/9 | 06:00:00 | 287.15 | 98858 | 6.2 | 250 | 10.2686 | 194.4 | 0 | 274.874 | 0 | 1
7/9 | 07:00:00 | 287.15 | 98858 | 6.7 | 250 | 10.2686 | 450 | 18 | 274.874 | 0 | 1
7/9 | 08:00:00 | 287.15 | 98858 | 5.1 | 250 | 9.6108 | 745.2 | 68.4 | 274.652 | 0 | 1
7/9 | 09:00:00 | 287.15 | 98858 | 5.1 | 270 | 9.6108 | 1029.6 | 75.6 | 274.652 | 0 | 1
7/9 | 10:00:00 | 287.15 | 98858 | 4.6 | 270 | 8.991 | 1274.4 | 104.4 | 274.428 | 0 | 1
7/9 | 11:00:00 | 288.15 | 98867 | 7.2 | 260 | 9.6099 | 1450.8 | 154.8 | 275.608 | 0 | 1
7/9 | 12:00:00 | 287.15 | 98858 | 6.2 | 270 | 9.6108 | 1551.6 | 154.8 | 274.652 | 0 | 1
7/9 | 13:00:00 | 288.15 | 98867 | 8.2 | 260 | 8.9902 | 1573.2 | 158.4 | 275.384 | 0 | 1
7/9 | 14:00:00 | 288.15 | 98867 | 7.7 | 280 | 8.4065 | 1504.8 | 370.8 | 275.158 | 0 | 1
7/9 | 15:00:00 | 288.15 | 98867 | 8.8 | 270 | 8.4065 | 2437.2 | 1857.6 | 274.672 | 0 | 1
7/9 | 16:00:00 | 290.15 | 98883 | 8.8 | 270 | 8.4052 | 2041.2 | 2008.8 | 276.579 | 0 | 1
7/9 | 17:00:00 | 289.15 | 98875 | 8.2 | 260 | 8.4059 | 1548 | 1684.8 | 275.626 | 0 | 1
7/9 | 18:00:00 | 289.15 | 98875 | 8.8 | 270 | 8.4059 | 1015.2 | 1249.2 | 275.626 | 0 | 1
7/9 | 19:00:00 | 289.15 | 98875 | 5.1 | 270 | 8.4059 | 514.8 | 576 | 275.626 | 0 | 1
7/9 | 20:00:00 | 289.15 | 98875 | 5.1 | 270 | 8.4059 | 147.6 | 3.6 | 275.626 | 0 | 1
7/9 | 21:00:00 | 287.15 | 98858 | 2.1 | 270 | 8.4073 | 0 | 0 | 273.451 | 0 | 1
7/9 | 22:00:00 | 286.15 | 98850 | 1.5 | 226 | 8.408 | 0 | 0 | 272.499 | 0 | 1
7/9 | 23:00:00 | 285.15 | 98841 | 1.5 | 64 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
7/9 | 24:00:00 | 285.15 | 98841 | 2.1 | 210 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
7/10 | 01:00:00 | 286.15 | 98850 | 1.5 | 263 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
7/10 | 02:00:00 | 287.15 | 98858 | 3.1 | 240 | 8.991 | 0 | 0 | 273.676 | 0 | 1
7/10 | 03:00:00 | 287.15 | 98858 | 1 | 34 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
7/10 | 04:00:00 | 287.15 | 98858 | 2.6 | 210 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
7/10 | 05:00:00 | 287.15 | 98858 | 3.6 | 210 | 9.6108 | 36 | 0 | 274.652 | 0 | 1
7/10 | 06:00:00 | 288.15 | 98867 | 3.1 | 210 | 9.6099 | 349.2 | 403.2 | 275.122 | 0 | 1
7/10 | 07:00:00 | 288.15 | 98867 | 2.6 | 220 | 10.2677 | 446.4 | 25.2 | 275.831 | 0 | 1
7/10 | 08:00:00 | 288.15 | 98867 | 2.6 | 210 | 10.2677 | 741.6 | 64.8 | 275.831 | 0 | 1
7/10 | 09:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.2668 | 1026 | 75.6 | 276.789 | 0 | 1
7/10 | 10:00:00 | 288.15 | 98867 | 4.1 | 210 | 10.9655 | 1267.2 | 104.4 | 276.053 | 0 | 1
7/10 | 11:00:00 | 289.15 | 98875 | 4.1 | 200 | 11.7047 | 1443.6 | 151.2 | 277.232 | 0 | 1
7/10 | 12:00:00 | 289.15 | 98875 | 3.6 | 230 | 10.9646 | 1544.4 | 154.8 | 277.011 | 0 | 1
7/10 | 13:00:00 | 289.15 | 98875 | 3.1 | 220 | 11.7047 | 1558.8 | 154.8 | 277.232 | 0 | 1
7/10 | 14:00:00 | 290.15 | 98883 | 3.1 | 210 | 11.7037 | 1490.4 | 360 | 278.191 | 0 | 1
7/10 | 15:00:00 | 292.15 | 98900 | 5.1 | 210 | 12.4861 | 2412 | 1958.4 | 279.836 | 0 | 1
7/10 | 16:00:00 | 293.15 | 98908 | 7.7 | 220 | 12.485 | 2019.6 | 2120.4 | 280.793 | 0 | 1
7/10 | 17:00:00 | 292.15 | 98900 | 6.7 | 220 | 12.4861 | 1530 | 1760.4 | 279.836 | 0 | 1
7/10 | 18:00:00 | 292.15 | 98900 | 6.2 | 220 | 12.4861 | 1004.4 | 1303.2 | 279.836 | 0 | 1
7/10 | 19:00:00 | 291.15 | 98892 | 5.7 | 220 | 12.4871 | 507.6 | 594 | 278.878 | 0 | 1
7/10 | 20:00:00 | 290.15 | 98883 | 6.7 | 220 | 12.4883 | 144 | 0 | 277.92 | 0 | 1
7/10 | 21:00:00 | 290.15 | 98883 | 6.2 | 220 | 12.4883 | 0 | 0 | 277.92 | 0 | 1
7/10 | 22:00:00 | 290.15 | 98883 | 8.2 | 220 | 11.7037 | 0 | 0 | 278.191 | 0 | 1
7/10 | 23:00:00 | 289.15 | 98875 | 7.2 | 220 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
7/10 | 24:00:00 | 289.15 | 98875 | 5.7 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
7/11 | 01:00:00 | 289.15 | 98875 | 6.2 | 200 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
7/11 | 02:00:00 | 289.15 | 98875 | 6.2 | 210 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
7/11 | 03:00:00 | 289.15 | 98875 | 4.1 | 240 | 10.2668 | 0 | 0 | 276.3 | 0 | 1
7/11 | 04:00:00 | 288.15 | 98867 | 5.7 | 240 | 9.6099 | 0 | 0 | 275.122 | 0 | 1
7/11 | 05:00:00 | 288.15 | 98867 | 3.1 | 250 | 9.6099 | 64.8 | 0 | 275.122 | 0 | 1
7/11 | 06:00:00 | 288.15 | 98867 | 3.1 | 250 | 9.6099 | 190.8 | 0 | 275.608 | 0 | 1
7/11 | 07:00:00 | 288.15 | 98867 | 2.1 | 220 | 10.2677 | 799.2 | 792 | 275.344 | 0 | 1
7/11 | 08:00:00 | 290.15 | 98883 | 5.1 | 230 | 10.266 | 1328.4 | 1508.4 | 277.255 | 0 | 1
7/11 | 09:00:00 | 290.15 | 98883 | 5.1 | 230 | 9.6084 | 1843.2 | 1659.6 | 277.031 | 0 | 1
7/11 | 10:00:00 | 291.15 | 98892 | 6.2 | 230 | 8.9879 | 1267.2 | 313.2 | 278.251 | 0 | 1
7/11 | 11:00:00 | 290.15 | 98883 | 5.1 | 220 | 8.9887 | 2610 | 1828.8 | 276.806 | 0 | 1
7/11 | 12:00:00 | 291.15 | 98892 | 4.6 | 230 | 9.6075 | 2790 | 2253.6 | 277.986 | 0 | 1
7/11 | 13:00:00 | 291.15 | 98892 | 6.2 | 230 | 9.6075 | 2822.4 | 2257.2 | 277.986 | 0 | 1
7/11 | 14:00:00 | 292.15 | 98900 | 6.2 | 240 | 9.6067 | 2696.4 | 2235.6 | 278.941 | 0 | 1
7/11 | 15:00:00 | 292.15 | 98900 | 6.7 | 230 | 9.6067 | 2422.8 | 2019.6 | 278.941 | 0 | 1
7/11 | 16:00:00 | 290.15 | 98883 | 5.7 | 220 | 10.266 | 2023.2 | 1980 | 277.255 | 0 | 1
7/11 | 17:00:00 | 291.15 | 98892 | 4.6 | 230 | 10.265 | 1533.6 | 1656 | 278.211 | 0 | 1
7/11 | 18:00:00 | 292.15 | 98900 | 3.6 | 250 | 9.6067 | 1004.4 | 1231.2 | 278.941 | 0 | 1
7/11 | 19:00:00 | 290.15 | 98883 | 6.2 | 240 | 8.4052 | 507.6 | 568.8 | 276.579 | 0 | 1
7/11 | 20:00:00 | 289.15 | 98875 | 4.6 | 220 | 8.9895 | 140.4 | 0 | 275.852 | 0 | 1
7/11 | 21:00:00 | 289.15 | 98875 | 5.7 | 210 | 8.9895 | 0 | 0 | 275.852 | 0 | 1
7/11 | 22:00:00 | 288.15 | 98867 | 4.6 | 200 | 8.9902 | 0 | 0 | 274.898 | 0 | 1
7/11 | 23:00:00 | 288.15 | 98867 | 5.7 | 210 | 8.9902 | 0 | 0 | 274.898 | 0 | 1
7/11 | 24:00:00 | 287.15 | 98858 | 5.7 | 210 | 8.991 | 0 | 0 | 273.944 | 0 | 1
7/12 | 01:00:00 | 287.15 | 98858 | 6.7 | 210 | 8.991 | 0 | 0 | 273.944 | 0 | 1
7/12 | 02:00:00 | 287.15 | 98858 | 5.7 | 220 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
7/12 | 03:00:00 | 287.15 | 98858 | 5.7 | 220 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
7/12 | 04:00:00 | 287.15 | 98858 | 6.2 | 220 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
7/12 | 05:00:00 | 286.15 | 98850 | 6.2 | 220 | 9.6116 | 36 | 0 | 273.695 | 0 | 1
7/12 | 06:00:00 | 286.15 | 98850 | 5.1 | 220 | 9.6116 | 187.2 | 0 | 273.695 | 0 | 1
7/12 | 07:00:00 | 287.15 | 98858 | 5.1 | 250 | 9.6108 | 439.2 | 18 | 274.652 | 0 | 1
7/12 | 08:00:00 | 287.15 | 98858 | 6.2 | 260 | 10.2686 | 734.4 | 64.8 | 274.874 | 0 | 1
7/12 | 09:00:00 | 288.15 | 98867 | 6.2 | 260 | 10.2677 | 1018.8 | 230.4 | 275.831 | 0 | 1
7/12 | 10:00:00 | 288.15 | 98867 | 7.2 | 260 | 10.2677 | 2271.6 | 1807.2 | 275.344 | 0 | 1
7/12 | 11:00:00 | 287.15 | 98858 | 9.3 | 270 | 9.6108 | 2599.2 | 1814.4 | 274.167 | 0 | 1
7/12 | 12:00:00 | 288.15 | 98867 | 7.7 | 270 | 9.6099 | 1544.4 | 367.2 | 275.608 | 0 | 1
7/12 | 13:00:00 | 288.15 | 98867 | 7.7 | 270 | 10.2677 | 1558.8 | 367.2 | 275.831 | 0 | 1
7/12 | 14:00:00 | 289.15 | 98875 | 8.2 | 260 | 10.2668 | 2689.2 | 1828.8 | 276.3 | 0 | 1
7/12 | 15:00:00 | 289.15 | 98875 | 8.2 | 260 | 9.6091 | 2419.2 | 2016 | 276.076 | 0 | 1
7/12 | 16:00:00 | 288.15 | 98867 | 9.3 | 270 | 9.6099 | 2023.2 | 1987.2 | 275.122 | 0 | 1
7/12 | 17:00:00 | 289.15 | 98875 | 8.2 | 280 | 8.9895 | 1533.6 | 1670.4 | 275.852 | 0 | 1
7/12 | 18:00:00 | 289.15 | 98875 | 9.3 | 270 | 8.4059 | 1004.4 | 1238.4 | 275.626 | 0 | 1
7/12 | 19:00:00 | 288.15 | 98867 | 7.2 | 270 | 8.9902 | 504 | 558 | 274.898 | 0 | 1
7/12 | 20:00:00 | 287.15 | 98858 | 6.7 | 270 | 8.991 | 140.4 | 0 | 273.944 | 0 | 1
7/12 | 21:00:00 | 286.15 | 98850 | 5.1 | 270 | 8.408 | 0 | 0 | 272.499 | 0 | 1
7/12 | 22:00:00 | 285.15 | 98841 | 3.6 | 270 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
7/12 | 23:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
7/12 | 24:00:00 | 284.15 | 98833 | 2.6 | 280 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
7/13 | 01:00:00 | 283.15 | 98824 | 2.1 | 270 | 7.8605 | 0 | 0 | 269.684 | 0 | 1
7/13 | 02:00:00 | 284.15 | 98833 | 4.6 | 280 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
7/13 | 03:00:00 | 284.15 | 98833 | 4.1 | 280 | 8.4095 | 0 | 0 | 271.449 | 0 | 1
7/13 | 04:00:00 | 284.15 | 98833 | 4.1 | 300 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
7/13 | 05:00:00 | 284.15 | 98833 | 1.5 | 280 | 7.8598 | 64.8 | 0 | 270.371 | 0 | 1
7/13 | 06:00:00 | 284.15 | 98833 | 3.6 | 290 | 7.8598 | 352.8 | 338.4 | 270.371 | 0 | 1
7/13 | 07:00:00 | 285.15 | 98841 | 4.1 | 300 | 7.8591 | 838.8 | 1108.8 | 271.323 | 0 | 1
7/13 | 08:00:00 | 286.15 | 98850 | 5.1 | 300 | 7.3412 | 1404 | 1818 | 272.048 | 0 | 1
7/13 | 09:00:00 | 287.15 | 98858 | 3.6 | 320 | 6.854 | 1843.2 | 1994.4 | 273.038 | 0 | 1
7/13 | 10:00:00 | 288.15 | 98867 | 4.1 | 320 | 6.8534 | 2286 | 1864.8 | 273.988 | 0 | 1
7/13 | 11:00:00 | 288.15 | 98867 | 4.1 | 320 | 6.8534 | 1450.8 | 903.6 | 274.473 | 0 | 1
7/13 | 12:00:00 | 289.15 | 98875 | 4.6 | 300 | 6.3955 | 2804.4 | 1911.6 | 274.708 | 0 | 1
7/13 | 13:00:00 | 288.15 | 98867 | 6.7 | 310 | 6.396 | 2836.8 | 2275.2 | 273.758 | 0 | 1
7/13 | 14:00:00 | 288.15 | 98867 | 6.2 | 280 | 5.9661 | 2714.4 | 2264.4 | 273.525 | 0 | 1
7/13 | 15:00:00 | 288.15 | 98867 | 5.1 | 280 | 6.8534 | 2433.6 | 2210.4 | 273.988 | 0 | 1
7/13 | 16:00:00 | 289.15 | 98875 | 6.2 | 300 | 6.3955 | 2034 | 1965.6 | 274.708 | 0 | 1
7/13 | 17:00:00 | 288.15 | 98867 | 6.2 | 290 | 6.396 | 1540.8 | 1648.8 | 273.758 | 0 | 1
7/13 | 18:00:00 | 288.15 | 98867 | 6.7 | 290 | 6.396 | 1065.6 | 1425.6 | 273.49 | 0 | 1
7/13 | 19:00:00 | 287.15 | 98858 | 5.7 | 310 | 6.3966 | 500.4 | 468 | 272.808 | 0 | 1
7/13 | 20:00:00 | 286.15 | 98850 | 5.1 | 300 | 6.3971 | 144 | 18 | 271.592 | 0 | 1
7/13 | 21:00:00 | 285.15 | 98841 | 4.6 | 280 | 6.8552 | 0 | 0 | 270.871 | 0 | 1
7/13 | 22:00:00 | 285.15 | 98841 | 4.6 | 280 | 6.3977 | 0 | 0 | 270.643 | 0 | 1
7/13 | 23:00:00 | 284.15 | 98833 | 4.1 | 280 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
7/13 | 24:00:00 | 284.15 | 98833 | 5.7 | 280 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
7/14 | 01:00:00 | 284.15 | 98833 | 5.7 | 280 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
7/14 | 02:00:00 | 284.15 | 98833 | 4.6 | 290 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
7/14 | 03:00:00 | 284.15 | 98833 | 3.6 | 290 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
7/14 | 04:00:00 | 284.15 | 98833 | 3.6 | 270 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
7/14 | 05:00:00 | 283.15 | 98824 | 2.1 | 270 | 6.8564 | 61.2 | 0 | 268.971 | 0 | 1
7/14 | 06:00:00 | 284.15 | 98833 | 2.6 | 280 | 6.8558 | 345.6 | 277.2 | 269.921 | 0 | 1
7/14 | 07:00:00 | 284.15 | 98833 | 3.6 | 270 | 6.8558 | 604.8 | 302.4 | 270.549 | 0 | 1
7/14 | 08:00:00 | 285.15 | 98841 | 4.1 | 280 | 7.3418 | 1396.8 | 1674 | 271.097 | 0 | 1
7/14 | 09:00:00 | 285.15 | 98841 | 4.6 | 300 | 6.8552 | 1947.6 | 2311.2 | 270.871 | 0 | 1
7/14 | 10:00:00 | 288.15 | 98867 | 6.2 | 300 | 6.8534 | 2278.8 | 2030.4 | 273.988 | 0 | 1
7/14 | 11:00:00 | 289.15 | 98875 | 6.7 | 310 | 5.9656 | 2617.2 | 2163.6 | 274.475 | 0 | 1
7/14 | 12:00:00 | 288.15 | 98867 | 7.7 | 290 | 6.396 | 2970 | 2617.2 | 273.49 | 0 | 1
7/14 | 13:00:00 | 288.15 | 98867 | 7.2 | 280 | 6.8534 | 2826 | 2206.8 | 273.988 | 0 | 1
7/14 | 14:00:00 | 289.15 | 98875 | 8.2 | 270 | 6.3955 | 2707.2 | 2257.2 | 274.708 | 0 | 1
7/14 | 15:00:00 | 286.15 | 98850 | 7.7 | 270 | 7.8584 | 2419.2 | 2041.2 | 272.541 | 0 | 1
7/14 | 16:00:00 | 286.15 | 98850 | 6.2 | 280 | 7.8584 | 2019.6 | 1933.2 | 272.541 | 0 | 1
7/14 | 17:00:00 | 288.15 | 98867 | 8.2 | 280 | 7.3399 | 1530 | 1641.6 | 274.218 | 0 | 1
7/14 | 18:00:00 | 288.15 | 98867 | 8.2 | 280 | 7.3399 | 1054.8 | 1407.6 | 273.95 | 0 | 1
7/14 | 19:00:00 | 288.15 | 98867 | 8.8 | 280 | 6.8534 | 525.6 | 576 | 273.72 | 0 | 1
7/14 | 20:00:00 | 286.15 | 98850 | 6.7 | 280 | 7.3412 | 140.4 | 18 | 272.048 | 0 | 1
7/14 | 21:00:00 | 285.15 | 98841 | 8.2 | 270 | 7.3418 | 0 | 0 | 271.097 | 0 | 1
7/14 | 22:00:00 | 284.15 | 98833 | 6.2 | 270 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
7/14 | 23:00:00 | 284.15 | 98833 | 5.7 | 280 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
7/14 | 24:00:00 | 283.15 | 98824 | 4.6 | 290 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
7/15 | 01:00:00 | 283.15 | 98824 | 5.1 | 290 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
7/15 | 02:00:00 | 283.15 | 98824 | 5.7 | 290 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
7/15 | 03:00:00 | 283.15 | 98824 | 5.1 | 290 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
7/15 | 04:00:00 | 282.15 | 98815 | 3.1 | 280 | 7.3438 | 0 | 0 | 268.245 | 0 | 1
7/15 | 05:00:00 | 282.15 | 98815 | 3.6 | 280 | 6.8571 | 57.6 | 0 | 268.021 | 0 | 1
7/15 | 06:00:00 | 283.15 | 98824 | 4.1 | 280 | 7.3431 | 338.4 | 320.4 | 269.196 | 0 | 1
7/15 | 07:00:00 | 284.15 | 98833 | 5.1 | 290 | 7.3425 | 824.4 | 1094.4 | 270.147 | 0 | 1
7/15 | 08:00:00 | 286.15 | 98850 | 4.6 | 300 | 7.8584 | 1386 | 1717.2 | 272.274 | 0 | 1
7/15 | 09:00:00 | 287.15 | 98858 | 4.6 | 310 | 7.8578 | 1933.2 | 2307.6 | 273.226 | 0 | 1
7/15 | 10:00:00 | 288.15 | 98867 | 4.1 | 300 | 7.857 | 2404.8 | 2534.4 | 274.177 | 0 | 1
7/15 | 11:00:00 | 288.15 | 98867 | 4.1 | 330 | 7.857 | 2595.6 | 2167.2 | 274.446 | 0 | 1
7/15 | 12:00:00 | 288.15 | 98867 | 2.6 | 350 | 7.857 | 2782.8 | 2253.6 | 274.446 | 0 | 1
7/15 | 13:00:00 | 290.15 | 98883 | 2.1 | 320 | 7.8557 | 2815.2 | 2260.8 | 276.351 | 0 | 1
7/15 | 14:00:00 | 290.15 | 98883 | 4.1 | 270 | 7.3387 | 2692.8 | 2246.4 | 276.121 | 0 | 1
7/15 | 15:00:00 | 292.15 | 98900 | 6.7 | 270 | 7.8544 | 2415.6 | 2041.2 | 278.256 | 0 | 1
7/15 | 16:00:00 | 292.15 | 98900 | 6.2 | 280 | 7.8544 | 2138.4 | 2412 | 277.983 | 0 | 1
7/15 | 17:00:00 | 291.15 | 98892 | 7.2 | 280 | 7.855 | 1616.4 | 1969.2 | 277.032 | 0 | 1
7/15 | 18:00:00 | 290.15 | 98883 | 7.2 | 290 | 7.8557 | 1047.6 | 1346.4 | 276.08 | 0 | 1
7/15 | 19:00:00 | 288.15 | 98867 | 7.2 | 270 | 7.3399 | 518.4 | 565.2 | 273.95 | 0 | 1
7/15 | 20:00:00 | 287.15 | 98858 | 6.7 | 280 | 7.3406 | 136.8 | 10.8 | 272.999 | 0 | 1
7/15 | 21:00:00 | 286.15 | 98850 | 6.2 | 270 | 7.8584 | 0 | 0 | 272.909 | 0 | 1
7/15 | 22:00:00 | 285.15 | 98841 | 5.7 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
7/15 | 23:00:00 | 285.15 | 98841 | 6.7 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
7/15 | 24:00:00 | 284.15 | 98833 | 5.1 | 280 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
7/16 | 01:00:00 | 284.15 | 98833 | 5.1 | 280 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
7/16 | 02:00:00 | 283.15 | 98824 | 3.6 | 280 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
7/16 | 03:00:00 | 284.15 | 98833 | 4.1 | 290 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
7/16 | 04:00:00 | 283.15 | 98824 | 2.1 | 240 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
7/16 | 05:00:00 | 284.15 | 98833 | 3.1 | 250 | 7.8598 | 21.6 | 0 | 271.225 | 0 | 1
7/16 | 06:00:00 | 285.15 | 98841 | 3.6 | 250 | 7.8591 | 194.4 | 0 | 272.069 | 0 | 1
7/16 | 07:00:00 | 285.15 | 98841 | 2.6 | 240 | 7.8591 | 471.6 | 50.4 | 272.069 | 0 | 1
7/16 | 08:00:00 | 286.15 | 98850 | 3.6 | 230 | 7.3412 | 1126.8 | 856.8 | 272.563 | 0 | 1
7/16 | 09:00:00 | 286.15 | 98850 | 4.1 | 230 | 7.3412 | 1008 | 68.4 | 272.796 | 0 | 1
7/16 | 10:00:00 | 287.15 | 98858 | 4.6 | 200 | 7.8578 | 1252.8 | 205.2 | 273.977 | 0 | 1
7/16 | 11:00:00 | 287.15 | 98858 | 4.1 | 220 | 8.4073 | 1432.8 | 154.8 | 274.203 | 0 | 1
7/16 | 12:00:00 | 288.15 | 98867 | 3.6 | 220 | 8.9902 | 1533.6 | 158.4 | 275.384 | 0 | 1
7/16 | 13:00:00 | 288.15 | 98867 | 5.7 | 230 | 9.6099 | 1551.6 | 154.8 | 275.608 | 0 | 1
7/16 | 14:00:00 | 288.15 | 98867 | 3.6 | 230 | 10.2677 | 1479.6 | 154.8 | 275.831 | 0 | 1
7/16 | 15:00:00 | 290.15 | 98883 | 3.6 | 240 | 10.9637 | 1328.4 | 104.4 | 277.969 | 0 | 1
7/16 | 16:00:00 | 289.15 | 98875 | 3.1 | 240 | 10.9646 | 1105.2 | 97.2 | 277.011 | 0 | 1
7/16 | 17:00:00 | 290.15 | 98883 | 4.1 | 230 | 11.7037 | 835.2 | 75.6 | 278.191 | 0 | 1
7/16 | 18:00:00 | 291.15 | 98892 | 3.6 | 250 | 12.4871 | 540 | 75.6 | 279.371 | 0 | 1
7/16 | 19:00:00 | 291.15 | 98892 | 5.1 | 260 | 12.4871 | 266.4 | 0 | 279.371 | 0 | 1
7/16 | 20:00:00 | 291.15 | 98892 | 4.6 | 230 | 12.4871 | 126 | 0 | 278.878 | 0 | 1
7/16 | 21:00:00 | 290.15 | 98883 | 4.6 | 250 | 11.7037 | 0 | 0 | 277.428 | 0 | 1
7/16 | 22:00:00 | 290.15 | 98883 | 4.1 | 220 | 11.7037 | 0 | 0 | 277.7 | 0 | 1
7/16 | 23:00:00 | 290.15 | 98883 | 4.1 | 240 | 11.7037 | 0 | 0 | 277.7 | 0 | 1
7/16 | 24:00:00 | 290.15 | 98883 | 5.1 | 240 | 10.9637 | 0 | 0 | 277.478 | 0 | 1
7/17 | 01:00:00 | 289.15 | 98875 | 7.2 | 250 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
7/17 | 02:00:00 | 289.15 | 98875 | 7.2 | 260 | 11.7047 | 0 | 0 | 276.743 | 0 | 1
7/17 | 03:00:00 | 289.15 | 98875 | 6.2 | 260 | 11.7047 | 0 | 0 | 276.743 | 0 | 1
7/17 | 04:00:00 | 289.15 | 98875 | 5.1 | 250 | 11.7047 | 0 | 0 | 277.232 | 0 | 1
7/17 | 05:00:00 | 289.15 | 98875 | 3.6 | 260 | 10.9646 | 28.8 | 0 | 277.011 | 0 | 1
7/17 | 06:00:00 | 288.15 | 98867 | 4.6 | 290 | 10.9655 | 169.2 | 0 | 276.053 | 0 | 1
7/17 | 07:00:00 | 287.15 | 98858 | 5.1 | 280 | 10.2686 | 417.6 | 14.4 | 274.874 | 0 | 1
7/17 | 08:00:00 | 288.15 | 98867 | 3.6 | 250 | 9.6099 | 712.8 | 61.2 | 275.608 | 0 | 1
7/17 | 09:00:00 | 287.15 | 98858 | 3.6 | 250 | 9.6108 | 997.2 | 72 | 274.652 | 0 | 1
7/17 | 10:00:00 | 287.15 | 98858 | 3.1 | 230 | 9.6108 | 1245.6 | 104.4 | 274.652 | 0 | 1
7/17 | 11:00:00 | 288.15 | 98867 | 5.1 | 260 | 9.6099 | 1425.6 | 151.2 | 275.608 | 0 | 1
7/17 | 12:00:00 | 289.15 | 98875 | 5.7 | 250 | 9.6091 | 1530 | 154.8 | 276.565 | 0 | 1
7/17 | 13:00:00 | 290.15 | 98883 | 6.2 | 260 | 9.6084 | 1548 | 367.2 | 277.521 | 0 | 1
7/17 | 14:00:00 | 291.15 | 98892 | 7.7 | 250 | 9.6075 | 2667.6 | 1832.4 | 277.986 | 0 | 1
7/17 | 15:00:00 | 291.15 | 98892 | 8.2 | 250 | 9.6075 | 2394 | 2012.4 | 277.986 | 0 | 1
7/17 | 16:00:00 | 290.15 | 98883 | 8.2 | 260 | 9.6084 | 1994.4 | 1972.8 | 277.031 | 0 | 1
7/17 | 17:00:00 | 290.15 | 98883 | 7.7 | 260 | 9.6084 | 1504.8 | 1641.6 | 277.031 | 0 | 1
7/17 | 18:00:00 | 290.15 | 98883 | 7.7 | 280 | 8.9887 | 972 | 1198.8 | 276.806 | 0 | 1
7/17 | 19:00:00 | 289.15 | 98875 | 6.7 | 290 | 8.4059 | 478.8 | 522 | 275.626 | 0 | 1
7/17 | 20:00:00 | 288.15 | 98867 | 7.7 | 280 | 8.4065 | 129.6 | 0 | 274.404 | 0 | 1
7/17 | 21:00:00 | 287.15 | 98858 | 5.7 | 270 | 8.4073 | 0 | 0 | 273.451 | 0 | 1
7/17 | 22:00:00 | 287.15 | 98858 | 5.7 | 260 | 8.991 | 0 | 0 | 274.428 | 0 | 1
7/17 | 23:00:00 | 286.15 | 98850 | 5.7 | 260 | 8.9918 | 0 | 0 | 273.583 | 0 | 1
7/17 | 24:00:00 | 286.15 | 98850 | 5.1 | 270 | 8.9918 | 0 | 0 | 273.583 | 0 | 1
7/18 | 01:00:00 | 286.15 | 98850 | 5.1 | 280 | 9.6116 | 0 | 0 | 273.806 | 0 | 1
7/18 | 02:00:00 | 287.15 | 98858 | 6.2 | 260 | 10.2686 | 0 | 0 | 274.985 | 0 | 1
7/18 | 03:00:00 | 287.15 | 98858 | 5.7 | 260 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
7/18 | 04:00:00 | 287.15 | 98858 | 6.2 | 260 | 8.991 | 0 | 0 | 273.676 | 0 | 1
7/18 | 05:00:00 | 286.15 | 98850 | 7.2 | 270 | 8.9918 | 50.4 | 0 | 272.723 | 0 | 1
7/18 | 06:00:00 | 286.15 | 98850 | 7.7 | 270 | 8.408 | 316.8 | 345.6 | 272.499 | 0 | 1
7/18 | 07:00:00 | 286.15 | 98850 | 7.2 | 270 | 8.408 | 795.6 | 1047.6 | 272.499 | 0 | 1
7/18 | 08:00:00 | 287.15 | 98858 | 8.8 | 270 | 8.4073 | 1281.6 | 1486.8 | 273.719 | 0 | 1
7/18 | 09:00:00 | 288.15 | 98867 | 7.2 | 270 | 8.4065 | 1796.4 | 1782 | 274.672 | 0 | 1
7/18 | 10:00:00 | 288.15 | 98867 | 9.3 | 270 | 8.4065 | 2379.6 | 2426.4 | 274.404 | 0 | 1
7/18 | 11:00:00 | 289.15 | 98875 | 7.2 | 250 | 8.4059 | 2728.8 | 2732.4 | 275.356 | 0 | 1
7/18 | 12:00:00 | 291.15 | 98892 | 7.2 | 260 | 8.4044 | 2926.8 | 2800.8 | 277.261 | 0 | 1
7/18 | 13:00:00 | 290.15 | 98883 | 8.2 | 250 | 7.8557 | 2966.4 | 2811.6 | 276.08 | 0 | 1
7/18 | 14:00:00 | 290.15 | 98883 | 7.7 | 280 | 8.4052 | 2829.6 | 2772 | 276.308 | 0 | 1
7/18 | 15:00:00 | 291.15 | 98892 | 7.7 | 270 | 8.4044 | 2541.6 | 2595.6 | 277.261 | 0 | 1
7/18 | 16:00:00 | 291.15 | 98892 | 7.2 | 270 | 8.9879 | 2113.2 | 2322 | 277.488 | 0 | 1
7/18 | 17:00:00 | 292.15 | 98900 | 6.7 | 260 | 8.9872 | 1522.8 | 1720.8 | 278.714 | 0 | 1
7/18 | 18:00:00 | 292.15 | 98900 | 8.2 | 270 | 8.4037 | 1008 | 1364.4 | 278.351 | 0 | 1
7/18 | 19:00:00 | 291.15 | 98892 | 7.7 | 270 | 7.855 | 493.2 | 507.6 | 277.17 | 0 | 1
7/18 | 20:00:00 | 290.15 | 98883 | 4.6 | 270 | 7.8557 | 122.4 | 0 | 276.351 | 0 | 1
7/18 | 21:00:00 | 289.15 | 98875 | 3.6 | 270 | 8.4059 | 0 | 0 | 275.754 | 0 | 1
7/18 | 22:00:00 | 288.15 | 98867 | 6.2 | 280 | 8.4065 | 0 | 0 | 274.924 | 0 | 1
7/18 | 23:00:00 | 288.15 | 98867 | 4.1 | 290 | 8.9902 | 0 | 0 | 275.269 | 0 | 1
7/18 | 24:00:00 | 288.15 | 98867 | 4.6 | 280 | 9.6099 | 0 | 0 | 275.608 | 0 | 1
7/19 | 01:00:00 | 288.15 | 98867 | 2.1 | 270 | 10.2677 | 0 | 0 | 275.943 | 0 | 1
7/19 | 02:00:00 | 288.15 | 98867 | 6.2 | 270 | 10.2677 | 0 | 0 | 275.943 | 0 | 1
7/19 | 03:00:00 | 288.15 | 98867 | 6.2 | 270 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
7/19 | 04:00:00 | 288.15 | 98867 | 7.7 | 270 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
7/19 | 05:00:00 | 288.15 | 98867 | 8.2 | 270 | 10.9655 | 46.8 | 0 | 275.565 | 0 | 1
7/19 | 06:00:00 | 289.15 | 98875 | 5.7 | 270 | 10.9646 | 162 | 0 | 277.011 | 0 | 1
7/19 | 07:00:00 | 289.15 | 98875 | 4.6 | 260 | 11.7047 | 406.8 | 10.8 | 277.232 | 0 | 1
7/19 | 08:00:00 | 289.15 | 98875 | 5.7 | 260 | 11.7047 | 698.4 | 61.2 | 277.232 | 0 | 1
7/19 | 09:00:00 | 290.15 | 98883 | 5.7 | 260 | 12.4883 | 982.8 | 270 | 278.412 | 0 | 1
7/19 | 10:00:00 | 292.15 | 98900 | 6.2 | 270 | 12.4861 | 2214 | 1918.8 | 279.836 | 0 | 1
7/19 | 11:00:00 | 294.15 | 98916 | 7.7 | 260 | 12.484 | 2541.6 | 2275.2 | 281.751 | 0 | 1
7/19 | 12:00:00 | 295.15 | 98924 | 6.2 | 260 | 13.3141 | 2890.8 | 2786.4 | 282.655 | 0 | 1
7/19 | 13:00:00 | 296.15 | 98932 | 6.2 | 270 | 12.482 | 2930.4 | 2779.2 | 283.389 | 0 | 1
7/19 | 14:00:00 | 296.15 | 98932 | 5.7 | 280 | 12.482 | 2638.8 | 2286 | 283.667 | 0 | 1
7/19 | 15:00:00 | 297.15 | 98940 | 3.6 | 270 | 12.4809 | 2368.8 | 2170.8 | 284.625 | 0 | 1
7/19 | 16:00:00 | 297.15 | 98940 | 3.1 | 260 | 12.4809 | 1972.8 | 2095.2 | 284.625 | 0 | 1
7/19 | 17:00:00 | 297.15 | 98940 | 3.1 | 260 | 13.3119 | 1479.6 | 1717.2 | 284.849 | 0 | 1
7/19 | 18:00:00 | 297.15 | 98940 | 3.1 | 260 | 12.4809 | 954 | 1245.6 | 284.625 | 0 | 1
7/19 | 19:00:00 | 297.15 | 98940 | 3.1 | 300 | 13.3119 | 489.6 | 658.8 | 284.57 | 0 | 1
7/19 | 20:00:00 | 295.15 | 98924 | 3.1 | 310 | 12.483 | 118.8 | 0 | 282.433 | 0 | 1
7/19 | 21:00:00 | 294.15 | 98916 | 2.6 | 310 | 12.484 | 0 | 0 | 281.476 | 0 | 1
7/19 | 22:00:00 | 292.15 | 98900 | 0.5 | 298 | 12.4861 | 0 | 0 | 280.331 | 0 | 1
7/19 | 23:00:00 | 292.15 | 98900 | 0.5 | 350 | 12.4861 | 0 | 0 | 279.562 | 0 | 1
7/19 | 24:00:00 | 291.15 | 98892 | 1.5 | 290 | 11.7026 | 0 | 0 | 279.15 | 0 | 1
7/20 | 01:00:00 | 291.15 | 98892 | 0.5 | 320 | 11.7026 | 0 | 0 | 279.15 | 0 | 1
7/20 | 02:00:00 | 290.15 | 98883 | 0 | 103 | 11.7037 | 0 | 0 | 278.304 | 0 | 1
7/20 | 03:00:00 | 290.15 | 98883 | 0.5 | 199 | 11.7037 | 0 | 0 | 278.304 | 0 | 1
7/20 | 04:00:00 | 290.15 | 98883 | 1 | 128 | 11.7037 | 0 | 0 | 278.304 | 0 | 1
7/20 | 05:00:00 | 290.15 | 98883 | 1 | 58 | 11.7037 | 18 | 0 | 278.304 | 0 | 1
7/20 | 06:00:00 | 291.15 | 98892 | 1.5 | 60 | 11.7026 | 176.4 | 0 | 279.15 | 0 | 1
7/20 | 07:00:00 | 292.15 | 98900 | 1.5 | 36 | 12.4861 | 446.4 | 75.6 | 280.331 | 0 | 1
7/20 | 08:00:00 | 294.15 | 98916 | 1.5 | 152 | 13.3152 | 932.4 | 511.2 | 282.354 | 0 | 1
7/20 | 09:00:00 | 296.15 | 98932 | 2.1 | 120 | 13.313 | 1872 | 2181.6 | 283.613 | 0 | 1
7/20 | 10:00:00 | 297.15 | 98940 | 2.6 | 130 | 13.3119 | 2336.4 | 2610 | 284.57 | 0 | 1
7/20 | 11:00:00 | 298.15 | 98948 | 4.1 | 160 | 13.3108 | 2685.6 | 2790 | 285.528 | 0 | 1
7/20 | 12:00:00 | 300.15 | 98964 | 4.1 | 150 | 12.4778 | 2887.2 | 2858.4 | 287.217 | 0 | 1
7/20 | 13:00:00 | 300.15 | 98964 | 3.6 | 170 | 12.4778 | 2923.2 | 2872.8 | 287.217 | 0 | 1
7/20 | 14:00:00 | 301.15 | 98971 | 3.6 | 170 | 10.9538 | 2800.8 | 2775.6 | 287.716 | 0 | 1
7/20 | 15:00:00 | 301.15 | 98971 | 5.1 | 140 | 10.9538 | 2545.2 | 2754 | 287.568 | 0 | 1
7/20 | 16:00:00 | 301.15 | 98971 | 5.7 | 130 | 10.9538 | 2116.8 | 2509.2 | 287.568 | 0 | 1
7/20 | 17:00:00 | 301.15 | 98971 | 4.6 | 140 | 10.9538 | 1591.2 | 2106 | 287.568 | 0 | 1
7/20 | 18:00:00 | 301.15 | 98971 | 5.7 | 140 | 11.6931 | 1015.2 | 1306.8 | 287.798 | 0 | 1
7/20 | 19:00:00 | 300.15 | 98964 | 5.1 | 140 | 12.4778 | 482.4 | 655.2 | 287.217 | 0 | 1
7/20 | 20:00:00 | 298.15 | 98948 | 4.6 | 100 | 14.1913 | 108 | 0 | 286.164 | 0 | 1
7/20 | 21:00:00 | 297.15 | 98940 | 4.1 | 110 | 14.1924 | 0 | 0 | 285.205 | 0 | 1
7/20 | 22:00:00 | 296.15 | 98932 | 4.6 | 120 | 13.313 | 0 | 0 | 284.022 | 0 | 1
7/20 | 23:00:00 | 296.15 | 98932 | 4.6 | 130 | 13.313 | 0 | 0 | 284.022 | 0 | 1
7/20 | 24:00:00 | 295.15 | 98924 | 4.6 | 130 | 13.3141 | 0 | 0 | 283.191 | 0 | 1
7/21 | 01:00:00 | 294.15 | 98916 | 4.6 | 140 | 12.484 | 0 | 0 | 282.009 | 0 | 1
7/21 | 02:00:00 | 293.15 | 98908 | 3.6 | 130 | 12.485 | 0 | 0 | 281.172 | 0 | 1
7/21 | 03:00:00 | 292.15 | 98900 | 2.6 | 80 | 12.4861 | 0 | 0 | 280.331 | 0 | 1
7/21 | 04:00:00 | 290.15 | 98883 | 2.6 | 70 | 11.7037 | 0 | 0 | 276.985 | 0 | 1
7/21 | 05:00:00 | 290.15 | 98883 | 3.1 | 60 | 11.7037 | 46.8 | 0 | 276.985 | 0 | 1
7/21 | 06:00:00 | 290.15 | 98883 | 4.6 | 70 | 11.7037 | 298.8 | 324 | 276.985 | 0 | 1
7/21 | 07:00:00 | 291.15 | 98892 | 3.6 | 80 | 12.4871 | 774 | 1184.4 | 278.16 | 0 | 1
7/21 | 08:00:00 | 293.15 | 98908 | 1.5 | 92 | 12.485 | 1317.6 | 1864.8 | 280.519 | 0 | 1
7/21 | 09:00:00 | 294.15 | 98916 | 0 | 238 | 13.3152 | 1861.2 | 2383.2 | 281.697 | 0 | 1
7/21 | 10:00:00 | 294.15 | 98916 | 3.6 | 340 | 13.3152 | 2329.2 | 2602.8 | 281.697 | 0 | 1
7/21 | 11:00:00 | 295.15 | 98924 | 5.1 | 20 | 13.3141 | 2678.4 | 2732.4 | 282.655 | 0 | 1
7/21 | 12:00:00 | 296.15 | 98932 | 5.1 | 20 | 10.9582 | 2725.2 | 2203.2 | 283.216 | 0 | 1
7/21 | 13:00:00 | 295.15 | 98924 | 4.1 | 300 | 12.483 | 2750.4 | 2228.4 | 282.709 | 0 | 1
7/21 | 14:00:00 | 297.15 | 98940 | 7.2 | 290 | 11.6968 | 2790 | 2725.2 | 284.121 | 0 | 1
7/21 | 15:00:00 | 297.15 | 98940 | 6.7 | 290 | 10.9573 | 2505.6 | 2642.4 | 283.894 | 0 | 1
7/21 | 16:00:00 | 297.15 | 98940 | 7.2 | 290 | 11.6968 | 2080.8 | 2433.6 | 284.121 | 0 | 1
7/21 | 17:00:00 | 296.15 | 98932 | 7.7 | 270 | 10.9582 | 1562.4 | 2008.8 | 282.939 | 0 | 1
7/21 | 18:00:00 | 295.15 | 98924 | 8.8 | 280 | 10.9591 | 1000.8 | 1263.6 | 281.984 | 0 | 1
7/21 | 19:00:00 | 294.15 | 98916 | 6.7 | 280 | 10.96 | 478.8 | 608.4 | 281.028 | 0 | 1
7/21 | 20:00:00 | 292.15 | 98900 | 6.2 | 270 | 10.9618 | 104.4 | 0 | 279.391 | 0 | 1
7/21 | 21:00:00 | 290.15 | 98883 | 4.6 | 270 | 10.9637 | 0 | 0 | 277.207 | 0 | 1
7/21 | 22:00:00 | 290.15 | 98883 | 3.1 | 260 | 10.266 | 0 | 0 | 277.255 | 0 | 1
7/21 | 23:00:00 | 289.15 | 98875 | 5.7 | 280 | 10.2668 | 0 | 0 | 276.029 | 0 | 1
7/21 | 24:00:00 | 288.15 | 98867 | 6.2 | 270 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
7/22 | 01:00:00 | 287.15 | 98858 | 4.1 | 270 | 9.6108 | 0 | 0 | 274.763 | 0 | 1
7/22 | 02:00:00 | 287.15 | 98858 | 4.6 | 260 | 9.6108 | 0 | 0 | 274.763 | 0 | 1
7/22 | 03:00:00 | 287.15 | 98858 | 2.6 | 250 | 9.6108 | 0 | 0 | 274.763 | 0 | 1
7/22 | 04:00:00 | 287.15 | 98858 | 2.1 | 250 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
7/22 | 05:00:00 | 287.15 | 98858 | 1.5 | 314 | 9.6108 | 39.6 | 0 | 274.167 | 0 | 1
7/22 | 06:00:00 | 287.15 | 98858 | 3.1 | 270 | 9.6108 | 288 | 295.2 | 273.899 | 0 | 1
7/22 | 07:00:00 | 288.15 | 98867 | 3.6 | 270 | 10.2677 | 756 | 993.6 | 275.075 | 0 | 1
7/22 | 08:00:00 | 289.15 | 98875 | 3.6 | 290 | 9.6091 | 1317.6 | 1753.2 | 275.806 | 0 | 1
7/22 | 09:00:00 | 290.15 | 98883 | 4.1 | 250 | 9.6084 | 1864.8 | 2275.2 | 276.76 | 0 | 1
7/22 | 10:00:00 | 292.15 | 98900 | 4.1 | 270 | 9.6067 | 2203.2 | 2048.4 | 278.941 | 0 | 1
7/22 | 11:00:00 | 291.15 | 98892 | 2.6 | 240 | 8.9879 | 2538 | 1814.4 | 277.76 | 0 | 1
7/22 | 12:00:00 | 292.15 | 98900 | 2.6 | 240 | 9.6067 | 2725.2 | 2242.8 | 278.941 | 0 | 1
7/22 | 13:00:00 | 292.15 | 98900 | 3.1 | 250 | 9.6067 | 2757.6 | 2250 | 278.941 | 0 | 1
7/22 | 14:00:00 | 293.15 | 98908 | 3.6 | 250 | 11.7007 | 2624.4 | 1789.2 | 280.571 | 0 | 1
7/22 | 15:00:00 | 292.15 | 98900 | 3.6 | 250 | 12.4861 | 2347.2 | 2167.2 | 279.836 | 0 | 1
7/22 | 16:00:00 | 292.15 | 98900 | 3.6 | 250 | 13.3174 | 1947.6 | 2073.6 | 280.056 | 0 | 1
7/22 | 17:00:00 | 293.15 | 98908 | 2.6 | 250 | 14.1971 | 1454.4 | 1692 | 281.235 | 0 | 1
7/22 | 18:00:00 | 292.15 | 98900 | 3.1 | 260 | 14.1983 | 928.8 | 1108.8 | 280.275 | 0 | 1
7/22 | 19:00:00 | 292.15 | 98900 | 1.5 | 285 | 14.1983 | 442.8 | 489.6 | 280.275 | 0 | 1
7/22 | 20:00:00 | 291.15 | 98892 | 1 | 240 | 13.3185 | 100.8 | 0 | 279.097 | 0 | 1
7/22 | 21:00:00 | 291.15 | 98892 | 1 | 270 | 13.3185 | 0 | 0 | 279.097 | 0 | 1
7/22 | 22:00:00 | 290.15 | 98883 | 2.1 | 270 | 12.4883 | 0 | 0 | 277.92 | 0 | 1
7/22 | 23:00:00 | 290.15 | 98883 | 2.1 | 260 | 12.2481 | 0 | 0 | 277.854 | 0 | 1
7/22 | 24:00:00 | 289.15 | 98875 | 2.1 | 280 | 11.7047 | 0 | 0 | 276.743 | 0 | 1
7/23 | 01:00:00 | 289.15 | 98875 | 0 | 126 | 11.7047 | 0 | 0 | 277.345 | 0 | 1
7/23 | 02:00:00 | 289.15 | 98875 | 1.5 | 270 | 11.7047 | 0 | 0 | 276.472 | 0 | 1
7/23 | 03:00:00 | 289.15 | 98875 | 1.5 | 250 | 11.7047 | 0 | 0 | 276.472 | 0 | 1
7/23 | 04:00:00 | 288.15 | 98867 | 1.5 | 150 | 10.9655 | 0 | 0 | 275.296 | 0 | 1
7/23 | 05:00:00 | 288.15 | 98867 | 1 | 220 | 10.9655 | 10.8 | 0 | 276.165 | 0 | 1
7/23 | 06:00:00 | 289.15 | 98875 | 1 | 260 | 11.7047 | 90 | 0 | 277.345 | 0 | 1
7/23 | 07:00:00 | 290.15 | 98883 | 1 | 279 | 12.4883 | 702 | 889.2 | 277.92 | 0 | 1
7/23 | 08:00:00 | 290.15 | 98883 | 2.6 | 230 | 11.7037 | 1227.6 | 1418.4 | 277.7 | 0 | 1
7/23 | 09:00:00 | 291.15 | 98892 | 2.1 | 230 | 10.9627 | 1746 | 1713.6 | 278.434 | 0 | 1
7/23 | 10:00:00 | 291.15 | 98892 | 2.6 | 200 | 11.7026 | 2318.4 | 2451.6 | 278.384 | 0 | 1
7/23 | 11:00:00 | 292.15 | 98900 | 3.1 | 240 | 11.7017 | 2671.2 | 2685.6 | 279.34 | 0 | 1
7/23 | 12:00:00 | 294.15 | 98916 | 3.1 | 180 | 12.484 | 2700 | 2224.8 | 281.751 | 0 | 1
7/23 | 13:00:00 | 295.15 | 98924 | 3.6 | 180 | 13.3141 | 2732.4 | 2322 | 282.932 | 0 | 1
7/23 | 14:00:00 | 295.15 | 98924 | 3.1 | 240 | 12.483 | 2613.6 | 2282.4 | 282.709 | 0 | 1
7/23 | 15:00:00 | 296.15 | 98932 | 2.6 | 220 | 13.313 | 2336.4 | 2214 | 283.89 | 0 | 1
7/23 | 16:00:00 | 297.15 | 98940 | 2.6 | 45 | 13.3119 | 2059.2 | 2480.4 | 284.57 | 0 | 1
7/23 | 17:00:00 | 296.15 | 98932 | 3.1 | 210 | 13.313 | 1540.8 | 2109.6 | 283.613 | 0 | 1
7/23 | 18:00:00 | 295.15 | 98924 | 2.6 | 230 | 13.3141 | 921.6 | 1108.8 | 282.932 | 0 | 1
7/23 | 19:00:00 | 293.15 | 98908 | 5.7 | 290 | 13.3163 | 460.8 | 640.8 | 280.74 | 0 | 1
7/23 | 20:00:00 | 292.15 | 98900 | 4.1 | 300 | 12.4861 | 61.2 | 0 | 280.331 | 0 | 1
7/23 | 21:00:00 | 291.15 | 98892 | 5.7 | 280 | 12.4871 | 0 | 0 | 279.484 | 0 | 1
7/23 | 22:00:00 | 290.15 | 98883 | 4.1 | 270 | 11.7037 | 0 | 0 | 278.304 | 0 | 1
7/23 | 23:00:00 | 290.15 | 98883 | 4.1 | 270 | 11.7037 | 0 | 0 | 278.304 | 0 | 1
7/23 | 24:00:00 | 289.15 | 98875 | 1.5 | 234 | 11.7047 | 0 | 0 | 276.743 | 0 | 1
7/24 | 01:00:00 | 289.15 | 98875 | 1.5 | 300 | 11.7047 | 0 | 0 | 276.743 | 0 | 1
7/24 | 02:00:00 | 289.15 | 98875 | 2.1 | 260 | 11.7047 | 0 | 0 | 276.743 | 0 | 1
7/24 | 03:00:00 | 288.15 | 98867 | 3.6 | 280 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
7/24 | 04:00:00 | 287.15 | 98858 | 3.6 | 290 | 10.2686 | 0 | 0 | 274.389 | 0 | 1
7/24 | 05:00:00 | 287.15 | 98858 | 3.1 | 280 | 10.2686 | 36 | 0 | 274.389 | 0 | 1
7/24 | 06:00:00 | 287.15 | 98858 | 3.6 | 290 | 10.2686 | 259.2 | 194.4 | 274.389 | 0 | 1
7/24 | 07:00:00 | 288.15 | 98867 | 2.1 | 260 | 10.2677 | 694.8 | 802.8 | 275.344 | 0 | 1
7/24 | 08:00:00 | 289.15 | 98875 | 2.1 | 300 | 10.9646 | 1296 | 1548 | 276.251 | 0 | 1
7/24 | 09:00:00 | 290.15 | 98883 | 1.5 | 275 | 10.9637 | 1843.2 | 2282.4 | 277.207 | 0 | 1
7/24 | 10:00:00 | 292.15 | 98900 | 3.1 | 280 | 10.9618 | 2181.6 | 1782 | 279.391 | 0 | 1
7/24 | 11:00:00 | 292.15 | 98900 | 2.1 | 260 | 11.7017 | 1393.2 | 352.8 | 280.109 | 0 | 1
7/24 | 12:00:00 | 292.15 | 98900 | 1.5 | 127 | 11.7017 | 1497.6 | 360 | 280.109 | 0 | 1
7/24 | 13:00:00 | 293.15 | 98908 | 3.6 | 290 | 12.485 | 2728.8 | 1936.8 | 280.793 | 0 | 1
7/24 | 14:00:00 | 293.15 | 98908 | 3.6 | 260 | 11.7007 | 2610 | 2059.2 | 280.571 | 0 | 1
7/24 | 15:00:00 | 295.15 | 98924 | 3.6 | 250 | 12.483 | 2476.8 | 2512.8 | 282.433 | 0 | 1
7/24 | 16:00:00 | 294.15 | 98916 | 3.1 | 240 | 11.6997 | 1936.8 | 1832.4 | 281.528 | 0 | 1
7/24 | 17:00:00 | 294.15 | 98916 | 2.6 | 270 | 12.484 | 1443.6 | 1558.8 | 281.751 | 0 | 1
7/24 | 18:00:00 | 294.15 | 98916 | 2.6 | 280 | 12.484 | 777.6 | 576 | 282.009 | 0 | 1
7/24 | 19:00:00 | 293.15 | 98908 | 2.6 | 300 | 11.7007 | 363.6 | 198 | 280.828 | 0 | 1
7/24 | 20:00:00 | 292.15 | 98900 | 2.6 | 310 | 11.7017 | 68.4 | 0 | 279.991 | 0 | 1
7/24 | 21:00:00 | 290.15 | 98883 | 4.1 | 310 | 10.9637 | 0 | 0 | 277.969 | 0 | 1
7/24 | 22:00:00 | 289.15 | 98875 | 4.6 | 300 | 10.9646 | 0 | 0 | 276.251 | 0 | 1
7/24 | 23:00:00 | 289.15 | 98875 | 3.6 | 290 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
7/24 | 24:00:00 | 289.15 | 98875 | 3.1 | 290 | 10.2668 | 0 | 0 | 276.029 | 0 | 1
7/25 | 01:00:00 | 288.15 | 98867 | 2.1 | 290 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
7/25 | 02:00:00 | 288.15 | 98867 | 3.1 | 290 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
7/25 | 03:00:00 | 287.15 | 98858 | 2.1 | 270 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
7/25 | 04:00:00 | 286.15 | 98850 | 2.1 | 280 | 9.6116 | 0 | 0 | 272.945 | 0 | 1
7/25 | 05:00:00 | 286.15 | 98850 | 1.5 | 260 | 8.9918 | 32.4 | 0 | 272.99 | 0 | 1
7/25 | 06:00:00 | 288.15 | 98867 | 2.1 | 260 | 9.6099 | 252 | 198 | 275.122 | 0 | 1
7/25 | 07:00:00 | 288.15 | 98867 | 3.1 | 260 | 10.2677 | 687.6 | 795.6 | 275.344 | 0 | 1
7/25 | 08:00:00 | 290.15 | 98883 | 1 | 237 | 10.9637 | 1213.2 | 1270.8 | 277.478 | 0 | 1
7/25 | 09:00:00 | 291.15 | 98892 | 2.1 | 220 | 10.9627 | 1832.4 | 2102.4 | 278.162 | 0 | 1
7/25 | 10:00:00 | 292.15 | 98900 | 2.1 | 220 | 11.7017 | 2170.8 | 2019.6 | 279.614 | 0 | 1
7/25 | 11:00:00 | 292.15 | 98900 | 3.1 | 170 | 11.7017 | 2502 | 1782 | 279.614 | 0 | 1
7/25 | 12:00:00 | 293.15 | 98908 | 3.1 | 210 | 12.485 | 2685.6 | 2289.6 | 280.793 | 0 | 1
7/25 | 13:00:00 | 292.15 | 98900 | 4.1 | 260 | 12.4861 | 2721.6 | 2296.8 | 279.836 | 0 | 1
7/25 | 14:00:00 | 293.15 | 98908 | 4.1 | 200 | 12.485 | 2599.2 | 2282.4 | 280.793 | 0 | 1
7/25 | 15:00:00 | 292.15 | 98900 | 3.1 | 210 | 11.7017 | 2329.2 | 1807.2 | 279.614 | 0 | 1
7/25 | 16:00:00 | 292.15 | 98900 | 2.6 | 200 | 12.4861 | 1069.2 | 288 | 280.331 | 0 | 1
7/25 | 17:00:00 | 292.15 | 98900 | 3.6 | 220 | 11.7017 | 799.2 | 72 | 280.109 | 0 | 1
7/25 | 18:00:00 | 291.15 | 98892 | 1.5 | 220 | 12.4871 | 504 | 68.4 | 279.371 | 0 | 1
7/25 | 19:00:00 | 291.15 | 98892 | 4.6 | 220 | 12.4871 | 421.2 | 486 | 278.878 | 0 | 1
7/25 | 20:00:00 | 291.15 | 98892 | 3.1 | 200 | 12.4871 | 86.4 | 0 | 278.878 | 0 | 1
7/25 | 21:00:00 | 290.15 | 98883 | 2.6 | 230 | 12.4883 | 0 | 0 | 277.92 | 0 | 1
7/25 | 22:00:00 | 289.15 | 98875 | 4.1 | 260 | 10.2668 | 0 | 0 | 276.029 | 0 | 1
7/25 | 23:00:00 | 288.15 | 98867 | 2.6 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
7/25 | 24:00:00 | 288.15 | 98867 | 4.6 | 250 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
7/26 | 01:00:00 | 288.15 | 98867 | 4.6 | 260 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
7/26 | 02:00:00 | 287.15 | 98858 | 5.1 | 260 | 10.2686 | 0 | 0 | 274.12 | 0 | 1
7/26 | 03:00:00 | 287.15 | 98858 | 4.1 | 260 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
7/26 | 04:00:00 | 286.15 | 98850 | 3.6 | 260 | 9.6116 | 0 | 0 | 272.945 | 0 | 1
7/26 | 05:00:00 | 286.15 | 98850 | 3.1 | 270 | 8.9918 | 32.4 | 0 | 272.723 | 0 | 1
7/26 | 06:00:00 | 286.15 | 98850 | 5.1 | 270 | 8.9918 | 259.2 | 262.8 | 272.723 | 0 | 1
7/26 | 07:00:00 | 287.15 | 98858 | 5.1 | 260 | 8.991 | 720 | 957.6 | 273.676 | 0 | 1
7/26 | 08:00:00 | 288.15 | 98867 | 6.7 | 260 | 9.6099 | 1206 | 1422 | 275.122 | 0 | 1
7/26 | 09:00:00 | 288.15 | 98867 | 6.2 | 260 | 8.9902 | 1728 | 1814.4 | 274.898 | 0 | 1
7/26 | 10:00:00 | 289.15 | 98875 | 6.2 | 260 | 8.9895 | 2174.4 | 2055.6 | 275.852 | 0 | 1
7/26 | 11:00:00 | 290.15 | 98883 | 6.7 | 260 | 8.9887 | 2509.2 | 1814.4 | 276.806 | 0 | 1
7/26 | 12:00:00 | 288.15 | 98867 | 5.1 | 250 | 9.6099 | 2696.4 | 2239.2 | 275.122 | 0 | 1
7/26 | 13:00:00 | 288.15 | 98867 | 6.7 | 260 | 8.9902 | 2732.4 | 2250 | 274.898 | 0 | 1
7/26 | 14:00:00 | 288.15 | 98867 | 5.7 | 260 | 8.9902 | 2610 | 2228.4 | 274.898 | 0 | 1
7/26 | 15:00:00 | 290.15 | 98883 | 6.2 | 260 | 9.6084 | 2332.8 | 2008.8 | 277.031 | 0 | 1
7/26 | 16:00:00 | 290.15 | 98883 | 5.1 | 250 | 8.9887 | 1933.2 | 1958.4 | 276.806 | 0 | 1
7/26 | 17:00:00 | 289.15 | 98875 | 6.2 | 260 | 8.9895 | 1440 | 1609.2 | 275.852 | 0 | 1
7/26 | 18:00:00 | 290.15 | 98883 | 6.2 | 260 | 8.9887 | 903.6 | 1018.8 | 276.806 | 0 | 1
7/26 | 19:00:00 | 288.15 | 98867 | 5.1 | 260 | 8.9902 | 414 | 439.2 | 274.898 | 0 | 1
7/26 | 20:00:00 | 288.15 | 98867 | 6.2 | 260 | 8.9902 | 82.8 | 0 | 274.898 | 0 | 1
7/26 | 21:00:00 | 287.15 | 98858 | 4.1 | 250 | 8.991 | 0 | 0 | 273.676 | 0 | 1
7/26 | 22:00:00 | 286.15 | 98850 | 2.1 | 250 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
7/26 | 23:00:00 | 286.15 | 98850 | 1 | 202 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
7/26 | 24:00:00 | 285.15 | 98841 | 3.6 | 260 | 8.9926 | 0 | 0 | 272.627 | 0 | 1
7/27 | 01:00:00 | 285.15 | 98841 | 3.1 | 230 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
7/27 | 02:00:00 | 285.15 | 98841 | 2.6 | 240 | 8.9926 | 0 | 0 | 271.77 | 0 | 1
7/27 | 03:00:00 | 286.15 | 98850 | 3.1 | 250 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
7/27 | 04:00:00 | 285.15 | 98841 | 3.1 | 260 | 8.9926 | 0 | 0 | 271.77 | 0 | 1
7/27 | 05:00:00 | 286.15 | 98850 | 3.6 | 260 | 9.6116 | 28.8 | 0 | 272.945 | 0 | 1
7/27 | 06:00:00 | 286.15 | 98850 | 1.5 | 250 | 9.6116 | 237.6 | 176.4 | 273.212 | 0 | 1
7/27 | 07:00:00 | 287.15 | 98858 | 2.1 | 220 | 9.6108 | 370.8 | 3.6 | 274.652 | 0 | 1
7/27 | 08:00:00 | 289.15 | 98875 | 5.1 | 260 | 9.6091 | 1195.2 | 1116 | 276.076 | 0 | 1
7/27 | 09:00:00 | 289.15 | 98875 | 6.2 | 250 | 9.6091 | 1717.2 | 1796.4 | 276.076 | 0 | 1
7/27 | 10:00:00 | 291.15 | 98892 | 6.7 | 260 | 10.265 | 2160 | 2034 | 278.211 | 0 | 1
7/27 | 11:00:00 | 291.15 | 98892 | 6.2 | 260 | 9.6075 | 2494.8 | 1807.2 | 277.986 | 0 | 1
7/27 | 12:00:00 | 290.15 | 98883 | 5.1 | 230 | 9.6084 | 2685.6 | 2242.8 | 277.031 | 0 | 1
7/27 | 13:00:00 | 291.15 | 98892 | 3.1 | 260 | 10.265 | 2718 | 2246.4 | 278.211 | 0 | 1
7/27 | 14:00:00 | 291.15 | 98892 | 5.1 | 230 | 10.265 | 2595.6 | 2221.2 | 278.211 | 0 | 1
7/27 | 15:00:00 | 290.15 | 98883 | 4.6 | 230 | 10.266 | 2322 | 2001.6 | 277.255 | 0 | 1
7/27 | 16:00:00 | 291.15 | 98892 | 4.1 | 260 | 10.265 | 1918.8 | 1936.8 | 278.211 | 0 | 1
7/27 | 17:00:00 | 291.15 | 98892 | 3.6 | 250 | 10.265 | 1425.6 | 1591.2 | 278.211 | 0 | 1
7/27 | 18:00:00 | 290.15 | 98883 | 4.1 | 250 | 10.266 | 892.8 | 1116 | 277.255 | 0 | 1
7/27 | 19:00:00 | 290.15 | 98883 | 4.1 | 220 | 10.266 | 432 | 543.6 | 276.984 | 0 | 1
7/27 | 20:00:00 | 289.15 | 98875 | 4.1 | 230 | 10.2668 | 82.8 | 0 | 276.029 | 0 | 1
7/27 | 21:00:00 | 289.15 | 98875 | 3.6 | 210 | 10.2668 | 0 | 0 | 276.029 | 0 | 1
7/27 | 22:00:00 | 289.15 | 98875 | 3.1 | 200 | 10.2668 | 0 | 0 | 276.3 | 0 | 1
7/27 | 23:00:00 | 289.15 | 98875 | 3.1 | 190 | 10.2668 | 0 | 0 | 276.789 | 0 | 1
7/27 | 24:00:00 | 288.15 | 98867 | 3.6 | 200 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
7/28 | 01:00:00 | 288.15 | 98867 | 4.1 | 200 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
7/28 | 02:00:00 | 288.15 | 98867 | 5.1 | 210 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
7/28 | 03:00:00 | 289.15 | 98875 | 6.2 | 220 | 10.2668 | 0 | 0 | 276.789 | 0 | 1
7/28 | 04:00:00 | 288.15 | 98867 | 5.1 | 230 | 10.9655 | 0 | 0 | 276.053 | 0 | 1
7/28 | 05:00:00 | 288.15 | 98867 | 4.1 | 260 | 10.9655 | 14.4 | 0 | 276.053 | 0 | 1
7/28 | 06:00:00 | 288.15 | 98867 | 4.6 | 280 | 10.9655 | 126 | 0 | 276.053 | 0 | 1
7/28 | 07:00:00 | 288.15 | 98867 | 7.2 | 290 | 10.2677 | 658.8 | 921.6 | 275.344 | 0 | 1
7/28 | 08:00:00 | 289.15 | 98875 | 4.6 | 300 | 10.9646 | 1180.8 | 1393.2 | 276.522 | 0 | 1
7/28 | 09:00:00 | 289.15 | 98875 | 5.1 | 310 | 10.2668 | 1702.8 | 1774.8 | 276.3 | 0 | 1
7/28 | 10:00:00 | 290.15 | 98883 | 4.1 | 320 | 10.266 | 2149.2 | 2034 | 277.255 | 0 | 1
7/28 | 11:00:00 | 290.15 | 98883 | 3.6 | 300 | 10.266 | 2484 | 1796.4 | 277.255 | 0 | 1
7/28 | 12:00:00 | 291.15 | 98892 | 4.6 | 300 | 10.265 | 2674.8 | 2239.2 | 278.211 | 0 | 1
7/28 | 13:00:00 | 291.15 | 98892 | 5.7 | 280 | 10.265 | 2710.8 | 2246.4 | 278.211 | 0 | 1
7/28 | 14:00:00 | 292.15 | 98900 | 5.7 | 280 | 9.6067 | 2588.4 | 2224.8 | 278.941 | 0 | 1
7/28 | 15:00:00 | 292.15 | 98900 | 6.2 | 270 | 9.6067 | 2314.8 | 2008.8 | 278.941 | 0 | 1
7/28 | 16:00:00 | 292.15 | 98900 | 6.7 | 270 | 9.6067 | 1911.6 | 1872 | 278.941 | 0 | 1
7/28 | 17:00:00 | 291.15 | 98892 | 7.7 | 280 | 9.6075 | 1504.8 | 1972.8 | 277.714 | 0 | 1
7/28 | 18:00:00 | 290.15 | 98883 | 7.7 | 290 | 8.9887 | 939.6 | 1220.4 | 276.535 | 0 | 1
7/28 | 19:00:00 | 288.15 | 98867 | 5.7 | 270 | 8.9902 | 424.8 | 532.8 | 274.629 | 0 | 1
7/28 | 20:00:00 | 287.15 | 98858 | 6.2 | 290 | 8.991 | 79.2 | 0 | 273.676 | 0 | 1
7/28 | 21:00:00 | 286.15 | 98850 | 5.1 | 270 | 8.408 | 0 | 0 | 273.248 | 0 | 1
7/28 | 22:00:00 | 285.15 | 98841 | 5.1 | 280 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
7/28 | 23:00:00 | 285.15 | 98841 | 5.1 | 280 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
7/28 | 24:00:00 | 285.15 | 98841 | 4.6 | 290 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
7/29 | 01:00:00 | 285.15 | 98841 | 5.7 | 280 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
7/29 | 02:00:00 | 284.15 | 98833 | 5.1 | 280 | 8.4095 | 0 | 0 | 271.449 | 0 | 1
7/29 | 03:00:00 | 283.15 | 98824 | 3.1 | 280 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
7/29 | 04:00:00 | 283.15 | 98824 | 3.1 | 280 | 7.8605 | 0 | 0 | 269.42 | 0 | 1
7/29 | 05:00:00 | 284.15 | 98833 | 3.1 | 250 | 8.4095 | 21.6 | 0 | 270.595 | 0 | 1
7/29 | 06:00:00 | 285.15 | 98841 | 2.6 | 270 | 8.9926 | 237.6 | 223.2 | 271.77 | 0 | 1
7/29 | 07:00:00 | 286.15 | 98850 | 2.6 | 250 | 8.9918 | 691.2 | 925.2 | 272.723 | 0 | 1
7/29 | 08:00:00 | 287.15 | 98858 | 2.1 | 220 | 8.991 | 1249.2 | 1710 | 273.676 | 0 | 1
7/29 | 09:00:00 | 288.15 | 98867 | 3.1 | 210 | 8.4065 | 1803.6 | 2242.8 | 274.404 | 0 | 1
7/29 | 10:00:00 | 288.15 | 98867 | 2.1 | 180 | 8.9902 | 2149.2 | 1803.6 | 274.898 | 0 | 1
7/29 | 11:00:00 | 289.15 | 98875 | 3.6 | 200 | 8.9895 | 1378.8 | 104.4 | 276.34 | 0 | 1
7/29 | 12:00:00 | 287.15 | 98858 | 3.6 | 200 | 10.2686 | 1479.6 | 154.8 | 274.874 | 0 | 1
7/29 | 13:00:00 | 287.15 | 98858 | 3.6 | 190 | 9.6108 | 1501.2 | 154.8 | 274.652 | 0 | 1
7/29 | 14:00:00 | 287.15 | 98858 | 3.6 | 150 | 10.2686 | 1429.2 | 151.2 | 274.874 | 0 | 1
7/29 | 15:00:00 | 287.15 | 98858 | 3.6 | 150 | 10.2686 | 1278 | 104.4 | 274.874 | 0 | 1
7/29 | 16:00:00 | 286.15 | 98850 | 3.6 | 150 | 9.6116 | 1054.8 | 93.6 | 273.695 | 0 | 1
7/29 | 17:00:00 | 286.15 | 98850 | 3.6 | 160 | 9.6116 | 781.2 | 93.6 | 273.695 | 0 | 1
7/29 | 18:00:00 | 287.15 | 98858 | 3.1 | 160 | 10.2686 | 874.8 | 867.6 | 274.389 | 0 | 1
7/29 | 19:00:00 | 288.15 | 98867 | 1.5 | 34 | 10.9655 | 388.8 | 399.6 | 275.565 | 0 | 1
7/29 | 20:00:00 | 288.15 | 98867 | 1.5 | 97 | 10.9655 | 39.6 | 0 | 276.053 | 0 | 1
7/29 | 21:00:00 | 288.15 | 98867 | 3.6 | 260 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
7/29 | 22:00:00 | 288.15 | 98867 | 3.6 | 270 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
7/29 | 23:00:00 | 288.15 | 98867 | 2.1 | 240 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
7/29 | 24:00:00 | 288.15 | 98867 | 3.6 | 240 | 10.9655 | 0 | 0 | 275.296 | 0 | 1
7/30 | 01:00:00 | 288.15 | 98867 | 1.5 | 224 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
7/30 | 02:00:00 | 288.15 | 98867 | 2.6 | 240 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
7/30 | 03:00:00 | 288.15 | 98867 | 2.6 | 240 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
7/30 | 04:00:00 | 288.15 | 98867 | 3.1 | 230 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
7/30 | 05:00:00 | 288.15 | 98867 | 1.5 | 177 | 10.9655 | 18 | 0 | 275.565 | 0 | 1
7/30 | 06:00:00 | 288.15 | 98867 | 2.6 | 230 | 10.9655 | 118.8 | 0 | 276.053 | 0 | 1
7/30 | 07:00:00 | 288.15 | 98867 | 2.6 | 260 | 10.9655 | 356.4 | 0 | 276.053 | 0 | 1
7/30 | 08:00:00 | 288.15 | 98867 | 3.1 | 270 | 10.9655 | 1162.8 | 1087.2 | 275.565 | 0 | 1
7/30 | 09:00:00 | 289.15 | 98875 | 4.1 | 290 | 10.9646 | 1681.2 | 1749.6 | 276.522 | 0 | 1
7/30 | 10:00:00 | 289.15 | 98875 | 3.1 | 280 | 10.9646 | 2127.6 | 2019.6 | 276.522 | 0 | 1
7/30 | 11:00:00 | 290.15 | 98883 | 4.1 | 290 | 11.7037 | 2458.8 | 1828.8 | 277.7 | 0 | 1
7/30 | 12:00:00 | 291.15 | 98892 | 3.6 | 330 | 11.7026 | 1468.8 | 277.2 | 279.15 | 0 | 1
7/30 | 13:00:00 | 288.15 | 98867 | 3.1 | 20 | 10.9655 | 2689.2 | 1522.8 | 275.565 | 0 | 1
7/30 | 14:00:00 | 288.15 | 98867 | 2.6 | 40 | 10.9655 | 1422 | 356.4 | 276.053 | 0 | 1
7/30 | 15:00:00 | 289.15 | 98875 | 1 | 208 | 10.9646 | 1270.8 | 115.2 | 277.011 | 0 | 1
7/30 | 16:00:00 | 289.15 | 98875 | 1 | 142 | 10.9646 | 1886.4 | 1681.2 | 276.522 | 0 | 1
7/30 | 17:00:00 | 290.15 | 98883 | 1.5 | 89 | 10.9637 | 1393.2 | 1562.4 | 277.478 | 0 | 1
7/30 | 18:00:00 | 290.15 | 98883 | 3.1 | 220 | 10.9637 | 860.4 | 968.4 | 277.478 | 0 | 1
7/30 | 19:00:00 | 289.15 | 98875 | 2.6 | 190 | 11.7047 | 381.6 | 381.6 | 276.743 | 0 | 1
7/30 | 20:00:00 | 289.15 | 98875 | 2.6 | 290 | 10.2668 | 68.4 | 0 | 276.3 | 0 | 1
7/30 | 21:00:00 | 287.15 | 98858 | 2.6 | 30 | 9.6108 | 0 | 0 | 274.167 | 0 | 1
7/30 | 22:00:00 | 286.15 | 98850 | 1 | 55 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
7/30 | 23:00:00 | 286.15 | 98850 | 1 | 152 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
7/30 | 24:00:00 | 286.15 | 98850 | 1 | 330 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
7/31 | 01:00:00 | 285.15 | 98841 | 0.5 | 152 | 8.9926 | 0 | 0 | 272.036 | 0 | 1
7/31 | 02:00:00 | 284.15 | 98833 | 1.5 | 290 | 8.4095 | 0 | 0 | 270.595 | 0 | 1
7/31 | 03:00:00 | 286.15 | 98850 | 3.6 | 280 | 8.6955 | 0 | 0 | 272.878 | 0 | 1
7/31 | 04:00:00 | 285.15 | 98841 | 3.1 | 280 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
7/31 | 05:00:00 | 285.15 | 98841 | 4.1 | 280 | 8.9926 | 7.2 | 0 | 272.517 | 0 | 1
7/31 | 06:00:00 | 285.15 | 98841 | 3.6 | 290 | 8.9926 | 208.8 | 129.6 | 272.036 | 0 | 1
7/31 | 07:00:00 | 285.15 | 98841 | 3.6 | 290 | 8.4088 | 633.6 | 745.2 | 271.813 | 0 | 1
7/31 | 08:00:00 | 286.15 | 98850 | 5.1 | 280 | 8.408 | 1231.2 | 1522.8 | 272.499 | 0 | 1
7/31 | 09:00:00 | 288.15 | 98867 | 6.2 | 290 | 7.857 | 1785.6 | 2232 | 274.177 | 0 | 1
7/31 | 10:00:00 | 289.15 | 98875 | 7.2 | 280 | 8.4059 | 2131.2 | 2055.6 | 275.626 | 0 | 1
7/31 | 11:00:00 | 290.15 | 98883 | 6.7 | 280 | 8.4052 | 2469.6 | 2055.6 | 276.579 | 0 | 1
7/31 | 12:00:00 | 289.15 | 98875 | 5.7 | 290 | 8.4059 | 2660.4 | 2246.4 | 275.626 | 0 | 1
7/31 | 13:00:00 | 289.15 | 98875 | 6.2 | 290 | 8.4059 | 2696.4 | 2253.6 | 275.626 | 0 | 1
7/31 | 14:00:00 | 290.15 | 98883 | 6.7 | 280 | 7.8557 | 2574 | 1850.4 | 276.351 | 0 | 1
7/31 | 15:00:00 | 289.15 | 98875 | 6.7 | 280 | 7.8564 | 1274.4 | 180 | 275.885 | 0 | 1
7/31 | 16:00:00 | 288.15 | 98867 | 6.2 | 270 | 7.857 | 1051.2 | 68.4 | 274.931 | 0 | 1
7/31 | 17:00:00 | 288.15 | 98867 | 4.6 | 270 | 7.857 | 1393.2 | 1263.6 | 274.446 | 0 | 1
7/31 | 18:00:00 | 288.15 | 98867 | 5.7 | 270 | 8.4065 | 856.8 | 982.8 | 274.672 | 0 | 1
7/31 | 19:00:00 | 286.35 | 98852 | 5.9 | 275 | 8.1289 | 374.4 | 320.4 | 272.844 | 0 | 1
7/31 | 20:00:00 | 285.95 | 98848 | 5.7 | 272 | 8.2956 | 64.8 | 0 | 272.53 | 0 | 1
7/31 | 21:00:00 | 285.35 | 98843 | 5.5 | 270 | 8.296 | 0 | 0 | 271.959 | 0 | 1
7/31 | 22:00:00 | 285.15 | 98841 | 4.5 | 265 | 8.1298 | 0 | 0 | 272.292 | 0 | 1
7/31 | 23:00:00 | 285.15 | 98841 | 2.9 | 205 | 7.8591 | 0 | 0 | 272.179 | 0 | 1
7/31 | 24:00:00 | 285.15 | 98841 | 2 | 145 | 7.5965 | 0 | 0 | 272.066 | 0 | 1
8/1 | 01:00:00 | 285.15 | 98841 | 0.6 | 88 | 7.4428 | 0 | 0 | 271.888 | 0 | 1
8/1 | 02:00:00 | 285.15 | 98841 | 0.6 | 34 | 7.5965 | 0 | 0 | 272.066 | 0 | 1
8/1 | 03:00:00 | 284.95 | 98839 | 0.9 | 69 | 7.7533 | 0 | 0 | 271.943 | 0 | 1
8/1 | 04:00:00 | 284.65 | 98837 | 0.9 | 76 | 7.8594 | 0 | 0 | 271.592 | 0 | 1
8/1 | 05:00:00 | 284.65 | 98837 | 0.9 | 82 | 7.8594 | 3.6 | 0 | 271.702 | 0 | 1
8/1 | 06:00:00 | 284.65 | 98837 | 0.8 | 95 | 7.8594 | 64.8 | 0 | 271.702 | 0 | 1
8/1 | 07:00:00 | 284.15 | 98833 | 1 | 45 | 7.8598 | 208.8 | 0 | 271.225 | 0 | 1
8/1 | 08:00:00 | 285.15 | 98841 | 0.5 | 66 | 7.8591 | 385.2 | 0 | 272.179 | 0 | 1
8/1 | 09:00:00 | 285.15 | 98841 | 0.5 | 99 | 7.8591 | 921.6 | 122.4 | 272.069 | 0 | 1
8/1 | 10:00:00 | 286.15 | 98850 | 0.5 | 204 | 8.408 | 1173.6 | 100.8 | 273.248 | 0 | 1
8/1 | 11:00:00 | 287.15 | 98858 | 1 | 31 | 8.4073 | 1357.2 | 108 | 274.203 | 0 | 1
8/1 | 12:00:00 | 288.15 | 98867 | 0.5 | 257 | 8.9902 | 1461.6 | 154.8 | 275.384 | 0 | 1
8/1 | 13:00:00 | 289.15 | 98875 | 0.5 | 259 | 8.9895 | 1483.2 | 158.4 | 276.34 | 0 | 1
8/1 | 14:00:00 | 289.15 | 98875 | 1.5 | 97 | 8.4059 | 1414.8 | 154.8 | 276.113 | 0 | 1
8/1 | 15:00:00 | 289.15 | 98875 | 3.1 | 180 | 8.9895 | 1260 | 104.4 | 276.34 | 0 | 1
8/1 | 16:00:00 | 289.15 | 98875 | 2.6 | 190 | 8.9895 | 1033.2 | 93.6 | 276.34 | 0 | 1
8/1 | 17:00:00 | 289.15 | 98875 | 2.6 | 170 | 8.9895 | 759.6 | 68.4 | 276.34 | 0 | 1
8/1 | 18:00:00 | 289.15 | 98875 | 1.5 | 305 | 8.9895 | 460.8 | 21.6 | 276.34 | 0 | 1
8/1 | 19:00:00 | 289.15 | 98875 | 0.5 | 39 | 8.9895 | 198 | 0 | 276.34 | 0 | 1
8/1 | 20:00:00 | 288.15 | 98867 | 1.5 | 24 | 8.4065 | 32.4 | 0 | 275.158 | 0 | 1
8/1 | 21:00:00 | 287.15 | 98858 | 1 | 280 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
8/1 | 22:00:00 | 287.15 | 98858 | 1 | 280 | 8.991 | 0 | 0 | 273.944 | 0 | 1
8/1 | 23:00:00 | 286.15 | 98850 | 2.1 | 280 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
8/1 | 24:00:00 | 285.15 | 98841 | 1.5 | 250 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/2 | 01:00:00 | 285.15 | 98841 | 1 | 250 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
8/2 | 02:00:00 | 285.15 | 98841 | 1 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/2 | 03:00:00 | 285.15 | 98841 | 2.1 | 250 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/2 | 04:00:00 | 284.15 | 98833 | 2.1 | 280 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
8/2 | 05:00:00 | 284.15 | 98833 | 3.1 | 270 | 7.3425 | 3.6 | 0 | 270.147 | 0 | 1
8/2 | 06:00:00 | 285.15 | 98841 | 1.5 | 270 | 7.8591 | 198 | 79.2 | 271.323 | 0 | 1
8/2 | 07:00:00 | 286.15 | 98850 | 3.1 | 260 | 7.8584 | 464.4 | 154.8 | 272.909 | 0 | 1
8/2 | 08:00:00 | 287.15 | 98858 | 4.1 | 280 | 7.8578 | 975.6 | 716.4 | 273.743 | 0 | 1
8/2 | 09:00:00 | 289.15 | 98875 | 4.1 | 240 | 7.8564 | 1623.6 | 1501.2 | 275.398 | 0 | 1
8/2 | 10:00:00 | 290.15 | 98883 | 4.1 | 250 | 7.8557 | 2232 | 2379.6 | 276.08 | 0 | 1
8/2 | 11:00:00 | 291.15 | 98892 | 4.6 | 260 | 7.855 | 2592 | 2703.6 | 277.032 | 0 | 1
8/2 | 12:00:00 | 292.15 | 98900 | 4.1 | 240 | 8.4037 | 2793.6 | 2775.6 | 278.213 | 0 | 1
8/2 | 13:00:00 | 293.15 | 98908 | 4.6 | 240 | 8.403 | 2829.6 | 2790 | 279.165 | 0 | 1
8/2 | 14:00:00 | 293.15 | 98908 | 5.1 | 240 | 7.8537 | 2700 | 2674.8 | 278.935 | 0 | 1
8/2 | 15:00:00 | 294.15 | 98916 | 5.1 | 220 | 8.4023 | 2264.4 | 1994.4 | 280.392 | 0 | 1
8/2 | 16:00:00 | 294.15 | 98916 | 6.2 | 250 | 7.8531 | 1857.6 | 2008.8 | 280.16 | 0 | 1
8/2 | 17:00:00 | 293.15 | 98908 | 6.2 | 280 | 8.9864 | 1436.4 | 1911.6 | 279.394 | 0 | 1
8/2 | 18:00:00 | 292.15 | 98900 | 6.2 | 270 | 8.9872 | 871.2 | 1155.6 | 278.441 | 0 | 1
8/2 | 19:00:00 | 291.15 | 98892 | 6.7 | 260 | 8.4044 | 367.2 | 442.8 | 277.261 | 0 | 1
8/2 | 20:00:00 | 289.15 | 98875 | 5.1 | 250 | 8.4059 | 61.2 | 0 | 275.356 | 0 | 1
8/2 | 21:00:00 | 288.15 | 98867 | 6.2 | 240 | 8.9902 | 0 | 0 | 274.629 | 0 | 1
8/2 | 22:00:00 | 287.15 | 98858 | 5.1 | 230 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
8/2 | 23:00:00 | 287.15 | 98858 | 3.1 | 230 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
8/2 | 24:00:00 | 287.15 | 98858 | 4.1 | 250 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
8/3 | 01:00:00 | 286.15 | 98850 | 5.7 | 270 | 9.6116 | 0 | 0 | 272.945 | 0 | 1
8/3 | 02:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
8/3 | 03:00:00 | 285.15 | 98841 | 3.6 | 270 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
8/3 | 04:00:00 | 283.15 | 98824 | 3.1 | 270 | 7.8605 | 0 | 0 | 269.42 | 0 | 1
8/3 | 05:00:00 | 284.15 | 98833 | 3.6 | 240 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
8/3 | 06:00:00 | 286.15 | 98850 | 5.7 | 250 | 8.408 | 190.8 | 136.8 | 272.499 | 0 | 1
8/3 | 07:00:00 | 287.15 | 98858 | 6.7 | 260 | 8.991 | 594 | 691.2 | 273.944 | 0 | 1
8/3 | 08:00:00 | 287.15 | 98858 | 9.3 | 270 | 8.991 | 1116 | 1357.2 | 273.944 | 0 | 1
8/3 | 09:00:00 | 288.15 | 98867 | 10.3 | 270 | 8.9902 | 1638 | 1767.6 | 274.898 | 0 | 1
8/3 | 10:00:00 | 289.15 | 98875 | 9.3 | 280 | 7.8564 | 2095.2 | 1980 | 275.398 | 0 | 1
8/3 | 11:00:00 | 290.15 | 98883 | 8.7 | 260 | 7.8557 | 2433.6 | 2210.4 | 276.351 | 0 | 1
8/3 | 12:00:00 | 289.15 | 98875 | 7.7 | 280 | 7.8564 | 2624.4 | 2246.4 | 275.398 | 0 | 1
8/3 | 13:00:00 | 289.15 | 98875 | 9.8 | 270 | 7.8564 | 2660.4 | 2253.6 | 275.398 | 0 | 1
8/3 | 14:00:00 | 290.15 | 98883 | 9.3 | 270 | 7.8557 | 2534.4 | 2228.4 | 276.351 | 0 | 1
8/3 | 15:00:00 | 290.15 | 98883 | 9.3 | 270 | 7.8557 | 2253.6 | 2026.8 | 276.351 | 0 | 1
8/3 | 16:00:00 | 290.15 | 98883 | 10.3 | 270 | 7.8557 | 1846.8 | 1864.8 | 276.351 | 0 | 1
8/3 | 17:00:00 | 290.15 | 98883 | 10.3 | 270 | 7.8557 | 1346.4 | 1465.2 | 276.351 | 0 | 1
8/3 | 18:00:00 | 289.15 | 98875 | 10.8 | 280 | 7.8564 | 813.6 | 982.8 | 275.398 | 0 | 1
8/3 | 19:00:00 | 288.15 | 98867 | 6.7 | 270 | 7.857 | 356.4 | 356.4 | 274.177 | 0 | 1
8/3 | 20:00:00 | 287.15 | 98858 | 7.7 | 260 | 8.4073 | 57.6 | 0 | 273.451 | 0 | 1
8/3 | 21:00:00 | 287.15 | 98858 | 7.2 | 270 | 8.4073 | 0 | 0 | 273.451 | 0 | 1
8/3 | 22:00:00 | 286.15 | 98850 | 6.2 | 260 | 8.408 | 0 | 0 | 272.499 | 0 | 1
8/3 | 23:00:00 | 286.15 | 98850 | 5.7 | 260 | 8.408 | 0 | 0 | 272.499 | 0 | 1
8/3 | 24:00:00 | 286.15 | 98850 | 6.7 | 270 | 7.8584 | 0 | 0 | 272.274 | 0 | 1
8/4 | 01:00:00 | 286.15 | 98850 | 6.7 | 270 | 7.8584 | 0 | 0 | 272.274 | 0 | 1
8/4 | 02:00:00 | 285.15 | 98841 | 7.2 | 270 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
8/4 | 03:00:00 | 285.15 | 98841 | 5.1 | 260 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
8/4 | 04:00:00 | 285.15 | 98841 | 8.2 | 270 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
8/4 | 05:00:00 | 285.15 | 98841 | 6.7 | 270 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
8/4 | 06:00:00 | 286.15 | 98850 | 6.2 | 270 | 8.408 | 172.8 | 25.2 | 272.766 | 0 | 1
8/4 | 07:00:00 | 287.15 | 98858 | 8.2 | 260 | 8.991 | 583.2 | 680.4 | 273.944 | 0 | 1
8/4 | 08:00:00 | 287.15 | 98858 | 7.2 | 260 | 8.4073 | 1105.2 | 1357.2 | 273.719 | 0 | 1
8/4 | 09:00:00 | 288.15 | 98867 | 7.2 | 260 | 8.4065 | 1627.2 | 1774.8 | 274.672 | 0 | 1
8/4 | 10:00:00 | 288.15 | 98867 | 8.2 | 270 | 8.4065 | 2080.8 | 2044.8 | 274.672 | 0 | 1
8/4 | 11:00:00 | 288.15 | 98867 | 7.7 | 270 | 8.4065 | 2419.2 | 2052 | 274.672 | 0 | 1
8/4 | 12:00:00 | 289.15 | 98875 | 6.7 | 260 | 8.4059 | 2613.6 | 2242.8 | 275.626 | 0 | 1
8/4 | 13:00:00 | 289.15 | 98875 | 5.7 | 260 | 8.4059 | 2646 | 2250 | 275.626 | 0 | 1
8/4 | 14:00:00 | 289.15 | 98875 | 6.7 | 270 | 8.4059 | 2520 | 2224.8 | 275.626 | 0 | 1
8/4 | 15:00:00 | 289.15 | 98875 | 6.2 | 270 | 8.4059 | 2239.2 | 2019.6 | 275.626 | 0 | 1
8/4 | 16:00:00 | 289.15 | 98875 | 6.7 | 260 | 7.8564 | 1836 | 1861.2 | 275.398 | 0 | 1
8/4 | 17:00:00 | 289.15 | 98875 | 6.7 | 260 | 7.8564 | 1335.6 | 1519.2 | 275.398 | 0 | 1
8/4 | 18:00:00 | 288.15 | 98867 | 5.1 | 260 | 8.4065 | 846 | 1130.4 | 274.404 | 0 | 1
8/4 | 19:00:00 | 288.15 | 98867 | 3.6 | 250 | 8.9902 | 324 | 309.6 | 274.898 | 0 | 1
8/4 | 20:00:00 | 288.15 | 98867 | 4.1 | 260 | 8.4065 | 50.4 | 0 | 274.672 | 0 | 1
8/4 | 21:00:00 | 286.15 | 98850 | 4.1 | 250 | 8.9918 | 0 | 0 | 272.99 | 0 | 1
8/4 | 22:00:00 | 286.15 | 98850 | 4.6 | 270 | 8.408 | 0 | 0 | 273.248 | 0 | 1
8/4 | 23:00:00 | 285.15 | 98841 | 3.1 | 220 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
8/4 | 24:00:00 | 285.15 | 98841 | 3.6 | 210 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
8/5 | 01:00:00 | 285.15 | 98841 | 1.5 | 230 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
8/5 | 02:00:00 | 285.15 | 98841 | 1.5 | 205 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
8/5 | 03:00:00 | 285.15 | 98841 | 2.1 | 220 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
8/5 | 04:00:00 | 285.15 | 98841 | 1.5 | 240 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
8/5 | 05:00:00 | 285.15 | 98841 | 1.5 | 263 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
8/5 | 06:00:00 | 285.15 | 98841 | 3.1 | 280 | 8.9926 | 90 | 0 | 272.517 | 0 | 1
8/5 | 07:00:00 | 286.15 | 98850 | 3.6 | 300 | 8.9918 | 572.4 | 806.4 | 272.99 | 0 | 1
8/5 | 08:00:00 | 287.15 | 98858 | 4.1 | 310 | 8.4073 | 1094.4 | 1346.4 | 273.719 | 0 | 1
8/5 | 09:00:00 | 288.15 | 98867 | 7.2 | 310 | 8.9902 | 1612.8 | 1382.4 | 274.898 | 0 | 1
8/5 | 10:00:00 | 288.15 | 98867 | 7.7 | 300 | 7.857 | 1148.4 | 172.8 | 274.931 | 0 | 1
8/5 | 11:00:00 | 289.15 | 98875 | 6.2 | 310 | 7.3393 | 2415.6 | 1900.8 | 275.169 | 0 | 1
8/5 | 12:00:00 | 290.15 | 98883 | 8.2 | 280 | 6.8523 | 2613.6 | 2257.2 | 275.89 | 0 | 1
8/5 | 13:00:00 | 290.15 | 98883 | 9.3 | 280 | 7.3387 | 2642.4 | 2257.2 | 276.121 | 0 | 1
8/5 | 14:00:00 | 290.15 | 98883 | 8.2 | 280 | 7.8557 | 2512.8 | 2228.4 | 276.351 | 0 | 1
8/5 | 15:00:00 | 290.15 | 98883 | 9.8 | 290 | 12.4883 | 2206.8 | 2206.8 | 277.92 | 0 | 1
8/5 | 16:00:00 | 290.15 | 98883 | 9.8 | 290 | 12.4883 | 1803.6 | 1951.2 | 277.92 | 0 | 1
8/5 | 17:00:00 | 289.15 | 98875 | 10.3 | 280 | 11.7047 | 1389.6 | 1818 | 276.472 | 0 | 1
8/5 | 18:00:00 | 289.15 | 98875 | 10.3 | 280 | 11.7047 | 828 | 1087.2 | 276.472 | 0 | 1
8/5 | 19:00:00 | 287.15 | 98858 | 8.7 | 290 | 10.2686 | 334.8 | 385.2 | 274.12 | 0 | 1
8/5 | 20:00:00 | 286.15 | 98850 | 6.7 | 270 | 9.6116 | 14.4 | 0 | 273.806 | 0 | 1
8/5 | 21:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.9926 | 0 | 0 | 272.627 | 0 | 1
8/5 | 22:00:00 | 285.15 | 98841 | 7.7 | 270 | 8.9926 | 0 | 0 | 272.627 | 0 | 1
8/5 | 23:00:00 | 284.15 | 98833 | 6.7 | 270 | 8.4095 | 0 | 0 | 271.449 | 0 | 1
8/5 | 24:00:00 | 284.15 | 98833 | 6.7 | 270 | 8.4095 | 0 | 0 | 271.449 | 0 | 1
8/6 | 01:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/6 | 02:00:00 | 283.15 | 98824 | 6.2 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/6 | 03:00:00 | 283.15 | 98824 | 7.7 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/6 | 04:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/6 | 05:00:00 | 283.15 | 98824 | 4.1 | 260 | 7.8605 | 0 | 0 | 269.684 | 0 | 1
8/6 | 06:00:00 | 283.15 | 98824 | 6.2 | 280 | 7.8605 | 169.2 | 68.4 | 269.42 | 0 | 1
8/6 | 07:00:00 | 284.15 | 98833 | 5.1 | 290 | 8.4095 | 597.6 | 806.4 | 270.595 | 0 | 1
8/6 | 08:00:00 | 285.15 | 98841 | 5.1 | 280 | 8.9926 | 1148.4 | 1616.4 | 271.77 | 0 | 1
8/6 | 09:00:00 | 287.15 | 98858 | 7.2 | 280 | 10.2686 | 1695.6 | 2170.8 | 274.12 | 0 | 1
8/6 | 10:00:00 | 288.15 | 98867 | 7.7 | 280 | 10.9655 | 2170.8 | 2476.8 | 275.296 | 0 | 1
8/6 | 11:00:00 | 288.15 | 98867 | 7.7 | 290 | 7.3399 | 2548.8 | 2624.4 | 273.95 | 0 | 1
8/6 | 12:00:00 | 288.15 | 98867 | 7.7 | 270 | 7.3399 | 2599.2 | 2188.8 | 274.218 | 0 | 1
8/6 | 13:00:00 | 289.15 | 98875 | 8.2 | 270 | 7.3393 | 2631.6 | 2257.2 | 275.169 | 0 | 1
8/6 | 14:00:00 | 289.15 | 98875 | 7.7 | 270 | 7.3393 | 2505.6 | 2232 | 275.169 | 0 | 1
8/6 | 15:00:00 | 290.15 | 98883 | 8.2 | 270 | 6.8523 | 2228.4 | 2041.2 | 275.89 | 0 | 1
8/6 | 16:00:00 | 289.15 | 98875 | 8.7 | 270 | 6.8529 | 1814.4 | 1868.4 | 274.939 | 0 | 1
8/6 | 17:00:00 | 289.15 | 98875 | 8.2 | 280 | 7.3393 | 1310.4 | 1512 | 275.169 | 0 | 1
8/6 | 18:00:00 | 288.15 | 98867 | 7.2 | 270 | 6.8534 | 824.4 | 1177.2 | 273.72 | 0 | 1
8/6 | 19:00:00 | 287.15 | 98858 | 6.7 | 260 | 6.854 | 324 | 316.8 | 272.77 | 0 | 1
8/6 | 20:00:00 | 286.15 | 98850 | 5.1 | 270 | 6.8546 | 46.8 | 0 | 271.821 | 0 | 1
8/6 | 21:00:00 | 285.15 | 98841 | 7.2 | 290 | 6.8552 | 0 | 0 | 270.871 | 0 | 1
8/6 | 22:00:00 | 284.15 | 98833 | 5.1 | 340 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
8/6 | 23:00:00 | 284.15 | 98833 | 6.2 | 310 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
8/6 | 24:00:00 | 284.15 | 98833 | 4.1 | 310 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
8/7 | 01:00:00 | 284.15 | 98833 | 3.6 | 320 | 6.8558 | 0 | 0 | 270.549 | 0 | 1
8/7 | 02:00:00 | 283.15 | 98824 | 2.6 | 320 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
8/7 | 03:00:00 | 281.15 | 98806 | 3.1 | 290 | 6.4 | 0 | 0 | 267.688 | 0 | 1
8/7 | 04:00:00 | 281.15 | 98806 | 2.6 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1
8/7 | 05:00:00 | 281.15 | 98806 | 3.1 | 310 | 6.4 | 0 | 0 | 267.688 | 0 | 1
8/7 | 06:00:00 | 282.15 | 98815 | 3.1 | 290 | 6.8571 | 68.4 | 0 | 268.867 | 0 | 1
8/7 | 07:00:00 | 284.15 | 98833 | 3.6 | 320 | 6.8558 | 424.8 | 201.6 | 270.549 | 0 | 1
8/7 | 08:00:00 | 286.15 | 98850 | 4.1 | 320 | 6.8546 | 1141.2 | 1476 | 271.821 | 0 | 1
8/7 | 09:00:00 | 287.15 | 98858 | 5.7 | 350 | 5.5627 | 1706.4 | 2181.6 | 272.077 | 0 | 1
8/7 | 10:00:00 | 288.15 | 98867 | 6.2 | 350 | 5.5621 | 2066.4 | 2163.6 | 273.292 | 0 | 1
8/7 | 11:00:00 | 289.15 | 98875 | 6.2 | 360 | 5.5617 | 2408.4 | 2242.8 | 274.24 | 0 | 1
8/7 | 12:00:00 | 288.15 | 98867 | 5.1 | 360 | 5.5621 | 2602.8 | 2282.4 | 273.292 | 0 | 1
8/7 | 13:00:00 | 288.15 | 98867 | 5.7 | 360 | 5.5621 | 2635.2 | 2286 | 273.292 | 0 | 1
8/7 | 14:00:00 | 289.15 | 98875 | 4.6 | 360 | 6.3955 | 2498.4 | 2242.8 | 274.708 | 0 | 1
8/7 | 15:00:00 | 289.15 | 98875 | 4.6 | 10 | 6.8529 | 2214 | 2037.6 | 274.939 | 0 | 1
8/7 | 16:00:00 | 289.15 | 98875 | 4.6 | 350 | 6.3955 | 1803.6 | 1868.4 | 274.708 | 0 | 1
8/7 | 17:00:00 | 289.15 | 98875 | 5.1 | 360 | 5.9656 | 1303.2 | 1461.6 | 274.475 | 0 | 1
8/7 | 18:00:00 | 289.15 | 98875 | 4.1 | 360 | 6.3955 | 766.8 | 950.4 | 274.708 | 0 | 1
8/7 | 19:00:00 | 288.15 | 98867 | 3.1 | 340 | 5.9661 | 313.2 | 302.4 | 273.258 | 0 | 1
8/7 | 20:00:00 | 286.15 | 98850 | 2.6 | 300 | 6.3971 | 39.6 | 0 | 271.858 | 0 | 1
8/7 | 21:00:00 | 286.15 | 98850 | 3.1 | 320 | 5.9671 | 0 | 0 | 271.496 | 0 | 1
8/7 | 22:00:00 | 285.15 | 98841 | 2.6 | 360 | 6.8552 | 0 | 0 | 271.384 | 0 | 1
8/7 | 23:00:00 | 283.15 | 98824 | 0.5 | 317 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
8/7 | 24:00:00 | 283.15 | 98824 | 1 | 102 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
8/8 | 01:00:00 | 282.15 | 98815 | 2.1 | 300 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
8/8 | 02:00:00 | 283.15 | 98824 | 2.6 | 350 | 6.3988 | 0 | 0 | 269.37 | 0 | 1
8/8 | 03:00:00 | 282.15 | 98815 | 3.1 | 350 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
8/8 | 04:00:00 | 281.15 | 98806 | 2.6 | 310 | 6.4 | 0 | 0 | 267.688 | 0 | 1
8/8 | 05:00:00 | 282.15 | 98815 | 3.6 | 350 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
8/8 | 06:00:00 | 282.15 | 98815 | 3.1 | 360 | 6.3994 | 93.6 | 0 | 268.532 | 0 | 1
8/8 | 07:00:00 | 284.15 | 98833 | 2.1 | 330 | 6.8558 | 417.6 | 158.4 | 270.549 | 0 | 1
8/8 | 08:00:00 | 284.15 | 98833 | 1.5 | 128 | 6.8558 | 817.2 | 435.6 | 270.549 | 0 | 1
8/8 | 09:00:00 | 286.15 | 98850 | 1.5 | 224 | 7.3412 | 1375.2 | 961.2 | 272.563 | 0 | 1
8/8 | 10:00:00 | 288.15 | 98867 | 2.6 | 320 | 7.3399 | 2167.2 | 2235.6 | 273.95 | 0 | 1
8/8 | 11:00:00 | 290.15 | 98883 | 2.6 | 300 | 7.3387 | 2527.2 | 2692.8 | 275.851 | 0 | 1
8/8 | 12:00:00 | 291.15 | 98892 | 2.6 | 300 | 7.338 | 2732.4 | 2772 | 276.802 | 0 | 1
8/8 | 13:00:00 | 293.15 | 98908 | 5.1 | 300 | 7.3368 | 2768.4 | 2786.4 | 278.703 | 0 | 1
8/8 | 14:00:00 | 292.15 | 98900 | 6.2 | 290 | 7.8544 | 2628 | 2728.8 | 277.983 | 0 | 1
8/8 | 15:00:00 | 292.15 | 98900 | 5.1 | 280 | 7.8544 | 2329.2 | 2430 | 277.983 | 0 | 1
8/8 | 16:00:00 | 293.15 | 98908 | 4.6 | 290 | 7.8537 | 1785.6 | 1832.4 | 279.208 | 0 | 1
8/8 | 17:00:00 | 292.15 | 98900 | 6.2 | 270 | 7.8544 | 1353.6 | 1699.2 | 277.983 | 0 | 1
8/8 | 18:00:00 | 292.15 | 98900 | 6.2 | 270 | 7.8544 | 792 | 1112.4 | 277.983 | 0 | 1
8/8 | 19:00:00 | 291.15 | 98892 | 5.1 | 280 | 7.855 | 298.8 | 259.2 | 277.17 | 0 | 1
8/8 | 20:00:00 | 289.15 | 98875 | 5.1 | 280 | 7.8564 | 36 | 0 | 275.398 | 0 | 1
8/8 | 21:00:00 | 288.15 | 98867 | 4.6 | 290 | 7.3399 | 0 | 0 | 274.218 | 0 | 1
8/8 | 22:00:00 | 286.15 | 98850 | 5.7 | 290 | 7.3412 | 0 | 0 | 272.563 | 0 | 1
8/8 | 23:00:00 | 286.15 | 98850 | 5.1 | 300 | 7.3412 | 0 | 0 | 272.563 | 0 | 1
8/8 | 24:00:00 | 285.15 | 98841 | 0.5 | 24 | 7.3418 | 0 | 0 | 271.729 | 0 | 1
8/9 | 01:00:00 | 285.15 | 98841 | 3.6 | 320 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/9 | 02:00:00 | 284.15 | 98833 | 1.5 | 290 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
8/9 | 03:00:00 | 284.15 | 98833 | 1.5 | 290 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
8/9 | 04:00:00 | 284.15 | 98833 | 1 | 360 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
8/9 | 05:00:00 | 284.15 | 98833 | 2.1 | 300 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
8/9 | 06:00:00 | 285.15 | 98841 | 2.6 | 290 | 8.4088 | 75.6 | 0 | 272.294 | 0 | 1
8/9 | 07:00:00 | 285.15 | 98841 | 2.1 | 280 | 8.4088 | 295.2 | 0 | 272.294 | 0 | 1
8/9 | 08:00:00 | 287.15 | 98858 | 4.1 | 310 | 8.4073 | 806.4 | 439.2 | 274.088 | 0 | 1
8/9 | 09:00:00 | 287.15 | 98858 | 3.1 | 310 | 8.4073 | 1206 | 558 | 274.088 | 0 | 1
8/9 | 10:00:00 | 289.15 | 98875 | 2.1 | 280 | 8.9895 | 1749.6 | 1087.2 | 276.104 | 0 | 1
8/9 | 11:00:00 | 290.15 | 98883 | 1.5 | 320 | 8.4052 | 2322 | 1875.6 | 276.579 | 0 | 1
8/9 | 12:00:00 | 292.15 | 98900 | 1 | 277 | 8.9872 | 2707.2 | 2689.2 | 278.441 | 0 | 1
8/9 | 13:00:00 | 293.15 | 98908 | 2.6 | 217 | 8.9864 | 2743.2 | 2764.8 | 279.394 | 0 | 1
8/9 | 14:00:00 | 293.15 | 98908 | 4.6 | 260 | 8.403 | 2610 | 2718 | 279.165 | 0 | 1
8/9 | 15:00:00 | 294.15 | 98916 | 5.1 | 300 | 7.8531 | 2314.8 | 2113.2 | 279.886 | 0 | 1
8/9 | 16:00:00 | 293.15 | 98908 | 5.1 | 300 | 8.403 | 979.2 | 234 | 279.933 | 0 | 1
8/9 | 17:00:00 | 291.15 | 98892 | 2.6 | 30 | 8.9879 | 702 | 64.8 | 278.251 | 0 | 1
8/9 | 18:00:00 | 290.15 | 98883 | 3.1 | 50 | 8.9887 | 406.8 | 10.8 | 277.295 | 0 | 1
8/9 | 19:00:00 | 289.15 | 98875 | 2.1 | 80 | 8.9895 | 151.2 | 0 | 276.34 | 0 | 1
8/9 | 20:00:00 | 288.15 | 98867 | 1 | 146 | 8.4065 | 18 | 0 | 275.158 | 0 | 1
8/9 | 21:00:00 | 287.15 | 98858 | 1 | 152 | 8.4073 | 0 | 0 | 274.203 | 0 | 1
8/9 | 22:00:00 | 286.15 | 98850 | 3.6 | 260 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
8/9 | 23:00:00 | 286.15 | 98850 | 1 | 225 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
8/9 | 24:00:00 | 286.15 | 98850 | 0.5 | 250 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
8/10 | 01:00:00 | 286.15 | 98850 | 2.1 | 270 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
8/10 | 02:00:00 | 286.15 | 98850 | 3.1 | 280 | 9.6116 | 0 | 0 | 272.945 | 0 | 1
8/10 | 03:00:00 | 286.15 | 98850 | 2.1 | 290 | 9.6116 | 0 | 0 | 272.945 | 0 | 1
8/10 | 04:00:00 | 287.15 | 98858 | 2.6 | 300 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
8/10 | 05:00:00 | 287.15 | 98858 | 2.1 | 260 | 10.2686 | 0 | 0 | 274.389 | 0 | 1
8/10 | 06:00:00 | 287.15 | 98858 | 2.6 | 290 | 10.2686 | 72 | 0 | 274.874 | 0 | 1
8/10 | 07:00:00 | 287.15 | 98858 | 3.1 | 270 | 10.2686 | 288 | 0 | 274.874 | 0 | 1
8/10 | 08:00:00 | 288.15 | 98867 | 2.6 | 270 | 10.9655 | 572.4 | 39.6 | 276.053 | 0 | 1
8/10 | 09:00:00 | 289.15 | 98875 | 4.6 | 270 | 10.9646 | 860.4 | 79.2 | 277.011 | 0 | 1
8/10 | 10:00:00 | 290.15 | 98883 | 4.1 | 290 | 10.9637 | 1108.8 | 248.4 | 277.969 | 0 | 1
8/10 | 11:00:00 | 290.15 | 98883 | 4.1 | 280 | 10.9637 | 2340 | 1692 | 277.478 | 0 | 1
8/10 | 12:00:00 | 292.15 | 98900 | 5.1 | 280 | 10.9618 | 1404 | 360 | 279.885 | 0 | 1
8/10 | 13:00:00 | 292.15 | 98900 | 4.1 | 290 | 10.9618 | 1422 | 360 | 279.885 | 0 | 1
8/10 | 14:00:00 | 291.15 | 98892 | 5.1 | 270 | 10.9627 | 2433.6 | 1846.8 | 278.434 | 0 | 1
8/10 | 15:00:00 | 293.15 | 98908 | 6.7 | 270 | 11.7007 | 2149.2 | 1789.2 | 280.571 | 0 | 1
8/10 | 16:00:00 | 292.15 | 98900 | 6.7 | 280 | 10.9618 | 968.4 | 226.8 | 279.885 | 0 | 1
8/10 | 17:00:00 | 293.15 | 98908 | 7.7 | 290 | 10.9609 | 691.2 | 61.2 | 280.843 | 0 | 1
8/10 | 18:00:00 | 292.15 | 98900 | 6.7 | 280 | 10.9618 | 396 | 10.8 | 279.885 | 0 | 1
8/10 | 19:00:00 | 291.15 | 98892 | 5.7 | 270 | 10.9627 | 144 | 0 | 278.927 | 0 | 1
8/10 | 20:00:00 | 290.15 | 98883 | 6.7 | 260 | 10.266 | 28.8 | 0 | 277.255 | 0 | 1
8/10 | 21:00:00 | 289.15 | 98875 | 6.7 | 270 | 10.2668 | 0 | 0 | 276.029 | 0 | 1
8/10 | 22:00:00 | 288.15 | 98867 | 6.7 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
8/10 | 23:00:00 | 288.15 | 98867 | 7.2 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
8/10 | 24:00:00 | 288.15 | 98867 | 6.2 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
8/11 | 01:00:00 | 287.15 | 98858 | 5.7 | 280 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
8/11 | 02:00:00 | 287.15 | 98858 | 6.7 | 270 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
8/11 | 03:00:00 | 287.15 | 98858 | 5.7 | 290 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
8/11 | 04:00:00 | 287.15 | 98858 | 5.7 | 290 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
8/11 | 05:00:00 | 286.15 | 98850 | 4.1 | 280 | 8.9918 | 0 | 0 | 273.583 | 0 | 1
8/11 | 06:00:00 | 286.15 | 98850 | 2.6 | 280 | 8.9918 | 129.6 | 3.6 | 272.723 | 0 | 1
8/11 | 07:00:00 | 287.15 | 98858 | 3.1 | 310 | 8.991 | 280.8 | 0 | 274.428 | 0 | 1
8/11 | 08:00:00 | 288.15 | 98867 | 1 | 261 | 9.6099 | 565.2 | 39.6 | 275.608 | 0 | 1
8/11 | 09:00:00 | 289.15 | 98875 | 3.1 | 260 | 9.6091 | 856.8 | 79.2 | 276.565 | 0 | 1
8/11 | 10:00:00 | 289.15 | 98875 | 3.6 | 260 | 10.2668 | 1105.2 | 97.2 | 276.789 | 0 | 1
8/11 | 11:00:00 | 290.15 | 98883 | 4.1 | 260 | 10.9637 | 1288.8 | 104.4 | 277.969 | 0 | 1
8/11 | 12:00:00 | 291.15 | 98892 | 6.2 | 270 | 10.265 | 1400.4 | 360 | 278.703 | 0 | 1
8/11 | 13:00:00 | 293.15 | 98908 | 5.1 | 270 | 10.2634 | 2556 | 2019.6 | 280.122 | 0 | 1
8/11 | 14:00:00 | 294.15 | 98916 | 6.7 | 270 | 9.6051 | 2430 | 2048.4 | 280.85 | 0 | 1
8/11 | 15:00:00 | 293.15 | 98908 | 5.7 | 280 | 9.6059 | 2145.6 | 2059.2 | 279.895 | 0 | 1
8/11 | 16:00:00 | 292.15 | 98900 | 5.1 | 310 | 10.2642 | 1731.6 | 1825.2 | 279.166 | 0 | 1
8/11 | 17:00:00 | 293.15 | 98908 | 5.1 | 300 | 10.2634 | 1231.2 | 1461.6 | 280.122 | 0 | 1
8/11 | 18:00:00 | 292.15 | 98900 | 4.6 | 310 | 10.2642 | 745.2 | 1008 | 278.893 | 0 | 1
8/11 | 19:00:00 | 290.15 | 98883 | 5.7 | 320 | 10.3339 | 266.4 | 288 | 277.006 | 0 | 1
8/11 | 20:00:00 | 289.15 | 98875 | 3.6 | 300 | 9.0498 | 25.2 | 0 | 275.604 | 0 | 1
8/11 | 21:00:00 | 288.15 | 98867 | 4.1 | 280 | 8.7525 | 0 | 0 | 274.539 | 0 | 1
8/11 | 22:00:00 | 287.15 | 98858 | 3.1 | 270 | 8.4641 | 0 | 0 | 273.474 | 0 | 1
8/11 | 23:00:00 | 287.15 | 98858 | 4.6 | 280 | 8.8122 | 0 | 0 | 273.609 | 0 | 1
8/11 | 24:00:00 | 286.15 | 98850 | 4.1 | 290 | 8.522 | 0 | 0 | 272.544 | 0 | 1
8/12 | 01:00:00 | 286.15 | 98850 | 4.1 | 280 | 8.522 | 0 | 0 | 272.544 | 0 | 1
8/12 | 02:00:00 | 286.15 | 98850 | 5.1 | 290 | 8.5795 | 0 | 0 | 272.833 | 0 | 1
8/12 | 03:00:00 | 286.15 | 98850 | 4.6 | 290 | 8.5795 | 0 | 0 | 272.833 | 0 | 1
8/12 | 04:00:00 | 286.15 | 98850 | 4.1 | 290 | 8.5795 | 0 | 0 | 273.316 | 0 | 1
8/12 | 05:00:00 | 286.15 | 98850 | 4.1 | 300 | 8.6373 | 0 | 0 | 272.856 | 0 | 1
8/12 | 06:00:00 | 286.15 | 98850 | 2.1 | 320 | 8.3515 | 64.8 | 0 | 273.226 | 0 | 1
8/12 | 07:00:00 | 286.15 | 98850 | 1.5 | 208 | 8.3515 | 277.2 | 0 | 273.226 | 0 | 1
8/12 | 08:00:00 | 286.15 | 98850 | 1 | 96 | 8.9318 | 561.6 | 39.6 | 273.45 | 0 | 1
8/12 | 09:00:00 | 287.15 | 98858 | 2.1 | 10 | 9.2963 | 849.6 | 79.2 | 274.54 | 0 | 1
8/12 | 10:00:00 | 286.15 | 98850 | 1.5 | 54 | 9.6116 | 1101.6 | 248.4 | 273.695 | 0 | 1
8/12 | 11:00:00 | 288.15 | 98867 | 1.5 | 303 | 10.2677 | 2318.4 | 1699.2 | 275.344 | 0 | 1
8/12 | 12:00:00 | 288.15 | 98867 | 2.1 | 70 | 10.2677 | 1393.2 | 280.8 | 275.831 | 0 | 1
8/12 | 13:00:00 | 288.15 | 98867 | 2.1 | 20 | 9.6099 | 2545.2 | 1818 | 275.122 | 0 | 1
8/12 | 14:00:00 | 289.15 | 98875 | 2.1 | 90 | 9.6091 | 2415.6 | 1864.8 | 276.076 | 0 | 1
8/12 | 15:00:00 | 289.15 | 98875 | 0.5 | 30 | 9.6091 | 1184.4 | 259.2 | 276.565 | 0 | 1
8/12 | 16:00:00 | 288.15 | 98867 | 1.5 | 60 | 10.2677 | 954 | 97.2 | 275.831 | 0 | 1
8/12 | 17:00:00 | 288.15 | 98867 | 2.1 | 330 | 10.2677 | 1216.8 | 1144.8 | 275.344 | 0 | 1
8/12 | 18:00:00 | 287.15 | 98858 | 1.5 | 20 | 10.2686 | 691.2 | 986.4 | 274.389 | 0 | 1
8/12 | 19:00:00 | 287.15 | 98858 | 0 | 75 | 10.2686 | 133.2 | 0 | 274.874 | 0 | 1
8/12 | 20:00:00 | 287.15 | 98858 | 3.6 | 260 | 8.4073 | 10.8 | 0 | 274.203 | 0 | 1
8/12 | 21:00:00 | 286.15 | 98850 | 4.1 | 270 | 7.8584 | 0 | 0 | 272.541 | 0 | 1
8/12 | 22:00:00 | 285.15 | 98841 | 3.6 | 270 | 7.3418 | 0 | 0 | 271.363 | 0 | 1
8/12 | 23:00:00 | 285.15 | 98841 | 5.1 | 270 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
8/12 | 24:00:00 | 284.15 | 98833 | 4.6 | 270 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
8/13 | 01:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
8/13 | 02:00:00 | 283.15 | 98824 | 3.6 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/13 | 03:00:00 | 284.15 | 98833 | 2.6 | 260 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
8/13 | 04:00:00 | 283.15 | 98824 | 1.5 | 250 | 7.8605 | 0 | 0 | 269.42 | 0 | 1
8/13 | 05:00:00 | 284.15 | 98833 | 3.6 | 220 | 8.4095 | 0 | 0 | 270.859 | 0 | 1
8/13 | 06:00:00 | 284.15 | 98833 | 2.6 | 210 | 7.8598 | 61.2 | 0 | 271.115 | 0 | 1
8/13 | 07:00:00 | 284.15 | 98833 | 2.1 | 200 | 7.8598 | 270 | 0 | 271.115 | 0 | 1
8/13 | 08:00:00 | 284.15 | 98833 | 3.6 | 200 | 8.4095 | 1000.8 | 997.2 | 270.859 | 0 | 1
8/13 | 09:00:00 | 285.15 | 98841 | 3.1 | 200 | 8.9926 | 842.4 | 104.4 | 272.517 | 0 | 1
8/13 | 10:00:00 | 286.15 | 98850 | 4.6 | 210 | 8.9918 | 1094.4 | 97.2 | 273.473 | 0 | 1
8/13 | 11:00:00 | 286.15 | 98850 | 4.1 | 220 | 8.9918 | 1281.6 | 108 | 273.473 | 0 | 1
8/13 | 12:00:00 | 287.15 | 98858 | 3.1 | 220 | 9.6108 | 1386 | 154.8 | 274.652 | 0 | 1
8/13 | 13:00:00 | 288.15 | 98867 | 4.1 | 230 | 9.6099 | 1404 | 154.8 | 275.608 | 0 | 1
8/13 | 14:00:00 | 287.15 | 98858 | 3.6 | 210 | 10.2686 | 1332 | 108 | 274.874 | 0 | 1
8/13 | 15:00:00 | 288.15 | 98867 | 2.6 | 200 | 10.9655 | 1170 | 111.6 | 276.053 | 0 | 1
8/13 | 16:00:00 | 289.15 | 98875 | 3.6 | 240 | 10.9646 | 1699.2 | 1573.2 | 276.522 | 0 | 1
8/13 | 17:00:00 | 290.15 | 98883 | 8.2 | 270 | 9.6084 | 1202.4 | 1447.2 | 277.031 | 0 | 1
8/13 | 18:00:00 | 289.15 | 98875 | 6.7 | 290 | 7.8564 | 680.4 | 676.8 | 275.398 | 0 | 1
8/13 | 19:00:00 | 288.15 | 98867 | 8.2 | 280 | 7.3399 | 244.8 | 190.8 | 273.95 | 0 | 1
8/13 | 20:00:00 | 287.15 | 98858 | 8.7 | 270 | 7.3406 | 14.4 | 0 | 272.999 | 0 | 1
8/13 | 21:00:00 | 286.15 | 98850 | 3.6 | 290 | 7.8584 | 0 | 0 | 272.274 | 0 | 1
8/13 | 22:00:00 | 286.15 | 98850 | 6.7 | 280 | 7.8584 | 0 | 0 | 272.909 | 0 | 1
8/13 | 23:00:00 | 285.15 | 98841 | 6.2 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/13 | 24:00:00 | 285.15 | 98841 | 7.7 | 270 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
8/14 | 01:00:00 | 284.15 | 98833 | 6.2 | 290 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
8/14 | 02:00:00 | 285.15 | 98841 | 6.2 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/14 | 03:00:00 | 285.15 | 98841 | 7.7 | 290 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/14 | 04:00:00 | 285.15 | 98841 | 6.2 | 280 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/14 | 05:00:00 | 285.15 | 98841 | 7.2 | 290 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
8/14 | 06:00:00 | 285.15 | 98841 | 6.7 | 300 | 7.8591 | 100.8 | 0 | 271.588 | 0 | 1
8/14 | 07:00:00 | 286.15 | 98850 | 5.7 | 310 | 7.8584 | 266.4 | 0 | 273.023 | 0 | 1
8/14 | 08:00:00 | 286.15 | 98850 | 6.7 | 310 | 8.408 | 986.4 | 993.6 | 272.766 | 0 | 1
8/14 | 09:00:00 | 288.15 | 98867 | 8.2 | 340 | 8.4065 | 1512 | 1339.2 | 274.672 | 0 | 1
8/14 | 10:00:00 | 287.15 | 98858 | 7.2 | 350 | 8.991 | 1087.2 | 252 | 274.428 | 0 | 1
8/14 | 11:00:00 | 289.15 | 98875 | 8.2 | 10 | 8.9895 | 2300.4 | 1857.6 | 275.852 | 0 | 1
8/14 | 12:00:00 | 289.15 | 98875 | 6.7 | 10 | 8.4059 | 2498.4 | 2235.6 | 275.626 | 0 | 1
8/14 | 13:00:00 | 289.15 | 98875 | 8.2 | 360 | 8.4059 | 2527.2 | 2242.8 | 275.626 | 0 | 1
8/14 | 14:00:00 | 289.15 | 98875 | 6.2 | 360 | 8.4059 | 2397.6 | 2062.8 | 275.626 | 0 | 1
8/14 | 15:00:00 | 289.15 | 98875 | 5.7 | 360 | 8.4059 | 2109.6 | 1818 | 275.626 | 0 | 1
8/14 | 16:00:00 | 289.15 | 98875 | 5.7 | 360 | 7.8564 | 943.2 | 262.8 | 275.885 | 0 | 1
8/14 | 17:00:00 | 289.15 | 98875 | 4.1 | 360 | 8.4059 | 1191.6 | 1144.8 | 275.626 | 0 | 1
8/14 | 18:00:00 | 289.15 | 98875 | 3.6 | 20 | 8.4059 | 367.2 | 3.6 | 276.113 | 0 | 1
8/14 | 19:00:00 | 289.15 | 98875 | 3.1 | 20 | 8.4059 | 219.6 | 158.4 | 275.626 | 0 | 1
8/14 | 20:00:00 | 287.15 | 98858 | 1.5 | 30 | 8.4073 | 10.8 | 0 | 273.719 | 0 | 1
8/14 | 21:00:00 | 287.15 | 98858 | 0.5 | 10 | 7.8578 | 0 | 0 | 273.743 | 0 | 1
8/14 | 22:00:00 | 286.15 | 98850 | 0.5 | 23 | 8.408 | 0 | 0 | 273.248 | 0 | 1
8/14 | 23:00:00 | 286.15 | 98850 | 0 | 44 | 8.408 | 0 | 0 | 273.248 | 0 | 1
8/14 | 24:00:00 | 285.15 | 98841 | 0.5 | 40 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
8/15 | 01:00:00 | 285.15 | 98841 | 0.5 | 40 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/15 | 02:00:00 | 284.15 | 98833 | 0.5 | 320 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
8/15 | 03:00:00 | 284.15 | 98833 | 2.1 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
8/15 | 04:00:00 | 284.15 | 98833 | 2.1 | 260 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
8/15 | 05:00:00 | 284.15 | 98833 | 2.1 | 260 | 8.4095 | 0 | 0 | 270.595 | 0 | 1
8/15 | 06:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.9926 | 97.2 | 0 | 272.036 | 0 | 1
8/15 | 07:00:00 | 286.15 | 98850 | 6.2 | 270 | 8.9918 | 493.2 | 666 | 272.723 | 0 | 1
8/15 | 08:00:00 | 287.15 | 98858 | 7.7 | 270 | 8.991 | 1033.2 | 1350 | 273.676 | 0 | 1
8/15 | 09:00:00 | 288.15 | 98867 | 8.2 | 270 | 8.4065 | 1587.6 | 2116.8 | 274.404 | 0 | 1
8/15 | 10:00:00 | 289.15 | 98875 | 6.2 | 270 | 8.4059 | 1951.2 | 1933.2 | 275.626 | 0 | 1
8/15 | 11:00:00 | 289.15 | 98875 | 7.2 | 260 | 8.4059 | 2293.2 | 2044.8 | 275.626 | 0 | 1
8/15 | 12:00:00 | 289.15 | 98875 | 7.2 | 270 | 8.4059 | 2484 | 2232 | 275.626 | 0 | 1
8/15 | 13:00:00 | 289.15 | 98875 | 6.7 | 270 | 8.4059 | 2516.4 | 2185.2 | 275.626 | 0 | 1
8/15 | 14:00:00 | 290.15 | 98883 | 7.2 | 270 | 8.4052 | 2527.2 | 2523.6 | 276.308 | 0 | 1
8/15 | 15:00:00 | 291.15 | 98892 | 7.2 | 260 | 8.4044 | 2127.6 | 2163.6 | 277.532 | 0 | 1
8/15 | 16:00:00 | 291.15 | 98892 | 7.2 | 270 | 8.9879 | 1778.4 | 2257.2 | 277.488 | 0 | 1
8/15 | 17:00:00 | 290.15 | 98883 | 9.3 | 270 | 8.9887 | 1245.6 | 1555.2 | 276.535 | 0 | 1
8/15 | 18:00:00 | 289.15 | 98875 | 9.8 | 280 | 8.9895 | 648 | 774 | 275.852 | 0 | 1
8/15 | 19:00:00 | 288.15 | 98867 | 7.7 | 270 | 8.9902 | 208.8 | 136.8 | 274.898 | 0 | 1
8/15 | 20:00:00 | 288.15 | 98867 | 5.7 | 270 | 8.9902 | 7.2 | 0 | 274.898 | 0 | 1
8/15 | 21:00:00 | 287.15 | 98858 | 6.7 | 280 | 9.6108 | 0 | 0 | 274.167 | 0 | 1
8/15 | 22:00:00 | 287.15 | 98858 | 5.1 | 270 | 9.6108 | 0 | 0 | 274.167 | 0 | 1
8/15 | 23:00:00 | 287.15 | 98858 | 4.6 | 270 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
8/15 | 24:00:00 | 287.15 | 98858 | 6.7 | 280 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
8/16 | 01:00:00 | 287.15 | 98858 | 5.7 | 280 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
8/16 | 02:00:00 | 288.15 | 98867 | 3.1 | 290 | 10.2677 | 0 | 0 | 275.831 | 0 | 1
8/16 | 03:00:00 | 288.15 | 98867 | 3.1 | 250 | 10.2677 | 0 | 0 | 275.831 | 0 | 1
8/16 | 04:00:00 | 288.15 | 98867 | 3.6 | 260 | 10.2677 | 0 | 0 | 275.831 | 0 | 1
8/16 | 05:00:00 | 288.15 | 98867 | 3.1 | 260 | 10.9655 | 0 | 0 | 275.296 | 0 | 1
8/16 | 06:00:00 | 288.15 | 98867 | 2.6 | 270 | 10.9655 | 50.4 | 0 | 276.053 | 0 | 1
8/16 | 07:00:00 | 288.15 | 98867 | 3.6 | 280 | 10.9655 | 453.6 | 612 | 275.565 | 0 | 1
8/16 | 08:00:00 | 289.15 | 98875 | 3.1 | 280 | 10.9646 | 957.6 | 1083.6 | 276.522 | 0 | 1
8/16 | 09:00:00 | 289.15 | 98875 | 3.1 | 270 | 10.9646 | 1476 | 1299.6 | 276.522 | 0 | 1
8/16 | 10:00:00 | 290.15 | 98883 | 3.1 | 260 | 11.7037 | 1069.2 | 241.2 | 278.191 | 0 | 1
8/16 | 11:00:00 | 291.15 | 98892 | 2.1 | 230 | 11.7026 | 2260.8 | 1818 | 278.657 | 0 | 1
8/16 | 12:00:00 | 292.15 | 98900 | 0.5 | 138 | 10.9618 | 2455.2 | 2037.6 | 279.391 | 0 | 1
8/16 | 13:00:00 | 293.15 | 98908 | 1.5 | 81 | 11.7007 | 2484 | 1854 | 280.571 | 0 | 1
8/16 | 14:00:00 | 293.15 | 98908 | 1.5 | 301 | 10.9609 | 1306.8 | 270 | 280.843 | 0 | 1
8/16 | 15:00:00 | 293.15 | 98908 | 2.1 | 250 | 10.9609 | 1148.4 | 100.8 | 280.843 | 0 | 1
8/16 | 16:00:00 | 293.15 | 98908 | 1.5 | 35 | 10.9609 | 918 | 86.4 | 280.843 | 0 | 1
8/16 | 17:00:00 | 293.15 | 98908 | 0.5 | 80 | 10.9609 | 637.2 | 54 | 280.843 | 0 | 1
8/16 | 18:00:00 | 293.15 | 98908 | 1 | 106 | 10.9609 | 349.2 | 0 | 280.843 | 0 | 1
8/16 | 19:00:00 | 292.15 | 98900 | 1.5 | 130 | 10.9618 | 169.2 | 0 | 279.646 | 0 | 1
8/16 | 20:00:00 | 292.15 | 98900 | 1.5 | 120 | 10.9618 | 0 | 0 | 279.885 | 0 | 1
8/16 | 21:00:00 | 291.15 | 98892 | 2.1 | 100 | 10.9627 | 0 | 0 | 278.927 | 0 | 1
8/16 | 22:00:00 | 290.15 | 98883 | 3.6 | 140 | 10.9637 | 0 | 0 | 277.969 | 0 | 1
8/16 | 23:00:00 | 289.15 | 98875 | 3.1 | 150 | 10.9646 | 0 | 0 | 277.123 | 0 | 1
8/16 | 24:00:00 | 289.15 | 98875 | 3.1 | 150 | 10.2668 | 0 | 0 | 276.789 | 0 | 1
8/17 | 01:00:00 | 288.15 | 98867 | 3.6 | 150 | 10.2677 | 0 | 0 | 275.943 | 0 | 1
8/17 | 02:00:00 | 289.15 | 98875 | 2.6 | 150 | 10.2668 | 0 | 0 | 276.3 | 0 | 1
8/17 | 03:00:00 | 288.15 | 98867 | 2.6 | 160 | 10.2677 | 0 | 0 | 275.344 | 0 | 1
8/17 | 04:00:00 | 287.15 | 98858 | 2.1 | 170 | 9.6108 | 0 | 0 | 274.167 | 0 | 1
8/17 | 05:00:00 | 286.15 | 98850 | 1 | 222 | 8.9918 | 0 | 0 | 272.99 | 0 | 1
8/17 | 06:00:00 | 287.15 | 98858 | 0.5 | 269 | 9.6108 | 36 | 0 | 274.763 | 0 | 1
8/17 | 07:00:00 | 288.15 | 98867 | 0.5 | 277 | 10.2677 | 183.6 | 0 | 275.943 | 0 | 1
8/17 | 08:00:00 | 290.15 | 98883 | 1 | 169 | 10.266 | 727.2 | 381.6 | 277.629 | 0 | 1
8/17 | 09:00:00 | 292.15 | 98900 | 2.1 | 200 | 10.9618 | 1551.6 | 1832.4 | 279.117 | 0 | 1
8/17 | 10:00:00 | 293.15 | 98908 | 2.1 | 200 | 10.9609 | 1915.2 | 1886.4 | 280.347 | 0 | 1
8/17 | 11:00:00 | 294.15 | 98916 | 4.1 | 220 | 10.2625 | 2257.2 | 2016 | 281.078 | 0 | 1
8/17 | 12:00:00 | 295.15 | 98924 | 4.1 | 230 | 9.6043 | 2451.6 | 2134.8 | 281.805 | 0 | 1
8/17 | 13:00:00 | 295.15 | 98924 | 2.6 | 230 | 9.6043 | 2631.6 | 2674.8 | 281.529 | 0 | 1
8/17 | 14:00:00 | 296.15 | 98932 | 3.1 | 14 | 8.9842 | 2494.8 | 2674.8 | 282.253 | 0 | 1
8/17 | 15:00:00 | 297.15 | 98940 | 4.6 | 220 | 8.9835 | 2188.8 | 2527.2 | 283.206 | 0 | 1
8/17 | 16:00:00 | 296.15 | 98932 | 3.1 | 230 | 8.4009 | 1767.6 | 2314.8 | 281.877 | 0 | 1
8/17 | 17:00:00 | 296.15 | 98932 | 4.1 | 220 | 8.9842 | 1220.4 | 1742.4 | 282.108 | 0 | 1
8/17 | 18:00:00 | 296.15 | 98932 | 2.6 | 220 | 8.9842 | 658.8 | 925.2 | 282.108 | 0 | 1
8/17 | 19:00:00 | 294.15 | 98916 | 3.1 | 170 | 9.6051 | 198 | 158.4 | 280.576 | 0 | 1
8/17 | 20:00:00 | 293.15 | 98908 | 2.1 | 170 | 9.6059 | 0 | 0 | 279.622 | 0 | 1
8/17 | 21:00:00 | 292.15 | 98900 | 2.1 | 170 | 9.6067 | 0 | 0 | 278.941 | 0 | 1
8/17 | 22:00:00 | 290.15 | 98883 | 1 | 230 | 9.6084 | 0 | 0 | 277.285 | 0 | 1
8/17 | 23:00:00 | 288.15 | 98867 | 2.6 | 90 | 9.6099 | 0 | 0 | 275.608 | 0 | 1
8/17 | 24:00:00 | 289.15 | 98875 | 0.5 | 240 | 9.6091 | 0 | 0 | 276.449 | 0 | 1
8/18 | 01:00:00 | 287.15 | 98858 | 3.6 | 140 | 9.6108 | 0 | 0 | 274.763 | 0 | 1
8/18 | 02:00:00 | 287.15 | 98858 | 3.1 | 140 | 9.6108 | 0 | 0 | 274.763 | 0 | 1
8/18 | 03:00:00 | 286.15 | 98850 | 1.5 | 157 | 9.6116 | 0 | 0 | 273.806 | 0 | 1
8/18 | 04:00:00 | 286.15 | 98850 | 0.5 | 72 | 8.9918 | 0 | 0 | 272.287 | 0 | 1
8/18 | 05:00:00 | 286.15 | 98850 | 0 | 67 | 9.6116 | 0 | 0 | 272.509 | 0 | 1
8/18 | 06:00:00 | 286.15 | 98850 | 0 | 217 | 8.9918 | 82.8 | 0 | 272.723 | 0 | 1
8/18 | 07:00:00 | 288.15 | 98867 | 1 | 245 | 9.6099 | 457.2 | 612 | 274.852 | 0 | 1
8/18 | 08:00:00 | 290.15 | 98883 | 1.5 | 55 | 9.6084 | 993.6 | 1310.4 | 276.76 | 0 | 1
8/18 | 09:00:00 | 291.15 | 98892 | 2.6 | 240 | 10.265 | 1540.8 | 2044.8 | 277.939 | 0 | 1
8/18 | 10:00:00 | 293.15 | 98908 | 3.1 | 250 | 10.2634 | 2023.2 | 2412 | 279.848 | 0 | 1
8/18 | 11:00:00 | 294.15 | 98916 | 3.1 | 240 | 9.6051 | 2246.4 | 2098.8 | 280.85 | 0 | 1
8/18 | 12:00:00 | 295.15 | 98924 | 3.6 | 220 | 9.6043 | 2437.2 | 2134.8 | 281.805 | 0 | 1
8/18 | 13:00:00 | 295.15 | 98924 | 3.1 | 260 | 9.6043 | 2617.2 | 2671.2 | 281.529 | 0 | 1
8/18 | 14:00:00 | 296.15 | 98932 | 3.6 | 260 | 9.6035 | 2473.2 | 2664 | 282.483 | 0 | 1
8/18 | 15:00:00 | 295.15 | 98924 | 3.1 | 250 | 9.6043 | 2167.2 | 2412 | 281.529 | 0 | 1
8/18 | 16:00:00 | 293.15 | 98908 | 6.2 | 300 | 10.2634 | 1623.6 | 1764 | 280.122 | 0 | 1
8/18 | 17:00:00 | 293.15 | 98908 | 6.2 | 300 | 10.2634 | 1123.2 | 1378.8 | 280.122 | 0 | 1
8/18 | 18:00:00 | 292.15 | 98900 | 6.2 | 300 | 10.2642 | 601.2 | 716.4 | 279.166 | 0 | 1
8/18 | 19:00:00 | 291.15 | 98892 | 6.2 | 290 | 9.6075 | 176.4 | 75.6 | 277.986 | 0 | 1
8/18 | 20:00:00 | 289.15 | 98875 | 5.7 | 290 | 9.6091 | 0 | 0 | 276.449 | 0 | 1
8/18 | 21:00:00 | 289.15 | 98875 | 3.6 | 300 | 10.2668 | 0 | 0 | 276.789 | 0 | 1
8/18 | 22:00:00 | 289.15 | 98875 | 3.6 | 290 | 10.2668 | 0 | 0 | 276.789 | 0 | 1
8/18 | 23:00:00 | 289.15 | 98875 | 3.6 | 310 | 9.6091 | 0 | 0 | 276.449 | 0 | 1
8/18 | 24:00:00 | 288.15 | 98867 | 2.6 | 330 | 10.2677 | 0 | 0 | 275.943 | 0 | 1
8/19 | 01:00:00 | 288.15 | 98867 | 4.6 | 290 | 10.2677 | 0 | 0 | 275.943 | 0 | 1
8/19 | 02:00:00 | 287.15 | 98858 | 3.6 | 300 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
8/19 | 03:00:00 | 287.15 | 98858 | 3.6 | 300 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
8/19 | 04:00:00 | 286.15 | 98850 | 3.1 | 300 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
8/19 | 05:00:00 | 286.15 | 98850 | 2.6 | 300 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
8/19 | 06:00:00 | 286.15 | 98850 | 3.1 | 300 | 9.6116 | 75.6 | 0 | 273.212 | 0 | 1
8/19 | 07:00:00 | 286.15 | 98850 | 4.1 | 310 | 8.9918 | 446.4 | 601.2 | 272.723 | 0 | 1
8/19 | 08:00:00 | 286.15 | 98850 | 3.6 | 300 | 8.408 | 982.8 | 1310.4 | 272.499 | 0 | 1
8/19 | 09:00:00 | 288.15 | 98867 | 5.7 | 300 | 8.9902 | 1533.6 | 2059.2 | 274.629 | 0 | 1
8/19 | 10:00:00 | 289.15 | 98875 | 4.1 | 310 | 8.4059 | 1900.8 | 1915.2 | 275.626 | 0 | 1
8/19 | 11:00:00 | 290.15 | 98883 | 3.6 | 320 | 8.4052 | 2239.2 | 2041.2 | 276.579 | 0 | 1
8/19 | 12:00:00 | 291.15 | 98892 | 5.7 | 300 | 7.338 | 2437.2 | 2239.2 | 277.073 | 0 | 1
8/19 | 13:00:00 | 291.15 | 98892 | 5.7 | 290 | 7.855 | 2462.4 | 2242.8 | 277.303 | 0 | 1
8/19 | 14:00:00 | 291.15 | 98892 | 5.1 | 290 | 7.855 | 2329.2 | 2217.6 | 277.303 | 0 | 1
8/19 | 15:00:00 | 291.15 | 98892 | 4.1 | 330 | 6.8517 | 2044.8 | 2005.2 | 276.841 | 0 | 1
8/19 | 16:00:00 | 290.15 | 98883 | 5.1 | 300 | 7.8557 | 1616.4 | 1756.8 | 276.351 | 0 | 1
8/19 | 17:00:00 | 290.15 | 98883 | 6.2 | 280 | 8.4052 | 1108.8 | 1386 | 276.579 | 0 | 1
8/19 | 18:00:00 | 290.15 | 98883 | 6.7 | 280 | 8.4052 | 622.8 | 864 | 276.308 | 0 | 1
8/19 | 19:00:00 | 289.15 | 98875 | 6.7 | 280 | 8.4059 | 165.6 | 50.4 | 275.626 | 0 | 1
8/19 | 20:00:00 | 288.15 | 98867 | 5.7 | 290 | 8.9902 | 0 | 0 | 274.898 | 0 | 1
8/19 | 21:00:00 | 287.15 | 98858 | 4.1 | 300 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
8/19 | 22:00:00 | 286.15 | 98850 | 5.7 | 300 | 8.408 | 0 | 0 | 272.766 | 0 | 1
8/19 | 23:00:00 | 286.15 | 98850 | 6.2 | 300 | 8.408 | 0 | 0 | 272.766 | 0 | 1
8/19 | 24:00:00 | 285.15 | 98841 | 5.1 | 300 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
8/20 | 01:00:00 | 285.15 | 98841 | 5.1 | 310 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
8/20 | 02:00:00 | 285.15 | 98841 | 5.1 | 320 | 7.3418 | 0 | 0 | 271.729 | 0 | 1
8/20 | 03:00:00 | 284.15 | 98833 | 4.6 | 320 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
8/20 | 04:00:00 | 285.15 | 98841 | 3.1 | 340 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/20 | 05:00:00 | 285.15 | 98841 | 4.1 | 350 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/20 | 06:00:00 | 285.15 | 98841 | 4.6 | 310 | 7.3418 | 39.6 | 0 | 271.843 | 0 | 1
8/20 | 07:00:00 | 285.15 | 98841 | 4.6 | 320 | 7.3418 | 230.4 | 0 | 271.843 | 0 | 1
8/20 | 08:00:00 | 286.15 | 98850 | 5.1 | 350 | 7.3412 | 507.6 | 14.4 | 272.796 | 0 | 1
8/20 | 09:00:00 | 287.15 | 98858 | 6.2 | 350 | 7.3406 | 799.2 | 57.6 | 273.75 | 0 | 1
8/20 | 10:00:00 | 287.15 | 98858 | 5.7 | 340 | 7.3406 | 1051.2 | 165.6 | 273.75 | 0 | 1
8/20 | 11:00:00 | 289.15 | 98875 | 5.1 | 340 | 7.3393 | 2232 | 1890 | 275.169 | 0 | 1
8/20 | 12:00:00 | 289.15 | 98875 | 5.1 | 320 | 7.3393 | 2426.4 | 2239.2 | 275.169 | 0 | 1
8/20 | 13:00:00 | 290.15 | 98883 | 3.6 | 340 | 7.3387 | 2451.6 | 2246.4 | 276.121 | 0 | 1
8/20 | 14:00:00 | 291.15 | 98892 | 4.1 | 350 | 7.338 | 2314.8 | 2228.4 | 277.073 | 0 | 1
8/20 | 15:00:00 | 291.15 | 98892 | 5.1 | 360 | 6.8517 | 2026.8 | 2001.6 | 276.841 | 0 | 1
8/20 | 16:00:00 | 293.15 | 98908 | 5.1 | 350 | 6.3933 | 1609.2 | 1778.4 | 278.508 | 0 | 1
8/20 | 17:00:00 | 292.15 | 98900 | 5.1 | 360 | 6.8511 | 1166.4 | 1584 | 277.52 | 0 | 1
8/20 | 18:00:00 | 292.15 | 98900 | 3.6 | 10 | 6.8511 | 612 | 900 | 277.52 | 0 | 1
8/20 | 19:00:00 | 290.15 | 98883 | 1.5 | 40 | 7.8557 | 158.4 | 72 | 276.351 | 0 | 1
8/20 | 20:00:00 | 289.15 | 98875 | 2.1 | 350 | 7.8564 | 0 | 0 | 275.398 | 0 | 1
8/20 | 21:00:00 | 287.15 | 98858 | 2.1 | 10 | 7.8578 | 0 | 0 | 273.743 | 0 | 1
8/20 | 22:00:00 | 287.15 | 98858 | 2.6 | 350 | 7.8578 | 0 | 0 | 273.743 | 0 | 1
8/20 | 23:00:00 | 286.15 | 98850 | 2.6 | 290 | 7.8584 | 0 | 0 | 272.909 | 0 | 1
8/20 | 24:00:00 | 284.15 | 98833 | 1.5 | 270 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
8/21 | 01:00:00 | 284.15 | 98833 | 2.6 | 270 | 8.4095 | 0 | 0 | 271.449 | 0 | 1
8/21 | 02:00:00 | 284.15 | 98833 | 3.6 | 270 | 8.4095 | 0 | 0 | 271.449 | 0 | 1
8/21 | 03:00:00 | 283.15 | 98824 | 3.1 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/21 | 04:00:00 | 283.15 | 98824 | 3.1 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/21 | 05:00:00 | 283.15 | 98824 | 3.6 | 290 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/21 | 06:00:00 | 282.15 | 98815 | 1 | 41 | 7.3438 | 72 | 0 | 268.245 | 0 | 1
8/21 | 07:00:00 | 284.15 | 98833 | 3.1 | 280 | 8.4095 | 424.8 | 568.8 | 270.595 | 0 | 1
8/21 | 08:00:00 | 286.15 | 98850 | 3.6 | 280 | 8.9918 | 954 | 1126.8 | 272.723 | 0 | 1
8/21 | 09:00:00 | 288.15 | 98867 | 2.6 | 250 | 9.6099 | 871.2 | 165.6 | 275.608 | 0 | 1
8/21 | 10:00:00 | 290.15 | 98883 | 4.1 | 260 | 9.6084 | 1616.4 | 1058.4 | 277.285 | 0 | 1
8/21 | 11:00:00 | 291.15 | 98892 | 3.6 | 250 | 8.9879 | 2170.8 | 1857.6 | 277.76 | 0 | 1
8/21 | 12:00:00 | 292.15 | 98900 | 2.1 | 260 | 8.9872 | 2545.2 | 2653.2 | 278.441 | 0 | 1
8/21 | 13:00:00 | 294.15 | 98916 | 3.1 | 260 | 8.9857 | 2574 | 2721.6 | 280.347 | 0 | 1
8/21 | 14:00:00 | 294.15 | 98916 | 4.1 | 270 | 8.9857 | 2430 | 2656.8 | 280.347 | 0 | 1
8/21 | 15:00:00 | 294.15 | 98916 | 4.6 | 260 | 8.4023 | 2124 | 2466 | 280.117 | 0 | 1
8/21 | 16:00:00 | 294.15 | 98916 | 4.1 | 270 | 8.9857 | 1677.6 | 2206.8 | 280.347 | 0 | 1
8/21 | 17:00:00 | 294.15 | 98916 | 3.6 | 260 | 8.9857 | 1134 | 1616.4 | 280.347 | 0 | 1
8/21 | 18:00:00 | 293.15 | 98908 | 3.6 | 270 | 8.403 | 586.8 | 806.4 | 279.165 | 0 | 1
8/21 | 19:00:00 | 292.15 | 98900 | 2.6 | 250 | 8.4037 | 151.2 | 46.8 | 278.351 | 0 | 1
8/21 | 20:00:00 | 291.15 | 98892 | 2.1 | 240 | 8.4044 | 0 | 0 | 277.261 | 0 | 1
8/21 | 21:00:00 | 291.15 | 98892 | 2.6 | 240 | 8.9879 | 0 | 0 | 277.488 | 0 | 1
8/21 | 22:00:00 | 291.15 | 98892 | 2.1 | 220 | 10.265 | 0 | 0 | 278.703 | 0 | 1
8/21 | 23:00:00 | 291.15 | 98892 | 4.1 | 220 | 10.9627 | 0 | 0 | 278.927 | 0 | 1
8/21 | 24:00:00 | 290.15 | 98883 | 3.6 | 210 | 10.9637 | 0 | 0 | 277.969 | 0 | 1
8/22 | 01:00:00 | 290.15 | 98883 | 2.6 | 200 | 11.7037 | 0 | 0 | 278.191 | 0 | 1
8/22 | 02:00:00 | 289.15 | 98875 | 2.6 | 210 | 11.7047 | 0 | 0 | 277.232 | 0 | 1
8/22 | 03:00:00 | 289.15 | 98875 | 3.1 | 240 | 11.7047 | 0 | 0 | 277.232 | 0 | 1
8/22 | 04:00:00 | 289.15 | 98875 | 3.1 | 240 | 11.7047 | 0 | 0 | 277.232 | 0 | 1
8/22 | 05:00:00 | 289.15 | 98875 | 3.6 | 250 | 11.7047 | 0 | 0 | 277.232 | 0 | 1
8/22 | 06:00:00 | 289.15 | 98875 | 4.1 | 270 | 11.7047 | 36 | 0 | 277.232 | 0 | 1
8/22 | 07:00:00 | 289.15 | 98875 | 3.6 | 270 | 10.9646 | 216 | 0 | 277.011 | 0 | 1
8/22 | 08:00:00 | 288.15 | 98867 | 2.1 | 260 | 10.9655 | 489.6 | 28.8 | 276.053 | 0 | 1
8/22 | 09:00:00 | 288.15 | 98867 | 2.1 | 260 | 10.9655 | 777.6 | 72 | 276.053 | 0 | 1
8/22 | 10:00:00 | 288.15 | 98867 | 4.6 | 270 | 10.9655 | 1026 | 93.6 | 276.053 | 0 | 1
8/22 | 11:00:00 | 288.15 | 98867 | 4.1 | 280 | 10.2677 | 1213.2 | 266.4 | 275.831 | 0 | 1
8/22 | 12:00:00 | 288.15 | 98867 | 4.6 | 310 | 10.2677 | 2379.6 | 1868.4 | 275.344 | 0 | 1
8/22 | 13:00:00 | 289.15 | 98875 | 5.1 | 310 | 9.6091 | 2408.4 | 1879.2 | 276.076 | 0 | 1
8/22 | 14:00:00 | 289.15 | 98875 | 4.6 | 340 | 9.6091 | 1260 | 320.4 | 276.565 | 0 | 1
8/22 | 15:00:00 | 287.15 | 98858 | 6.2 | 20 | 9.6108 | 1980 | 1774.8 | 274.167 | 0 | 1
8/22 | 16:00:00 | 289.15 | 98875 | 6.2 | 360 | 8.9895 | 1562.4 | 1738.8 | 275.852 | 0 | 1
8/22 | 17:00:00 | 290.15 | 98883 | 4.6 | 20 | 8.9887 | 1058.4 | 1339.2 | 276.806 | 0 | 1
8/22 | 18:00:00 | 289.15 | 98875 | 3.1 | 20 | 8.4059 | 576 | 802.8 | 275.356 | 0 | 1
8/22 | 19:00:00 | 288.15 | 98867 | 1.5 | 40 | 8.4065 | 136.8 | 0 | 274.672 | 0 | 1
8/22 | 20:00:00 | 288.15 | 98867 | 1 | 10 | 8.4065 | 0 | 0 | 275.158 | 0 | 1
8/22 | 21:00:00 | 287.15 | 98858 | 1 | 350 | 8.4073 | 0 | 0 | 274.203 | 0 | 1
8/22 | 22:00:00 | 287.15 | 98858 | 1.5 | 340 | 8.4073 | 0 | 0 | 274.203 | 0 | 1
8/22 | 23:00:00 | 285.15 | 98841 | 3.1 | 300 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/22 | 24:00:00 | 285.15 | 98841 | 2.6 | 300 | 6.8552 | 0 | 0 | 271.616 | 0 | 1
8/23 | 01:00:00 | 284.15 | 98833 | 3.6 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
8/23 | 02:00:00 | 283.15 | 98824 | 3.6 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
8/23 | 03:00:00 | 282.15 | 98815 | 3.6 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
8/23 | 04:00:00 | 282.15 | 98815 | 3.1 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
8/23 | 05:00:00 | 283.15 | 98824 | 5.7 | 260 | 6.3988 | 0 | 0 | 269.37 | 0 | 1
8/23 | 06:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 64.8 | 0 | 268.971 | 0 | 1
8/23 | 07:00:00 | 284.15 | 98833 | 3.6 | 260 | 7.8598 | 403.2 | 446.4 | 270.371 | 0 | 1
8/23 | 08:00:00 | 285.15 | 98841 | 2.6 | 240 | 8.4088 | 928.8 | 1407.6 | 271.547 | 0 | 1
8/23 | 09:00:00 | 287.15 | 98858 | 5.1 | 220 | 8.991 | 1393.2 | 1630.8 | 273.944 | 0 | 1
8/23 | 10:00:00 | 288.15 | 98867 | 4.1 | 240 | 8.4065 | 1846.8 | 1965.6 | 274.672 | 0 | 1
8/23 | 11:00:00 | 289.15 | 98875 | 6.2 | 240 | 8.4059 | 2185.2 | 2113.2 | 275.626 | 0 | 1
8/23 | 12:00:00 | 290.15 | 98883 | 7.2 | 250 | 6.8523 | 2530.8 | 2527.2 | 275.62 | 0 | 1
8/23 | 13:00:00 | 291.15 | 98892 | 7.7 | 250 | 7.338 | 2408.4 | 2185.2 | 277.073 | 0 | 1
8/23 | 14:00:00 | 290.15 | 98883 | 7.7 | 250 | 7.3387 | 2268 | 2224.8 | 276.121 | 0 | 1
8/23 | 15:00:00 | 291.15 | 98892 | 7.2 | 240 | 7.855 | 1972.8 | 1969.2 | 277.303 | 0 | 1
8/23 | 16:00:00 | 291.15 | 98892 | 5.1 | 240 | 7.338 | 1551.6 | 1645.2 | 277.073 | 0 | 1
8/23 | 17:00:00 | 290.15 | 98883 | 7.7 | 240 | 7.8557 | 1044 | 1252.8 | 276.351 | 0 | 1
8/23 | 18:00:00 | 289.15 | 98875 | 7.2 | 230 | 8.4059 | 525.6 | 766.8 | 275.626 | 0 | 1
8/23 | 19:00:00 | 289.15 | 98875 | 5.7 | 220 | 8.9895 | 68.4 | 0 | 276.34 | 0 | 1
8/23 | 20:00:00 | 288.15 | 98867 | 6.7 | 230 | 9.6099 | 0 | 0 | 275.608 | 0 | 1
8/23 | 21:00:00 | 289.15 | 98875 | 3.6 | 220 | 9.6091 | 0 | 0 | 276.565 | 0 | 1
8/23 | 22:00:00 | 288.15 | 98867 | 5.7 | 210 | 8.9902 | 0 | 0 | 275.384 | 0 | 1
8/23 | 23:00:00 | 288.15 | 98867 | 9.3 | 220 | 8.9902 | 0 | 0 | 274.898 | 0 | 1
8/23 | 24:00:00 | 288.15 | 98867 | 8.2 | 220 | 8.9902 | 0 | 0 | 274.898 | 0 | 1
8/24 | 01:00:00 | 288.15 | 98867 | 7.2 | 230 | 8.4065 | 0 | 0 | 274.924 | 0 | 1
8/24 | 02:00:00 | 287.15 | 98858 | 6.2 | 220 | 8.4073 | 0 | 0 | 274.088 | 0 | 1
8/24 | 03:00:00 | 287.15 | 98858 | 6.7 | 210 | 8.4073 | 0 | 0 | 274.088 | 0 | 1
8/24 | 04:00:00 | 287.15 | 98858 | 9.3 | 220 | 8.991 | 0 | 0 | 274.428 | 0 | 1
8/24 | 05:00:00 | 288.15 | 98867 | 11.3 | 220 | 9.6099 | 0 | 0 | 275.122 | 0 | 1
8/24 | 06:00:00 | 287.15 | 98858 | 8.7 | 210 | 9.6108 | 57.6 | 0 | 274.167 | 0 | 1
8/24 | 07:00:00 | 287.15 | 98858 | 8.7 | 210 | 8.991 | 205.2 | 0 | 274.428 | 0 | 1
8/24 | 08:00:00 | 287.15 | 98858 | 7.2 | 210 | 9.6108 | 475.2 | 25.2 | 274.652 | 0 | 1
8/24 | 09:00:00 | 287.15 | 98858 | 8.2 | 220 | 9.6108 | 763.2 | 72 | 274.652 | 0 | 1
8/24 | 10:00:00 | 287.15 | 98858 | 7.2 | 210 | 10.2686 | 1011.6 | 93.6 | 274.874 | 0 | 1
8/24 | 11:00:00 | 287.15 | 98858 | 7.2 | 220 | 10.2686 | 1198.8 | 266.4 | 274.874 | 0 | 1
8/24 | 12:00:00 | 286.15 | 98850 | 7.2 | 260 | 8.9918 | 2358 | 1738.8 | 272.99 | 0 | 1
8/24 | 13:00:00 | 287.15 | 98858 | 4.1 | 250 | 9.6108 | 1321.2 | 327.6 | 274.652 | 0 | 1
8/24 | 14:00:00 | 288.15 | 98867 | 7.7 | 270 | 7.3399 | 2253.6 | 1904.4 | 274.218 | 0 | 1
8/24 | 15:00:00 | 289.15 | 98875 | 8.7 | 260 | 6.8529 | 2080.8 | 2455.2 | 274.67 | 0 | 1
8/24 | 16:00:00 | 289.15 | 98875 | 8.7 | 280 | 6.3955 | 1634.4 | 2077.2 | 274.439 | 0 | 1
8/24 | 17:00:00 | 288.15 | 98867 | 8.2 | 270 | 6.396 | 1094.4 | 1472.4 | 273.49 | 0 | 1
8/24 | 18:00:00 | 288.15 | 98867 | 6.7 | 250 | 6.8534 | 511.2 | 518.4 | 273.988 | 0 | 1
8/24 | 19:00:00 | 286.15 | 98850 | 4.6 | 230 | 7.3412 | 115.2 | 0 | 272.314 | 0 | 1
8/24 | 20:00:00 | 285.15 | 98841 | 3.1 | 250 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
8/24 | 21:00:00 | 285.15 | 98841 | 3.6 | 250 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
8/24 | 22:00:00 | 285.15 | 98841 | 3.6 | 240 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
8/24 | 23:00:00 | 283.15 | 98824 | 1.5 | 300 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
8/24 | 24:00:00 | 284.15 | 98833 | 3.6 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
8/25 | 01:00:00 | 283.15 | 98824 | 4.1 | 260 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
8/25 | 02:00:00 | 282.15 | 98815 | 3.1 | 240 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
8/25 | 03:00:00 | 283.15 | 98824 | 2.6 | 230 | 7.8605 | 0 | 0 | 269.684 | 0 | 1
8/25 | 04:00:00 | 282.15 | 98815 | 3.6 | 230 | 7.3438 | 0 | 0 | 268.245 | 0 | 1
8/25 | 05:00:00 | 282.15 | 98815 | 3.6 | 250 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
8/25 | 06:00:00 | 282.15 | 98815 | 2.1 | 250 | 7.3438 | 54 | 0 | 268.508 | 0 | 1
8/25 | 07:00:00 | 283.15 | 98824 | 3.1 | 250 | 7.8605 | 360 | 324 | 269.684 | 0 | 1
8/25 | 08:00:00 | 283.15 | 98824 | 3.6 | 240 | 7.8605 | 849.6 | 1029.6 | 269.684 | 0 | 1
8/25 | 09:00:00 | 285.15 | 98841 | 4.6 | 250 | 8.4088 | 1368 | 1620 | 271.813 | 0 | 1
8/25 | 10:00:00 | 286.15 | 98850 | 5.7 | 250 | 7.8584 | 1821.6 | 1893.6 | 272.541 | 0 | 1
8/25 | 11:00:00 | 283.15 | 98824 | 3.1 | 240 | 7.8605 | 2160 | 2188.8 | 269.684 | 0 | 1
8/25 | 12:00:00 | 283.15 | 98824 | 6.2 | 290 | 6.8564 | 2354.4 | 2102.4 | 269.234 | 0 | 1
8/25 | 13:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.8598 | 2516.4 | 2538 | 270.371 | 0 | 1
8/25 | 14:00:00 | 286.15 | 98850 | 5.1 | 260 | 7.8584 | 2232 | 2059.2 | 272.541 | 0 | 1
8/25 | 15:00:00 | 286.15 | 98850 | 4.6 | 260 | 8.408 | 1933.2 | 2019.6 | 272.766 | 0 | 1
8/25 | 16:00:00 | 287.15 | 98858 | 8.2 | 270 | 7.3406 | 1609.2 | 2131.2 | 272.999 | 0 | 1
8/25 | 17:00:00 | 287.15 | 98858 | 7.2 | 270 | 6.854 | 1072.8 | 1501.2 | 272.77 | 0 | 1
8/25 | 18:00:00 | 286.15 | 98850 | 7.7 | 260 | 6.8546 | 525.6 | 626.4 | 271.821 | 0 | 1
8/25 | 19:00:00 | 284.15 | 98833 | 4.6 | 250 | 7.8598 | 111.6 | 0 | 270.371 | 0 | 1
8/25 | 20:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
8/25 | 21:00:00 | 282.15 | 98815 | 4.1 | 240 | 7.3438 | 0 | 0 | 268.245 | 0 | 1
8/25 | 22:00:00 | 282.15 | 98815 | 4.1 | 270 | 7.3438 | 0 | 0 | 268.245 | 0 | 1
8/25 | 23:00:00 | 282.15 | 98815 | 5.1 | 260 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
8/25 | 24:00:00 | 282.15 | 98815 | 5.7 | 270 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
8/26 | 01:00:00 | 282.15 | 98815 | 4.1 | 250 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
8/26 | 02:00:00 | 282.15 | 98815 | 3.1 | 250 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
8/26 | 03:00:00 | 282.15 | 98815 | 4.1 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
8/26 | 04:00:00 | 282.15 | 98815 | 3.6 | 270 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
8/26 | 05:00:00 | 282.15 | 98815 | 4.1 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
8/26 | 06:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.8571 | 50.4 | 0 | 268.283 | 0 | 1
8/26 | 07:00:00 | 282.15 | 98815 | 4.1 | 240 | 6.8571 | 349.2 | 316.8 | 268.283 | 0 | 1
8/26 | 08:00:00 | 283.15 | 98824 | 4.1 | 250 | 7.3431 | 838.8 | 1022.4 | 269.46 | 0 | 1
8/26 | 09:00:00 | 285.15 | 98841 | 4.1 | 240 | 7.8591 | 1353.6 | 1519.2 | 271.588 | 0 | 1
8/26 | 10:00:00 | 285.15 | 98841 | 6.2 | 250 | 6.8552 | 1814.4 | 1908 | 271.136 | 0 | 1
8/26 | 11:00:00 | 286.15 | 98850 | 7.7 | 240 | 7.3412 | 2149.2 | 2196 | 272.314 | 0 | 1
8/26 | 12:00:00 | 286.15 | 98850 | 9.3 | 250 | 6.8546 | 2340 | 2257.2 | 272.087 | 0 | 1
8/26 | 13:00:00 | 286.15 | 98850 | 8.7 | 260 | 6.8546 | 2365.2 | 2260.8 | 272.087 | 0 | 1
8/26 | 14:00:00 | 286.15 | 98850 | 6.2 | 240 | 7.8584 | 2217.6 | 2206.8 | 272.541 | 0 | 1
8/26 | 15:00:00 | 285.15 | 98841 | 6.7 | 270 | 8.4088 | 1918.8 | 1771.2 | 271.813 | 0 | 1
8/26 | 16:00:00 | 285.15 | 98841 | 7.2 | 250 | 7.3418 | 831.6 | 241.2 | 271.843 | 0 | 1
8/26 | 17:00:00 | 286.15 | 98850 | 8.7 | 260 | 7.8584 | 990 | 1022.4 | 272.541 | 0 | 1
8/26 | 18:00:00 | 286.15 | 98850 | 7.7 | 250 | 7.8584 | 478.8 | 478.8 | 272.541 | 0 | 1
8/26 | 19:00:00 | 286.15 | 98850 | 6.2 | 250 | 7.8584 | 97.2 | 0 | 272.541 | 0 | 1
8/26 | 20:00:00 | 286.15 | 98850 | 6.7 | 250 | 7.8584 | 0 | 0 | 273.023 | 0 | 1
8/26 | 21:00:00 | 286.15 | 98850 | 8.2 | 250 | 7.8584 | 0 | 0 | 272.541 | 0 | 1
8/26 | 22:00:00 | 285.15 | 98841 | 7.2 | 240 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
8/26 | 23:00:00 | 285.15 | 98841 | 7.7 | 250 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
8/26 | 24:00:00 | 285.15 | 98841 | 7.2 | 250 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
8/27 | 01:00:00 | 285.15 | 98841 | 5.7 | 250 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
8/27 | 02:00:00 | 285.15 | 98841 | 4.6 | 250 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
8/27 | 03:00:00 | 284.15 | 98833 | 4.6 | 240 | 8.4095 | 0 | 0 | 270.859 | 0 | 1
8/27 | 04:00:00 | 285.15 | 98841 | 6.2 | 250 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
8/27 | 05:00:00 | 285.15 | 98841 | 5.7 | 260 | 8.9926 | 0 | 0 | 271.77 | 0 | 1
8/27 | 06:00:00 | 285.15 | 98841 | 5.7 | 250 | 8.9926 | 46.8 | 0 | 271.77 | 0 | 1
8/27 | 07:00:00 | 285.15 | 98841 | 3.6 | 240 | 8.9926 | 356.4 | 464.4 | 271.77 | 0 | 1
8/27 | 08:00:00 | 286.15 | 98850 | 2.6 | 230 | 8.9918 | 871.2 | 1342.8 | 272.723 | 0 | 1
8/27 | 09:00:00 | 286.15 | 98850 | 4.6 | 260 | 8.9918 | 1335.6 | 1602 | 272.99 | 0 | 1
8/27 | 10:00:00 | 287.15 | 98858 | 4.6 | 240 | 8.991 | 1789.2 | 1929.6 | 273.944 | 0 | 1
8/27 | 11:00:00 | 287.15 | 98858 | 5.1 | 250 | 8.4073 | 2127.6 | 2030.4 | 273.719 | 0 | 1
8/27 | 12:00:00 | 288.15 | 98867 | 5.1 | 260 | 8.4065 | 2314.8 | 2077.2 | 274.672 | 0 | 1
8/27 | 13:00:00 | 288.15 | 98867 | 4.6 | 250 | 8.4065 | 2340 | 2080.8 | 274.672 | 0 | 1
8/27 | 14:00:00 | 288.15 | 98867 | 4.1 | 250 | 8.9902 | 2192.4 | 2041.2 | 274.898 | 0 | 1
8/27 | 15:00:00 | 289.15 | 98875 | 5.1 | 270 | 8.4059 | 1900.8 | 2008.8 | 275.626 | 0 | 1
8/27 | 16:00:00 | 289.15 | 98875 | 5.7 | 250 | 8.4059 | 1476 | 1706.4 | 275.626 | 0 | 1
8/27 | 17:00:00 | 289.15 | 98875 | 5.1 | 260 | 8.4059 | 968.4 | 1274.4 | 275.626 | 0 | 1
8/27 | 18:00:00 | 288.15 | 98867 | 4.6 | 260 | 7.857 | 464.4 | 460.8 | 274.446 | 0 | 1
8/27 | 19:00:00 | 288.15 | 98867 | 3.6 | 260 | 7.857 | 93.6 | 0 | 274.177 | 0 | 1
8/27 | 20:00:00 | 287.15 | 98858 | 2.6 | 250 | 8.4073 | 0 | 0 | 274.088 | 0 | 1
8/27 | 21:00:00 | 285.15 | 98841 | 3.6 | 250 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
8/27 | 22:00:00 | 285.15 | 98841 | 3.6 | 250 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
8/27 | 23:00:00 | 284.15 | 98833 | 4.6 | 250 | 8.4095 | 0 | 0 | 271.449 | 0 | 1
8/27 | 24:00:00 | 284.15 | 98833 | 1.5 | 260 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
8/28 | 01:00:00 | 284.15 | 98833 | 2.1 | 210 | 8.4095 | 0 | 0 | 271.449 | 0 | 1
8/28 | 02:00:00 | 285.15 | 98841 | 3.1 | 210 | 8.9926 | 0 | 0 | 272.627 | 0 | 1
8/28 | 03:00:00 | 286.15 | 98850 | 3.1 | 210 | 8.9918 | 0 | 0 | 273.583 | 0 | 1
8/28 | 04:00:00 | 285.15 | 98841 | 3.1 | 240 | 8.4088 | 0 | 0 | 272.404 | 0 | 1
8/28 | 05:00:00 | 286.15 | 98850 | 3.1 | 210 | 8.408 | 0 | 0 | 273.248 | 0 | 1
8/28 | 06:00:00 | 286.15 | 98850 | 2.1 | 210 | 8.408 | 25.2 | 0 | 273.248 | 0 | 1
8/28 | 07:00:00 | 286.15 | 98850 | 3.6 | 210 | 8.9918 | 136.8 | 0 | 273.583 | 0 | 1
8/28 | 08:00:00 | 287.15 | 98858 | 5.7 | 220 | 8.991 | 856.8 | 1051.2 | 273.676 | 0 | 1
8/28 | 09:00:00 | 287.15 | 98858 | 5.7 | 230 | 9.6108 | 1400.4 | 1926 | 273.899 | 0 | 1
8/28 | 10:00:00 | 289.15 | 98875 | 6.7 | 220 | 9.6091 | 1879.2 | 2365.2 | 275.806 | 0 | 1
8/28 | 11:00:00 | 290.15 | 98883 | 7.7 | 230 | 10.266 | 2102.4 | 2073.6 | 277.255 | 0 | 1
8/28 | 12:00:00 | 291.15 | 98892 | 9.8 | 230 | 9.6075 | 2293.2 | 2059.2 | 277.986 | 0 | 1
8/28 | 13:00:00 | 290.15 | 98883 | 7.7 | 240 | 10.266 | 2311.2 | 2052 | 277.255 | 0 | 1
8/28 | 14:00:00 | 292.15 | 98900 | 6.2 | 230 | 10.2642 | 2170.8 | 2019.6 | 279.166 | 0 | 1
8/28 | 15:00:00 | 291.15 | 98892 | 7.7 | 230 | 10.265 | 1872 | 1969.2 | 278.211 | 0 | 1
8/28 | 16:00:00 | 292.15 | 98900 | 8.7 | 230 | 10.2642 | 1450.8 | 1321.2 | 279.166 | 0 | 1
8/28 | 17:00:00 | 292.15 | 98900 | 7.2 | 240 | 10.2642 | 525.6 | 50.4 | 279.66 | 0 | 1
8/28 | 18:00:00 | 292.15 | 98900 | 7.7 | 240 | 10.2642 | 446.4 | 633.6 | 279.166 | 0 | 1
8/28 | 19:00:00 | 290.15 | 98883 | 8.2 | 230 | 10.266 | 43.2 | 0 | 277.746 | 0 | 1
8/28 | 20:00:00 | 290.15 | 98883 | 8.2 | 230 | 10.266 | 0 | 0 | 277.746 | 0 | 1
8/28 | 21:00:00 | 290.15 | 98883 | 8.7 | 230 | 10.266 | 0 | 0 | 277.746 | 0 | 1
8/28 | 22:00:00 | 290.15 | 98883 | 6.7 | 230 | 10.266 | 0 | 0 | 277.746 | 0 | 1
8/28 | 23:00:00 | 289.15 | 98875 | 5.1 | 230 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
8/28 | 24:00:00 | 289.15 | 98875 | 6.7 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
8/29 | 01:00:00 | 289.15 | 98875 | 7.2 | 230 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
8/29 | 02:00:00 | 289.15 | 98875 | 6.7 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
8/29 | 03:00:00 | 289.15 | 98875 | 5.7 | 220 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
8/29 | 04:00:00 | 289.15 | 98875 | 6.7 | 230 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
8/29 | 05:00:00 | 289.15 | 98875 | 6.7 | 220 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
8/29 | 06:00:00 | 289.15 | 98875 | 6.7 | 230 | 10.9646 | 39.6 | 0 | 276.251 | 0 | 1
8/29 | 07:00:00 | 289.15 | 98875 | 6.7 | 230 | 11.7047 | 334.8 | 504 | 276.472 | 0 | 1
8/29 | 08:00:00 | 290.15 | 98883 | 6.2 | 230 | 11.7037 | 439.2 | 14.4 | 278.191 | 0 | 1
8/29 | 09:00:00 | 290.15 | 98883 | 6.2 | 230 | 12.4883 | 720 | 54 | 278.412 | 0 | 1
8/29 | 10:00:00 | 290.15 | 98883 | 5.7 | 250 | 12.0903 | 968.4 | 230.4 | 278.301 | 0 | 1
8/29 | 11:00:00 | 289.15 | 98875 | 5.7 | 270 | 11.7047 | 2080.8 | 1663.2 | 276.743 | 0 | 1
8/29 | 12:00:00 | 289.15 | 98875 | 6.7 | 280 | 10.2668 | 1260 | 118.8 | 276.789 | 0 | 1
8/29 | 13:00:00 | 289.15 | 98875 | 6.2 | 270 | 8.9895 | 1278 | 108 | 276.34 | 0 | 1
8/29 | 14:00:00 | 290.15 | 98883 | 6.7 | 280 | 8.4052 | 1198.8 | 108 | 277.068 | 0 | 1
8/29 | 15:00:00 | 291.15 | 98892 | 8.7 | 290 | 7.338 | 1036.8 | 194.4 | 277.563 | 0 | 1
8/29 | 16:00:00 | 291.15 | 98892 | 6.2 | 270 | 8.4044 | 799.2 | 104.4 | 278.023 | 0 | 1
8/29 | 17:00:00 | 290.15 | 98883 | 5.7 | 280 | 8.4052 | 990 | 1188 | 276.308 | 0 | 1
8/29 | 18:00:00 | 289.15 | 98875 | 5.1 | 260 | 7.8564 | 457.2 | 536.4 | 275.129 | 0 | 1
8/29 | 19:00:00 | 288.15 | 98867 | 4.6 | 270 | 7.857 | 79.2 | 0 | 274.177 | 0 | 1
8/29 | 20:00:00 | 286.15 | 98850 | 2.1 | 280 | 7.8584 | 0 | 0 | 272.909 | 0 | 1
8/29 | 21:00:00 | 285.15 | 98841 | 1.5 | 191 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
8/29 | 22:00:00 | 284.15 | 98833 | 3.1 | 260 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
8/29 | 23:00:00 | 284.15 | 98833 | 2.6 | 300 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
8/29 | 24:00:00 | 283.15 | 98824 | 3.1 | 240 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/30 | 01:00:00 | 283.15 | 98824 | 1.5 | 270 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
8/30 | 02:00:00 | 282.15 | 98815 | 2.6 | 300 | 7.3438 | 0 | 0 | 269.092 | 0 | 1
8/30 | 03:00:00 | 282.15 | 98815 | 2.1 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
8/30 | 04:00:00 | 283.15 | 98824 | 1.5 | 290 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
8/30 | 05:00:00 | 283.15 | 98824 | 0 | 277 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
8/30 | 06:00:00 | 283.15 | 98824 | 1 | 186 | 7.8605 | 18 | 0 | 270.161 | 0 | 1
8/30 | 07:00:00 | 284.15 | 98833 | 1 | 55 | 8.4095 | 169.2 | 0 | 271.339 | 0 | 1
8/30 | 08:00:00 | 285.15 | 98841 | 1 | 183 | 8.4088 | 435.6 | 21.6 | 272.294 | 0 | 1
8/30 | 09:00:00 | 286.15 | 98850 | 1.5 | 221 | 8.9918 | 720 | 68.4 | 273.473 | 0 | 1
8/30 | 10:00:00 | 287.15 | 98858 | 2.1 | 110 | 8.991 | 968.4 | 93.6 | 274.428 | 0 | 1
8/30 | 11:00:00 | 288.15 | 98867 | 2.6 | 140 | 9.6099 | 1152 | 262.8 | 275.608 | 0 | 1
8/30 | 12:00:00 | 290.15 | 98883 | 3.1 | 140 | 10.266 | 2257.2 | 1864.8 | 277.255 | 0 | 1
8/30 | 13:00:00 | 292.15 | 98900 | 2.6 | 120 | 10.9618 | 2412 | 2563.2 | 279.117 | 0 | 1
8/30 | 14:00:00 | 294.15 | 98916 | 2.6 | 160 | 11.6997 | 2127.6 | 2070 | 281.528 | 0 | 1
8/30 | 15:00:00 | 295.15 | 98924 | 3.1 | 170 | 12.483 | 1828.8 | 2084.4 | 282.709 | 0 | 1
8/30 | 16:00:00 | 294.15 | 98916 | 3.6 | 150 | 12.484 | 1404 | 1821.6 | 281.751 | 0 | 1
8/30 | 17:00:00 | 295.15 | 98924 | 3.1 | 160 | 12.483 | 961.2 | 1555.2 | 282.433 | 0 | 1
8/30 | 18:00:00 | 294.15 | 98916 | 2.1 | 160 | 12.484 | 435.6 | 640.8 | 281.476 | 0 | 1
8/30 | 19:00:00 | 293.15 | 98908 | 3.6 | 90 | 12.485 | 72 | 0 | 280.519 | 0 | 1
8/30 | 20:00:00 | 292.15 | 98900 | 3.1 | 90 | 12.4861 | 0 | 0 | 279.562 | 0 | 1
8/30 | 21:00:00 | 292.15 | 98900 | 3.1 | 110 | 12.4861 | 0 | 0 | 280.331 | 0 | 1
8/30 | 22:00:00 | 291.15 | 98892 | 4.1 | 120 | 12.4871 | 0 | 0 | 279.484 | 0 | 1
8/30 | 23:00:00 | 290.15 | 98883 | 4.6 | 140 | 10.9637 | 0 | 0 | 277.969 | 0 | 1
8/30 | 24:00:00 | 289.15 | 98875 | 4.1 | 140 | 10.9646 | 0 | 0 | 277.123 | 0 | 1
8/31 | 01:00:00 | 289.15 | 98875 | 3.1 | 150 | 10.2668 | 0 | 0 | 276.789 | 0 | 1
8/31 | 02:00:00 | 287.15 | 98858 | 3.6 | 140 | 10.2686 | 0 | 0 | 274.985 | 0 | 1
8/31 | 03:00:00 | 287.15 | 98858 | 2.6 | 130 | 10.2686 | 0 | 0 | 274.985 | 0 | 1
8/31 | 04:00:00 | 286.15 | 98850 | 3.1 | 110 | 9.6116 | 0 | 0 | 273.806 | 0 | 1
8/31 | 05:00:00 | 285.15 | 98841 | 2.6 | 100 | 8.9926 | 0 | 0 | 271.336 | 0 | 1
8/31 | 06:00:00 | 285.15 | 98841 | 3.1 | 100 | 8.9926 | 28.8 | 0 | 272.036 | 0 | 1
8/31 | 07:00:00 | 286.15 | 98850 | 3.1 | 90 | 9.6116 | 295.2 | 352.8 | 273.212 | 0 | 1
8/31 | 08:00:00 | 287.15 | 98858 | 3.1 | 28 | 10.2686 | 259.2 | 0 | 274.985 | 0 | 1
8/31 | 09:00:00 | 288.15 | 98867 | 3.1 | 110 | 10.9655 | 705.6 | 90 | 276.053 | 0 | 1
8/31 | 10:00:00 | 290.15 | 98883 | 2.1 | 110 | 11.7037 | 1825.2 | 1850.4 | 277.428 | 0 | 1
8/31 | 11:00:00 | 292.15 | 98900 | 3.1 | 120 | 12.4861 | 2170.8 | 2592 | 279.562 | 0 | 1
8/31 | 12:00:00 | 293.15 | 98908 | 3.1 | 130 | 13.3163 | 2361.6 | 2707.2 | 280.74 | 0 | 1
8/31 | 13:00:00 | 295.15 | 98924 | 3.1 | 120 | 13.3141 | 2246.4 | 2264.4 | 282.932 | 0 | 1
8/31 | 14:00:00 | 297.15 | 98940 | 3.6 | 130 | 14.1924 | 2098.8 | 2160 | 285.072 | 0 | 1
8/31 | 15:00:00 | 298.15 | 98948 | 4.1 | 140 | 14.1913 | 1803.6 | 2048.4 | 286.031 | 0 | 1
8/31 | 16:00:00 | 298.15 | 98948 | 4.6 | 160 | 13.3108 | 1386 | 1587.6 | 285.808 | 0 | 1
8/31 | 17:00:00 | 294.65 | 98920 | 2.8 | 243 | 12.4835 | 781.2 | 640.8 | 282.488 | 0 | 1
8/31 | 18:00:00 | 291.15 | 98892 | 1 | 313 | 10.9627 | 421.2 | 302.4 | 278.162 | 0 | 1
8/31 | 19:00:00 | 290.35 | 98885 | 3 | 148 | 10.4021 | 64.8 | 0 | 277.491 | 0 | 1
8/31 | 20:00:00 | 290.35 | 98885 | 2.6 | 154 | 10.4021 | 0 | 0 | 277.491 | 0 | 1
8/31 | 21:00:00 | 290.15 | 98883 | 1.7 | 145 | 10.266 | 0 | 0 | 277.255 | 0 | 1
8/31 | 22:00:00 | 288.35 | 98868 | 1.5 | 122 | 9.6098 | 0 | 0 | 275.684 | 0 | 1
8/31 | 23:00:00 | 286.65 | 98854 | 1.4 | 89 | 8.8719 | 0 | 0 | 273.791 | 0 | 1
8/31 | 24:00:00 | 284.95 | 98839 | 1.4 | 70 | 8.13 | 0 | 0 | 271.991 | 0 | 1
9/1 | 01:00:00 | 282.95 | 98822 | 1.4 | 65 | 7.4443 | 0 | 0 | 269.791 | 0 | 1
9/1 | 02:00:00 | 282.65 | 98820 | 1.4 | 67 | 7.2437 | 0 | 0 | 269.415 | 0 | 1
9/1 | 03:00:00 | 282.35 | 98817 | 1.5 | 77 | 7.2439 | 0 | 0 | 269.129 | 0 | 1
9/1 | 04:00:00 | 282.15 | 98815 | 1.4 | 105 | 7.2441 | 0 | 0 | 268.938 | 0 | 1
9/1 | 05:00:00 | 282.65 | 98820 | 1.3 | 91 | 7.2437 | 0 | 0 | 269.415 | 0 | 1
9/1 | 06:00:00 | 283.65 | 98828 | 1.4 | 101 | 7.4438 | 25.2 | 0 | 269.98 | 0 | 1
9/1 | 07:00:00 | 282.15 | 98815 | 0.5 | 172 | 7.3438 | 158.4 | 0 | 268.983 | 0 | 1
9/1 | 08:00:00 | 284.15 | 98833 | 1 | 3 | 7.3425 | 806.4 | 972 | 270.147 | 0 | 1
9/1 | 09:00:00 | 286.15 | 98850 | 2.1 | 120 | 7.8584 | 975.6 | 572.4 | 272.909 | 0 | 1
9/1 | 10:00:00 | 288.15 | 98867 | 2.1 | 53 | 7.857 | 1825.2 | 2070 | 274.177 | 0 | 1
9/1 | 11:00:00 | 289.15 | 98875 | 2.1 | 192 | 7.3393 | 2059.2 | 2037.6 | 275.169 | 0 | 1
9/1 | 12:00:00 | 288.15 | 98867 | 3.1 | 150 | 6.8534 | 2246.4 | 1929.6 | 273.988 | 0 | 1
9/1 | 13:00:00 | 289.15 | 98875 | 3.1 | 180 | 6.8529 | 1256.4 | 187.2 | 275.426 | 0 | 1
9/1 | 14:00:00 | 289.15 | 98875 | 3.6 | 150 | 6.8529 | 1173.6 | 212.4 | 275.426 | 0 | 1
9/1 | 15:00:00 | 290.15 | 98883 | 4.1 | 180 | 6.8523 | 1008 | 72 | 276.378 | 0 | 1
9/1 | 16:00:00 | 290.15 | 98883 | 4.1 | 150 | 6.8523 | 1386 | 1519.2 | 275.89 | 0 | 1
9/1 | 17:00:00 | 291.15 | 98892 | 3.6 | 150 | 6.8517 | 932.4 | 1371.6 | 276.57 | 0 | 1
9/1 | 18:00:00 | 290.15 | 98883 | 3.6 | 150 | 6.3949 | 406.8 | 478.8 | 275.388 | 0 | 1
9/1 | 19:00:00 | 289.15 | 98875 | 3.1 | 170 | 6.3955 | 61.2 | 0 | 274.439 | 0 | 1
9/1 | 20:00:00 | 288.15 | 98867 | 3.6 | 150 | 6.8534 | 0 | 0 | 273.988 | 0 | 1
9/1 | 21:00:00 | 286.15 | 98850 | 3.6 | 150 | 7.3412 | 0 | 0 | 272.563 | 0 | 1
9/1 | 22:00:00 | 285.15 | 98841 | 4.1 | 140 | 7.3418 | 0 | 0 | 271.729 | 0 | 1
9/1 | 23:00:00 | 284.15 | 98833 | 3.1 | 150 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/1 | 24:00:00 | 284.15 | 98833 | 3.6 | 160 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/2 | 01:00:00 | 284.15 | 98833 | 4.1 | 170 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/2 | 02:00:00 | 284.15 | 98833 | 4.6 | 170 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/2 | 03:00:00 | 284.15 | 98833 | 4.6 | 160 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/2 | 04:00:00 | 284.15 | 98833 | 3.1 | 160 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/2 | 05:00:00 | 284.15 | 98833 | 2.6 | 160 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/2 | 06:00:00 | 284.15 | 98833 | 3.6 | 160 | 7.3425 | 14.4 | 0 | 270.89 | 0 | 1
9/2 | 07:00:00 | 284.15 | 98833 | 2.1 | 244 | 7.3425 | 176.4 | 0 | 270.89 | 0 | 1
9/2 | 08:00:00 | 285.15 | 98841 | 2.6 | 150 | 7.8591 | 457.2 | 46.8 | 272.069 | 0 | 1
9/2 | 09:00:00 | 285.15 | 98841 | 2.6 | 150 | 7.8591 | 774 | 334.8 | 272.069 | 0 | 1
9/2 | 10:00:00 | 287.15 | 98858 | 2.1 | 210 | 8.4073 | 1807.2 | 1857.6 | 273.451 | 0 | 1
9/2 | 11:00:00 | 290.15 | 98883 | 3.6 | 240 | 8.9887 | 2034 | 2080.8 | 276.806 | 0 | 1
9/2 | 12:00:00 | 292.15 | 98900 | 5.1 | 260 | 8.9872 | 2217.6 | 2138.4 | 278.714 | 0 | 1
9/2 | 13:00:00 | 292.15 | 98900 | 8.2 | 240 | 8.9872 | 2368.8 | 2530.8 | 278.441 | 0 | 1
9/2 | 14:00:00 | 291.15 | 98892 | 7.2 | 230 | 8.9879 | 2088 | 2102.4 | 277.76 | 0 | 1
9/2 | 15:00:00 | 292.15 | 98900 | 4.1 | 250 | 9.6067 | 1782 | 1933.2 | 278.941 | 0 | 1
9/2 | 16:00:00 | 291.15 | 98892 | 7.2 | 260 | 8.4044 | 1360.8 | 1641.6 | 277.532 | 0 | 1
9/2 | 17:00:00 | 291.15 | 98892 | 4.6 | 280 | 9.6075 | 853.2 | 1155.6 | 277.986 | 0 | 1
9/2 | 18:00:00 | 291.15 | 98892 | 4.1 | 260 | 9.6075 | 388.8 | 500.4 | 277.714 | 0 | 1
9/2 | 19:00:00 | 289.15 | 98875 | 2.6 | 260 | 8.9895 | 57.6 | 0 | 275.582 | 0 | 1
9/2 | 20:00:00 | 289.15 | 98875 | 2.6 | 240 | 8.9895 | 0 | 0 | 275.852 | 0 | 1
9/2 | 21:00:00 | 289.15 | 98875 | 3.1 | 220 | 8.4059 | 0 | 0 | 275.356 | 0 | 1
9/2 | 22:00:00 | 289.15 | 98875 | 4.1 | 230 | 7.8564 | 0 | 0 | 275.129 | 0 | 1
9/2 | 23:00:00 | 288.15 | 98867 | 5.7 | 230 | 8.4065 | 0 | 0 | 274.404 | 0 | 1
9/2 | 24:00:00 | 287.15 | 98858 | 4.6 | 230 | 8.4073 | 0 | 0 | 274.088 | 0 | 1
9/3 | 01:00:00 | 287.15 | 98858 | 2.1 | 220 | 8.4073 | 0 | 0 | 274.203 | 0 | 1
9/3 | 02:00:00 | 287.15 | 98858 | 2.1 | 170 | 8.4073 | 0 | 0 | 274.203 | 0 | 1
9/3 | 03:00:00 | 288.15 | 98867 | 2.6 | 210 | 8.9902 | 0 | 0 | 275.384 | 0 | 1
9/3 | 04:00:00 | 289.15 | 98875 | 3.1 | 210 | 8.9895 | 0 | 0 | 276.34 | 0 | 1
9/3 | 05:00:00 | 289.15 | 98875 | 3.1 | 220 | 8.9895 | 0 | 0 | 276.34 | 0 | 1
9/3 | 06:00:00 | 288.15 | 98867 | 2.1 | 200 | 8.9902 | 18 | 0 | 274.898 | 0 | 1
9/3 | 07:00:00 | 288.15 | 98867 | 3.1 | 170 | 8.9902 | 262.8 | 262.8 | 274.898 | 0 | 1
9/3 | 08:00:00 | 289.15 | 98875 | 4.1 | 210 | 9.6091 | 727.2 | 903.6 | 276.076 | 0 | 1
9/3 | 09:00:00 | 289.15 | 98875 | 5.1 | 230 | 8.9895 | 1238.4 | 1540.8 | 275.852 | 0 | 1
9/3 | 10:00:00 | 289.15 | 98875 | 3.6 | 230 | 8.9895 | 1684.8 | 1900.8 | 275.852 | 0 | 1
9/3 | 11:00:00 | 290.15 | 98883 | 3.6 | 220 | 9.6084 | 2012.4 | 1818 | 277.031 | 0 | 1
9/3 | 12:00:00 | 290.15 | 98883 | 3.6 | 230 | 9.6084 | 1216.8 | 118.8 | 277.521 | 0 | 1
9/3 | 13:00:00 | 291.15 | 98892 | 3.6 | 230 | 10.265 | 1227.6 | 108 | 278.703 | 0 | 1
9/3 | 14:00:00 | 291.15 | 98892 | 4.1 | 220 | 9.6075 | 1144.8 | 104.4 | 278.478 | 0 | 1
9/3 | 15:00:00 | 291.15 | 98892 | 5.1 | 220 | 9.6075 | 979.2 | 104.4 | 278.478 | 0 | 1
9/3 | 16:00:00 | 291.15 | 98892 | 3.6 | 240 | 9.6075 | 1335.6 | 1274.4 | 277.986 | 0 | 1
9/3 | 17:00:00 | 290.15 | 98883 | 5.7 | 230 | 10.266 | 831.6 | 1015.2 | 277.255 | 0 | 1
9/3 | 18:00:00 | 290.15 | 98883 | 4.6 | 220 | 10.266 | 349.2 | 388.8 | 277.255 | 0 | 1
9/3 | 19:00:00 | 289.15 | 98875 | 3.6 | 220 | 10.2668 | 25.2 | 0 | 276.789 | 0 | 1
9/3 | 20:00:00 | 289.15 | 98875 | 2.1 | 240 | 10.2668 | 0 | 0 | 276.3 | 0 | 1
9/3 | 21:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.2668 | 0 | 0 | 276.3 | 0 | 1
9/3 | 22:00:00 | 289.15 | 98875 | 3.1 | 190 | 10.2668 | 0 | 0 | 276.3 | 0 | 1
9/3 | 23:00:00 | 288.15 | 98867 | 2.6 | 190 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
9/3 | 24:00:00 | 288.15 | 98867 | 2.6 | 240 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
9/4 | 01:00:00 | 288.15 | 98867 | 3.6 | 250 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
9/4 | 02:00:00 | 288.15 | 98867 | 2.1 | 280 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
9/4 | 03:00:00 | 287.15 | 98858 | 2.1 | 290 | 9.6108 | 0 | 0 | 273.899 | 0 | 1
9/4 | 04:00:00 | 286.15 | 98850 | 2.6 | 310 | 9.6116 | 0 | 0 | 272.945 | 0 | 1
9/4 | 05:00:00 | 285.15 | 98841 | 2.1 | 290 | 8.9926 | 0 | 0 | 272.036 | 0 | 1
9/4 | 06:00:00 | 285.15 | 98841 | 2.6 | 300 | 8.4088 | 7.2 | 0 | 272.294 | 0 | 1
9/4 | 07:00:00 | 285.15 | 98841 | 2.6 | 300 | 8.4088 | 252 | 248.4 | 271.813 | 0 | 1
9/4 | 08:00:00 | 286.15 | 98850 | 2.1 | 290 | 8.9918 | 716.4 | 896.4 | 272.99 | 0 | 1
9/4 | 09:00:00 | 287.15 | 98858 | 1.5 | 327 | 8.4073 | 1224 | 1540.8 | 273.719 | 0 | 1
9/4 | 10:00:00 | 288.15 | 98867 | 1 | 218 | 8.4065 | 1670.4 | 1900.8 | 274.672 | 0 | 1
9/4 | 11:00:00 | 289.15 | 98875 | 1 | 71 | 8.4059 | 2001.6 | 1832.4 | 275.626 | 0 | 1
9/4 | 12:00:00 | 289.15 | 98875 | 1 | 131 | 8.4059 | 1213.2 | 277.2 | 276.113 | 0 | 1
9/4 | 13:00:00 | 289.15 | 98875 | 0.5 | 11 | 8.4059 | 1220.4 | 108 | 276.113 | 0 | 1
9/4 | 14:00:00 | 289.15 | 98875 | 1 | 109 | 8.9895 | 1137.6 | 104.4 | 276.34 | 0 | 1
9/4 | 15:00:00 | 289.15 | 98875 | 3.6 | 270 | 8.4059 | 968.4 | 241.2 | 276.113 | 0 | 1
9/4 | 16:00:00 | 289.15 | 98875 | 3.6 | 260 | 8.4059 | 1400.4 | 1558.8 | 275.356 | 0 | 1
9/4 | 17:00:00 | 289.15 | 98875 | 2.1 | 250 | 7.8564 | 817.2 | 1026 | 275.398 | 0 | 1
9/4 | 18:00:00 | 288.15 | 98867 | 2.6 | 230 | 7.857 | 356.4 | 399.6 | 274.177 | 0 | 1
9/4 | 19:00:00 | 288.15 | 98867 | 1.5 | 177 | 6.8534 | 43.2 | 0 | 273.72 | 0 | 1
9/4 | 20:00:00 | 288.15 | 98867 | 3.1 | 230 | 6.396 | 0 | 0 | 273.49 | 0 | 1
9/4 | 21:00:00 | 287.15 | 98858 | 5.7 | 250 | 5.9666 | 0 | 0 | 272.576 | 0 | 1
9/4 | 22:00:00 | 285.15 | 98841 | 4.1 | 250 | 7.3418 | 0 | 0 | 271.363 | 0 | 1
9/4 | 23:00:00 | 284.15 | 98833 | 3.6 | 240 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/4 | 24:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
9/5 | 01:00:00 | 283.15 | 98824 | 3.1 | 210 | 6.3988 | 0 | 0 | 269.37 | 0 | 1
9/5 | 02:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
9/5 | 03:00:00 | 281.15 | 98806 | 1.5 | 190 | 6.4 | 0 | 0 | 267.688 | 0 | 1
9/5 | 04:00:00 | 282.15 | 98815 | 3.1 | 180 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
9/5 | 05:00:00 | 282.15 | 98815 | 2.1 | 200 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
9/5 | 06:00:00 | 283.15 | 98824 | 4.6 | 210 | 6.8564 | 7.2 | 0 | 269.234 | 0 | 1
9/5 | 07:00:00 | 283.15 | 98824 | 4.6 | 210 | 6.8564 | 259.2 | 241.2 | 268.971 | 0 | 1
9/5 | 08:00:00 | 284.15 | 98833 | 7.7 | 210 | 6.8558 | 705.6 | 946.8 | 270.185 | 0 | 1
9/5 | 09:00:00 | 284.15 | 98833 | 7.7 | 240 | 6.3982 | 1216.8 | 1461.6 | 269.957 | 0 | 1
9/5 | 10:00:00 | 284.15 | 98833 | 6.7 | 250 | 6.8558 | 1663.2 | 1875.6 | 270.185 | 0 | 1
9/5 | 11:00:00 | 284.15 | 98833 | 5.7 | 260 | 7.3425 | 1990.8 | 2167.2 | 270.411 | 0 | 1
9/5 | 12:00:00 | 284.15 | 98833 | 6.2 | 240 | 7.3425 | 2174.4 | 2235.6 | 270.411 | 0 | 1
9/5 | 13:00:00 | 286.15 | 98850 | 9.3 | 250 | 7.3412 | 2188.8 | 2239.2 | 272.314 | 0 | 1
9/5 | 14:00:00 | 286.15 | 98850 | 9.8 | 270 | 6.8546 | 2041.2 | 2199.6 | 272.087 | 0 | 1
9/5 | 15:00:00 | 286.15 | 98850 | 10.8 | 270 | 6.8546 | 1735.2 | 1936.8 | 272.087 | 0 | 1
9/5 | 16:00:00 | 286.15 | 98850 | 9.3 | 260 | 7.3412 | 1303.2 | 1580.4 | 272.314 | 0 | 1
9/5 | 17:00:00 | 287.15 | 98858 | 8.7 | 260 | 7.3406 | 849.6 | 1332 | 272.999 | 0 | 1
9/5 | 18:00:00 | 287.15 | 98858 | 7.7 | 250 | 6.854 | 338.4 | 381.6 | 272.77 | 0 | 1
9/5 | 19:00:00 | 286.15 | 98850 | 6.2 | 250 | 6.8546 | 36 | 0 | 272.087 | 0 | 1
9/5 | 20:00:00 | 285.15 | 98841 | 6.7 | 240 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
9/5 | 21:00:00 | 284.15 | 98833 | 5.1 | 220 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/5 | 22:00:00 | 284.15 | 98833 | 5.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/5 | 23:00:00 | 284.15 | 98833 | 5.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/5 | 24:00:00 | 285.15 | 98841 | 4.6 | 220 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
9/6 | 01:00:00 | 285.15 | 98841 | 6.7 | 220 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
9/6 | 02:00:00 | 286.15 | 98850 | 6.7 | 220 | 8.408 | 0 | 0 | 272.766 | 0 | 1
9/6 | 03:00:00 | 287.15 | 98858 | 9.8 | 220 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
9/6 | 04:00:00 | 286.15 | 98850 | 8.2 | 210 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
9/6 | 05:00:00 | 286.15 | 98850 | 7.7 | 210 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
9/6 | 06:00:00 | 286.15 | 98850 | 7.2 | 220 | 8.9918 | 3.6 | 0 | 273.473 | 0 | 1
9/6 | 07:00:00 | 286.15 | 98850 | 8.7 | 220 | 8.9918 | 129.6 | 0 | 273.473 | 0 | 1
9/6 | 08:00:00 | 287.15 | 98858 | 8.2 | 230 | 9.6108 | 687.6 | 835.2 | 274.167 | 0 | 1
9/6 | 09:00:00 | 288.15 | 98867 | 7.2 | 260 | 9.6099 | 1188 | 1501.2 | 275.122 | 0 | 1
9/6 | 10:00:00 | 285.15 | 98841 | 8.2 | 270 | 8.4088 | 1638 | 1875.6 | 271.813 | 0 | 1
9/6 | 11:00:00 | 285.15 | 98841 | 9.8 | 250 | 7.8591 | 1972.8 | 2149.2 | 271.588 | 0 | 1
9/6 | 12:00:00 | 286.15 | 98850 | 9.8 | 250 | 8.408 | 2149.2 | 2062.8 | 272.766 | 0 | 1
9/6 | 13:00:00 | 288.15 | 98867 | 11.3 | 250 | 7.857 | 2167.2 | 2224.8 | 274.446 | 0 | 1
9/6 | 14:00:00 | 285.15 | 98841 | 8.2 | 250 | 7.8591 | 2016 | 2170.8 | 271.588 | 0 | 1
9/6 | 15:00:00 | 286.15 | 98850 | 9.8 | 250 | 7.3412 | 1713.6 | 1908 | 272.314 | 0 | 1
9/6 | 16:00:00 | 287.15 | 98858 | 11.3 | 250 | 6.854 | 1281.6 | 1508.4 | 273.038 | 0 | 1
9/6 | 17:00:00 | 287.15 | 98858 | 12.9 | 240 | 6.854 | 781.2 | 1072.8 | 273.038 | 0 | 1
9/6 | 18:00:00 | 286.15 | 98850 | 12.3 | 240 | 6.8546 | 324 | 352.8 | 271.821 | 0 | 1
9/6 | 19:00:00 | 285.15 | 98841 | 11.8 | 250 | 6.3977 | 32.4 | 0 | 270.643 | 0 | 1
9/6 | 20:00:00 | 285.15 | 98841 | 10.3 | 250 | 6.8552 | 0 | 0 | 271.136 | 0 | 1
9/6 | 21:00:00 | 285.15 | 98841 | 9.3 | 250 | 7.3418 | 0 | 0 | 271.363 | 0 | 1
9/6 | 22:00:00 | 284.15 | 98833 | 11.8 | 260 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/6 | 23:00:00 | 284.15 | 98833 | 10.8 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
9/6 | 24:00:00 | 284.15 | 98833 | 10.3 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/7 | 01:00:00 | 284.15 | 98833 | 9.8 | 270 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/7 | 02:00:00 | 285.15 | 98841 | 9.3 | 270 | 7.3418 | 0 | 0 | 271.363 | 0 | 1
9/7 | 03:00:00 | 284.15 | 98833 | 8.7 | 270 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/7 | 04:00:00 | 284.15 | 98833 | 7.7 | 270 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/7 | 05:00:00 | 284.15 | 98833 | 5.7 | 250 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/7 | 06:00:00 | 284.15 | 98833 | 5.1 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/7 | 07:00:00 | 285.15 | 98841 | 4.1 | 250 | 7.8591 | 122.4 | 0 | 272.069 | 0 | 1
9/7 | 08:00:00 | 285.15 | 98841 | 4.6 | 250 | 7.8591 | 374.4 | 7.2 | 272.069 | 0 | 1
9/7 | 09:00:00 | 285.15 | 98841 | 6.2 | 260 | 8.4088 | 651.6 | 61.2 | 272.294 | 0 | 1
9/7 | 10:00:00 | 285.15 | 98841 | 6.7 | 270 | 8.4088 | 900 | 122.4 | 272.294 | 0 | 1
9/7 | 11:00:00 | 285.15 | 98841 | 6.7 | 260 | 8.4088 | 1951.2 | 1818 | 271.813 | 0 | 1
9/7 | 12:00:00 | 286.15 | 98850 | 8.7 | 260 | 7.8584 | 2134.8 | 2217.6 | 272.541 | 0 | 1
9/7 | 13:00:00 | 287.15 | 98858 | 6.2 | 250 | 8.4073 | 2145.6 | 2062.8 | 273.719 | 0 | 1
9/7 | 14:00:00 | 287.15 | 98858 | 8.7 | 260 | 7.8578 | 1994.4 | 2167.2 | 273.493 | 0 | 1
9/7 | 15:00:00 | 287.15 | 98858 | 8.2 | 260 | 8.4073 | 1684.8 | 1922.4 | 273.719 | 0 | 1
9/7 | 16:00:00 | 287.15 | 98858 | 9.8 | 260 | 7.8578 | 1260 | 1479.6 | 273.493 | 0 | 1
9/7 | 17:00:00 | 286.15 | 98850 | 8.2 | 260 | 7.8584 | 759.6 | 1008 | 272.541 | 0 | 1
9/7 | 18:00:00 | 285.15 | 98841 | 8.7 | 260 | 7.8591 | 288 | 244.8 | 271.588 | 0 | 1
9/7 | 19:00:00 | 284.15 | 98833 | 6.7 | 250 | 7.3425 | 25.2 | 0 | 270.411 | 0 | 1
9/7 | 20:00:00 | 283.15 | 98824 | 6.7 | 250 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
9/7 | 21:00:00 | 283.15 | 98824 | 5.7 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
9/7 | 22:00:00 | 283.15 | 98824 | 5.1 | 240 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
9/7 | 23:00:00 | 283.15 | 98824 | 5.7 | 250 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
9/7 | 24:00:00 | 283.15 | 98824 | 5.7 | 260 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
9/8 | 01:00:00 | 283.15 | 98824 | 6.7 | 260 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
9/8 | 02:00:00 | 284.15 | 98833 | 5.1 | 250 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/8 | 03:00:00 | 283.15 | 98824 | 5.1 | 260 | 7.8605 | 0 | 0 | 269.684 | 0 | 1
9/8 | 04:00:00 | 284.15 | 98833 | 1.5 | 159 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/8 | 05:00:00 | 284.15 | 98833 | 3.1 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/8 | 06:00:00 | 284.15 | 98833 | 1.5 | 264 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
9/8 | 07:00:00 | 284.15 | 98833 | 1.5 | 67 | 8.4095 | 118.8 | 0 | 271.339 | 0 | 1
9/8 | 08:00:00 | 284.15 | 98833 | 2.1 | 250 | 8.4095 | 367.2 | 3.6 | 271.339 | 0 | 1
9/8 | 09:00:00 | 285.15 | 98841 | 3.1 | 240 | 8.4088 | 644.4 | 61.2 | 272.294 | 0 | 1
9/8 | 10:00:00 | 285.15 | 98841 | 5.7 | 260 | 8.9926 | 889.2 | 43.2 | 272.517 | 0 | 1
9/8 | 11:00:00 | 286.15 | 98850 | 4.6 | 230 | 8.9918 | 1072.8 | 100.8 | 273.473 | 0 | 1
9/8 | 12:00:00 | 287.15 | 98858 | 5.1 | 250 | 9.6108 | 1170 | 104.4 | 274.652 | 0 | 1
9/8 | 13:00:00 | 287.15 | 98858 | 6.7 | 250 | 9.6108 | 1177.2 | 104.4 | 274.652 | 0 | 1
9/8 | 14:00:00 | 288.15 | 98867 | 6.2 | 260 | 9.6099 | 1090.8 | 115.2 | 275.608 | 0 | 1
9/8 | 15:00:00 | 288.15 | 98867 | 7.7 | 260 | 8.9902 | 1663.2 | 1494 | 274.898 | 0 | 1
9/8 | 16:00:00 | 288.15 | 98867 | 7.2 | 260 | 8.9902 | 1234.8 | 1551.6 | 274.898 | 0 | 1
9/8 | 17:00:00 | 288.15 | 98867 | 6.7 | 260 | 8.9902 | 738 | 932.4 | 274.898 | 0 | 1
9/8 | 18:00:00 | 288.15 | 98867 | 6.2 | 270 | 8.9902 | 270 | 284.4 | 274.898 | 0 | 1
9/8 | 19:00:00 | 287.15 | 98858 | 6.7 | 280 | 8.4073 | 18 | 0 | 273.451 | 0 | 1
9/8 | 20:00:00 | 286.15 | 98850 | 6.2 | 280 | 7.3412 | 0 | 0 | 272.048 | 0 | 1
9/8 | 21:00:00 | 285.15 | 98841 | 4.6 | 270 | 7.3418 | 0 | 0 | 271.097 | 0 | 1
9/8 | 22:00:00 | 285.15 | 98841 | 2.6 | 280 | 7.3418 | 0 | 0 | 271.729 | 0 | 1
9/8 | 23:00:00 | 284.15 | 98833 | 2.6 | 300 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/8 | 24:00:00 | 284.15 | 98833 | 1.5 | 290 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/9 | 01:00:00 | 284.15 | 98833 | 2.1 | 180 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/9 | 02:00:00 | 285.15 | 98841 | 1.5 | 63 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
9/9 | 03:00:00 | 285.15 | 98841 | 1 | 180 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
9/9 | 04:00:00 | 285.15 | 98841 | 1 | 180 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
9/9 | 05:00:00 | 285.15 | 98841 | 1.5 | 300 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
9/9 | 06:00:00 | 285.15 | 98841 | 2.6 | 170 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
9/9 | 07:00:00 | 285.15 | 98841 | 3.1 | 180 | 8.9926 | 111.6 | 0 | 272.517 | 0 | 1
9/9 | 08:00:00 | 286.15 | 98850 | 2.1 | 190 | 8.9918 | 360 | 3.6 | 273.473 | 0 | 1
9/9 | 09:00:00 | 287.15 | 98858 | 3.1 | 220 | 10.2686 | 633.6 | 57.6 | 274.874 | 0 | 1
9/9 | 10:00:00 | 289.15 | 98875 | 4.1 | 240 | 10.9646 | 878.4 | 43.2 | 277.011 | 0 | 1
9/9 | 11:00:00 | 290.15 | 98883 | 4.1 | 250 | 10.9637 | 1058.4 | 100.8 | 277.969 | 0 | 1
9/9 | 12:00:00 | 290.15 | 98883 | 5.7 | 240 | 10.9637 | 1155.6 | 266.4 | 277.969 | 0 | 1
9/9 | 13:00:00 | 292.15 | 98900 | 5.1 | 250 | 10.9618 | 2095.2 | 1699.2 | 279.391 | 0 | 1
9/9 | 14:00:00 | 291.15 | 98892 | 6.2 | 260 | 9.6075 | 1080 | 259.2 | 278.478 | 0 | 1
9/9 | 15:00:00 | 291.15 | 98892 | 5.1 | 240 | 9.6075 | 1641.6 | 1472.4 | 277.986 | 0 | 1
9/9 | 16:00:00 | 291.15 | 98892 | 5.7 | 240 | 8.9879 | 1213.2 | 1540.8 | 277.76 | 0 | 1
9/9 | 17:00:00 | 292.15 | 98900 | 5.1 | 250 | 8.9872 | 716.4 | 910.8 | 278.714 | 0 | 1
9/9 | 18:00:00 | 291.15 | 98892 | 5.1 | 260 | 9.6075 | 255.6 | 259.2 | 277.986 | 0 | 1
9/9 | 19:00:00 | 290.15 | 98883 | 1.5 | 160 | 9.6084 | 14.4 | 0 | 276.76 | 0 | 1
9/9 | 20:00:00 | 289.15 | 98875 | 2.6 | 220 | 9.6091 | 0 | 0 | 275.806 | 0 | 1
9/9 | 21:00:00 | 288.15 | 98867 | 1.5 | 332 | 9.6099 | 0 | 0 | 274.852 | 0 | 1
9/9 | 22:00:00 | 289.15 | 98875 | 3.1 | 220 | 10.2668 | 0 | 0 | 276.029 | 0 | 1
9/9 | 23:00:00 | 288.15 | 98867 | 1.5 | 180 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
9/9 | 24:00:00 | 288.15 | 98867 | 2.1 | 220 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
9/10 | 01:00:00 | 288.15 | 98867 | 2.1 | 150 | 10.2677 | 0 | 0 | 275.075 | 0 | 1
9/10 | 02:00:00 | 288.15 | 98867 | 3.6 | 190 | 10.9655 | 0 | 0 | 275.565 | 0 | 1
9/10 | 03:00:00 | 289.15 | 98875 | 2.6 | 140 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
9/10 | 04:00:00 | 289.15 | 98875 | 3.1 | 140 | 10.9646 | 0 | 0 | 276.522 | 0 | 1
9/10 | 05:00:00 | 289.15 | 98875 | 5.7 | 150 | 10.9646 | 0 | 0 | 277.011 | 0 | 1
9/10 | 06:00:00 | 289.15 | 98875 | 4.6 | 160 | 11.7047 | 0 | 0 | 277.232 | 0 | 1
9/10 | 07:00:00 | 289.15 | 98875 | 4.1 | 160 | 11.7047 | 64.8 | 0 | 277.345 | 0 | 1
9/10 | 08:00:00 | 289.15 | 98875 | 4.6 | 170 | 11.7047 | 349.2 | 0 | 277.232 | 0 | 1
9/10 | 09:00:00 | 290.15 | 98883 | 4.1 | 160 | 12.4883 | 622.8 | 43.2 | 278.412 | 0 | 1
9/10 | 10:00:00 | 291.15 | 98892 | 4.6 | 160 | 12.4871 | 864 | 194.4 | 279.371 | 0 | 1
9/10 | 11:00:00 | 292.15 | 98900 | 3.6 | 160 | 13.3174 | 1879.2 | 1864.8 | 280.056 | 0 | 1
9/10 | 12:00:00 | 294.15 | 98916 | 6.2 | 200 | 10.96 | 1144.8 | 115.2 | 281.801 | 0 | 1
9/10 | 13:00:00 | 293.15 | 98908 | 5.1 | 210 | 10.2634 | 1152 | 266.4 | 280.618 | 0 | 1
9/10 | 14:00:00 | 295.15 | 98924 | 8.7 | 220 | 9.6043 | 1926 | 1800 | 281.805 | 0 | 1
9/10 | 15:00:00 | 294.15 | 98916 | 6.7 | 210 | 10.96 | 1612.8 | 1828.8 | 281.303 | 0 | 1
9/10 | 16:00:00 | 294.15 | 98916 | 5.1 | 240 | 9.6051 | 1191.6 | 1519.2 | 280.85 | 0 | 1
9/10 | 17:00:00 | 293.15 | 98908 | 5.7 | 230 | 8.9864 | 698.4 | 889.2 | 279.668 | 0 | 1
9/10 | 18:00:00 | 291.15 | 98892 | 5.7 | 220 | 9.6075 | 241.2 | 230.4 | 277.986 | 0 | 1
9/10 | 19:00:00 | 290.15 | 98883 | 3.6 | 240 | 9.6084 | 7.2 | 0 | 276.76 | 0 | 1
9/10 | 20:00:00 | 289.15 | 98875 | 4.6 | 220 | 7.8564 | 0 | 0 | 275.129 | 0 | 1
9/10 | 21:00:00 | 288.15 | 98867 | 4.1 | 200 | 7.3399 | 0 | 0 | 273.95 | 0 | 1
9/10 | 22:00:00 | 288.15 | 98867 | 5.7 | 210 | 7.3399 | 0 | 0 | 273.95 | 0 | 1
9/10 | 23:00:00 | 287.15 | 98858 | 5.1 | 230 | 7.8578 | 0 | 0 | 273.226 | 0 | 1
9/10 | 24:00:00 | 286.15 | 98850 | 7.2 | 210 | 7.3412 | 0 | 0 | 272.048 | 0 | 1
9/11 | 01:00:00 | 286.15 | 98850 | 8.2 | 210 | 7.3412 | 0 | 0 | 272.048 | 0 | 1
9/11 | 02:00:00 | 286.15 | 98850 | 7.7 | 210 | 7.8584 | 0 | 0 | 272.274 | 0 | 1
9/11 | 03:00:00 | 286.15 | 98850 | 5.7 | 210 | 7.8584 | 0 | 0 | 272.541 | 0 | 1
9/11 | 04:00:00 | 286.15 | 98850 | 6.2 | 200 | 7.8584 | 0 | 0 | 272.541 | 0 | 1
9/11 | 05:00:00 | 285.15 | 98841 | 4.6 | 220 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
9/11 | 06:00:00 | 286.15 | 98850 | 5.7 | 220 | 7.8584 | 0 | 0 | 272.541 | 0 | 1
9/11 | 07:00:00 | 285.15 | 98841 | 5.1 | 230 | 7.3418 | 194.4 | 144 | 271.097 | 0 | 1
9/11 | 08:00:00 | 286.15 | 98850 | 6.2 | 230 | 7.3412 | 658.8 | 1040.4 | 272.048 | 0 | 1
9/11 | 09:00:00 | 287.15 | 98858 | 5.7 | 230 | 7.3406 | 1119.6 | 1339.2 | 273.266 | 0 | 1
9/11 | 10:00:00 | 287.15 | 98858 | 6.2 | 220 | 7.3406 | 867.6 | 259.2 | 273.75 | 0 | 1
9/11 | 11:00:00 | 288.15 | 98867 | 7.2 | 220 | 6.8534 | 1893.6 | 1825.2 | 273.988 | 0 | 1
9/11 | 12:00:00 | 289.15 | 98875 | 7.2 | 240 | 6.8529 | 1148.4 | 248.4 | 275.426 | 0 | 1
9/11 | 13:00:00 | 287.15 | 98858 | 9.3 | 230 | 7.3406 | 2077.2 | 1900.8 | 273.266 | 0 | 1
9/11 | 14:00:00 | 288.15 | 98867 | 9.8 | 230 | 6.396 | 1926 | 2170.8 | 273.758 | 0 | 1
9/11 | 15:00:00 | 289.15 | 98875 | 7.7 | 230 | 5.9656 | 1616.4 | 1872 | 274.475 | 0 | 1
9/11 | 16:00:00 | 289.15 | 98875 | 8.2 | 230 | 6.3955 | 1180.8 | 1508.4 | 274.708 | 0 | 1
9/11 | 17:00:00 | 288.15 | 98867 | 9.3 | 230 | 5.9661 | 723.6 | 1148.4 | 273.258 | 0 | 1
9/11 | 18:00:00 | 288.15 | 98867 | 7.7 | 230 | 6.396 | 226.8 | 262.8 | 273.758 | 0 | 1
9/11 | 19:00:00 | 287.15 | 98858 | 8.2 | 230 | 6.3966 | 0 | 0 | 272.808 | 0 | 1
9/11 | 20:00:00 | 286.15 | 98850 | 7.2 | 230 | 5.9671 | 0 | 0 | 271.361 | 0 | 1
9/11 | 21:00:00 | 286.15 | 98850 | 6.7 | 230 | 6.3971 | 0 | 0 | 271.858 | 0 | 1
9/11 | 22:00:00 | 286.15 | 98850 | 5.1 | 210 | 6.8546 | 0 | 0 | 272.087 | 0 | 1
9/11 | 23:00:00 | 286.15 | 98850 | 5.7 | 220 | 7.3412 | 0 | 0 | 272.314 | 0 | 1
9/11 | 24:00:00 | 286.15 | 98850 | 4.6 | 220 | 7.8584 | 0 | 0 | 272.541 | 0 | 1
9/12 | 01:00:00 | 285.15 | 98841 | 5.7 | 220 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
9/12 | 02:00:00 | 284.15 | 98833 | 5.1 | 190 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
9/12 | 03:00:00 | 284.15 | 98833 | 5.7 | 180 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
9/12 | 04:00:00 | 285.15 | 98841 | 5.1 | 200 | 8.9926 | 0 | 0 | 272.036 | 0 | 1
9/12 | 05:00:00 | 287.15 | 98858 | 5.1 | 210 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
9/12 | 06:00:00 | 288.15 | 98867 | 7.2 | 220 | 10.2677 | 0 | 0 | 275.831 | 0 | 1
9/12 | 07:00:00 | 289.15 | 98875 | 8.7 | 230 | 10.2668 | 172.8 | 100.8 | 276.3 | 0 | 1
9/12 | 08:00:00 | 290.15 | 98883 | 8.7 | 240 | 9.6084 | 604.8 | 788.4 | 277.031 | 0 | 1
9/12 | 09:00:00 | 289.15 | 98875 | 10.3 | 240 | 9.6091 | 1098 | 1440 | 276.076 | 0 | 1
9/12 | 10:00:00 | 289.15 | 98875 | 12.9 | 240 | 7.8564 | 1544.4 | 1767.6 | 275.398 | 0 | 1
9/12 | 11:00:00 | 288.15 | 98867 | 11.8 | 240 | 7.857 | 1868.4 | 2116.8 | 274.446 | 0 | 1
9/12 | 12:00:00 | 290.15 | 98883 | 11.8 | 240 | 7.3387 | 2048.4 | 2214 | 276.121 | 0 | 1
9/12 | 13:00:00 | 290.15 | 98883 | 14.4 | 250 | 6.8523 | 2059.2 | 1908 | 275.89 | 0 | 1
9/12 | 14:00:00 | 289.15 | 98875 | 14.9 | 250 | 6.8529 | 1054.8 | 172.8 | 275.426 | 0 | 1
9/12 | 15:00:00 | 290.15 | 98883 | 14.9 | 250 | 6.3949 | 882 | 129.6 | 276.145 | 0 | 1
9/12 | 16:00:00 | 289.15 | 98875 | 17 | 250 | 6.3955 | 640.8 | 46.8 | 275.194 | 0 | 1
9/12 | 17:00:00 | 289.15 | 98875 | 13.9 | 240 | 6.3955 | 367.2 | 7.2 | 275.194 | 0 | 1
9/12 | 18:00:00 | 288.15 | 98867 | 18.5 | 260 | 6.396 | 118.8 | 0 | 274.242 | 0 | 1
9/12 | 19:00:00 | 287.15 | 98858 | 13.9 | 250 | 6.854 | 0 | 0 | 273.521 | 0 | 1
9/12 | 20:00:00 | 287.15 | 98858 | 12.9 | 250 | 6.854 | 0 | 0 | 273.038 | 0 | 1
9/12 | 21:00:00 | 287.15 | 98858 | 12.9 | 250 | 6.854 | 0 | 0 | 273.038 | 0 | 1
9/12 | 22:00:00 | 286.15 | 98850 | 12.9 | 250 | 6.3971 | 0 | 0 | 271.592 | 0 | 1
9/12 | 23:00:00 | 286.15 | 98850 | 11.3 | 250 | 6.3971 | 0 | 0 | 271.592 | 0 | 1
9/12 | 24:00:00 | 286.15 | 98850 | 11.3 | 250 | 6.3971 | 0 | 0 | 271.592 | 0 | 1
9/13 | 01:00:00 | 285.15 | 98841 | 10.8 | 250 | 6.3977 | 0 | 0 | 270.643 | 0 | 1
9/13 | 02:00:00 | 285.15 | 98841 | 11.3 | 250 | 6.8552 | 0 | 0 | 270.871 | 0 | 1
9/13 | 03:00:00 | 285.15 | 98841 | 10.8 | 250 | 6.3977 | 0 | 0 | 270.643 | 0 | 1
9/13 | 04:00:00 | 285.15 | 98841 | 11.8 | 250 | 6.8552 | 0 | 0 | 271.136 | 0 | 1
9/13 | 05:00:00 | 284.15 | 98833 | 10.8 | 250 | 6.8558 | 0 | 0 | 269.921 | 0 | 1
9/13 | 06:00:00 | 283.15 | 98824 | 10.8 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
9/13 | 07:00:00 | 283.15 | 98824 | 11.8 | 250 | 6.8564 | 176.4 | 111.6 | 268.971 | 0 | 1
9/13 | 08:00:00 | 284.15 | 98833 | 11.8 | 250 | 6.3982 | 630 | 1011.6 | 269.693 | 0 | 1
9/13 | 09:00:00 | 285.15 | 98841 | 12.3 | 250 | 6.3977 | 1155.6 | 1666.8 | 270.643 | 0 | 1
9/13 | 10:00:00 | 287.15 | 98858 | 13.4 | 250 | 5.9666 | 1537.2 | 1566 | 272.576 | 0 | 1
9/13 | 11:00:00 | 287.15 | 98858 | 11.8 | 250 | 5.5627 | 1864.8 | 2163.6 | 272.343 | 0 | 1
9/13 | 12:00:00 | 288.15 | 98867 | 11.3 | 250 | 5.5621 | 2041.2 | 2250 | 273.292 | 0 | 1
9/13 | 13:00:00 | 286.15 | 98850 | 11.3 | 260 | 6.3971 | 2041.2 | 2232 | 271.858 | 0 | 1
9/13 | 14:00:00 | 286.15 | 98850 | 10.3 | 250 | 6.8546 | 1879.2 | 2145.6 | 272.087 | 0 | 1
9/13 | 15:00:00 | 287.15 | 98858 | 10.3 | 260 | 5.9666 | 1573.2 | 1836 | 272.576 | 0 | 1
9/13 | 16:00:00 | 286.15 | 98850 | 8.7 | 250 | 6.3971 | 1137.6 | 1418.4 | 271.858 | 0 | 1
9/13 | 17:00:00 | 285.15 | 98841 | 9.3 | 260 | 5.9676 | 644.4 | 892.8 | 270.678 | 0 | 1
9/13 | 18:00:00 | 284.15 | 98833 | 9.8 | 260 | 6.3982 | 198 | 118.8 | 269.957 | 0 | 1
9/13 | 19:00:00 | 283.15 | 98824 | 8.7 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
9/13 | 20:00:00 | 283.15 | 98824 | 8.2 | 260 | 5.5646 | 0 | 0 | 268.287 | 0 | 1
9/13 | 21:00:00 | 283.15 | 98824 | 9.8 | 260 | 6.3988 | 0 | 0 | 268.744 | 0 | 1
9/13 | 22:00:00 | 283.15 | 98824 | 9.8 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
9/13 | 23:00:00 | 283.15 | 98824 | 12.3 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
9/13 | 24:00:00 | 283.15 | 98824 | 11.8 | 270 | 6.3988 | 0 | 0 | 268.744 | 0 | 1
9/14 | 01:00:00 | 283.15 | 98824 | 8.7 | 260 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
9/14 | 02:00:00 | 284.15 | 98833 | 8.2 | 260 | 6.8558 | 0 | 0 | 270.663 | 0 | 1
9/14 | 03:00:00 | 284.15 | 98833 | 8.2 | 260 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/14 | 04:00:00 | 284.15 | 98833 | 7.7 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/14 | 05:00:00 | 284.15 | 98833 | 6.7 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
9/14 | 06:00:00 | 284.15 | 98833 | 5.1 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
9/14 | 07:00:00 | 284.15 | 98833 | 4.6 | 270 | 7.8598 | 86.4 | 0 | 271.115 | 0 | 1
9/14 | 08:00:00 | 285.15 | 98841 | 5.1 | 270 | 7.8591 | 320.4 | 0 | 272.069 | 0 | 1
9/14 | 09:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.4088 | 594 | 72 | 272.294 | 0 | 1
9/14 | 10:00:00 | 286.15 | 98850 | 5.7 | 280 | 8.408 | 1504.8 | 1400.4 | 272.766 | 0 | 1
9/14 | 11:00:00 | 286.15 | 98850 | 6.7 | 280 | 7.8584 | 1832.4 | 2102.4 | 272.541 | 0 | 1
9/14 | 12:00:00 | 287.15 | 98858 | 7.2 | 270 | 7.8578 | 2005.2 | 2192.4 | 273.493 | 0 | 1
9/14 | 13:00:00 | 287.15 | 98858 | 5.7 | 290 | 7.8578 | 2012.4 | 2196 | 273.493 | 0 | 1
9/14 | 14:00:00 | 288.15 | 98867 | 9.8 | 260 | 7.3399 | 1857.6 | 2127.6 | 274.218 | 0 | 1
9/14 | 15:00:00 | 288.15 | 98867 | 10.3 | 270 | 7.3399 | 1544.4 | 1551.6 | 274.218 | 0 | 1
9/14 | 16:00:00 | 288.15 | 98867 | 11.8 | 270 | 7.3399 | 1177.2 | 1677.6 | 273.95 | 0 | 1
9/14 | 17:00:00 | 285.15 | 98841 | 12.3 | 270 | 7.8591 | 658.8 | 1044 | 271.323 | 0 | 1
9/14 | 18:00:00 | 285.15 | 98841 | 9.8 | 270 | 7.8591 | 194.4 | 147.6 | 271.323 | 0 | 1
9/14 | 19:00:00 | 284.15 | 98833 | 7.2 | 270 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/14 | 20:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/14 | 21:00:00 | 284.15 | 98833 | 6.7 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/14 | 22:00:00 | 283.15 | 98824 | 4.6 | 270 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
9/14 | 23:00:00 | 282.15 | 98815 | 4.1 | 310 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
9/14 | 24:00:00 | 281.15 | 98806 | 4.1 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1
9/15 | 01:00:00 | 281.15 | 98806 | 3.6 | 260 | 6.4 | 0 | 0 | 267.688 | 0 | 1
9/15 | 02:00:00 | 280.15 | 98798 | 3.6 | 270 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
9/15 | 03:00:00 | 279.15 | 98789 | 3.1 | 290 | 5.9708 | 0 | 0 | 265.559 | 0 | 1
9/15 | 04:00:00 | 279.15 | 98789 | 1.5 | 270 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
9/15 | 05:00:00 | 279.15 | 98789 | 2.1 | 260 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
9/15 | 06:00:00 | 278.15 | 98780 | 2.1 | 270 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
9/15 | 07:00:00 | 279.15 | 98789 | 2.6 | 300 | 5.187 | 93.6 | 0 | 264.996 | 0 | 1
9/15 | 08:00:00 | 280.15 | 98798 | 2.1 | 300 | 5.9703 | 259.2 | 0 | 266.51 | 0 | 1
9/15 | 09:00:00 | 283.15 | 98824 | 2.1 | 30 | 5.9687 | 936 | 882 | 269.025 | 0 | 1
9/15 | 10:00:00 | 284.15 | 98833 | 1.5 | 39 | 5.9681 | 1425.6 | 1389.6 | 269.854 | 0 | 1
9/15 | 11:00:00 | 285.15 | 98841 | 1 | 208 | 6.3977 | 1933.2 | 2325.6 | 270.643 | 0 | 1
9/15 | 12:00:00 | 286.15 | 98850 | 1.5 | 86 | 5.9671 | 2120.4 | 2631.6 | 271.361 | 0 | 1
9/15 | 13:00:00 | 287.15 | 98858 | 2.1 | 60 | 5.9666 | 2127.6 | 2635.2 | 272.31 | 0 | 1
9/15 | 14:00:00 | 288.15 | 98867 | 2.1 | 50 | 5.9661 | 1954.8 | 2530.8 | 273.258 | 0 | 1
9/15 | 15:00:00 | 288.15 | 98867 | 2.1 | 110 | 5.9661 | 1620 | 2239.2 | 273.258 | 0 | 1
9/15 | 16:00:00 | 288.15 | 98867 | 3.1 | 110 | 5.5621 | 1162.8 | 1692 | 273.025 | 0 | 1
9/15 | 17:00:00 | 288.15 | 98867 | 3.1 | 120 | 5.5621 | 640.8 | 1040.4 | 273.025 | 0 | 1
9/15 | 18:00:00 | 287.15 | 98858 | 2.6 | 120 | 5.9666 | 180 | 183.6 | 272.445 | 0 | 1
9/15 | 19:00:00 | 285.15 | 98841 | 4.1 | 100 | 6.8552 | 0 | 0 | 271.384 | 0 | 1
9/15 | 20:00:00 | 283.15 | 98824 | 3.1 | 110 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
9/15 | 21:00:00 | 282.15 | 98815 | 3.6 | 100 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
9/15 | 22:00:00 | 283.15 | 98824 | 3.1 | 90 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
9/15 | 23:00:00 | 283.15 | 98824 | 3.1 | 90 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
9/15 | 24:00:00 | 283.15 | 98824 | 2.6 | 90 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
9/16 | 01:00:00 | 283.15 | 98824 | 3.1 | 80 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
9/16 | 02:00:00 | 283.15 | 98824 | 2.6 | 80 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
9/16 | 03:00:00 | 283.15 | 98824 | 2.6 | 70 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
9/16 | 04:00:00 | 284.15 | 98833 | 2.6 | 90 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
9/16 | 05:00:00 | 284.15 | 98833 | 3.6 | 120 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
9/16 | 06:00:00 | 285.15 | 98841 | 4.6 | 130 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
9/16 | 07:00:00 | 285.15 | 98841 | 6.2 | 130 | 8.4088 | 75.6 | 0 | 272.294 | 0 | 1
9/16 | 08:00:00 | 285.15 | 98841 | 5.1 | 130 | 8.4088 | 306 | 0 | 272.294 | 0 | 1
9/16 | 09:00:00 | 285.15 | 98841 | 5.1 | 140 | 8.4088 | 576 | 50.4 | 272.294 | 0 | 1
9/16 | 10:00:00 | 285.15 | 98841 | 5.1 | 150 | 8.4088 | 817.2 | 82.8 | 272.294 | 0 | 1
9/16 | 11:00:00 | 286.15 | 98850 | 6.2 | 150 | 8.9918 | 993.6 | 248.4 | 273.473 | 0 | 1
9/16 | 12:00:00 | 286.15 | 98850 | 6.2 | 150 | 8.408 | 1965.6 | 1846.8 | 272.766 | 0 | 1
9/16 | 13:00:00 | 287.15 | 98858 | 6.2 | 140 | 8.991 | 1965.6 | 1839.6 | 273.944 | 0 | 1
9/16 | 14:00:00 | 287.15 | 98858 | 4.6 | 150 | 8.991 | 1000.8 | 252 | 274.428 | 0 | 1
9/16 | 15:00:00 | 288.15 | 98867 | 5.1 | 150 | 7.857 | 831.6 | 61.2 | 274.931 | 0 | 1
9/16 | 16:00:00 | 288.15 | 98867 | 6.2 | 140 | 8.4065 | 590.4 | 54 | 275.158 | 0 | 1
9/16 | 17:00:00 | 288.15 | 98867 | 6.2 | 140 | 7.857 | 320.4 | 0 | 274.931 | 0 | 1
9/16 | 18:00:00 | 286.15 | 98850 | 4.1 | 230 | 9.6116 | 154.8 | 68.4 | 273.212 | 0 | 1
9/16 | 19:00:00 | 286.15 | 98850 | 2.6 | 200 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
9/16 | 20:00:00 | 285.15 | 98841 | 2.1 | 250 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
9/16 | 21:00:00 | 285.15 | 98841 | 3.1 | 230 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
9/16 | 22:00:00 | 284.15 | 98833 | 2.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/16 | 23:00:00 | 285.15 | 98841 | 4.1 | 220 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
9/16 | 24:00:00 | 284.15 | 98833 | 3.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/17 | 01:00:00 | 284.15 | 98833 | 4.1 | 220 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/17 | 02:00:00 | 284.15 | 98833 | 3.1 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/17 | 03:00:00 | 284.15 | 98833 | 2.1 | 180 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/17 | 04:00:00 | 284.15 | 98833 | 3.6 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/17 | 05:00:00 | 284.15 | 98833 | 4.6 | 230 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
9/17 | 06:00:00 | 284.15 | 98833 | 2.6 | 200 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/17 | 07:00:00 | 284.15 | 98833 | 2.6 | 210 | 7.8598 | 129.6 | 3.6 | 270.636 | 0 | 1
9/17 | 08:00:00 | 284.15 | 98833 | 4.6 | 220 | 7.8598 | 540 | 601.2 | 270.636 | 0 | 1
9/17 | 09:00:00 | 284.15 | 98833 | 5.7 | 230 | 7.8598 | 1022.4 | 1314 | 270.636 | 0 | 1
9/17 | 10:00:00 | 284.15 | 98833 | 6.7 | 230 | 7.3425 | 1461.6 | 1735.2 | 270.411 | 0 | 1
9/17 | 11:00:00 | 284.15 | 98833 | 5.7 | 250 | 7.8598 | 1778.4 | 2077.2 | 270.636 | 0 | 1
9/17 | 12:00:00 | 286.15 | 98850 | 6.7 | 260 | 7.3412 | 1951.2 | 2188.8 | 272.314 | 0 | 1
9/17 | 13:00:00 | 284.15 | 98833 | 7.2 | 250 | 6.8558 | 1958.4 | 2203.2 | 270.185 | 0 | 1
9/17 | 14:00:00 | 284.15 | 98833 | 4.6 | 260 | 7.3425 | 1792.8 | 2098.8 | 270.411 | 0 | 1
9/17 | 15:00:00 | 284.15 | 98833 | 5.1 | 240 | 7.3425 | 1479.6 | 1519.2 | 270.411 | 0 | 1
9/17 | 16:00:00 | 286.15 | 98850 | 7.2 | 260 | 7.3412 | 1108.8 | 1623.6 | 272.048 | 0 | 1
9/17 | 17:00:00 | 285.15 | 98841 | 6.7 | 260 | 6.8552 | 561.6 | 633.6 | 271.136 | 0 | 1
9/17 | 18:00:00 | 284.15 | 98833 | 3.6 | 270 | 7.3425 | 151.2 | 75.6 | 270.147 | 0 | 1
9/17 | 19:00:00 | 283.15 | 98824 | 3.6 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
9/17 | 20:00:00 | 282.15 | 98815 | 2.6 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
9/17 | 21:00:00 | 282.15 | 98815 | 3.1 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
9/17 | 22:00:00 | 282.15 | 98815 | 2.6 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
9/17 | 23:00:00 | 282.15 | 98815 | 2.6 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
9/17 | 24:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.4 | 0 | 0 | 266.846 | 0 | 1
9/18 | 01:00:00 | 281.15 | 98806 | 3.1 | 250 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
9/18 | 02:00:00 | 281.15 | 98806 | 1.5 | 260 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
9/18 | 03:00:00 | 281.15 | 98806 | 3.6 | 270 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
9/18 | 04:00:00 | 280.15 | 98798 | 2.6 | 250 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
9/18 | 05:00:00 | 280.15 | 98798 | 3.1 | 260 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
9/18 | 06:00:00 | 280.15 | 98798 | 3.1 | 260 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
9/18 | 07:00:00 | 282.15 | 98815 | 2.6 | 320 | 6.8571 | 118.8 | 0 | 268.283 | 0 | 1
9/18 | 08:00:00 | 282.15 | 98815 | 2.1 | 310 | 7.3438 | 558 | 903.6 | 268.245 | 0 | 1
9/18 | 09:00:00 | 283.15 | 98824 | 2.1 | 270 | 7.3431 | 1008 | 1310.4 | 269.46 | 0 | 1
9/18 | 10:00:00 | 285.15 | 98841 | 3.1 | 310 | 7.8591 | 1440 | 1720.8 | 271.588 | 0 | 1
9/18 | 11:00:00 | 285.15 | 98841 | 2.1 | 300 | 7.8591 | 1760.4 | 2066.4 | 271.588 | 0 | 1
9/18 | 12:00:00 | 286.15 | 98850 | 1.5 | 182 | 7.3412 | 1933.2 | 1872 | 272.314 | 0 | 1
9/18 | 13:00:00 | 286.15 | 98850 | 1.5 | 250 | 7.3412 | 1072.8 | 176.4 | 272.796 | 0 | 1
9/18 | 14:00:00 | 288.15 | 98867 | 2.6 | 290 | 7.3399 | 982.8 | 72 | 274.703 | 0 | 1
9/18 | 15:00:00 | 284.15 | 98833 | 1.5 | 248 | 7.8598 | 1454.4 | 1404 | 270.636 | 0 | 1
9/18 | 16:00:00 | 285.15 | 98841 | 4.6 | 340 | 7.3418 | 1026 | 1328.4 | 271.363 | 0 | 1
9/18 | 17:00:00 | 285.15 | 98841 | 4.1 | 360 | 7.3418 | 543.6 | 608.4 | 271.363 | 0 | 1
9/18 | 18:00:00 | 285.15 | 98841 | 2.1 | 320 | 7.3418 | 129.6 | 10.8 | 271.363 | 0 | 1
9/18 | 19:00:00 | 284.15 | 98833 | 3.1 | 360 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/18 | 20:00:00 | 284.15 | 98833 | 2.6 | 320 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/18 | 21:00:00 | 284.15 | 98833 | 5.7 | 300 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/18 | 22:00:00 | 284.15 | 98833 | 5.7 | 300 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/18 | 23:00:00 | 284.15 | 98833 | 6.2 | 300 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/18 | 24:00:00 | 284.15 | 98833 | 5.7 | 310 | 6.8558 | 0 | 0 | 269.921 | 0 | 1
9/19 | 01:00:00 | 283.15 | 98824 | 4.1 | 310 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
9/19 | 02:00:00 | 282.15 | 98815 | 4.1 | 300 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
9/19 | 03:00:00 | 281.15 | 98806 | 3.1 | 280 | 6.8577 | 0 | 0 | 267.071 | 0 | 1
9/19 | 04:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
9/19 | 05:00:00 | 283.15 | 98824 | 4.6 | 270 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
9/19 | 06:00:00 | 282.15 | 98815 | 3.1 | 290 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
9/19 | 07:00:00 | 282.15 | 98815 | 3.6 | 290 | 7.3438 | 111.6 | 0 | 268.508 | 0 | 1
9/19 | 08:00:00 | 284.15 | 98833 | 3.6 | 270 | 7.7013 | 511.2 | 572.4 | 270.569 | 0 | 1
9/19 | 09:00:00 | 285.15 | 98841 | 5.7 | 260 | 7.8591 | 1051.2 | 1562.4 | 271.323 | 0 | 1
9/19 | 10:00:00 | 286.15 | 98850 | 7.7 | 270 | 7.3412 | 1425.6 | 1494 | 272.314 | 0 | 1
9/19 | 11:00:00 | 287.15 | 98858 | 5.1 | 260 | 7.3406 | 1742.4 | 1609.2 | 273.266 | 0 | 1
9/19 | 12:00:00 | 286.15 | 98850 | 5.1 | 230 | 7.3412 | 1062 | 75.6 | 272.796 | 0 | 1
9/19 | 13:00:00 | 287.15 | 98858 | 6.2 | 240 | 7.3406 | 1062 | 205.2 | 273.75 | 0 | 1
9/19 | 14:00:00 | 287.15 | 98858 | 7.7 | 240 | 7.8578 | 968.4 | 136.8 | 273.977 | 0 | 1
9/19 | 15:00:00 | 286.15 | 98850 | 8.2 | 230 | 8.408 | 1429.2 | 1382.4 | 272.766 | 0 | 1
9/19 | 16:00:00 | 287.15 | 98858 | 7.2 | 230 | 8.991 | 997.2 | 1087.2 | 273.944 | 0 | 1
9/19 | 17:00:00 | 287.15 | 98858 | 6.2 | 230 | 8.991 | 288 | 0 | 274.428 | 0 | 1
9/19 | 18:00:00 | 287.15 | 98858 | 4.6 | 230 | 8.991 | 118.8 | 0 | 273.944 | 0 | 1
9/19 | 19:00:00 | 287.15 | 98858 | 4.6 | 220 | 8.991 | 0 | 0 | 273.944 | 0 | 1
9/19 | 20:00:00 | 287.15 | 98858 | 4.1 | 220 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
9/19 | 21:00:00 | 287.15 | 98858 | 3.1 | 220 | 8.991 | 0 | 0 | 274.428 | 0 | 1
9/19 | 22:00:00 | 287.15 | 98858 | 5.1 | 230 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
9/19 | 23:00:00 | 287.15 | 98858 | 5.7 | 230 | 8.991 | 0 | 0 | 274.428 | 0 | 1
9/19 | 24:00:00 | 287.15 | 98858 | 6.7 | 220 | 8.991 | 0 | 0 | 273.944 | 0 | 1
9/20 | 01:00:00 | 287.15 | 98858 | 7.7 | 230 | 8.991 | 0 | 0 | 273.944 | 0 | 1
9/20 | 02:00:00 | 287.15 | 98858 | 6.7 | 230 | 9.6108 | 0 | 0 | 274.167 | 0 | 1
9/20 | 03:00:00 | 287.15 | 98858 | 5.7 | 230 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
9/20 | 04:00:00 | 286.15 | 98850 | 7.2 | 270 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
9/20 | 05:00:00 | 285.15 | 98841 | 6.2 | 270 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
9/20 | 06:00:00 | 284.15 | 98833 | 2.1 | 260 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/20 | 07:00:00 | 284.15 | 98833 | 3.1 | 240 | 7.8598 | 57.6 | 0 | 271.115 | 0 | 1
9/20 | 08:00:00 | 285.15 | 98841 | 1 | 74 | 7.3418 | 277.2 | 0 | 271.843 | 0 | 1
9/20 | 09:00:00 | 285.15 | 98841 | 2.1 | 230 | 7.8591 | 540 | 32.4 | 272.069 | 0 | 1
9/20 | 10:00:00 | 285.15 | 98841 | 3.6 | 250 | 8.4088 | 777.6 | 79.2 | 272.294 | 0 | 1
9/20 | 11:00:00 | 285.15 | 98841 | 3.1 | 250 | 7.8591 | 954 | 140.4 | 272.069 | 0 | 1
9/20 | 12:00:00 | 285.15 | 98841 | 2.6 | 270 | 8.4088 | 1047.6 | 262.8 | 272.294 | 0 | 1
9/20 | 13:00:00 | 285.15 | 98841 | 4.6 | 270 | 8.4088 | 1886.4 | 1688.4 | 271.813 | 0 | 1
9/20 | 14:00:00 | 286.15 | 98850 | 4.6 | 260 | 7.8584 | 957.6 | 288 | 273.023 | 0 | 1
9/20 | 15:00:00 | 286.15 | 98850 | 5.1 | 260 | 7.8584 | 1411.2 | 1386 | 272.541 | 0 | 1
9/20 | 16:00:00 | 286.15 | 98850 | 5.1 | 250 | 7.3412 | 982.8 | 1296 | 272.314 | 0 | 1
9/20 | 17:00:00 | 285.15 | 98841 | 4.6 | 250 | 6.3977 | 504 | 576 | 270.907 | 0 | 1
9/20 | 18:00:00 | 285.15 | 98841 | 4.1 | 260 | 6.8552 | 108 | 0 | 271.136 | 0 | 1
9/20 | 19:00:00 | 284.15 | 98833 | 2.6 | 240 | 6.8558 | 0 | 0 | 269.921 | 0 | 1
9/20 | 20:00:00 | 284.15 | 98833 | 2.6 | 240 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
9/20 | 21:00:00 | 284.15 | 98833 | 4.1 | 240 | 6.8558 | 0 | 0 | 269.921 | 0 | 1
9/20 | 22:00:00 | 284.15 | 98833 | 3.1 | 220 | 6.8558 | 0 | 0 | 269.921 | 0 | 1
9/20 | 23:00:00 | 283.15 | 98824 | 3.1 | 220 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
9/20 | 24:00:00 | 283.15 | 98824 | 3.6 | 220 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
9/21 | 01:00:00 | 282.15 | 98815 | 3.6 | 220 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
9/21 | 02:00:00 | 282.15 | 98815 | 2.6 | 190 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
9/21 | 03:00:00 | 282.15 | 98815 | 1.5 | 90 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
9/21 | 04:00:00 | 282.15 | 98815 | 1.5 | 49 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
9/21 | 05:00:00 | 282.15 | 98815 | 2.1 | 230 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
9/21 | 06:00:00 | 282.15 | 98815 | 2.6 | 220 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
9/21 | 07:00:00 | 282.15 | 98815 | 4.1 | 210 | 6.8571 | 100.8 | 0 | 268.021 | 0 | 1
9/21 | 08:00:00 | 283.15 | 98824 | 4.1 | 220 | 6.8564 | 514.8 | 849.6 | 268.971 | 0 | 1
9/21 | 09:00:00 | 283.15 | 98824 | 5.1 | 220 | 6.8564 | 1018.8 | 1551.6 | 268.971 | 0 | 1
9/21 | 10:00:00 | 285.15 | 98841 | 6.7 | 220 | 6.8552 | 1476 | 2120.4 | 270.871 | 0 | 1
9/21 | 11:00:00 | 285.15 | 98841 | 6.7 | 220 | 6.3977 | 1710 | 1728 | 270.907 | 0 | 1
9/21 | 12:00:00 | 286.15 | 98850 | 8.7 | 220 | 6.8546 | 1875.6 | 2178 | 272.087 | 0 | 1
9/21 | 13:00:00 | 287.15 | 98858 | 11.8 | 230 | 6.3966 | 1879.2 | 2041.2 | 272.808 | 0 | 1
9/21 | 14:00:00 | 288.15 | 98867 | 10.8 | 230 | 6.396 | 1814.4 | 2286 | 273.49 | 0 | 1
9/21 | 15:00:00 | 287.15 | 98858 | 9.3 | 230 | 6.3966 | 1393.2 | 1396.8 | 272.808 | 0 | 1
9/21 | 16:00:00 | 287.15 | 98858 | 10.8 | 230 | 6.854 | 532.8 | 136.8 | 273.521 | 0 | 1
9/21 | 17:00:00 | 286.15 | 98850 | 8.7 | 230 | 7.3412 | 270 | 0 | 272.796 | 0 | 1
9/21 | 18:00:00 | 285.15 | 98841 | 6.7 | 250 | 8.4088 | 93.6 | 0 | 271.813 | 0 | 1
9/21 | 19:00:00 | 284.15 | 98833 | 6.2 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
9/21 | 20:00:00 | 285.15 | 98841 | 6.7 | 240 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
9/21 | 21:00:00 | 284.15 | 98833 | 5.1 | 250 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/21 | 22:00:00 | 284.15 | 98833 | 6.7 | 250 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/21 | 23:00:00 | 284.15 | 98833 | 5.7 | 260 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/21 | 24:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
9/22 | 01:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
9/22 | 02:00:00 | 283.15 | 98824 | 5.1 | 260 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
9/22 | 03:00:00 | 282.15 | 98815 | 5.1 | 250 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
9/22 | 04:00:00 | 281.15 | 98806 | 3.1 | 250 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
9/22 | 05:00:00 | 281.15 | 98806 | 3.6 | 260 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
9/22 | 06:00:00 | 282.15 | 98815 | 4.6 | 260 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
9/22 | 07:00:00 | 282.15 | 98815 | 3.6 | 250 | 6.3994 | 93.6 | 0 | 267.795 | 0 | 1
9/22 | 08:00:00 | 283.15 | 98824 | 5.7 | 250 | 6.3988 | 471.6 | 540 | 269.007 | 0 | 1
9/22 | 09:00:00 | 284.15 | 98833 | 7.2 | 250 | 6.3982 | 1004.4 | 1490.4 | 269.693 | 0 | 1
9/22 | 10:00:00 | 284.15 | 98833 | 7.7 | 260 | 5.9681 | 1461.6 | 2127.6 | 269.465 | 0 | 1
9/22 | 11:00:00 | 284.15 | 98833 | 6.2 | 270 | 6.3982 | 1692 | 1976.4 | 269.957 | 0 | 1
9/22 | 12:00:00 | 285.15 | 98841 | 8.7 | 260 | 5.5636 | 1864.8 | 2203.2 | 270.447 | 0 | 1
9/22 | 13:00:00 | 286.15 | 98850 | 10.3 | 270 | 5.5631 | 1861.2 | 2052 | 271.395 | 0 | 1
9/22 | 14:00:00 | 285.15 | 98841 | 10.3 | 260 | 5.1842 | 1800 | 2404.8 | 269.95 | 0 | 1
9/22 | 15:00:00 | 286.15 | 98850 | 7.7 | 260 | 5.1837 | 1461.6 | 2145.6 | 270.896 | 0 | 1
9/22 | 16:00:00 | 285.15 | 98841 | 6.7 | 260 | 5.1842 | 1000.8 | 1558.8 | 269.95 | 0 | 1
9/22 | 17:00:00 | 285.15 | 98841 | 7.7 | 270 | 5.9676 | 496.8 | 828 | 270.413 | 0 | 1
9/22 | 18:00:00 | 285.15 | 98841 | 6.2 | 260 | 5.9676 | 90 | 0 | 270.413 | 0 | 1
9/22 | 19:00:00 | 284.15 | 98833 | 3.6 | 240 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
9/22 | 20:00:00 | 284.15 | 98833 | 3.1 | 240 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/22 | 21:00:00 | 284.15 | 98833 | 2.6 | 240 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/22 | 22:00:00 | 284.15 | 98833 | 2.6 | 210 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/22 | 23:00:00 | 284.15 | 98833 | 3.1 | 210 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
9/22 | 24:00:00 | 285.15 | 98841 | 4.1 | 230 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
9/23 | 01:00:00 | 284.15 | 98833 | 2.1 | 200 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/23 | 02:00:00 | 284.15 | 98833 | 2.1 | 210 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/23 | 03:00:00 | 284.15 | 98833 | 3.6 | 230 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
9/23 | 04:00:00 | 283.15 | 98824 | 3.1 | 230 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
9/23 | 05:00:00 | 283.15 | 98824 | 2.6 | 210 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
9/23 | 06:00:00 | 283.15 | 98824 | 3.6 | 230 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
9/23 | 07:00:00 | 283.15 | 98824 | 2.1 | 230 | 7.3431 | 82.8 | 0 | 269.46 | 0 | 1
9/23 | 08:00:00 | 283.15 | 98824 | 2.1 | 180 | 7.3431 | 457.2 | 518.4 | 269.46 | 0 | 1
9/23 | 09:00:00 | 284.15 | 98833 | 3.6 | 230 | 7.3425 | 925.2 | 1058.4 | 270.411 | 0 | 1
9/23 | 10:00:00 | 285.15 | 98841 | 4.6 | 220 | 7.3418 | 752.4 | 111.6 | 271.843 | 0 | 1
9/23 | 11:00:00 | 285.15 | 98841 | 4.6 | 220 | 7.3418 | 925.2 | 136.8 | 271.843 | 0 | 1
9/23 | 12:00:00 | 286.15 | 98850 | 3.6 | 230 | 7.8584 | 1015.2 | 172.8 | 273.023 | 0 | 1
9/23 | 13:00:00 | 287.15 | 98858 | 4.6 | 230 | 7.8578 | 1828.8 | 1828.8 | 273.493 | 0 | 1
9/23 | 14:00:00 | 288.15 | 98867 | 4.1 | 230 | 7.857 | 1659.6 | 1674 | 274.446 | 0 | 1
9/23 | 15:00:00 | 288.15 | 98867 | 3.1 | 220 | 7.857 | 1342.8 | 1674 | 274.446 | 0 | 1
9/23 | 16:00:00 | 288.15 | 98867 | 4.6 | 230 | 7.3399 | 914.4 | 1238.4 | 274.218 | 0 | 1
9/23 | 17:00:00 | 288.15 | 98867 | 3.1 | 220 | 7.3399 | 446.4 | 504 | 274.218 | 0 | 1
9/23 | 18:00:00 | 287.15 | 98858 | 3.6 | 220 | 7.3406 | 79.2 | 0 | 273.266 | 0 | 1
9/23 | 19:00:00 | 286.15 | 98850 | 2.1 | 210 | 7.3412 | 0 | 0 | 272.314 | 0 | 1
9/23 | 20:00:00 | 286.15 | 98850 | 2.1 | 180 | 7.3412 | 0 | 0 | 272.314 | 0 | 1
9/23 | 21:00:00 | 285.15 | 98841 | 2.6 | 210 | 7.3418 | 0 | 0 | 271.097 | 0 | 1
9/23 | 22:00:00 | 285.15 | 98841 | 3.6 | 230 | 7.3418 | 0 | 0 | 271.097 | 0 | 1
9/23 | 23:00:00 | 285.15 | 98841 | 5.1 | 220 | 7.3418 | 0 | 0 | 271.729 | 0 | 1
9/23 | 24:00:00 | 285.15 | 98841 | 3.6 | 200 | 6.8552 | 0 | 0 | 271.384 | 0 | 1
9/24 | 01:00:00 | 283.15 | 98824 | 3.1 | 210 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
9/24 | 02:00:00 | 283.15 | 98824 | 3.1 | 210 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
9/24 | 03:00:00 | 283.15 | 98824 | 2.1 | 200 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
9/24 | 04:00:00 | 284.15 | 98833 | 2.1 | 210 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/24 | 05:00:00 | 284.15 | 98833 | 5.1 | 220 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/24 | 06:00:00 | 283.15 | 98824 | 3.6 | 220 | 7.3431 | 0 | 0 | 269.196 | 0 | 1
9/24 | 07:00:00 | 284.15 | 98833 | 2.1 | 220 | 7.3425 | 79.2 | 0 | 270.411 | 0 | 1
9/24 | 08:00:00 | 284.15 | 98833 | 5.1 | 220 | 7.3425 | 442.8 | 507.6 | 270.411 | 0 | 1
9/24 | 09:00:00 | 286.15 | 98850 | 4.1 | 200 | 7.8584 | 910.8 | 1044 | 272.541 | 0 | 1
9/24 | 10:00:00 | 286.15 | 98850 | 5.7 | 220 | 7.8584 | 741.6 | 230.4 | 273.023 | 0 | 1
9/24 | 11:00:00 | 286.15 | 98850 | 4.1 | 200 | 7.8584 | 1645.2 | 619.2 | 272.541 | 0 | 1
9/24 | 12:00:00 | 287.15 | 98858 | 4.6 | 200 | 8.4073 | 1000.8 | 115.2 | 274.203 | 0 | 1
9/24 | 13:00:00 | 287.15 | 98858 | 3.1 | 210 | 8.4073 | 1000.8 | 115.2 | 274.203 | 0 | 1
9/24 | 14:00:00 | 287.15 | 98858 | 3.6 | 220 | 7.8578 | 1638 | 1551.6 | 273.493 | 0 | 1
9/24 | 15:00:00 | 288.15 | 98867 | 2.6 | 240 | 8.4065 | 1317.6 | 1699.2 | 274.672 | 0 | 1
9/24 | 16:00:00 | 288.15 | 98867 | 3.6 | 210 | 8.9902 | 889.2 | 1018.8 | 274.898 | 0 | 1
9/24 | 17:00:00 | 288.15 | 98867 | 3.1 | 230 | 8.4065 | 237.6 | 0 | 275.158 | 0 | 1
9/24 | 18:00:00 | 287.15 | 98858 | 3.1 | 220 | 8.4073 | 39.6 | 0 | 274.203 | 0 | 1
9/24 | 19:00:00 | 287.15 | 98858 | 2.1 | 230 | 8.991 | 0 | 0 | 274.428 | 0 | 1
9/24 | 20:00:00 | 286.15 | 98850 | 2.1 | 170 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
9/24 | 21:00:00 | 286.15 | 98850 | 2.1 | 190 | 8.9918 | 0 | 0 | 272.99 | 0 | 1
9/24 | 22:00:00 | 286.15 | 98850 | 0.5 | 162 | 8.9918 | 0 | 0 | 272.99 | 0 | 1
9/24 | 23:00:00 | 286.15 | 98850 | 1.5 | 248 | 8.408 | 0 | 0 | 273.248 | 0 | 1
9/24 | 24:00:00 | 286.15 | 98850 | 1 | 327 | 8.408 | 0 | 0 | 273.248 | 0 | 1
9/25 | 01:00:00 | 286.15 | 98850 | 1 | 160 | 8.408 | 0 | 0 | 273.248 | 0 | 1
9/25 | 02:00:00 | 285.15 | 98841 | 2.1 | 190 | 8.4088 | 0 | 0 | 271.813 | 0 | 1
9/25 | 03:00:00 | 285.15 | 98841 | 2.1 | 200 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
9/25 | 04:00:00 | 285.15 | 98841 | 2.1 | 200 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
9/25 | 05:00:00 | 285.15 | 98841 | 3.1 | 170 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
9/25 | 06:00:00 | 285.15 | 98841 | 2.6 | 180 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
9/25 | 07:00:00 | 285.15 | 98841 | 2.6 | 170 | 8.4088 | 43.2 | 0 | 272.294 | 0 | 1
9/25 | 08:00:00 | 285.15 | 98841 | 3.6 | 180 | 8.4088 | 237.6 | 0 | 272.294 | 0 | 1
9/25 | 09:00:00 | 285.15 | 98841 | 2.6 | 190 | 8.9926 | 493.2 | 39.6 | 272.517 | 0 | 1
9/25 | 10:00:00 | 287.15 | 98858 | 3.1 | 180 | 9.6108 | 727.2 | 75.6 | 274.652 | 0 | 1
9/25 | 11:00:00 | 287.15 | 98858 | 3.6 | 210 | 9.6108 | 900 | 46.8 | 274.652 | 0 | 1
9/25 | 12:00:00 | 287.15 | 98858 | 4.1 | 220 | 10.2686 | 986.4 | 252 | 274.874 | 0 | 1
9/25 | 13:00:00 | 288.15 | 98867 | 4.1 | 230 | 9.6099 | 1778.4 | 1771.2 | 275.122 | 0 | 1
9/25 | 14:00:00 | 288.15 | 98867 | 5.1 | 220 | 8.4065 | 1612.8 | 1879.2 | 274.672 | 0 | 1
9/25 | 15:00:00 | 290.15 | 98883 | 4.6 | 230 | 8.4052 | 1375.2 | 2052 | 276.308 | 0 | 1
9/25 | 16:00:00 | 290.15 | 98883 | 4.6 | 220 | 8.4052 | 871.2 | 1274.4 | 276.579 | 0 | 1
9/25 | 17:00:00 | 290.15 | 98883 | 4.6 | 230 | 8.4052 | 435.6 | 651.6 | 276.308 | 0 | 1
9/25 | 18:00:00 | 288.15 | 98867 | 5.7 | 230 | 7.3399 | 72 | 0 | 273.95 | 0 | 1
9/25 | 19:00:00 | 288.15 | 98867 | 5.7 | 230 | 7.3399 | 0 | 0 | 273.95 | 0 | 1
9/25 | 20:00:00 | 288.15 | 98867 | 5.1 | 230 | 7.3399 | 0 | 0 | 273.95 | 0 | 1
9/25 | 21:00:00 | 288.15 | 98867 | 6.2 | 200 | 7.3399 | 0 | 0 | 273.95 | 0 | 1
9/25 | 22:00:00 | 287.15 | 98858 | 4.1 | 200 | 7.8578 | 0 | 0 | 273.493 | 0 | 1
9/25 | 23:00:00 | 287.15 | 98858 | 3.6 | 190 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
9/25 | 24:00:00 | 287.15 | 98858 | 3.6 | 210 | 8.4073 | 0 | 0 | 273.719 | 0 | 1
9/26 | 01:00:00 | 287.15 | 98858 | 4.1 | 220 | 7.8578 | 0 | 0 | 273.493 | 0 | 1
9/26 | 02:00:00 | 287.15 | 98858 | 5.7 | 250 | 7.8578 | 0 | 0 | 273.493 | 0 | 1
9/26 | 03:00:00 | 284.15 | 98833 | 6.2 | 250 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/26 | 04:00:00 | 284.15 | 98833 | 4.1 | 230 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/26 | 05:00:00 | 284.15 | 98833 | 4.6 | 250 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
9/26 | 06:00:00 | 284.15 | 98833 | 4.1 | 240 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
9/26 | 07:00:00 | 283.15 | 98824 | 2.1 | 270 | 7.3431 | 75.6 | 0 | 269.196 | 0 | 1
9/26 | 08:00:00 | 283.15 | 98824 | 3.6 | 280 | 7.3431 | 442.8 | 594 | 269.196 | 0 | 1
9/26 | 09:00:00 | 285.15 | 98841 | 4.6 | 270 | 7.8591 | 928.8 | 1461.6 | 271.323 | 0 | 1
9/26 | 10:00:00 | 286.15 | 98850 | 5.7 | 260 | 7.3412 | 1299.6 | 1443.6 | 272.314 | 0 | 1
9/26 | 11:00:00 | 287.15 | 98858 | 7.2 | 260 | 6.3966 | 1616.4 | 1854 | 272.808 | 0 | 1
9/26 | 12:00:00 | 288.15 | 98867 | 6.7 | 270 | 5.5621 | 1890 | 2480.4 | 273.025 | 0 | 1
9/26 | 13:00:00 | 288.15 | 98867 | 4.6 | 250 | 5.5621 | 1886.4 | 2548.8 | 273.025 | 0 | 1
9/26 | 14:00:00 | 289.15 | 98875 | 5.7 | 260 | 5.9656 | 1702.8 | 2361.6 | 274.206 | 0 | 1
9/26 | 15:00:00 | 288.15 | 98867 | 4.6 | 260 | 5.1829 | 1368 | 2059.2 | 272.79 | 0 | 1
9/26 | 16:00:00 | 288.15 | 98867 | 3.6 | 260 | 5.5621 | 907.2 | 1476 | 273.025 | 0 | 1
9/26 | 17:00:00 | 287.15 | 98858 | 2.1 | 230 | 5.9666 | 417.6 | 561.6 | 272.31 | 0 | 1
9/26 | 18:00:00 | 286.15 | 98850 | 1.5 | 42 | 6.3971 | 64.8 | 0 | 271.592 | 0 | 1
9/26 | 19:00:00 | 285.15 | 98841 | 0.5 | 355 | 6.3977 | 0 | 0 | 271.033 | 0 | 1
9/26 | 20:00:00 | 285.15 | 98841 | 1 | 150 | 5.5636 | 0 | 0 | 270.316 | 0 | 1
9/26 | 21:00:00 | 285.15 | 98841 | 1 | 193 | 5.5636 | 0 | 0 | 270.316 | 0 | 1
9/26 | 22:00:00 | 284.15 | 98833 | 2.1 | 140 | 5.9681 | 0 | 0 | 269.854 | 0 | 1
9/26 | 23:00:00 | 283.15 | 98824 | 2.6 | 200 | 5.9687 | 0 | 0 | 269.025 | 0 | 1
9/26 | 24:00:00 | 283.15 | 98824 | 2.6 | 180 | 5.9687 | 0 | 0 | 269.025 | 0 | 1
9/27 | 01:00:00 | 283.15 | 98824 | 2.1 | 210 | 5.9687 | 0 | 0 | 269.025 | 0 | 1
9/27 | 02:00:00 | 282.15 | 98815 | 2.6 | 200 | 5.9692 | 0 | 0 | 268.191 | 0 | 1
9/27 | 03:00:00 | 283.15 | 98824 | 2.6 | 220 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
9/27 | 04:00:00 | 284.15 | 98833 | 3.6 | 210 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
9/27 | 05:00:00 | 283.15 | 98824 | 2.1 | 220 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
9/27 | 06:00:00 | 284.15 | 98833 | 3.1 | 210 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
9/27 | 07:00:00 | 284.15 | 98833 | 2.6 | 230 | 8.4095 | 68.4 | 0 | 270.595 | 0 | 1
9/27 | 08:00:00 | 286.15 | 98850 | 3.1 | 240 | 8.408 | 428.4 | 691.2 | 272.499 | 0 | 1
9/27 | 09:00:00 | 287.15 | 98858 | 2.6 | 210 | 8.991 | 910.8 | 1533.6 | 273.676 | 0 | 1
9/27 | 10:00:00 | 288.15 | 98867 | 3.1 | 220 | 8.9902 | 1353.6 | 2034 | 274.629 | 0 | 1
9/27 | 11:00:00 | 290.15 | 98883 | 3.1 | 230 | 8.4052 | 1684.8 | 2358 | 276.308 | 0 | 1
9/27 | 12:00:00 | 292.15 | 98900 | 3.6 | 220 | 8.4037 | 1850.4 | 2494.8 | 278.213 | 0 | 1
9/27 | 13:00:00 | 293.15 | 98908 | 3.1 | 240 | 7.8537 | 1854 | 2516.4 | 278.935 | 0 | 1
9/27 | 14:00:00 | 294.15 | 98916 | 2.6 | 230 | 7.8531 | 1681.2 | 2408.4 | 279.742 | 0 | 1
9/27 | 15:00:00 | 293.15 | 98908 | 3.1 | 240 | 8.403 | 1321.2 | 1969.2 | 279.165 | 0 | 1
9/27 | 16:00:00 | 294.15 | 98916 | 2.6 | 210 | 8.4023 | 882 | 1555.2 | 280.117 | 0 | 1
9/27 | 17:00:00 | 293.15 | 98908 | 3.1 | 230 | 8.403 | 392.4 | 619.2 | 279.165 | 0 | 1
9/27 | 18:00:00 | 291.15 | 98892 | 2.6 | 220 | 8.4044 | 54 | 0 | 277.532 | 0 | 1
9/27 | 19:00:00 | 290.15 | 98883 | 1 | 38 | 8.4052 | 0 | 0 | 276.579 | 0 | 1
9/27 | 20:00:00 | 289.15 | 98875 | 1.5 | 160 | 8.4059 | 0 | 0 | 275.754 | 0 | 1
9/27 | 21:00:00 | 288.15 | 98867 | 2.6 | 180 | 8.4065 | 0 | 0 | 274.924 | 0 | 1
9/27 | 22:00:00 | 287.15 | 98858 | 2.1 | 200 | 8.4073 | 0 | 0 | 274.088 | 0 | 1
9/27 | 23:00:00 | 288.15 | 98867 | 1 | 250 | 8.4065 | 0 | 0 | 274.924 | 0 | 1
9/27 | 24:00:00 | 287.15 | 98858 | 1 | 250 | 8.4073 | 0 | 0 | 274.088 | 0 | 1
9/28 | 01:00:00 | 286.15 | 98850 | 2.1 | 190 | 8.9918 | 0 | 0 | 273.583 | 0 | 1
9/28 | 02:00:00 | 286.15 | 98850 | 2.1 | 190 | 8.9918 | 0 | 0 | 273.583 | 0 | 1
9/28 | 03:00:00 | 286.15 | 98850 | 2.6 | 170 | 8.408 | 0 | 0 | 273.248 | 0 | 1
9/28 | 04:00:00 | 285.15 | 98841 | 3.1 | 170 | 8.9926 | 0 | 0 | 271.336 | 0 | 1
9/28 | 05:00:00 | 285.15 | 98841 | 3.6 | 160 | 8.9926 | 0 | 0 | 271.336 | 0 | 1
9/28 | 06:00:00 | 284.15 | 98833 | 2.1 | 150 | 8.4095 | 0 | 0 | 270.162 | 0 | 1
9/28 | 07:00:00 | 285.15 | 98841 | 3.6 | 140 | 8.9926 | 64.8 | 0 | 271.336 | 0 | 1
9/28 | 08:00:00 | 285.15 | 98841 | 1.5 | 53 | 8.9926 | 417.6 | 694.8 | 271.336 | 0 | 1
9/28 | 09:00:00 | 287.15 | 98858 | 3.6 | 150 | 10.2686 | 900 | 1609.2 | 273.683 | 0 | 1
9/28 | 10:00:00 | 290.15 | 98883 | 2.6 | 160 | 10.9637 | 1346.4 | 2077.2 | 276.764 | 0 | 1
9/28 | 11:00:00 | 292.15 | 98900 | 2.6 | 140 | 10.9618 | 1674 | 2444.4 | 278.672 | 0 | 1
9/28 | 12:00:00 | 294.15 | 98916 | 1.5 | 325 | 11.6997 | 1814.4 | 2484 | 281.253 | 0 | 1
9/28 | 13:00:00 | 297.15 | 98940 | 5.1 | 190 | 10.9573 | 1810.8 | 2469.6 | 283.894 | 0 | 1
9/28 | 14:00:00 | 297.15 | 98940 | 3.6 | 190 | 10.9573 | 1630.8 | 2347.2 | 283.894 | 0 | 1
9/28 | 15:00:00 | 297.15 | 98940 | 3.6 | 170 | 10.6035 | 1296 | 1947.6 | 283.781 | 0 | 1
9/28 | 16:00:00 | 297.15 | 98940 | 4.6 | 170 | 10.26 | 849.6 | 1306.8 | 283.666 | 0 | 1
9/28 | 17:00:00 | 295.15 | 98924 | 5.1 | 170 | 9.6043 | 374.4 | 572.4 | 281.67 | 0 | 1
9/28 | 18:00:00 | 294.15 | 98916 | 2.6 | 160 | 9.6051 | 50.4 | 0 | 280.715 | 0 | 1
9/28 | 19:00:00 | 293.15 | 98908 | 3.6 | 170 | 8.9864 | 0 | 0 | 279.533 | 0 | 1
9/28 | 20:00:00 | 292.15 | 98900 | 4.1 | 160 | 9.6067 | 0 | 0 | 278.941 | 0 | 1
9/28 | 21:00:00 | 291.15 | 98892 | 3.1 | 150 | 9.6075 | 0 | 0 | 278.115 | 0 | 1
9/28 | 22:00:00 | 291.15 | 98892 | 1 | 140 | 9.6075 | 0 | 0 | 278.115 | 0 | 1
9/28 | 23:00:00 | 290.15 | 98883 | 1 | 4 | 9.6084 | 0 | 0 | 277.285 | 0 | 1
9/28 | 24:00:00 | 288.15 | 98867 | 3.6 | 130 | 8.9902 | 0 | 0 | 275.269 | 0 | 1
9/29 | 01:00:00 | 288.15 | 98867 | 3.6 | 150 | 9.6099 | 0 | 0 | 275.608 | 0 | 1
9/29 | 02:00:00 | 288.15 | 98867 | 3.1 | 170 | 9.6099 | 0 | 0 | 275.608 | 0 | 1
9/29 | 03:00:00 | 287.15 | 98858 | 3.6 | 160 | 9.6108 | 0 | 0 | 274.763 | 0 | 1
9/29 | 04:00:00 | 287.15 | 98858 | 0 | 130 | 9.6108 | 0 | 0 | 274.763 | 0 | 1
9/29 | 05:00:00 | 285.15 | 98841 | 3.6 | 140 | 8.9926 | 0 | 0 | 272.627 | 0 | 1
9/29 | 06:00:00 | 285.15 | 98841 | 2.6 | 140 | 8.9926 | 0 | 0 | 271.77 | 0 | 1
9/29 | 07:00:00 | 285.15 | 98841 | 4.1 | 130 | 8.9926 | 61.2 | 0 | 271.336 | 0 | 1
9/29 | 08:00:00 | 286.15 | 98850 | 2.1 | 335 | 9.6116 | 403.2 | 669.6 | 272.509 | 0 | 1
9/29 | 09:00:00 | 289.15 | 98875 | 0.5 | 95 | 10.2668 | 882 | 1591.2 | 275.589 | 0 | 1
9/29 | 10:00:00 | 291.15 | 98892 | 2.6 | 140 | 10.9627 | 1324.8 | 2055.6 | 277.718 | 0 | 1
9/29 | 11:00:00 | 293.15 | 98908 | 3.6 | 140 | 10.9609 | 1652.4 | 2448 | 279.626 | 0 | 1
9/29 | 12:00:00 | 295.15 | 98924 | 2.1 | 150 | 11.6988 | 1818 | 2570.4 | 281.758 | 0 | 1
9/29 | 13:00:00 | 297.15 | 98940 | 2.6 | 160 | 11.6968 | 1807.2 | 2566.8 | 283.667 | 0 | 1
9/29 | 14:00:00 | 298.15 | 98948 | 4.1 | 220 | 9.602 | 1630.8 | 2397.6 | 284.245 | 0 | 1
9/29 | 15:00:00 | 298.15 | 98948 | 4.1 | 200 | 9.602 | 1288.8 | 2016 | 284.245 | 0 | 1
9/29 | 16:00:00 | 298.15 | 98948 | 3.6 | 210 | 9.602 | 838.8 | 1332 | 284.245 | 0 | 1
9/29 | 17:00:00 | 297.15 | 98940 | 3.6 | 180 | 10.26 | 356.4 | 558 | 283.666 | 0 | 1
9/29 | 18:00:00 | 295.15 | 98924 | 2.6 | 170 | 10.2617 | 43.2 | 0 | 281.897 | 0 | 1
9/29 | 19:00:00 | 294.15 | 98916 | 2.6 | 160 | 10.2625 | 0 | 0 | 281.078 | 0 | 1
9/29 | 20:00:00 | 294.15 | 98916 | 2.6 | 190 | 9.6051 | 0 | 0 | 280.715 | 0 | 1
9/29 | 21:00:00 | 292.15 | 98900 | 2.1 | 200 | 9.6067 | 0 | 0 | 278.941 | 0 | 1
9/29 | 22:00:00 | 291.15 | 98892 | 1.5 | 200 | 9.6075 | 0 | 0 | 278.115 | 0 | 1
9/29 | 23:00:00 | 291.15 | 98892 | 1 | 210 | 9.6075 | 0 | 0 | 278.115 | 0 | 1
9/29 | 24:00:00 | 291.15 | 98892 | 1.5 | 180 | 9.6075 | 0 | 0 | 278.115 | 0 | 1
9/30 | 01:00:00 | 291.15 | 98892 | 1 | 170 | 9.6075 | 0 | 0 | 278.115 | 0 | 1
9/30 | 02:00:00 | 288.15 | 98867 | 1 | 170 | 8.9902 | 0 | 0 | 275.269 | 0 | 1
9/30 | 03:00:00 | 287.15 | 98858 | 0 | 263 | 8.991 | 0 | 0 | 274.428 | 0 | 1
9/30 | 04:00:00 | 287.15 | 98858 | 1.5 | 216 | 8.991 | 0 | 0 | 274.428 | 0 | 1
9/30 | 05:00:00 | 287.15 | 98858 | 3.6 | 160 | 8.991 | 0 | 0 | 274.428 | 0 | 1
9/30 | 06:00:00 | 287.15 | 98858 | 3.6 | 160 | 8.991 | 0 | 0 | 274.428 | 0 | 1
9/30 | 07:00:00 | 288.15 | 98867 | 4.1 | 150 | 8.9902 | 39.6 | 0 | 275.269 | 0 | 1
9/30 | 08:00:00 | 287.15 | 98858 | 3.6 | 140 | 8.991 | 223.2 | 0 | 274.428 | 0 | 1
9/30 | 09:00:00 | 289.15 | 98875 | 2.1 | 110 | 9.6091 | 867.6 | 1342.8 | 275.366 | 0 | 1
9/30 | 10:00:00 | 291.15 | 98892 | 4.1 | 140 | 9.6075 | 1130.4 | 1263.6 | 278.115 | 0 | 1
9/30 | 11:00:00 | 293.15 | 98908 | 3.6 | 130 | 10.2634 | 1494 | 1738.8 | 280.122 | 0 | 1
9/30 | 12:00:00 | 295.15 | 98924 | 3.6 | 140 | 10.9591 | 1699.2 | 2098.8 | 282.26 | 0 | 1
9/30 | 13:00:00 | 297.15 | 98940 | 4.6 | 140 | 10.9573 | 1749.6 | 2394 | 284.036 | 0 | 1
9/30 | 14:00:00 | 299.15 | 98956 | 6.7 | 170 | 9.6012 | 1609.2 | 2390.4 | 285.198 | 0 | 1
9/30 | 15:00:00 | 299.15 | 98956 | 4.6 | 170 | 8.982 | 1270.8 | 2026.8 | 284.814 | 0 | 1
9/30 | 16:00:00 | 298.15 | 98948 | 4.1 | 180 | 9.602 | 817.2 | 1314 | 284.245 | 0 | 1
9/30 | 17:00:00 | 297.15 | 98940 | 3.1 | 180 | 8.9835 | 345.6 | 558 | 283.061 | 0 | 1
9/30 | 18:00:00 | 296.15 | 98932 | 2.6 | 160 | 8.9842 | 39.6 | 0 | 282.108 | 0 | 1
9/30 | 19:00:00 | 292.95 | 98906 | 2.2 | 114 | 9.1076 | 0 | 0 | 279.249 | 0 | 1
9/30 | 20:00:00 | 292.35 | 98902 | 1.9 | 122 | 9.108 | 0 | 0 | 278.95 | 0 | 1
9/30 | 21:00:00 | 292.65 | 98904 | 2 | 137 | 9.1078 | 0 | 0 | 279.236 | 0 | 1
9/30 | 22:00:00 | 290.35 | 98885 | 3.1 | 201 | 8.6924 | 0 | 0 | 276.883 | 0 | 1
9/30 | 23:00:00 | 288.15 | 98866 | 3.8 | 262 | 8.1277 | 0 | 0 | 274.559 | 0 | 1
9/30 | 24:00:00 | 285.35 | 98843 | 4.1 | 285 | 7.3417 | 0 | 0 | 271.423 | 0 | 1
10/1 | 01:00:00 | 282.35 | 98817 | 4.8 | 305 | 6.6246 | 0 | 0 | 268.361 | 0 | 1
10/1 | 02:00:00 | 281.65 | 98811 | 4.5 | 310 | 6.1812 | 0 | 0 | 267.469 | 0 | 1
10/1 | 03:00:00 | 281.15 | 98806 | 4.6 | 312 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
10/1 | 04:00:00 | 280.95 | 98804 | 4.5 | 317 | 5.9699 | 0 | 0 | 266.43 | 0 | 1
10/1 | 05:00:00 | 281.15 | 98806 | 4.1 | 325 | 5.8869 | 0 | 0 | 266.835 | 0 | 1
10/1 | 06:00:00 | 281.35 | 98809 | 3.7 | 327 | 5.8867 | 0 | 0 | 267.025 | 0 | 1
10/1 | 07:00:00 | 280.15 | 98798 | 3.6 | 320 | 5.9703 | 46.8 | 0 | 265.931 | 0 | 1
10/1 | 08:00:00 | 282.15 | 98815 | 3.6 | 340 | 5.5651 | 374.4 | 514.8 | 267.339 | 0 | 1
10/1 | 09:00:00 | 282.15 | 98815 | 3.1 | 330 | 5.9692 | 849.6 | 1422 | 267.568 | 0 | 1
10/1 | 10:00:00 | 283.15 | 98824 | 3.1 | 10 | 5.9687 | 1288.8 | 1980 | 268.516 | 0 | 1
10/1 | 11:00:00 | 284.15 | 98833 | 4.1 | 360 | 6.3982 | 1515.6 | 1623.6 | 269.957 | 0 | 1
10/1 | 12:00:00 | 284.15 | 98833 | 2.6 | 360 | 6.8558 | 1670.4 | 1998 | 270.185 | 0 | 1
10/1 | 13:00:00 | 286.15 | 98850 | 4.1 | 310 | 7.3412 | 1760.4 | 2430 | 272.048 | 0 | 1
10/1 | 14:00:00 | 285.15 | 98841 | 4.6 | 300 | 7.3418 | 1576.8 | 2289.6 | 271.097 | 0 | 1
10/1 | 15:00:00 | 286.15 | 98850 | 4.1 | 280 | 7.3412 | 1238.4 | 1825.2 | 272.048 | 0 | 1
10/1 | 16:00:00 | 285.15 | 98841 | 4.6 | 310 | 7.3418 | 792 | 1328.4 | 271.097 | 0 | 1
10/1 | 17:00:00 | 284.15 | 98833 | 5.1 | 290 | 7.3425 | 324 | 421.2 | 270.147 | 0 | 1
10/1 | 18:00:00 | 283.15 | 98824 | 4.6 | 270 | 6.8564 | 32.4 | 0 | 268.971 | 0 | 1
10/1 | 19:00:00 | 282.15 | 98815 | 3.6 | 290 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
10/1 | 20:00:00 | 281.15 | 98806 | 4.1 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1
10/1 | 21:00:00 | 280.15 | 98798 | 3.6 | 280 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
10/1 | 22:00:00 | 281.15 | 98806 | 3.6 | 260 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
10/1 | 23:00:00 | 280.15 | 98798 | 2.6 | 240 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
10/1 | 24:00:00 | 282.15 | 98815 | 3.1 | 300 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
10/2 | 01:00:00 | 282.15 | 98815 | 4.6 | 290 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
10/2 | 02:00:00 | 281.15 | 98806 | 4.1 | 290 | 6.4 | 0 | 0 | 266.846 | 0 | 1
10/2 | 03:00:00 | 281.15 | 98806 | 3.1 | 300 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
10/2 | 04:00:00 | 282.15 | 98815 | 4.1 | 290 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
10/2 | 05:00:00 | 282.15 | 98815 | 3.6 | 290 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
10/2 | 06:00:00 | 282.15 | 98815 | 5.7 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
10/2 | 07:00:00 | 282.15 | 98815 | 3.1 | 270 | 6.3994 | 25.2 | 0 | 268.532 | 0 | 1
10/2 | 08:00:00 | 282.15 | 98815 | 3.6 | 260 | 6.8571 | 187.2 | 0 | 268.758 | 0 | 1
10/2 | 09:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.8571 | 781.2 | 918 | 268.283 | 0 | 1
10/2 | 10:00:00 | 283.15 | 98824 | 5.1 | 260 | 7.3431 | 1191.6 | 1299.6 | 269.46 | 0 | 1
10/2 | 11:00:00 | 284.15 | 98833 | 4.1 | 240 | 7.8598 | 828 | 126 | 271.115 | 0 | 1
10/2 | 12:00:00 | 284.15 | 98833 | 6.7 | 260 | 8.4095 | 910.8 | 133.2 | 271.339 | 0 | 1
10/2 | 13:00:00 | 285.15 | 98841 | 6.7 | 260 | 8.4088 | 1630.8 | 1569.6 | 271.813 | 0 | 1
10/2 | 14:00:00 | 285.15 | 98841 | 7.7 | 270 | 8.4088 | 1458 | 1447.2 | 271.813 | 0 | 1
10/2 | 15:00:00 | 286.15 | 98850 | 8.2 | 270 | 8.9918 | 630 | 86.4 | 273.473 | 0 | 1
10/2 | 16:00:00 | 286.15 | 98850 | 9.3 | 280 | 8.408 | 399.6 | 14.4 | 273.248 | 0 | 1
10/2 | 17:00:00 | 286.15 | 98850 | 8.7 | 270 | 8.408 | 288 | 356.4 | 272.766 | 0 | 1
10/2 | 18:00:00 | 285.15 | 98841 | 6.7 | 270 | 8.4088 | 21.6 | 0 | 271.813 | 0 | 1
10/2 | 19:00:00 | 286.15 | 98850 | 8.2 | 260 | 8.9918 | 0 | 0 | 272.99 | 0 | 1
10/2 | 20:00:00 | 286.15 | 98850 | 8.2 | 260 | 8.9918 | 0 | 0 | 272.99 | 0 | 1
10/2 | 21:00:00 | 286.15 | 98850 | 9.3 | 260 | 8.9918 | 0 | 0 | 272.99 | 0 | 1
10/2 | 22:00:00 | 286.15 | 98850 | 10.8 | 270 | 8.408 | 0 | 0 | 273.248 | 0 | 1
10/2 | 23:00:00 | 286.15 | 98850 | 11.3 | 260 | 8.408 | 0 | 0 | 273.248 | 0 | 1
10/2 | 24:00:00 | 286.15 | 98850 | 8.7 | 250 | 8.408 | 0 | 0 | 273.248 | 0 | 1
10/3 | 01:00:00 | 286.15 | 98850 | 8.2 | 240 | 8.408 | 0 | 0 | 272.766 | 0 | 1
10/3 | 02:00:00 | 286.15 | 98850 | 7.2 | 240 | 8.408 | 0 | 0 | 273.248 | 0 | 1
10/3 | 03:00:00 | 286.15 | 98850 | 7.7 | 240 | 8.408 | 0 | 0 | 273.248 | 0 | 1
10/3 | 04:00:00 | 286.15 | 98850 | 9.8 | 250 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
10/3 | 05:00:00 | 285.15 | 98841 | 10.8 | 250 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
10/3 | 06:00:00 | 285.15 | 98841 | 12.3 | 250 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
10/3 | 07:00:00 | 285.15 | 98841 | 10.8 | 250 | 8.4088 | 21.6 | 0 | 272.294 | 0 | 1
10/3 | 08:00:00 | 285.15 | 98841 | 13.9 | 250 | 8.4088 | 324 | 432 | 271.813 | 0 | 1
10/3 | 09:00:00 | 285.15 | 98841 | 17.5 | 250 | 8.4088 | 759.6 | 1213.2 | 271.813 | 0 | 1
10/3 | 10:00:00 | 286.15 | 98850 | 16.5 | 260 | 8.9918 | 1166.4 | 1267.2 | 272.99 | 0 | 1
10/3 | 11:00:00 | 285.15 | 98841 | 18 | 260 | 8.9926 | 813.6 | 118.8 | 272.517 | 0 | 1
10/3 | 12:00:00 | 285.15 | 98841 | 17.5 | 260 | 8.9926 | 1616.4 | 1555.2 | 272.036 | 0 | 1
10/3 | 13:00:00 | 284.15 | 98833 | 17 | 270 | 8.4095 | 1609.2 | 1915.2 | 270.859 | 0 | 1
10/3 | 14:00:00 | 285.15 | 98841 | 16.5 | 270 | 8.4088 | 1522.8 | 2250 | 271.547 | 0 | 1
10/3 | 15:00:00 | 286.15 | 98850 | 15.4 | 270 | 9.6116 | 1180.8 | 1875.6 | 272.945 | 0 | 1
10/3 | 16:00:00 | 285.15 | 98841 | 12.9 | 270 | 8.9926 | 741.6 | 1198.8 | 271.77 | 0 | 1
10/3 | 17:00:00 | 285.15 | 98841 | 12.9 | 270 | 5.5636 | 273.6 | 273.6 | 270.447 | 0 | 1
10/3 | 18:00:00 | 283.15 | 98824 | 10.3 | 270 | 5.9687 | 18 | 0 | 268.516 | 0 | 1
10/3 | 19:00:00 | 283.15 | 98824 | 9.8 | 280 | 5.5646 | 0 | 0 | 268.287 | 0 | 1
10/3 | 20:00:00 | 282.15 | 98815 | 8.7 | 280 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
10/3 | 21:00:00 | 283.15 | 98824 | 9.8 | 280 | 5.5646 | 0 | 0 | 268.287 | 0 | 1
10/3 | 22:00:00 | 282.15 | 98815 | 9.3 | 280 | 5.1856 | 0 | 0 | 267.11 | 0 | 1
10/3 | 23:00:00 | 282.15 | 98815 | 10.3 | 280 | 5.1856 | 0 | 0 | 267.11 | 0 | 1
10/3 | 24:00:00 | 281.15 | 98806 | 6.2 | 290 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
10/4 | 01:00:00 | 282.15 | 98815 | 7.2 | 270 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
10/4 | 02:00:00 | 281.15 | 98806 | 9.3 | 290 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
10/4 | 03:00:00 | 280.15 | 98798 | 7.2 | 280 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
10/4 | 04:00:00 | 280.15 | 98798 | 3.1 | 10 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
10/4 | 05:00:00 | 280.15 | 98798 | 3.6 | 290 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
10/4 | 06:00:00 | 280.15 | 98798 | 5.7 | 270 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
10/4 | 07:00:00 | 280.15 | 98798 | 5.1 | 260 | 5.5661 | 36 | 0 | 265.444 | 0 | 1
10/4 | 08:00:00 | 281.15 | 98806 | 4.6 | 250 | 5.5656 | 334.8 | 388.8 | 266.392 | 0 | 1
10/4 | 09:00:00 | 282.15 | 98815 | 7.2 | 280 | 5.5651 | 662.4 | 486 | 267.846 | 0 | 1
10/4 | 10:00:00 | 283.15 | 98824 | 7.2 | 280 | 5.5646 | 1101.6 | 1267.2 | 268.675 | 0 | 1
10/4 | 11:00:00 | 284.15 | 98833 | 7.2 | 280 | 5.5641 | 1461.6 | 1850.4 | 269.498 | 0 | 1
10/4 | 12:00:00 | 284.15 | 98833 | 5.7 | 270 | 5.1847 | 1616.4 | 2008.8 | 269.266 | 0 | 1
10/4 | 13:00:00 | 283.15 | 98824 | 6.2 | 310 | 5.9687 | 1695.6 | 2401.2 | 268.516 | 0 | 1
10/4 | 14:00:00 | 285.15 | 98841 | 5.7 | 280 | 5.5636 | 1512 | 2257.2 | 270.182 | 0 | 1
10/4 | 15:00:00 | 285.15 | 98841 | 6.7 | 280 | 5.1842 | 1177.2 | 1818 | 269.95 | 0 | 1
10/4 | 16:00:00 | 285.15 | 98841 | 5.7 | 270 | 5.1842 | 730.8 | 1285.2 | 269.95 | 0 | 1
10/4 | 17:00:00 | 283.15 | 98824 | 4.6 | 280 | 5.5646 | 273.6 | 331.2 | 268.287 | 0 | 1
10/4 | 18:00:00 | 283.15 | 98824 | 4.1 | 260 | 5.5646 | 10.8 | 0 | 268.287 | 0 | 1
10/4 | 19:00:00 | 282.15 | 98815 | 3.1 | 280 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
10/4 | 20:00:00 | 280.15 | 98798 | 0.5 | 55 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
10/4 | 21:00:00 | 280.15 | 98798 | 2.6 | 310 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
10/4 | 22:00:00 | 280.15 | 98798 | 2.6 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
10/4 | 23:00:00 | 279.15 | 98789 | 2.1 | 270 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
10/4 | 24:00:00 | 279.15 | 98789 | 2.1 | 250 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
10/5 | 01:00:00 | 278.15 | 98780 | 2.6 | 220 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/5 | 02:00:00 | 278.15 | 98780 | 2.1 | 240 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
10/5 | 03:00:00 | 278.15 | 98780 | 1.5 | 256 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
10/5 | 04:00:00 | 278.15 | 98780 | 2.1 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/5 | 05:00:00 | 278.15 | 98780 | 1.5 | 220 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
10/5 | 06:00:00 | 279.15 | 98789 | 2.6 | 230 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
10/5 | 07:00:00 | 278.15 | 98780 | 2.6 | 260 | 5.1875 | 14.4 | 0 | 264.154 | 0 | 1
10/5 | 08:00:00 | 279.15 | 98789 | 2.1 | 240 | 5.5666 | 320.4 | 417.6 | 264.497 | 0 | 1
10/5 | 09:00:00 | 280.15 | 98798 | 1 | 239 | 5.9703 | 777.6 | 1346.4 | 265.671 | 0 | 1
10/5 | 10:00:00 | 283.15 | 98824 | 2.1 | 130 | 5.9687 | 1209.6 | 1843.2 | 268.516 | 0 | 1
10/5 | 11:00:00 | 283.15 | 98824 | 2.6 | 150 | 5.9687 | 1526.4 | 2268 | 268.516 | 0 | 1
10/5 | 12:00:00 | 284.15 | 98833 | 2.1 | 150 | 5.9681 | 1688.4 | 2440.8 | 269.465 | 0 | 1
10/5 | 13:00:00 | 285.15 | 98841 | 2.1 | 110 | 5.9676 | 1674 | 2430 | 270.413 | 0 | 1
10/5 | 14:00:00 | 285.15 | 98841 | 2.6 | 130 | 5.5636 | 1490.4 | 2239.2 | 270.182 | 0 | 1
10/5 | 15:00:00 | 286.15 | 98850 | 1 | 50 | 5.5631 | 1148.4 | 1792.8 | 271.13 | 0 | 1
10/5 | 16:00:00 | 286.15 | 98850 | 2.1 | 150 | 5.5631 | 705.6 | 1249.2 | 271.13 | 0 | 1
10/5 | 17:00:00 | 285.15 | 98841 | 2.1 | 140 | 5.5636 | 255.6 | 306 | 270.182 | 0 | 1
10/5 | 18:00:00 | 283.15 | 98824 | 1.5 | 140 | 5.1851 | 3.6 | 0 | 268.319 | 0 | 1
10/5 | 19:00:00 | 282.15 | 98815 | 2.1 | 160 | 5.5651 | 0 | 0 | 267.601 | 0 | 1
10/5 | 20:00:00 | 283.15 | 98824 | 2.1 | 150 | 5.5646 | 0 | 0 | 268.55 | 0 | 1
10/5 | 21:00:00 | 282.15 | 98815 | 2.1 | 140 | 5.5651 | 0 | 0 | 267.601 | 0 | 1
10/5 | 22:00:00 | 281.15 | 98806 | 2.1 | 140 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
10/5 | 23:00:00 | 281.15 | 98806 | 2.6 | 150 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
10/5 | 24:00:00 | 280.15 | 98798 | 2.6 | 160 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
10/6 | 01:00:00 | 280.15 | 98798 | 3.1 | 160 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
10/6 | 02:00:00 | 280.15 | 98798 | 2.1 | 170 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
10/6 | 03:00:00 | 279.15 | 98789 | 3.6 | 150 | 5.5666 | 0 | 0 | 264.497 | 0 | 1
10/6 | 04:00:00 | 280.15 | 98798 | 4.1 | 160 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
10/6 | 05:00:00 | 282.15 | 98815 | 3.1 | 140 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/6 | 06:00:00 | 281.15 | 98806 | 3.1 | 130 | 6.4 | 0 | 0 | 267.58 | 0 | 1
10/6 | 07:00:00 | 281.15 | 98806 | 3.6 | 140 | 6.8577 | 14.4 | 0 | 267.805 | 0 | 1
10/6 | 08:00:00 | 283.15 | 98824 | 3.1 | 140 | 7.8605 | 158.4 | 0 | 270.161 | 0 | 1
10/6 | 09:00:00 | 284.15 | 98833 | 3.6 | 130 | 8.4095 | 396 | 21.6 | 271.339 | 0 | 1
10/6 | 10:00:00 | 285.15 | 98841 | 2.6 | 140 | 8.9926 | 615.6 | 64.8 | 272.517 | 0 | 1
10/6 | 11:00:00 | 287.15 | 98858 | 4.1 | 200 | 10.2686 | 777.6 | 43.2 | 274.874 | 0 | 1
10/6 | 12:00:00 | 289.15 | 98875 | 4.6 | 220 | 10.9646 | 856.8 | 46.8 | 277.011 | 0 | 1
10/6 | 13:00:00 | 290.15 | 98883 | 5.7 | 220 | 10.9637 | 849.6 | 46.8 | 277.969 | 0 | 1
10/6 | 14:00:00 | 289.15 | 98875 | 3.6 | 220 | 11.7047 | 752.4 | 104.4 | 277.232 | 0 | 1
10/6 | 15:00:00 | 288.15 | 98867 | 5.7 | 230 | 10.2677 | 1047.6 | 1184.4 | 275.344 | 0 | 1
10/6 | 16:00:00 | 289.15 | 98875 | 2.6 | 270 | 10.9646 | 633.6 | 907.2 | 276.522 | 0 | 1
10/6 | 17:00:00 | 288.15 | 98867 | 5.1 | 290 | 10.2677 | 223.2 | 259.2 | 275.344 | 0 | 1
10/6 | 18:00:00 | 287.15 | 98858 | 4.1 | 280 | 10.2686 | 0 | 0 | 274.874 | 0 | 1
10/6 | 19:00:00 | 286.15 | 98850 | 4.6 | 310 | 9.6116 | 0 | 0 | 273.695 | 0 | 1
10/6 | 20:00:00 | 285.15 | 98841 | 3.6 | 360 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
10/6 | 21:00:00 | 284.15 | 98833 | 2.6 | 300 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/6 | 22:00:00 | 283.15 | 98824 | 3.1 | 310 | 7.8605 | 0 | 0 | 269.684 | 0 | 1
10/6 | 23:00:00 | 283.15 | 98824 | 1.5 | 318 | 5.9687 | 0 | 0 | 268.779 | 0 | 1
10/6 | 24:00:00 | 282.15 | 98815 | 1.5 | 310 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
10/7 | 01:00:00 | 281.15 | 98806 | 2.1 | 310 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
10/7 | 02:00:00 | 280.15 | 98798 | 3.6 | 330 | 4.496 | 0 | 0 | 264.755 | 0 | 1
10/7 | 03:00:00 | 278.15 | 98780 | 3.6 | 310 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
10/7 | 04:00:00 | 277.15 | 98771 | 3.6 | 290 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
10/7 | 05:00:00 | 277.15 | 98771 | 4.1 | 280 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
10/7 | 06:00:00 | 276.15 | 98762 | 4.1 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
10/7 | 07:00:00 | 276.15 | 98762 | 3.6 | 270 | 4.1841 | 10.8 | 0 | 261.463 | 0 | 1
10/7 | 08:00:00 | 277.15 | 98771 | 4.1 | 300 | 4.1838 | 219.6 | 50.4 | 262.3 | 0 | 1
10/7 | 09:00:00 | 278.15 | 98780 | 3.6 | 260 | 4.8311 | 453.6 | 93.6 | 263.818 | 0 | 1
10/7 | 10:00:00 | 280.15 | 98798 | 3.1 | 250 | 4.8303 | 975.6 | 968.4 | 265.488 | 0 | 1
10/7 | 11:00:00 | 282.15 | 98815 | 2.1 | 300 | 5.1856 | 1335.6 | 1490.4 | 267.495 | 0 | 1
10/7 | 12:00:00 | 284.15 | 98833 | 1.5 | 58 | 5.1847 | 1598.4 | 2095.2 | 269.137 | 0 | 1
10/7 | 13:00:00 | 283.15 | 98824 | 5.1 | 310 | 5.1851 | 1540.8 | 1954.8 | 268.319 | 0 | 1
10/7 | 14:00:00 | 284.15 | 98833 | 4.6 | 310 | 5.1847 | 1443.6 | 2214 | 269.003 | 0 | 1
10/7 | 15:00:00 | 284.15 | 98833 | 3.1 | 300 | 5.5641 | 1105.2 | 1756.8 | 269.234 | 0 | 1
10/7 | 16:00:00 | 283.15 | 98824 | 3.6 | 300 | 5.5646 | 662.4 | 1195.2 | 268.287 | 0 | 1
10/7 | 17:00:00 | 282.15 | 98815 | 4.1 | 300 | 5.1856 | 223.2 | 255.6 | 267.11 | 0 | 1
10/7 | 18:00:00 | 282.15 | 98815 | 3.6 | 300 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
10/7 | 19:00:00 | 281.15 | 98806 | 3.6 | 300 | 5.5656 | 0 | 0 | 267.013 | 0 | 1
10/7 | 20:00:00 | 280.15 | 98798 | 4.1 | 310 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
10/7 | 21:00:00 | 279.15 | 98789 | 3.6 | 300 | 5.187 | 0 | 0 | 264.996 | 0 | 1
10/7 | 22:00:00 | 279.15 | 98789 | 3.6 | 300 | 5.187 | 0 | 0 | 264.996 | 0 | 1
10/7 | 23:00:00 | 278.15 | 98780 | 3.1 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/7 | 24:00:00 | 278.15 | 98780 | 3.6 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/8 | 01:00:00 | 277.15 | 98771 | 4.1 | 270 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
10/8 | 02:00:00 | 277.15 | 98771 | 3.6 | 270 | 5.1879 | 0 | 0 | 262.633 | 0 | 1
10/8 | 03:00:00 | 279.15 | 98789 | 2.6 | 270 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
10/8 | 04:00:00 | 280.15 | 98798 | 3.1 | 260 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
10/8 | 05:00:00 | 279.15 | 98789 | 1.5 | 260 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
10/8 | 06:00:00 | 278.15 | 98780 | 1.5 | 260 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
10/8 | 07:00:00 | 277.15 | 98771 | 1 | 32 | 5.1879 | 3.6 | 0 | 263.204 | 0 | 1
10/8 | 08:00:00 | 279.15 | 98789 | 1 | 167 | 5.5666 | 118.8 | 0 | 265.332 | 0 | 1
10/8 | 09:00:00 | 281.15 | 98806 | 0 | 206 | 5.9698 | 439.2 | 115.2 | 267.353 | 0 | 1
10/8 | 10:00:00 | 282.15 | 98815 | 3.1 | 310 | 5.5651 | 1152 | 1530 | 267.339 | 0 | 1
10/8 | 11:00:00 | 283.15 | 98824 | 4.1 | 300 | 5.5646 | 1465.2 | 2235.6 | 268.287 | 0 | 1
10/8 | 12:00:00 | 284.15 | 98833 | 4.1 | 300 | 5.5641 | 1530 | 1940.4 | 269.498 | 0 | 1
10/8 | 13:00:00 | 285.15 | 98841 | 4.6 | 330 | 4.8281 | 1519.2 | 1695.6 | 269.98 | 0 | 1
10/8 | 14:00:00 | 285.15 | 98841 | 4.6 | 310 | 6.3977 | 1332 | 1533.6 | 270.907 | 0 | 1
10/8 | 15:00:00 | 285.15 | 98841 | 3.1 | 300 | 6.8552 | 1076.4 | 1782 | 270.871 | 0 | 1
10/8 | 16:00:00 | 284.15 | 98833 | 3.1 | 300 | 6.3982 | 640.8 | 1155.6 | 269.693 | 0 | 1
10/8 | 17:00:00 | 284.15 | 98833 | 2.6 | 310 | 5.9681 | 194.4 | 262.8 | 269.728 | 0 | 1
10/8 | 18:00:00 | 283.15 | 98824 | 2.1 | 360 | 5.5646 | 0 | 0 | 268.287 | 0 | 1
10/8 | 19:00:00 | 282.15 | 98815 | 2.1 | 350 | 5.1856 | 0 | 0 | 267.495 | 0 | 1
10/8 | 20:00:00 | 281.15 | 98806 | 2.6 | 360 | 5.1861 | 0 | 0 | 266.667 | 0 | 1
10/8 | 21:00:00 | 279.15 | 98789 | 2.1 | 70 | 5.187 | 0 | 0 | 264.996 | 0 | 1
10/8 | 22:00:00 | 278.15 | 98780 | 2.1 | 100 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/8 | 23:00:00 | 278.15 | 98780 | 1.5 | 120 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/8 | 24:00:00 | 278.15 | 98780 | 1.5 | 70 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
10/9 | 01:00:00 | 278.15 | 98780 | 1.5 | 80 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
10/9 | 02:00:00 | 278.15 | 98780 | 1.5 | 110 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/9 | 03:00:00 | 277.15 | 98771 | 1.5 | 60 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
10/9 | 04:00:00 | 277.15 | 98771 | 1.5 | 90 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
10/9 | 05:00:00 | 276.15 | 98762 | 2.1 | 90 | 4.832 | 0 | 0 | 262.027 | 0 | 1
10/9 | 06:00:00 | 277.15 | 98771 | 2.6 | 80 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
10/9 | 07:00:00 | 277.15 | 98771 | 3.1 | 90 | 4.8316 | 7.2 | 0 | 262.149 | 0 | 1
10/9 | 08:00:00 | 277.15 | 98771 | 2.6 | 100 | 5.1879 | 266.4 | 338.4 | 262.376 | 0 | 1
10/9 | 09:00:00 | 278.15 | 98780 | 3.1 | 110 | 5.1875 | 709.2 | 1281.6 | 263.323 | 0 | 1
10/9 | 10:00:00 | 279.15 | 98789 | 2.6 | 140 | 5.5666 | 1130.4 | 1792.8 | 264.497 | 0 | 1
10/9 | 11:00:00 | 281.15 | 98806 | 4.6 | 150 | 5.5656 | 1443.6 | 2217.6 | 266.392 | 0 | 1
10/9 | 12:00:00 | 282.15 | 98815 | 5.1 | 150 | 5.5651 | 1508.4 | 1926 | 267.601 | 0 | 1
10/9 | 13:00:00 | 282.15 | 98815 | 4.6 | 140 | 5.9692 | 1490.4 | 1537.2 | 267.83 | 0 | 1
10/9 | 14:00:00 | 284.15 | 98833 | 4.6 | 150 | 6.3982 | 727.2 | 244.8 | 270.435 | 0 | 1
10/9 | 15:00:00 | 284.15 | 98833 | 6.2 | 170 | 6.3982 | 550.8 | 79.2 | 270.435 | 0 | 1
10/9 | 16:00:00 | 284.15 | 98833 | 5.7 | 130 | 6.3982 | 583.2 | 738 | 269.957 | 0 | 1
10/9 | 17:00:00 | 284.15 | 98833 | 5.1 | 130 | 6.3982 | 100.8 | 0 | 270.435 | 0 | 1
10/9 | 18:00:00 | 283.15 | 98824 | 5.7 | 140 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
10/9 | 19:00:00 | 282.15 | 98815 | 6.7 | 140 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/9 | 20:00:00 | 282.15 | 98815 | 6.2 | 140 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/9 | 21:00:00 | 282.15 | 98815 | 5.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/9 | 22:00:00 | 282.15 | 98815 | 5.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/9 | 23:00:00 | 281.15 | 98806 | 4.1 | 150 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
10/9 | 24:00:00 | 282.15 | 98815 | 2.6 | 170 | 7.3438 | 0 | 0 | 269.092 | 0 | 1
10/10 | 01:00:00 | 282.15 | 98815 | 1.5 | 180 | 7.3438 | 0 | 0 | 269.092 | 0 | 1
10/10 | 02:00:00 | 282.15 | 98815 | 0.5 | 216 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/10 | 03:00:00 | 282.15 | 98815 | 0.5 | 252 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/10 | 04:00:00 | 282.15 | 98815 | 1.5 | 280 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/10 | 05:00:00 | 282.15 | 98815 | 3.1 | 280 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/10 | 06:00:00 | 283.15 | 98824 | 5.1 | 290 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
10/10 | 07:00:00 | 282.15 | 98815 | 4.1 | 310 | 7.3438 | 3.6 | 0 | 268.245 | 0 | 1
10/10 | 08:00:00 | 282.15 | 98815 | 3.6 | 290 | 7.3438 | 241.2 | 237.6 | 268.508 | 0 | 1
10/10 | 09:00:00 | 284.15 | 98833 | 4.6 | 270 | 7.3425 | 687.6 | 1234.8 | 270.147 | 0 | 1
10/10 | 10:00:00 | 284.15 | 98833 | 5.7 | 280 | 7.3425 | 1044 | 1512 | 270.411 | 0 | 1
10/10 | 11:00:00 | 285.15 | 98841 | 5.7 | 280 | 7.3418 | 1332 | 1760.4 | 271.363 | 0 | 1
10/10 | 12:00:00 | 286.15 | 98850 | 4.6 | 280 | 7.8584 | 1476 | 1854 | 272.541 | 0 | 1
10/10 | 13:00:00 | 287.15 | 98858 | 5.7 | 280 | 7.8578 | 1548 | 2322 | 273.226 | 0 | 1
10/10 | 14:00:00 | 287.15 | 98858 | 6.2 | 270 | 7.8578 | 1360.8 | 2091.6 | 273.226 | 0 | 1
10/10 | 15:00:00 | 287.15 | 98858 | 6.2 | 270 | 8.4073 | 1022.4 | 1764 | 273.451 | 0 | 1
10/10 | 16:00:00 | 286.15 | 98850 | 5.1 | 280 | 8.408 | 594 | 1029.6 | 272.499 | 0 | 1
10/10 | 17:00:00 | 286.15 | 98850 | 5.1 | 280 | 8.408 | 165.6 | 136.8 | 272.766 | 0 | 1
10/10 | 18:00:00 | 285.15 | 98841 | 5.1 | 270 | 7.8591 | 0 | 0 | 272.069 | 0 | 1
10/10 | 19:00:00 | 285.15 | 98841 | 3.6 | 260 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
10/10 | 20:00:00 | 284.15 | 98833 | 3.6 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/10 | 21:00:00 | 284.15 | 98833 | 3.1 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/10 | 22:00:00 | 284.15 | 98833 | 0.5 | 196 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/10 | 23:00:00 | 284.15 | 98833 | 1.5 | 187 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/10 | 24:00:00 | 284.15 | 98833 | 2.6 | 230 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/11 | 01:00:00 | 284.15 | 98833 | 2.6 | 240 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/11 | 02:00:00 | 284.15 | 98833 | 2.1 | 240 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/11 | 03:00:00 | 284.15 | 98833 | 3.1 | 240 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/11 | 04:00:00 | 284.15 | 98833 | 6.2 | 260 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/11 | 05:00:00 | 284.15 | 98833 | 4.1 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
10/11 | 06:00:00 | 284.15 | 98833 | 6.2 | 270 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
10/11 | 07:00:00 | 283.15 | 98824 | 8.7 | 260 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
10/11 | 08:00:00 | 284.15 | 98833 | 4.6 | 250 | 7.3425 | 241.2 | 291.6 | 270.147 | 0 | 1
10/11 | 09:00:00 | 285.15 | 98841 | 6.7 | 260 | 7.8591 | 630 | 1026 | 271.588 | 0 | 1
10/11 | 10:00:00 | 284.15 | 98833 | 5.1 | 260 | 7.8598 | 1022.4 | 1432.8 | 270.636 | 0 | 1
10/11 | 11:00:00 | 285.15 | 98841 | 7.2 | 270 | 7.8591 | 1310.4 | 1738.8 | 271.588 | 0 | 1
10/11 | 12:00:00 | 287.15 | 98858 | 9.8 | 280 | 7.3406 | 1458 | 1609.2 | 273.266 | 0 | 1
10/11 | 13:00:00 | 287.15 | 98858 | 8.7 | 290 | 9.6108 | 1429.2 | 1796.4 | 274.167 | 0 | 1
10/11 | 14:00:00 | 285.15 | 98841 | 10.8 | 310 | 8.9926 | 1256.4 | 1728 | 272.036 | 0 | 1
10/11 | 15:00:00 | 286.15 | 98850 | 9.8 | 290 | 9.6116 | 939.6 | 1429.2 | 273.212 | 0 | 1
10/11 | 16:00:00 | 285.15 | 98841 | 10.3 | 300 | 8.9926 | 572.4 | 993.6 | 271.77 | 0 | 1
10/11 | 17:00:00 | 285.15 | 98841 | 8.7 | 300 | 8.4088 | 162 | 183.6 | 271.547 | 0 | 1
10/11 | 18:00:00 | 284.15 | 98833 | 9.3 | 300 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
10/11 | 19:00:00 | 282.15 | 98815 | 6.7 | 310 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
10/11 | 20:00:00 | 282.15 | 98815 | 7.2 | 300 | 5.5651 | 0 | 0 | 267.846 | 0 | 1
10/11 | 21:00:00 | 282.15 | 98815 | 7.2 | 300 | 5.5651 | 0 | 0 | 267.846 | 0 | 1
10/11 | 22:00:00 | 281.15 | 98806 | 6.2 | 300 | 5.5656 | 0 | 0 | 267.013 | 0 | 1
10/11 | 23:00:00 | 282.15 | 98815 | 6.7 | 330 | 5.5651 | 0 | 0 | 267.846 | 0 | 1
10/11 | 24:00:00 | 282.15 | 98815 | 6.7 | 340 | 5.1856 | 0 | 0 | 267.495 | 0 | 1
10/12 | 01:00:00 | 280.15 | 98798 | 5.7 | 290 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
10/12 | 02:00:00 | 280.15 | 98798 | 5.7 | 330 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
10/12 | 03:00:00 | 281.15 | 98806 | 7.2 | 350 | 4.8299 | 0 | 0 | 266.316 | 0 | 1
10/12 | 04:00:00 | 281.15 | 98806 | 5.7 | 340 | 4.8299 | 0 | 0 | 266.316 | 0 | 1
10/12 | 05:00:00 | 280.15 | 98798 | 4.6 | 310 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
10/12 | 06:00:00 | 278.15 | 98780 | 4.1 | 310 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
10/12 | 07:00:00 | 279.15 | 98789 | 4.6 | 280 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
10/12 | 08:00:00 | 279.15 | 98789 | 4.1 | 300 | 4.8307 | 172.8 | 10.8 | 264.656 | 0 | 1
10/12 | 09:00:00 | 280.15 | 98798 | 3.6 | 270 | 5.1865 | 489.6 | 320.4 | 265.834 | 0 | 1
10/12 | 10:00:00 | 282.15 | 98815 | 3.6 | 310 | 5.1856 | 961.2 | 1195.2 | 267.495 | 0 | 1
10/12 | 11:00:00 | 283.15 | 98824 | 3.6 | 300 | 5.5646 | 1378.8 | 2034 | 268.287 | 0 | 1
10/12 | 12:00:00 | 284.15 | 98833 | 2.1 | 350 | 5.5641 | 1533.6 | 2350.8 | 269.234 | 0 | 1
10/12 | 13:00:00 | 284.15 | 98833 | 3.1 | 330 | 5.5641 | 1512 | 2332.8 | 269.234 | 0 | 1
10/12 | 14:00:00 | 285.15 | 98841 | 3.1 | 320 | 5.5636 | 1324.8 | 2023.2 | 270.182 | 0 | 1
10/12 | 15:00:00 | 285.15 | 98841 | 3.1 | 310 | 5.9676 | 928.8 | 1368 | 270.678 | 0 | 1
10/12 | 16:00:00 | 284.15 | 98833 | 2.6 | 280 | 5.9681 | 525.6 | 853.2 | 269.728 | 0 | 1
10/12 | 17:00:00 | 284.15 | 98833 | 2.1 | 350 | 5.9681 | 140.4 | 64.8 | 269.728 | 0 | 1
10/12 | 18:00:00 | 284.15 | 98833 | 1 | 230 | 5.9681 | 0 | 0 | 269.728 | 0 | 1
10/12 | 19:00:00 | 283.15 | 98824 | 2.1 | 310 | 5.9687 | 0 | 0 | 268.779 | 0 | 1
10/12 | 20:00:00 | 281.15 | 98806 | 3.1 | 300 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
10/12 | 21:00:00 | 281.15 | 98806 | 3.1 | 320 | 5.5656 | 0 | 0 | 267.013 | 0 | 1
10/12 | 22:00:00 | 280.15 | 98798 | 2.1 | 290 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
10/12 | 23:00:00 | 279.15 | 98789 | 2.6 | 290 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
10/12 | 24:00:00 | 279.15 | 98789 | 2.6 | 290 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
10/13 | 01:00:00 | 278.15 | 98780 | 2.1 | 290 | 5.5671 | 0 | 0 | 264.381 | 0 | 1
10/13 | 02:00:00 | 278.15 | 98780 | 2.1 | 280 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/13 | 03:00:00 | 277.15 | 98771 | 3.1 | 260 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
10/13 | 04:00:00 | 277.15 | 98771 | 3.6 | 270 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
10/13 | 05:00:00 | 277.15 | 98771 | 3.1 | 280 | 5.1879 | 0 | 0 | 263.204 | 0 | 1
10/13 | 06:00:00 | 278.15 | 98780 | 3.6 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/13 | 07:00:00 | 278.15 | 98780 | 2.6 | 270 | 5.1875 | 0 | 0 | 264.154 | 0 | 1
10/13 | 08:00:00 | 278.15 | 98780 | 3.1 | 280 | 5.1875 | 93.6 | 0 | 264.154 | 0 | 1
10/13 | 09:00:00 | 281.15 | 98806 | 3.6 | 270 | 5.9698 | 388.8 | 72 | 267.353 | 0 | 1
10/13 | 10:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.3994 | 637.2 | 234 | 268.532 | 0 | 1
10/13 | 11:00:00 | 285.15 | 98841 | 3.1 | 260 | 6.8552 | 1123.2 | 1054.8 | 271.384 | 0 | 1
10/13 | 12:00:00 | 285.15 | 98841 | 3.6 | 290 | 6.8552 | 1501.2 | 2167.2 | 270.871 | 0 | 1
10/13 | 13:00:00 | 286.15 | 98850 | 5.1 | 290 | 7.3412 | 1479.6 | 2278.8 | 272.048 | 0 | 1
10/13 | 14:00:00 | 286.15 | 98850 | 4.1 | 320 | 7.3412 | 1292.4 | 2034 | 272.048 | 0 | 1
10/13 | 15:00:00 | 286.15 | 98850 | 3.1 | 300 | 7.3412 | 957.6 | 1602 | 272.048 | 0 | 1
10/13 | 16:00:00 | 286.15 | 98850 | 4.1 | 270 | 7.8584 | 536.4 | 993.6 | 272.274 | 0 | 1
10/13 | 17:00:00 | 285.15 | 98841 | 3.6 | 280 | 7.3418 | 136.8 | 133.2 | 271.097 | 0 | 1
10/13 | 18:00:00 | 285.15 | 98841 | 3.6 | 270 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
10/13 | 19:00:00 | 284.15 | 98833 | 3.1 | 270 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/13 | 20:00:00 | 284.15 | 98833 | 2.6 | 280 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/13 | 21:00:00 | 284.15 | 98833 | 3.1 | 280 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/13 | 22:00:00 | 284.15 | 98833 | 4.1 | 290 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
10/13 | 23:00:00 | 284.15 | 98833 | 4.1 | 280 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
10/13 | 24:00:00 | 284.15 | 98833 | 3.1 | 300 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
10/14 | 01:00:00 | 284.15 | 98833 | 3.6 | 290 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
10/14 | 02:00:00 | 284.15 | 98833 | 3.1 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/14 | 03:00:00 | 284.15 | 98833 | 2.6 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/14 | 04:00:00 | 284.15 | 98833 | 3.1 | 270 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/14 | 05:00:00 | 284.15 | 98833 | 2.6 | 270 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/14 | 06:00:00 | 284.15 | 98833 | 3.1 | 280 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/14 | 07:00:00 | 284.15 | 98833 | 3.1 | 270 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/14 | 08:00:00 | 284.15 | 98833 | 3.1 | 280 | 8.4095 | 190.8 | 219.6 | 270.859 | 0 | 1
10/14 | 09:00:00 | 284.15 | 98833 | 3.1 | 300 | 8.4095 | 583.2 | 889.2 | 270.859 | 0 | 1
10/14 | 10:00:00 | 286.15 | 98850 | 2.1 | 290 | 8.9918 | 964.8 | 1476 | 272.99 | 0 | 1
10/14 | 11:00:00 | 286.15 | 98850 | 1 | 230 | 8.9918 | 1245.6 | 1371.6 | 272.99 | 0 | 1
10/14 | 12:00:00 | 287.15 | 98858 | 1 | 200 | 8.991 | 770.4 | 115.2 | 274.428 | 0 | 1
10/14 | 13:00:00 | 287.15 | 98858 | 1.5 | 135 | 8.4073 | 759.6 | 43.2 | 274.203 | 0 | 1
10/14 | 14:00:00 | 287.15 | 98858 | 2.6 | 240 | 8.4073 | 662.4 | 97.2 | 274.203 | 0 | 1
10/14 | 15:00:00 | 287.15 | 98858 | 2.6 | 230 | 8.991 | 878.4 | 1209.6 | 273.944 | 0 | 1
10/14 | 16:00:00 | 287.15 | 98858 | 2.6 | 260 | 8.4073 | 486 | 914.4 | 273.719 | 0 | 1
10/14 | 17:00:00 | 287.15 | 98858 | 2.1 | 250 | 8.991 | 64.8 | 0 | 274.428 | 0 | 1
10/14 | 18:00:00 | 286.15 | 98850 | 1.5 | 3 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
10/14 | 19:00:00 | 286.15 | 98850 | 3.1 | 270 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
10/14 | 20:00:00 | 286.15 | 98850 | 2.6 | 270 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
10/14 | 21:00:00 | 285.15 | 98841 | 2.1 | 280 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/14 | 22:00:00 | 285.15 | 98841 | 2.6 | 300 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/14 | 23:00:00 | 285.15 | 98841 | 2.6 | 290 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/14 | 24:00:00 | 285.15 | 98841 | 2.1 | 290 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/15 | 01:00:00 | 285.15 | 98841 | 2.6 | 290 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/15 | 02:00:00 | 285.15 | 98841 | 1.5 | 290 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/15 | 03:00:00 | 285.15 | 98841 | 2.6 | 300 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/15 | 04:00:00 | 285.15 | 98841 | 2.1 | 310 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/15 | 05:00:00 | 285.15 | 98841 | 3.6 | 320 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/15 | 06:00:00 | 285.15 | 98841 | 3.1 | 310 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/15 | 07:00:00 | 285.15 | 98841 | 3.1 | 320 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/15 | 08:00:00 | 285.15 | 98841 | 1.5 | 252 | 8.9926 | 61.2 | 0 | 272.627 | 0 | 1
10/15 | 09:00:00 | 285.15 | 98841 | 0 | 218 | 8.9926 | 313.2 | 0 | 272.517 | 0 | 1
10/15 | 10:00:00 | 286.15 | 98850 | 2.6 | 360 | 9.6116 | 522 | 50.4 | 273.695 | 0 | 1
10/15 | 11:00:00 | 286.15 | 98850 | 2.1 | 10 | 9.6116 | 680.4 | 39.6 | 273.695 | 0 | 1
10/15 | 12:00:00 | 287.15 | 98858 | 2.6 | 10 | 9.6108 | 756 | 43.2 | 274.652 | 0 | 1
10/15 | 13:00:00 | 287.15 | 98858 | 1.5 | 121 | 9.6108 | 745.2 | 43.2 | 274.652 | 0 | 1
10/15 | 14:00:00 | 286.15 | 98850 | 1.5 | 240 | 9.6116 | 648 | 93.6 | 273.695 | 0 | 1
10/15 | 15:00:00 | 287.15 | 98858 | 1.5 | 189 | 9.6108 | 856.8 | 1184.4 | 274.167 | 0 | 1
10/15 | 16:00:00 | 287.15 | 98858 | 1 | 106 | 9.6108 | 259.2 | 0 | 274.652 | 0 | 1
10/15 | 17:00:00 | 287.15 | 98858 | 0.5 | 57 | 9.6108 | 57.6 | 0 | 274.652 | 0 | 1
10/15 | 18:00:00 | 286.15 | 98850 | 0 | 69 | 9.6116 | 0 | 0 | 273.695 | 0 | 1
10/15 | 19:00:00 | 286.15 | 98850 | 2.1 | 280 | 9.6116 | 0 | 0 | 273.695 | 0 | 1
10/15 | 20:00:00 | 286.15 | 98850 | 2.1 | 310 | 9.6116 | 0 | 0 | 273.212 | 0 | 1
10/15 | 21:00:00 | 286.15 | 98850 | 2.6 | 340 | 9.6116 | 0 | 0 | 273.695 | 0 | 1
10/15 | 22:00:00 | 286.15 | 98850 | 4.6 | 350 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
10/15 | 23:00:00 | 284.15 | 98833 | 6.2 | 20 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/15 | 24:00:00 | 284.15 | 98833 | 4.6 | 10 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/16 | 01:00:00 | 284.15 | 98833 | 8.2 | 20 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/16 | 02:00:00 | 284.15 | 98833 | 6.7 | 20 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/16 | 03:00:00 | 283.15 | 98824 | 7.7 | 30 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
10/16 | 04:00:00 | 283.15 | 98824 | 6.2 | 20 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
10/16 | 05:00:00 | 282.15 | 98815 | 7.2 | 10 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
10/16 | 06:00:00 | 282.15 | 98815 | 6.2 | 10 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
10/16 | 07:00:00 | 282.15 | 98815 | 3.1 | 340 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
10/16 | 08:00:00 | 282.15 | 98815 | 4.1 | 360 | 6.3994 | 169.2 | 129.6 | 268.057 | 0 | 1
10/16 | 09:00:00 | 282.15 | 98815 | 5.1 | 360 | 5.9692 | 554.4 | 918 | 267.83 | 0 | 1
10/16 | 10:00:00 | 282.15 | 98815 | 6.2 | 20 | 5.9692 | 936 | 1393.2 | 267.83 | 0 | 1
10/16 | 11:00:00 | 283.15 | 98824 | 7.2 | 10 | 5.5646 | 1220.4 | 1659.6 | 268.55 | 0 | 1
10/16 | 12:00:00 | 283.15 | 98824 | 7.2 | 10 | 5.5646 | 1443.6 | 2113.2 | 268.287 | 0 | 1
10/16 | 13:00:00 | 284.15 | 98833 | 6.2 | 10 | 5.1847 | 1342.8 | 1832.4 | 269.266 | 0 | 1
10/16 | 14:00:00 | 284.15 | 98833 | 5.1 | 10 | 5.1847 | 1162.8 | 1688.4 | 269.266 | 0 | 1
10/16 | 15:00:00 | 284.15 | 98833 | 5.7 | 360 | 5.5641 | 846 | 1360.8 | 269.498 | 0 | 1
10/16 | 16:00:00 | 284.15 | 98833 | 4.6 | 10 | 5.1847 | 453.6 | 507.6 | 269.266 | 0 | 1
10/16 | 17:00:00 | 283.15 | 98824 | 4.1 | 360 | 5.1851 | 100.8 | 3.6 | 268.056 | 0 | 1
10/16 | 18:00:00 | 282.15 | 98815 | 3.1 | 330 | 4.8294 | 0 | 0 | 267.139 | 0 | 1
10/16 | 19:00:00 | 280.15 | 98798 | 4.6 | 320 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
10/16 | 20:00:00 | 280.15 | 98798 | 5.1 | 320 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
10/16 | 21:00:00 | 280.15 | 98798 | 5.1 | 340 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
10/16 | 22:00:00 | 280.15 | 98798 | 4.6 | 320 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
10/16 | 23:00:00 | 280.15 | 98798 | 5.1 | 360 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
10/16 | 24:00:00 | 280.15 | 98798 | 5.1 | 360 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
10/17 | 01:00:00 | 280.15 | 98798 | 4.1 | 310 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
10/17 | 02:00:00 | 280.15 | 98798 | 3.6 | 340 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
10/17 | 03:00:00 | 280.15 | 98798 | 2.1 | 330 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
10/17 | 04:00:00 | 279.15 | 98789 | 3.1 | 300 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
10/17 | 05:00:00 | 279.15 | 98789 | 3.6 | 310 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
10/17 | 06:00:00 | 280.15 | 98798 | 3.6 | 320 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
10/17 | 07:00:00 | 280.15 | 98798 | 3.1 | 330 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
10/17 | 08:00:00 | 280.15 | 98798 | 3.1 | 350 | 5.9703 | 90 | 0 | 266.402 | 0 | 1
10/17 | 09:00:00 | 281.15 | 98806 | 3.1 | 310 | 5.9698 | 298.8 | 0 | 267.353 | 0 | 1
10/17 | 10:00:00 | 281.15 | 98806 | 3.1 | 340 | 5.9698 | 918 | 1166.4 | 266.881 | 0 | 1
10/17 | 11:00:00 | 282.15 | 98815 | 2.1 | 30 | 5.9692 | 1198.8 | 1710 | 267.83 | 0 | 1
10/17 | 12:00:00 | 282.15 | 98815 | 3.6 | 360 | 5.1856 | 1339.2 | 1598.4 | 267.371 | 0 | 1
10/17 | 13:00:00 | 283.15 | 98824 | 2.6 | 10 | 5.1851 | 1321.2 | 1584 | 268.319 | 0 | 1
10/17 | 14:00:00 | 284.15 | 98833 | 3.1 | 20 | 5.1847 | 1141.2 | 1357.2 | 269.266 | 0 | 1
10/17 | 15:00:00 | 283.15 | 98824 | 3.1 | 10 | 4.829 | 460.8 | 64.8 | 268.561 | 0 | 1
10/17 | 16:00:00 | 283.15 | 98824 | 3.1 | 350 | 5.1851 | 241.2 | 0 | 268.793 | 0 | 1
10/17 | 17:00:00 | 283.15 | 98824 | 1.5 | 10 | 5.1851 | 28.8 | 0 | 268.902 | 0 | 1
10/17 | 18:00:00 | 282.15 | 98815 | 1 | 340 | 5.1856 | 0 | 0 | 267.844 | 0 | 1
10/17 | 19:00:00 | 282.15 | 98815 | 0.5 | 330 | 5.5651 | 0 | 0 | 268.183 | 0 | 1
10/17 | 20:00:00 | 281.15 | 98806 | 0.5 | 6 | 5.5656 | 0 | 0 | 267.233 | 0 | 1
10/17 | 21:00:00 | 281.15 | 98806 | 0 | 355 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
10/17 | 22:00:00 | 281.15 | 98806 | 1 | 140 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
10/17 | 23:00:00 | 279.15 | 98789 | 1.5 | 180 | 5.187 | 0 | 0 | 264.996 | 0 | 1
10/17 | 24:00:00 | 280.15 | 98798 | 1 | 103 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
10/18 | 01:00:00 | 279.15 | 98789 | 1.5 | 250 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
10/18 | 02:00:00 | 278.15 | 98780 | 2.1 | 260 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
10/18 | 03:00:00 | 277.15 | 98771 | 2.1 | 250 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
10/18 | 04:00:00 | 277.15 | 98771 | 2.6 | 260 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
10/18 | 05:00:00 | 278.15 | 98780 | 2.6 | 260 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
10/18 | 06:00:00 | 278.15 | 98780 | 2.1 | 230 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
10/18 | 07:00:00 | 278.15 | 98780 | 2.1 | 210 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
10/18 | 08:00:00 | 278.15 | 98780 | 2.1 | 220 | 5.1875 | 82.8 | 0 | 264.047 | 0 | 1
10/18 | 09:00:00 | 279.15 | 98789 | 1.5 | 139 | 5.187 | 291.6 | 0 | 264.996 | 0 | 1
10/18 | 10:00:00 | 280.15 | 98798 | 3.1 | 240 | 5.1865 | 500.4 | 36 | 265.946 | 0 | 1
10/18 | 11:00:00 | 281.15 | 98806 | 3.6 | 220 | 5.1861 | 655.2 | 111.6 | 266.895 | 0 | 1
10/18 | 12:00:00 | 282.15 | 98815 | 4.1 | 240 | 5.5651 | 730.8 | 126 | 268.075 | 0 | 1
10/18 | 13:00:00 | 282.15 | 98815 | 7.7 | 260 | 5.1856 | 720 | 255.6 | 267.844 | 0 | 1
10/18 | 14:00:00 | 282.15 | 98815 | 6.7 | 260 | 5.5651 | 1184.4 | 1609.2 | 267.339 | 0 | 1
10/18 | 15:00:00 | 282.15 | 98815 | 7.7 | 260 | 5.9692 | 853.2 | 1580.4 | 267.568 | 0 | 1
10/18 | 16:00:00 | 282.15 | 98815 | 6.7 | 250 | 6.3994 | 442.8 | 853.2 | 267.795 | 0 | 1
10/18 | 17:00:00 | 282.15 | 98815 | 5.7 | 260 | 6.3994 | 90 | 0 | 267.795 | 0 | 1
10/18 | 18:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
10/18 | 19:00:00 | 282.15 | 98815 | 2.6 | 240 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
10/18 | 20:00:00 | 282.15 | 98815 | 3.6 | 240 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
10/18 | 21:00:00 | 282.15 | 98815 | 3.6 | 240 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
10/18 | 22:00:00 | 282.15 | 98815 | 5.1 | 240 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/18 | 23:00:00 | 282.15 | 98815 | 5.7 | 240 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
10/18 | 24:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
10/19 | 01:00:00 | 282.15 | 98815 | 4.1 | 230 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
10/19 | 02:00:00 | 281.15 | 98806 | 4.6 | 230 | 6.4 | 0 | 0 | 266.846 | 0 | 1
10/19 | 03:00:00 | 281.15 | 98806 | 3.6 | 240 | 6.4 | 0 | 0 | 266.846 | 0 | 1
10/19 | 04:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.4 | 0 | 0 | 267.107 | 0 | 1
10/19 | 05:00:00 | 281.15 | 98806 | 2.6 | 230 | 6.4 | 0 | 0 | 267.107 | 0 | 1
10/19 | 06:00:00 | 281.15 | 98806 | 2.1 | 210 | 6.8577 | 0 | 0 | 267.071 | 0 | 1
10/19 | 07:00:00 | 281.15 | 98806 | 2.6 | 230 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
10/19 | 08:00:00 | 281.15 | 98806 | 3.6 | 200 | 6.8577 | 140.4 | 68.4 | 267.332 | 0 | 1
10/19 | 09:00:00 | 281.15 | 98806 | 4.1 | 220 | 6.8577 | 504 | 842.4 | 267.332 | 0 | 1
10/19 | 10:00:00 | 283.15 | 98824 | 4.6 | 220 | 6.8564 | 874.8 | 1389.6 | 269.234 | 0 | 1
10/19 | 11:00:00 | 283.15 | 98824 | 4.1 | 210 | 6.8564 | 1152 | 1666.8 | 269.234 | 0 | 1
10/19 | 12:00:00 | 284.15 | 98833 | 4.6 | 210 | 7.3425 | 1288.8 | 1537.2 | 270.411 | 0 | 1
10/19 | 13:00:00 | 284.15 | 98833 | 6.7 | 200 | 6.8558 | 1267.2 | 1530 | 270.185 | 0 | 1
10/19 | 14:00:00 | 284.15 | 98833 | 3.1 | 210 | 6.8558 | 1090.8 | 1306.8 | 270.185 | 0 | 1
10/19 | 15:00:00 | 285.15 | 98841 | 2.6 | 200 | 6.3977 | 435.6 | 54 | 271.387 | 0 | 1
10/19 | 16:00:00 | 285.15 | 98841 | 3.1 | 180 | 5.9676 | 399.6 | 658.8 | 270.678 | 0 | 1
10/19 | 17:00:00 | 283.15 | 98824 | 3.6 | 200 | 5.5646 | 75.6 | 0 | 268.55 | 0 | 1
10/19 | 18:00:00 | 282.15 | 98815 | 2.6 | 180 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
10/19 | 19:00:00 | 281.15 | 98806 | 2.6 | 170 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
10/19 | 20:00:00 | 282.15 | 98815 | 3.6 | 170 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
10/19 | 21:00:00 | 282.15 | 98815 | 4.1 | 170 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
10/19 | 22:00:00 | 281.15 | 98806 | 4.1 | 160 | 6.4 | 0 | 0 | 267.688 | 0 | 1
10/19 | 23:00:00 | 281.15 | 98806 | 5.1 | 160 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
10/19 | 24:00:00 | 281.15 | 98806 | 6.7 | 160 | 5.5656 | 0 | 0 | 267.013 | 0 | 1
10/20 | 01:00:00 | 280.15 | 98798 | 5.7 | 170 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
10/20 | 02:00:00 | 280.15 | 98798 | 6.2 | 140 | 4.8303 | 0 | 0 | 265.246 | 0 | 1
10/20 | 03:00:00 | 279.15 | 98789 | 6.2 | 150 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
10/20 | 04:00:00 | 279.15 | 98789 | 6.2 | 140 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
10/20 | 05:00:00 | 278.15 | 98780 | 6.2 | 150 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
10/20 | 06:00:00 | 278.15 | 98780 | 7.7 | 130 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
10/20 | 07:00:00 | 278.15 | 98780 | 5.7 | 130 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
10/20 | 08:00:00 | 278.15 | 98780 | 6.7 | 120 | 4.8311 | 82.8 | 0 | 263.818 | 0 | 1
10/20 | 09:00:00 | 279.15 | 98789 | 8.2 | 130 | 5.187 | 493.2 | 676.8 | 264.528 | 0 | 1
10/20 | 10:00:00 | 280.15 | 98798 | 7.2 | 130 | 5.5661 | 864 | 1400.4 | 265.704 | 0 | 1
10/20 | 11:00:00 | 280.15 | 98798 | 8.2 | 140 | 5.5661 | 1141.2 | 1684.8 | 265.704 | 0 | 1
10/20 | 12:00:00 | 281.15 | 98806 | 8.2 | 130 | 5.5656 | 1278 | 1562.4 | 266.653 | 0 | 1
10/20 | 13:00:00 | 281.15 | 98806 | 6.7 | 130 | 5.5656 | 1252.8 | 1443.6 | 266.653 | 0 | 1
10/20 | 14:00:00 | 281.15 | 98806 | 5.1 | 130 | 5.9698 | 594 | 201.6 | 267.353 | 0 | 1
10/20 | 15:00:00 | 280.15 | 98798 | 6.7 | 140 | 6.4005 | 424.8 | 21.6 | 266.628 | 0 | 1
10/20 | 16:00:00 | 281.15 | 98806 | 5.7 | 130 | 6.4 | 212.4 | 0 | 267.58 | 0 | 1
10/20 | 17:00:00 | 281.15 | 98806 | 5.7 | 140 | 6.8577 | 39.6 | 0 | 267.805 | 0 | 1
10/20 | 18:00:00 | 281.15 | 98806 | 6.7 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
10/20 | 19:00:00 | 281.15 | 98806 | 4.6 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
10/20 | 20:00:00 | 281.15 | 98806 | 6.2 | 130 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
10/20 | 21:00:00 | 281.15 | 98806 | 5.7 | 120 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
10/20 | 22:00:00 | 281.15 | 98806 | 5.7 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
10/20 | 23:00:00 | 281.15 | 98806 | 4.1 | 130 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
10/20 | 24:00:00 | 281.15 | 98806 | 3.6 | 100 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
10/21 | 01:00:00 | 281.15 | 98806 | 4.1 | 110 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
10/21 | 02:00:00 | 282.15 | 98815 | 4.1 | 110 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/21 | 03:00:00 | 282.15 | 98815 | 3.6 | 110 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/21 | 04:00:00 | 282.15 | 98815 | 3.6 | 120 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/21 | 05:00:00 | 282.15 | 98815 | 4.1 | 150 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/21 | 06:00:00 | 282.15 | 98815 | 3.1 | 160 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/21 | 07:00:00 | 282.15 | 98815 | 3.1 | 160 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/21 | 08:00:00 | 283.15 | 98824 | 3.6 | 180 | 7.8605 | 64.8 | 0 | 270.161 | 0 | 1
10/21 | 09:00:00 | 283.15 | 98824 | 3.1 | 160 | 7.8605 | 262.8 | 0 | 270.161 | 0 | 1
10/21 | 10:00:00 | 283.15 | 98824 | 4.1 | 150 | 7.8605 | 464.4 | 28.8 | 270.161 | 0 | 1
10/21 | 11:00:00 | 283.15 | 98824 | 4.1 | 150 | 7.8605 | 615.6 | 100.8 | 270.161 | 0 | 1
10/21 | 12:00:00 | 284.15 | 98833 | 3.6 | 130 | 7.8598 | 691.2 | 115.2 | 271.115 | 0 | 1
10/21 | 13:00:00 | 284.15 | 98833 | 4.1 | 140 | 7.8598 | 676.8 | 115.2 | 271.115 | 0 | 1
10/21 | 14:00:00 | 284.15 | 98833 | 2.1 | 160 | 8.4095 | 579.6 | 32.4 | 271.339 | 0 | 1
10/21 | 15:00:00 | 284.15 | 98833 | 4.1 | 140 | 8.4095 | 410.4 | 21.6 | 271.339 | 0 | 1
10/21 | 16:00:00 | 284.15 | 98833 | 4.1 | 140 | 8.4095 | 201.6 | 0 | 271.339 | 0 | 1
10/21 | 17:00:00 | 284.15 | 98833 | 4.6 | 130 | 8.4095 | 64.8 | 0 | 270.859 | 0 | 1
10/21 | 18:00:00 | 284.15 | 98833 | 5.1 | 130 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/21 | 19:00:00 | 283.15 | 98824 | 5.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/21 | 20:00:00 | 283.15 | 98824 | 4.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/21 | 21:00:00 | 283.15 | 98824 | 4.6 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/21 | 22:00:00 | 283.15 | 98824 | 4.1 | 130 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/21 | 23:00:00 | 283.15 | 98824 | 4.6 | 130 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/21 | 24:00:00 | 283.15 | 98824 | 5.1 | 120 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/22 | 01:00:00 | 282.15 | 98815 | 4.6 | 120 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/22 | 02:00:00 | 282.15 | 98815 | 4.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/22 | 03:00:00 | 283.15 | 98824 | 4.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/22 | 04:00:00 | 282.15 | 98815 | 4.1 | 120 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/22 | 05:00:00 | 282.15 | 98815 | 4.6 | 130 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/22 | 06:00:00 | 283.15 | 98824 | 4.6 | 130 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/22 | 07:00:00 | 282.15 | 98815 | 3.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/22 | 08:00:00 | 282.15 | 98815 | 4.1 | 110 | 7.3438 | 61.2 | 0 | 268.983 | 0 | 1
10/22 | 09:00:00 | 282.15 | 98815 | 4.1 | 110 | 7.3438 | 255.6 | 0 | 268.983 | 0 | 1
10/22 | 10:00:00 | 283.15 | 98824 | 3.6 | 130 | 7.3431 | 457.2 | 28.8 | 269.936 | 0 | 1
10/22 | 11:00:00 | 283.15 | 98824 | 5.1 | 130 | 7.8605 | 604.8 | 97.2 | 270.161 | 0 | 1
10/22 | 12:00:00 | 283.15 | 98824 | 5.7 | 140 | 7.3431 | 680.4 | 115.2 | 269.936 | 0 | 1
10/22 | 13:00:00 | 283.15 | 98824 | 3.6 | 160 | 7.3431 | 666 | 111.6 | 269.936 | 0 | 1
10/22 | 14:00:00 | 284.15 | 98833 | 3.6 | 160 | 7.3425 | 568.8 | 90 | 270.89 | 0 | 1
10/22 | 15:00:00 | 284.15 | 98833 | 2.6 | 130 | 7.8598 | 399.6 | 18 | 271.115 | 0 | 1
10/22 | 16:00:00 | 284.15 | 98833 | 3.6 | 120 | 7.8598 | 194.4 | 0 | 271.115 | 0 | 1
10/22 | 17:00:00 | 284.15 | 98833 | 2.6 | 130 | 7.8598 | 32.4 | 0 | 271.115 | 0 | 1
10/22 | 18:00:00 | 284.15 | 98833 | 4.6 | 110 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/22 | 19:00:00 | 284.15 | 98833 | 3.1 | 150 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/22 | 20:00:00 | 284.15 | 98833 | 3.6 | 140 | 8.4095 | 0 | 0 | 270.859 | 0 | 1
10/22 | 21:00:00 | 284.15 | 98833 | 4.1 | 140 | 8.4095 | 0 | 0 | 270.859 | 0 | 1
10/22 | 22:00:00 | 284.15 | 98833 | 4.6 | 160 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/22 | 23:00:00 | 283.15 | 98824 | 4.1 | 160 | 7.8605 | 0 | 0 | 269.42 | 0 | 1
10/22 | 24:00:00 | 283.15 | 98824 | 4.6 | 160 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/23 | 01:00:00 | 283.15 | 98824 | 3.6 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/23 | 02:00:00 | 283.15 | 98824 | 3.6 | 150 | 7.8605 | 0 | 0 | 269.684 | 0 | 1
10/23 | 03:00:00 | 283.15 | 98824 | 4.1 | 150 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
10/23 | 04:00:00 | 283.15 | 98824 | 4.6 | 150 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
10/23 | 05:00:00 | 282.15 | 98815 | 3.6 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/23 | 06:00:00 | 282.15 | 98815 | 3.1 | 150 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/23 | 07:00:00 | 282.15 | 98815 | 3.6 | 150 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/23 | 08:00:00 | 282.15 | 98815 | 3.6 | 150 | 7.3438 | 57.6 | 0 | 268.983 | 0 | 1
10/23 | 09:00:00 | 283.15 | 98824 | 3.6 | 170 | 7.8605 | 244.8 | 0 | 270.161 | 0 | 1
10/23 | 10:00:00 | 283.15 | 98824 | 3.6 | 170 | 7.8605 | 802.8 | 1018.8 | 269.684 | 0 | 1
10/23 | 11:00:00 | 284.15 | 98833 | 3.1 | 180 | 7.8598 | 1072.8 | 1602 | 270.636 | 0 | 1
10/23 | 12:00:00 | 285.15 | 98841 | 3.1 | 200 | 7.8591 | 1206 | 1494 | 271.588 | 0 | 1
10/23 | 13:00:00 | 286.15 | 98850 | 2.1 | 220 | 7.8584 | 1180.8 | 1476 | 272.541 | 0 | 1
10/23 | 14:00:00 | 286.15 | 98850 | 2.1 | 230 | 7.8584 | 1004.4 | 1537.2 | 272.541 | 0 | 1
10/23 | 15:00:00 | 286.15 | 98850 | 2.1 | 230 | 7.8584 | 702 | 1188 | 272.541 | 0 | 1
10/23 | 16:00:00 | 286.15 | 98850 | 2.1 | 220 | 7.8584 | 352.8 | 709.2 | 272.274 | 0 | 1
10/23 | 17:00:00 | 285.15 | 98841 | 2.1 | 220 | 7.3418 | 54 | 0 | 271.097 | 0 | 1
10/23 | 18:00:00 | 284.15 | 98833 | 1.5 | 220 | 7.3425 | 0 | 0 | 270.147 | 0 | 1
10/23 | 19:00:00 | 284.15 | 98833 | 2.6 | 180 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/23 | 20:00:00 | 284.15 | 98833 | 2.6 | 180 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/23 | 21:00:00 | 283.15 | 98824 | 3.1 | 180 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
10/23 | 22:00:00 | 283.15 | 98824 | 2.6 | 160 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
10/23 | 23:00:00 | 283.15 | 98824 | 2.1 | 160 | 7.3431 | 0 | 0 | 270.046 | 0 | 1
10/23 | 24:00:00 | 283.15 | 98824 | 2.6 | 150 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
10/24 | 01:00:00 | 283.15 | 98824 | 3.1 | 140 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
10/24 | 02:00:00 | 283.15 | 98824 | 3.1 | 130 | 7.8605 | 0 | 0 | 269.42 | 0 | 1
10/24 | 03:00:00 | 283.15 | 98824 | 2.6 | 120 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/24 | 04:00:00 | 283.15 | 98824 | 3.1 | 130 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/24 | 05:00:00 | 283.15 | 98824 | 4.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/24 | 06:00:00 | 283.15 | 98824 | 5.1 | 140 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/24 | 07:00:00 | 283.15 | 98824 | 5.7 | 150 | 7.8605 | 0 | 0 | 270.27 | 0 | 1
10/24 | 08:00:00 | 283.15 | 98824 | 6.2 | 150 | 7.8605 | 32.4 | 0 | 270.27 | 0 | 1
10/24 | 09:00:00 | 284.15 | 98833 | 6.7 | 150 | 8.4095 | 144 | 0 | 271.449 | 0 | 1
10/24 | 10:00:00 | 284.15 | 98833 | 6.7 | 150 | 8.4095 | 266.4 | 0 | 271.449 | 0 | 1
10/24 | 11:00:00 | 285.15 | 98841 | 6.7 | 150 | 8.9926 | 356.4 | 0 | 272.627 | 0 | 1
10/24 | 12:00:00 | 285.15 | 98841 | 5.7 | 160 | 8.9926 | 399.6 | 0 | 272.627 | 0 | 1
10/24 | 13:00:00 | 286.15 | 98850 | 5.7 | 160 | 9.6116 | 392.4 | 0 | 273.806 | 0 | 1
10/24 | 14:00:00 | 287.15 | 98858 | 5.1 | 170 | 10.2686 | 979.2 | 1206 | 274.389 | 0 | 1
10/24 | 15:00:00 | 289.15 | 98875 | 6.2 | 210 | 9.6091 | 720 | 1465.2 | 275.806 | 0 | 1
10/24 | 16:00:00 | 288.15 | 98867 | 5.1 | 210 | 8.4065 | 316.8 | 532.8 | 274.672 | 0 | 1
10/24 | 17:00:00 | 286.15 | 98850 | 7.2 | 230 | 7.8584 | 46.8 | 0 | 272.541 | 0 | 1
10/24 | 18:00:00 | 286.15 | 98850 | 9.3 | 220 | 7.8584 | 0 | 0 | 273.023 | 0 | 1
10/24 | 19:00:00 | 285.15 | 98841 | 9.3 | 240 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
10/24 | 20:00:00 | 285.15 | 98841 | 11.8 | 240 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
10/24 | 21:00:00 | 285.15 | 98841 | 10.3 | 240 | 7.3418 | 0 | 0 | 271.363 | 0 | 1
10/24 | 22:00:00 | 285.15 | 98841 | 10.8 | 250 | 6.8552 | 0 | 0 | 270.871 | 0 | 1
10/24 | 23:00:00 | 285.15 | 98841 | 9.3 | 240 | 6.3977 | 0 | 0 | 270.643 | 0 | 1
10/24 | 24:00:00 | 284.15 | 98833 | 10.8 | 250 | 6.3982 | 0 | 0 | 270.204 | 0 | 1
10/25 | 01:00:00 | 283.15 | 98824 | 6.7 | 230 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
10/25 | 02:00:00 | 283.15 | 98824 | 8.2 | 230 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
10/25 | 03:00:00 | 284.15 | 98833 | 7.7 | 230 | 6.3982 | 0 | 0 | 269.693 | 0 | 1
10/25 | 04:00:00 | 284.15 | 98833 | 7.2 | 240 | 6.8558 | 0 | 0 | 269.921 | 0 | 1
10/25 | 05:00:00 | 284.15 | 98833 | 8.7 | 250 | 6.8558 | 0 | 0 | 269.921 | 0 | 1
10/25 | 06:00:00 | 284.15 | 98833 | 7.7 | 240 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/25 | 07:00:00 | 284.15 | 98833 | 7.2 | 240 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/25 | 08:00:00 | 284.15 | 98833 | 8.2 | 250 | 7.3425 | 50.4 | 0 | 270.89 | 0 | 1
10/25 | 09:00:00 | 284.15 | 98833 | 9.3 | 250 | 7.3425 | 230.4 | 0 | 270.89 | 0 | 1
10/25 | 10:00:00 | 285.15 | 98841 | 8.7 | 250 | 7.3418 | 424.8 | 50.4 | 271.843 | 0 | 1
10/25 | 11:00:00 | 285.15 | 98841 | 9.8 | 240 | 7.3418 | 1033.2 | 1285.2 | 271.363 | 0 | 1
10/25 | 12:00:00 | 285.15 | 98841 | 10.3 | 240 | 7.3418 | 648 | 226.8 | 271.843 | 0 | 1
10/25 | 13:00:00 | 285.15 | 98841 | 9.3 | 240 | 6.8552 | 1144.8 | 1371.6 | 271.136 | 0 | 1
10/25 | 14:00:00 | 285.15 | 98841 | 10.3 | 250 | 7.3418 | 536.4 | 169.2 | 271.843 | 0 | 1
10/25 | 15:00:00 | 284.15 | 98833 | 6.7 | 260 | 7.8598 | 666 | 885.6 | 270.636 | 0 | 1
10/25 | 16:00:00 | 284.15 | 98833 | 6.2 | 240 | 7.8598 | 302.4 | 378 | 270.636 | 0 | 1
10/25 | 17:00:00 | 284.15 | 98833 | 6.7 | 240 | 7.8598 | 39.6 | 0 | 270.636 | 0 | 1
10/25 | 18:00:00 | 284.15 | 98833 | 8.2 | 250 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/25 | 19:00:00 | 284.15 | 98833 | 8.2 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/25 | 20:00:00 | 284.15 | 98833 | 9.3 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/25 | 21:00:00 | 284.15 | 98833 | 8.7 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/25 | 22:00:00 | 284.15 | 98833 | 8.7 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/25 | 23:00:00 | 284.15 | 98833 | 10.8 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/25 | 24:00:00 | 284.15 | 98833 | 8.2 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/26 | 01:00:00 | 284.15 | 98833 | 7.7 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/26 | 02:00:00 | 284.15 | 98833 | 7.7 | 270 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/26 | 03:00:00 | 284.15 | 98833 | 8.2 | 280 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/26 | 04:00:00 | 283.15 | 98824 | 8.7 | 280 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/26 | 05:00:00 | 283.15 | 98824 | 7.2 | 280 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/26 | 06:00:00 | 284.15 | 98833 | 6.2 | 280 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/26 | 07:00:00 | 284.15 | 98833 | 6.2 | 290 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
10/26 | 08:00:00 | 283.15 | 98824 | 5.1 | 300 | 7.3431 | 46.8 | 0 | 269.936 | 0 | 1
10/26 | 09:00:00 | 283.15 | 98824 | 3.6 | 280 | 7.3431 | 223.2 | 0 | 269.936 | 0 | 1
10/26 | 10:00:00 | 284.15 | 98833 | 4.6 | 310 | 7.8598 | 414 | 21.6 | 271.115 | 0 | 1
10/26 | 11:00:00 | 284.15 | 98833 | 3.1 | 320 | 7.8598 | 561.6 | 90 | 271.115 | 0 | 1
10/26 | 12:00:00 | 285.15 | 98841 | 1.5 | 109 | 7.3418 | 637.2 | 108 | 271.843 | 0 | 1
10/26 | 13:00:00 | 285.15 | 98841 | 3.6 | 280 | 7.3418 | 622.8 | 104.4 | 271.843 | 0 | 1
10/26 | 14:00:00 | 284.15 | 98833 | 3.6 | 270 | 7.8598 | 943.2 | 1209.6 | 270.636 | 0 | 1
10/26 | 15:00:00 | 285.15 | 98841 | 1.5 | 71 | 7.3418 | 648 | 874.8 | 271.363 | 0 | 1
10/26 | 16:00:00 | 285.15 | 98841 | 1.5 | 260 | 7.8591 | 158.4 | 0 | 272.069 | 0 | 1
10/26 | 17:00:00 | 284.15 | 98833 | 1 | 237 | 7.8598 | 18 | 0 | 271.115 | 0 | 1
10/26 | 18:00:00 | 284.15 | 98833 | 1 | 120 | 7.3425 | 0 | 0 | 270.411 | 0 | 1
10/26 | 19:00:00 | 283.15 | 98824 | 1 | 50 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
10/26 | 20:00:00 | 283.15 | 98824 | 1 | 172 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
10/26 | 21:00:00 | 283.15 | 98824 | 2.1 | 100 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
10/26 | 22:00:00 | 282.15 | 98815 | 3.1 | 110 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/26 | 23:00:00 | 283.15 | 98824 | 3.1 | 130 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
10/26 | 24:00:00 | 282.15 | 98815 | 3.1 | 130 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/27 | 01:00:00 | 283.15 | 98824 | 3.6 | 130 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
10/27 | 02:00:00 | 282.15 | 98815 | 4.1 | 130 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/27 | 03:00:00 | 282.15 | 98815 | 3.6 | 140 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
10/27 | 04:00:00 | 282.15 | 98815 | 4.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/27 | 05:00:00 | 282.15 | 98815 | 4.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/27 | 06:00:00 | 282.15 | 98815 | 2.6 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/27 | 07:00:00 | 282.15 | 98815 | 4.1 | 140 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/27 | 08:00:00 | 282.15 | 98815 | 3.6 | 130 | 7.3438 | 43.2 | 0 | 268.983 | 0 | 1
10/27 | 09:00:00 | 282.15 | 98815 | 2.1 | 150 | 7.3438 | 212.4 | 0 | 268.983 | 0 | 1
10/27 | 10:00:00 | 283.15 | 98824 | 2.6 | 150 | 7.8605 | 406.8 | 21.6 | 270.161 | 0 | 1
10/27 | 11:00:00 | 283.15 | 98824 | 2.1 | 150 | 7.8605 | 550.8 | 86.4 | 270.161 | 0 | 1
10/27 | 12:00:00 | 284.15 | 98833 | 2.6 | 140 | 8.4095 | 622.8 | 36 | 271.339 | 0 | 1
10/27 | 13:00:00 | 284.15 | 98833 | 1.5 | 130 | 8.4095 | 608.4 | 36 | 271.339 | 0 | 1
10/27 | 14:00:00 | 285.15 | 98841 | 3.1 | 140 | 8.9926 | 511.2 | 54 | 272.517 | 0 | 1
10/27 | 15:00:00 | 285.15 | 98841 | 3.1 | 150 | 8.9926 | 349.2 | 10.8 | 272.517 | 0 | 1
10/27 | 16:00:00 | 286.15 | 98850 | 2.1 | 140 | 9.6116 | 151.2 | 0 | 273.695 | 0 | 1
10/27 | 17:00:00 | 286.15 | 98850 | 3.1 | 160 | 9.6116 | 14.4 | 0 | 273.695 | 0 | 1
10/27 | 18:00:00 | 287.15 | 98858 | 3.6 | 170 | 9.6108 | 0 | 0 | 274.652 | 0 | 1
10/27 | 19:00:00 | 287.15 | 98858 | 2.1 | 160 | 9.6108 | 0 | 0 | 274.167 | 0 | 1
10/27 | 20:00:00 | 286.15 | 98850 | 3.6 | 160 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
10/27 | 21:00:00 | 286.15 | 98850 | 4.1 | 170 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
10/27 | 22:00:00 | 285.15 | 98841 | 4.1 | 170 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
10/27 | 23:00:00 | 285.15 | 98841 | 3.6 | 190 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
10/27 | 24:00:00 | 285.15 | 98841 | 2.6 | 220 | 7.3418 | 0 | 0 | 271.097 | 0 | 1
10/28 | 01:00:00 | 285.15 | 98841 | 3.1 | 220 | 7.3418 | 0 | 0 | 271.097 | 0 | 1
10/28 | 02:00:00 | 284.15 | 98833 | 4.1 | 220 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
10/28 | 03:00:00 | 285.15 | 98841 | 3.1 | 190 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
10/28 | 04:00:00 | 285.15 | 98841 | 2.6 | 260 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
10/28 | 05:00:00 | 284.15 | 98833 | 3.1 | 230 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/28 | 06:00:00 | 284.15 | 98833 | 1.5 | 277 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/28 | 07:00:00 | 285.15 | 98841 | 2.6 | 240 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
10/28 | 08:00:00 | 285.15 | 98841 | 3.6 | 250 | 8.4088 | 75.6 | 0 | 271.813 | 0 | 1
10/28 | 09:00:00 | 285.15 | 98841 | 4.6 | 250 | 8.4088 | 370.8 | 615.6 | 271.813 | 0 | 1
10/28 | 10:00:00 | 286.15 | 98850 | 5.1 | 250 | 8.9918 | 756 | 1548 | 272.723 | 0 | 1
10/28 | 11:00:00 | 287.15 | 98858 | 6.2 | 240 | 8.4073 | 1033.2 | 1882.8 | 273.451 | 0 | 1
10/28 | 12:00:00 | 288.15 | 98867 | 4.6 | 240 | 8.4065 | 1101.6 | 1641.6 | 274.672 | 0 | 1
10/28 | 13:00:00 | 288.15 | 98867 | 6.2 | 260 | 8.4065 | 1080 | 1620 | 274.672 | 0 | 1
10/28 | 14:00:00 | 288.15 | 98867 | 6.2 | 260 | 8.4065 | 903.6 | 1465.2 | 274.672 | 0 | 1
10/28 | 15:00:00 | 288.15 | 98867 | 5.7 | 250 | 8.4065 | 608.4 | 1134 | 274.672 | 0 | 1
10/28 | 16:00:00 | 287.15 | 98858 | 4.6 | 260 | 8.4073 | 259.2 | 421.2 | 273.719 | 0 | 1
10/28 | 17:00:00 | 287.15 | 98858 | 5.1 | 270 | 7.8578 | 21.6 | 0 | 273.493 | 0 | 1
10/28 | 18:00:00 | 286.15 | 98850 | 3.1 | 260 | 7.8584 | 0 | 0 | 272.274 | 0 | 1
10/28 | 19:00:00 | 284.15 | 98833 | 2.6 | 310 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
10/28 | 20:00:00 | 284.15 | 98833 | 1.5 | 310 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/28 | 21:00:00 | 285.15 | 98841 | 1.5 | 240 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
10/28 | 22:00:00 | 285.15 | 98841 | 1.5 | 280 | 8.4088 | 0 | 0 | 272.294 | 0 | 1
10/28 | 23:00:00 | 284.15 | 98833 | 2.1 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/28 | 24:00:00 | 284.15 | 98833 | 2.1 | 300 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/29 | 01:00:00 | 284.15 | 98833 | 2.1 | 270 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/29 | 02:00:00 | 284.15 | 98833 | 1 | 300 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/29 | 03:00:00 | 282.15 | 98815 | 1.5 | 280 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
10/29 | 04:00:00 | 282.15 | 98815 | 1.5 | 270 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
10/29 | 05:00:00 | 283.15 | 98824 | 0 | 220 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
10/29 | 06:00:00 | 282.15 | 98815 | 1.5 | 140 | 7.3438 | 0 | 0 | 268.508 | 0 | 1
10/29 | 07:00:00 | 282.15 | 98815 | 2.1 | 170 | 7.3438 | 0 | 0 | 268.245 | 0 | 1
10/29 | 08:00:00 | 282.15 | 98815 | 2.6 | 160 | 7.3438 | 72 | 0 | 268.245 | 0 | 1
10/29 | 09:00:00 | 283.15 | 98824 | 2.6 | 180 | 7.3431 | 378 | 615.6 | 269.196 | 0 | 1
10/29 | 10:00:00 | 285.15 | 98841 | 2.6 | 180 | 7.8591 | 428.4 | 75.6 | 272.069 | 0 | 1
10/29 | 11:00:00 | 285.15 | 98841 | 2.1 | 170 | 7.8591 | 590.4 | 320.4 | 272.069 | 0 | 1
10/29 | 12:00:00 | 286.15 | 98850 | 2.6 | 180 | 8.408 | 1162.8 | 1652.4 | 272.064 | 0 | 1
10/29 | 13:00:00 | 287.15 | 98858 | 3.1 | 160 | 8.4073 | 1137.6 | 1854 | 273.015 | 0 | 1
10/29 | 14:00:00 | 288.15 | 98867 | 4.1 | 180 | 8.4065 | 766.8 | 820.8 | 274.924 | 0 | 1
10/29 | 15:00:00 | 288.15 | 98867 | 3.6 | 190 | 8.4065 | 594 | 1112.4 | 274.672 | 0 | 1
10/29 | 16:00:00 | 287.15 | 98858 | 2.6 | 170 | 8.991 | 259.2 | 324 | 273.676 | 0 | 1
10/29 | 17:00:00 | 286.15 | 98850 | 3.1 | 160 | 8.408 | 18 | 0 | 272.499 | 0 | 1
10/29 | 18:00:00 | 286.15 | 98850 | 3.1 | 170 | 8.9918 | 0 | 0 | 272.723 | 0 | 1
10/29 | 19:00:00 | 286.15 | 98850 | 2.1 | 160 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
10/29 | 20:00:00 | 286.15 | 98850 | 3.6 | 170 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
10/29 | 21:00:00 | 286.15 | 98850 | 3.6 | 150 | 8.9918 | 0 | 0 | 273.473 | 0 | 1
10/29 | 22:00:00 | 285.15 | 98841 | 3.1 | 160 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/29 | 23:00:00 | 285.15 | 98841 | 4.1 | 160 | 8.4088 | 0 | 0 | 271.547 | 0 | 1
10/29 | 24:00:00 | 284.15 | 98833 | 4.6 | 150 | 8.4095 | 0 | 0 | 270.595 | 0 | 1
10/30 | 01:00:00 | 284.15 | 98833 | 3.1 | 160 | 8.4095 | 0 | 0 | 270.595 | 0 | 1
10/30 | 02:00:00 | 284.15 | 98833 | 3.6 | 150 | 8.4095 | 0 | 0 | 270.595 | 0 | 1
10/30 | 03:00:00 | 283.15 | 98824 | 4.1 | 150 | 7.8605 | 0 | 0 | 269.42 | 0 | 1
10/30 | 04:00:00 | 283.15 | 98824 | 4.6 | 160 | 7.8605 | 0 | 0 | 269.42 | 0 | 1
10/30 | 05:00:00 | 283.15 | 98824 | 5.1 | 150 | 7.8605 | 0 | 0 | 269.42 | 0 | 1
10/30 | 06:00:00 | 282.15 | 98815 | 2.6 | 140 | 7.3438 | 0 | 0 | 268.245 | 0 | 1
10/30 | 07:00:00 | 282.15 | 98815 | 4.1 | 160 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
10/30 | 08:00:00 | 282.15 | 98815 | 6.2 | 160 | 7.3438 | 36 | 0 | 268.983 | 0 | 1
10/30 | 09:00:00 | 282.15 | 98815 | 5.7 | 160 | 7.3438 | 190.8 | 0 | 268.983 | 0 | 1
10/30 | 10:00:00 | 282.15 | 98815 | 5.7 | 170 | 7.3438 | 378 | 14.4 | 268.983 | 0 | 1
10/30 | 11:00:00 | 283.15 | 98824 | 6.2 | 160 | 7.8605 | 522 | 79.2 | 270.161 | 0 | 1
10/30 | 12:00:00 | 284.15 | 98833 | 6.2 | 160 | 8.4095 | 590.4 | 93.6 | 271.339 | 0 | 1
10/30 | 13:00:00 | 285.15 | 98841 | 5.1 | 150 | 8.4088 | 1101.6 | 1555.2 | 271.547 | 0 | 1
10/30 | 14:00:00 | 286.15 | 98850 | 6.2 | 150 | 7.8584 | 921.6 | 1688.4 | 272.274 | 0 | 1
10/30 | 15:00:00 | 286.15 | 98850 | 6.7 | 170 | 7.3412 | 612 | 1263.6 | 272.048 | 0 | 1
10/30 | 16:00:00 | 285.15 | 98841 | 6.7 | 160 | 7.3418 | 248.4 | 360 | 271.097 | 0 | 1
10/30 | 17:00:00 | 285.15 | 98841 | 7.2 | 160 | 7.8591 | 10.8 | 0 | 271.323 | 0 | 1
10/30 | 18:00:00 | 285.15 | 98841 | 6.7 | 170 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
10/30 | 19:00:00 | 285.15 | 98841 | 6.7 | 170 | 7.8591 | 0 | 0 | 271.323 | 0 | 1
10/30 | 20:00:00 | 284.15 | 98833 | 6.2 | 160 | 7.8598 | 0 | 0 | 269.94 | 0 | 1
10/30 | 21:00:00 | 284.15 | 98833 | 5.7 | 150 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
10/30 | 22:00:00 | 284.15 | 98833 | 5.7 | 160 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
10/30 | 23:00:00 | 284.15 | 98833 | 5.7 | 150 | 7.8598 | 0 | 0 | 270.371 | 0 | 1
10/30 | 24:00:00 | 284.15 | 98833 | 5.1 | 150 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
10/31 | 01:00:00 | 284.15 | 98833 | 4.1 | 170 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
10/31 | 02:00:00 | 283.15 | 98824 | 4.6 | 160 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/31 | 03:00:00 | 283.15 | 98824 | 5.1 | 170 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/31 | 04:00:00 | 284.15 | 98833 | 2.6 | 160 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/31 | 05:00:00 | 283.15 | 98824 | 1 | 189 | 7.8605 | 0 | 0 | 270.161 | 0 | 1
10/31 | 06:00:00 | 284.15 | 98833 | 1.5 | 130 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
10/31 | 07:00:00 | 285.15 | 98841 | 1.5 | 336 | 8.9926 | 0 | 0 | 272.517 | 0 | 1
10/31 | 08:00:00 | 285.15 | 98841 | 2.6 | 240 | 8.9926 | 32.4 | 0 | 272.517 | 0 | 1
10/31 | 09:00:00 | 285.15 | 98841 | 1.5 | 260 | 8.9926 | 327.6 | 374.4 | 272.036 | 0 | 1
10/31 | 10:00:00 | 285.15 | 98841 | 3.1 | 250 | 8.4088 | 662.4 | 1234.8 | 271.813 | 0 | 1
10/31 | 11:00:00 | 286.15 | 98850 | 4.6 | 260 | 8.408 | 918 | 1526.4 | 272.766 | 0 | 1
10/31 | 12:00:00 | 287.15 | 98858 | 4.1 | 260 | 8.4073 | 1047.6 | 1609.2 | 273.719 | 0 | 1
10/31 | 13:00:00 | 287.15 | 98858 | 4.1 | 250 | 8.4073 | 1022.4 | 1584 | 273.719 | 0 | 1
10/31 | 14:00:00 | 287.15 | 98858 | 4.1 | 260 | 8.4073 | 900 | 1710 | 273.451 | 0 | 1
10/31 | 15:00:00 | 287.15 | 98858 | 4.1 | 250 | 8.4073 | 594 | 1303.2 | 273.451 | 0 | 1
10/31 | 16:00:00 | 287.15 | 98858 | 2.6 | 250 | 8.4073 | 234 | 450 | 273.451 | 0 | 1
10/31 | 17:00:00 | 286.15 | 98850 | 2.6 | 220 | 7.8584 | 3.6 | 0 | 272.541 | 0 | 1
10/31 | 18:00:00 | 285.15 | 98841 | 2.1 | 180 | 7.8591 | 0 | 0 | 271.588 | 0 | 1
10/31 | 19:00:00 | 283.95 | 98831 | 2.2 | 220 | 7.4436 | 0 | 0 | 270.266 | 0 | 1
10/31 | 20:00:00 | 283.65 | 98829 | 2.1 | 225 | 7.3427 | 0 | 0 | 269.671 | 0 | 1
10/31 | 21:00:00 | 283.65 | 98829 | 1.9 | 227 | 7.3427 | 0 | 0 | 270.413 | 0 | 1
10/31 | 22:00:00 | 281.35 | 98808 | 3 | 245 | 6.3998 | 0 | 0 | 267.77 | 0 | 1
10/31 | 23:00:00 | 279.35 | 98790 | 4 | 275 | 5.6453 | 0 | 0 | 265.567 | 0 | 1
10/31 | 24:00:00 | 277.35 | 98772 | 5.2 | 307 | 4.901 | 0 | 0 | 263.212 | 0 | 1
11/1 | 01:00:00 | 275.15 | 98752 | 5.9 | 342 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
11/1 | 02:00:00 | 275.15 | 98752 | 5.9 | 347 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/1 | 03:00:00 | 275.15 | 98752 | 6.1 | 347 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/1 | 04:00:00 | 275.15 | 98752 | 5.9 | 352 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/1 | 05:00:00 | 275.35 | 98755 | 6.1 | 350 | 4.1845 | 0 | 0 | 259.99 | 0 | 1
11/1 | 06:00:00 | 275.65 | 98757 | 5.8 | 350 | 4.1844 | 0 | 0 | 260.274 | 0 | 1
11/1 | 07:00:00 | 275.15 | 98752 | 5.7 | 360 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
11/1 | 08:00:00 | 276.15 | 98762 | 5.7 | 350 | 4.1841 | 57.6 | 0 | 261.001 | 0 | 1
11/1 | 09:00:00 | 276.15 | 98762 | 5.1 | 350 | 4.1841 | 334.8 | 450 | 261.001 | 0 | 1
11/1 | 10:00:00 | 277.15 | 98771 | 5.7 | 330 | 4.4973 | 374.4 | 39.6 | 262.64 | 0 | 1
11/1 | 11:00:00 | 278.15 | 98780 | 5.7 | 330 | 4.4968 | 990 | 1515.6 | 262.865 | 0 | 1
11/1 | 12:00:00 | 279.15 | 98789 | 6.2 | 330 | 4.4964 | 1062 | 1468.8 | 264.069 | 0 | 1
11/1 | 13:00:00 | 279.15 | 98789 | 6.2 | 360 | 4.4964 | 1036.8 | 1447.2 | 264.069 | 0 | 1
11/1 | 14:00:00 | 279.15 | 98789 | 5.1 | 350 | 4.4964 | 914.4 | 1742.4 | 263.81 | 0 | 1
11/1 | 15:00:00 | 279.15 | 98789 | 6.7 | 350 | 4.183 | 604.8 | 1054.8 | 263.578 | 0 | 1
11/1 | 16:00:00 | 278.15 | 98780 | 5.7 | 340 | 4.1834 | 237.6 | 266.4 | 262.634 | 0 | 1
11/1 | 17:00:00 | 277.15 | 98771 | 4.1 | 350 | 4.1838 | 3.6 | 0 | 261.69 | 0 | 1
11/1 | 18:00:00 | 277.15 | 98771 | 4.6 | 350 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
11/1 | 19:00:00 | 276.15 | 98762 | 4.6 | 10 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
11/1 | 20:00:00 | 275.15 | 98752 | 3.6 | 350 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/1 | 21:00:00 | 276.15 | 98762 | 3.6 | 20 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
11/1 | 22:00:00 | 275.15 | 98752 | 4.1 | 10 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/1 | 23:00:00 | 276.15 | 98762 | 4.1 | 20 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
11/1 | 24:00:00 | 275.15 | 98752 | 3.1 | 30 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/2 | 01:00:00 | 276.15 | 98762 | 3.6 | 20 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
11/2 | 02:00:00 | 275.15 | 98752 | 4.1 | 20 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/2 | 03:00:00 | 275.15 | 98752 | 4.1 | 20 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/2 | 04:00:00 | 275.15 | 98752 | 4.1 | 10 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
11/2 | 05:00:00 | 276.15 | 98762 | 4.6 | 10 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
11/2 | 06:00:00 | 276.15 | 98762 | 4.6 | 20 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
11/2 | 07:00:00 | 276.15 | 98762 | 4.1 | 10 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
11/2 | 08:00:00 | 276.15 | 98762 | 4.6 | 10 | 4.4977 | 54 | 0 | 261.231 | 0 | 1
11/2 | 09:00:00 | 277.15 | 98771 | 4.1 | 20 | 4.8316 | 338.4 | 730.8 | 262.149 | 0 | 1
11/2 | 10:00:00 | 278.15 | 98780 | 5.1 | 10 | 5.1875 | 694.8 | 1440 | 263.323 | 0 | 1
11/2 | 11:00:00 | 279.15 | 98789 | 4.6 | 20 | 5.187 | 910.8 | 1288.8 | 264.528 | 0 | 1
11/2 | 12:00:00 | 279.15 | 98789 | 4.1 | 20 | 5.187 | 1040.4 | 1659.6 | 264.528 | 0 | 1
11/2 | 13:00:00 | 281.15 | 98806 | 5.1 | 50 | 4.8299 | 1076.4 | 1969.2 | 265.932 | 0 | 1
11/2 | 14:00:00 | 282.15 | 98815 | 6.2 | 50 | 4.8294 | 892.8 | 1717.2 | 266.878 | 0 | 1
11/2 | 15:00:00 | 281.15 | 98806 | 6.2 | 50 | 4.8299 | 583.2 | 1216.8 | 265.932 | 0 | 1
11/2 | 16:00:00 | 280.15 | 98798 | 5.7 | 40 | 4.8303 | 223.2 | 327.6 | 264.986 | 0 | 1
11/2 | 17:00:00 | 279.15 | 98789 | 4.6 | 30 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
11/2 | 18:00:00 | 279.15 | 98789 | 5.7 | 30 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
11/2 | 19:00:00 | 278.15 | 98780 | 5.1 | 20 | 5.1875 | 0 | 0 | 263.323 | 0 | 1
11/2 | 20:00:00 | 278.15 | 98780 | 5.7 | 20 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
11/2 | 21:00:00 | 278.15 | 98780 | 7.2 | 10 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
11/2 | 22:00:00 | 278.15 | 98780 | 6.7 | 10 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
11/2 | 23:00:00 | 278.15 | 98780 | 8.2 | 20 | 4.4968 | 0 | 0 | 263.588 | 0 | 1
11/2 | 24:00:00 | 278.15 | 98780 | 7.2 | 20 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
11/3 | 01:00:00 | 278.15 | 98780 | 8.2 | 20 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
11/3 | 02:00:00 | 279.15 | 98789 | 8.2 | 20 | 4.4964 | 0 | 0 | 264.536 | 0 | 1
11/3 | 03:00:00 | 279.15 | 98789 | 8.2 | 20 | 4.8307 | 0 | 0 | 264.767 | 0 | 1
11/3 | 04:00:00 | 278.15 | 98780 | 7.7 | 10 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
11/3 | 05:00:00 | 278.15 | 98780 | 8.7 | 10 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
11/3 | 06:00:00 | 279.15 | 98789 | 8.7 | 10 | 4.8307 | 0 | 0 | 264.767 | 0 | 1
11/3 | 07:00:00 | 278.15 | 98780 | 8.7 | 10 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
11/3 | 08:00:00 | 279.15 | 98789 | 8.2 | 10 | 4.8307 | 46.8 | 0 | 264.299 | 0 | 1
11/3 | 09:00:00 | 279.15 | 98789 | 8.2 | 20 | 4.8307 | 324 | 669.6 | 264.041 | 0 | 1
11/3 | 10:00:00 | 279.15 | 98789 | 8.7 | 20 | 5.187 | 637.2 | 1173.6 | 264.528 | 0 | 1
11/3 | 11:00:00 | 279.15 | 98789 | 7.7 | 20 | 5.187 | 892.8 | 1486.8 | 264.528 | 0 | 1
11/3 | 12:00:00 | 280.15 | 98798 | 8.7 | 10 | 5.1865 | 1018.8 | 1335.6 | 265.476 | 0 | 1
11/3 | 13:00:00 | 280.15 | 98798 | 8.2 | 10 | 5.5661 | 550.8 | 194.4 | 266.174 | 0 | 1
11/3 | 14:00:00 | 280.15 | 98798 | 8.7 | 20 | 6.4005 | 453.6 | 28.8 | 266.628 | 0 | 1
11/3 | 15:00:00 | 280.15 | 98798 | 7.2 | 20 | 5.9703 | 295.2 | 0 | 266.402 | 0 | 1
11/3 | 16:00:00 | 280.15 | 98798 | 6.7 | 10 | 5.9703 | 111.6 | 0 | 266.402 | 0 | 1
11/3 | 17:00:00 | 280.15 | 98798 | 7.2 | 10 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
11/3 | 18:00:00 | 279.15 | 98789 | 6.7 | 360 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
11/3 | 19:00:00 | 279.15 | 98789 | 7.2 | 360 | 5.9708 | 0 | 0 | 265.451 | 0 | 1
11/3 | 20:00:00 | 280.15 | 98798 | 7.2 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/3 | 21:00:00 | 280.15 | 98798 | 4.6 | 20 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/3 | 22:00:00 | 280.15 | 98798 | 2.6 | 40 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/3 | 23:00:00 | 281.15 | 98806 | 3.1 | 40 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/3 | 24:00:00 | 281.15 | 98806 | 3.6 | 40 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/4 | 01:00:00 | 281.15 | 98806 | 3.6 | 40 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/4 | 02:00:00 | 280.15 | 98798 | 3.1 | 40 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/4 | 03:00:00 | 280.15 | 98798 | 3.1 | 40 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/4 | 04:00:00 | 280.15 | 98798 | 2.1 | 40 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/4 | 05:00:00 | 280.15 | 98798 | 3.1 | 20 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/4 | 06:00:00 | 279.15 | 98789 | 2.1 | 30 | 5.9708 | 0 | 0 | 264.723 | 0 | 1
11/4 | 07:00:00 | 279.15 | 98789 | 3.1 | 30 | 5.9708 | 0 | 0 | 264.723 | 0 | 1
11/4 | 08:00:00 | 279.15 | 98789 | 3.1 | 20 | 5.5666 | 18 | 0 | 265.332 | 0 | 1
11/4 | 09:00:00 | 279.15 | 98789 | 3.1 | 20 | 5.9708 | 97.2 | 0 | 265.559 | 0 | 1
11/4 | 10:00:00 | 279.15 | 98789 | 3.1 | 30 | 5.9708 | 619.2 | 885.6 | 264.982 | 0 | 1
11/4 | 11:00:00 | 281.15 | 98806 | 3.1 | 30 | 6.4 | 871.2 | 1144.8 | 267.107 | 0 | 1
11/4 | 12:00:00 | 281.15 | 98806 | 3.1 | 40 | 6.4 | 554.4 | 93.6 | 267.58 | 0 | 1
11/4 | 13:00:00 | 282.15 | 98815 | 3.6 | 40 | 6.3994 | 540 | 90 | 268.532 | 0 | 1
11/4 | 14:00:00 | 282.15 | 98815 | 3.6 | 40 | 6.3994 | 802.8 | 1080 | 268.057 | 0 | 1
11/4 | 15:00:00 | 282.15 | 98815 | 3.6 | 30 | 6.3994 | 514.8 | 752.4 | 268.057 | 0 | 1
11/4 | 16:00:00 | 282.15 | 98815 | 4.6 | 30 | 5.9692 | 104.4 | 0 | 268.304 | 0 | 1
11/4 | 17:00:00 | 281.15 | 98806 | 4.6 | 20 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
11/4 | 18:00:00 | 281.15 | 98806 | 3.6 | 40 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
11/4 | 19:00:00 | 281.15 | 98806 | 4.1 | 50 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
11/4 | 20:00:00 | 281.15 | 98806 | 3.1 | 50 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
11/4 | 21:00:00 | 280.15 | 98798 | 4.1 | 50 | 5.5661 | 0 | 0 | 266.282 | 0 | 1
11/4 | 22:00:00 | 280.15 | 98798 | 3.1 | 40 | 5.5661 | 0 | 0 | 266.282 | 0 | 1
11/4 | 23:00:00 | 280.15 | 98798 | 4.1 | 30 | 5.5661 | 0 | 0 | 266.282 | 0 | 1
11/4 | 24:00:00 | 280.15 | 98798 | 3.6 | 40 | 5.5661 | 0 | 0 | 266.282 | 0 | 1
11/5 | 01:00:00 | 280.15 | 98798 | 4.6 | 30 | 5.5661 | 0 | 0 | 266.282 | 0 | 1
11/5 | 02:00:00 | 280.15 | 98798 | 4.1 | 30 | 5.5661 | 0 | 0 | 266.282 | 0 | 1
11/5 | 03:00:00 | 280.15 | 98798 | 4.6 | 20 | 5.5661 | 0 | 0 | 266.282 | 0 | 1
11/5 | 04:00:00 | 280.15 | 98798 | 4.1 | 30 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
11/5 | 05:00:00 | 280.15 | 98798 | 4.6 | 30 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
11/5 | 06:00:00 | 280.15 | 98798 | 5.1 | 30 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
11/5 | 07:00:00 | 280.15 | 98798 | 5.1 | 30 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
11/5 | 08:00:00 | 280.15 | 98798 | 5.1 | 30 | 6.4005 | 21.6 | 0 | 266.628 | 0 | 1
11/5 | 09:00:00 | 280.15 | 98798 | 5.1 | 30 | 6.4005 | 154.8 | 0 | 266.628 | 0 | 1
11/5 | 10:00:00 | 280.15 | 98798 | 5.1 | 30 | 6.4005 | 205.2 | 0 | 266.736 | 0 | 1
11/5 | 11:00:00 | 280.15 | 98798 | 5.1 | 20 | 6.4005 | 288 | 0 | 266.736 | 0 | 1
11/5 | 12:00:00 | 280.15 | 98798 | 4.1 | 30 | 6.4005 | 543.6 | 90 | 266.628 | 0 | 1
11/5 | 13:00:00 | 281.15 | 98806 | 3.6 | 30 | 6.4 | 529.2 | 90 | 267.58 | 0 | 1
11/5 | 14:00:00 | 281.15 | 98806 | 3.6 | 10 | 6.8577 | 435.6 | 28.8 | 267.805 | 0 | 1
11/5 | 15:00:00 | 281.15 | 98806 | 4.6 | 20 | 6.8577 | 277.2 | 0 | 267.805 | 0 | 1
11/5 | 16:00:00 | 281.15 | 98806 | 4.1 | 20 | 6.8577 | 97.2 | 0 | 267.805 | 0 | 1
11/5 | 17:00:00 | 281.15 | 98806 | 3.6 | 20 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/5 | 18:00:00 | 281.15 | 98806 | 4.6 | 20 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
11/5 | 19:00:00 | 281.15 | 98806 | 3.6 | 20 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
11/5 | 20:00:00 | 281.15 | 98806 | 3.6 | 30 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/5 | 21:00:00 | 281.15 | 98806 | 3.6 | 30 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/5 | 22:00:00 | 281.15 | 98806 | 3.6 | 30 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/5 | 23:00:00 | 281.15 | 98806 | 3.6 | 20 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/5 | 24:00:00 | 281.15 | 98806 | 4 | 223 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
11/6 | 01:00:00 | 281.15 | 98806 | 4.5 | 228 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
11/6 | 02:00:00 | 281.15 | 98806 | 4.9 | 350 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
11/6 | 03:00:00 | 281.15 | 98806 | 5.3 | 340 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
11/6 | 04:00:00 | 281.15 | 98806 | 5.8 | 140 | 6.8577 | 0 | 0 | 267.914 | 0 | 1
11/6 | 05:00:00 | 281.15 | 98806 | 6.2 | 10 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/6 | 06:00:00 | 280.15 | 98798 | 4.6 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/6 | 07:00:00 | 280.15 | 98798 | 4.6 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/6 | 08:00:00 | 280.15 | 98798 | 3.6 | 360 | 6.4005 | 18 | 0 | 266.628 | 0 | 1
11/6 | 09:00:00 | 280.15 | 98798 | 4.1 | 20 | 6.4005 | 147.6 | 0 | 266.628 | 0 | 1
11/6 | 10:00:00 | 280.15 | 98798 | 5.1 | 20 | 6.4005 | 324 | 7.2 | 266.628 | 0 | 1
11/6 | 11:00:00 | 280.15 | 98798 | 4.6 | 20 | 5.9703 | 464.4 | 50.4 | 266.402 | 0 | 1
11/6 | 12:00:00 | 280.15 | 98798 | 4.6 | 10 | 6.4005 | 532.8 | 90 | 266.628 | 0 | 1
11/6 | 13:00:00 | 280.15 | 98798 | 3.6 | 10 | 6.4005 | 518.4 | 86.4 | 266.628 | 0 | 1
11/6 | 14:00:00 | 280.15 | 98798 | 4.6 | 10 | 6.4005 | 424.8 | 25.2 | 266.628 | 0 | 1
11/6 | 15:00:00 | 280.15 | 98798 | 4.1 | 10 | 5.9703 | 270 | 0 | 266.402 | 0 | 1
11/6 | 16:00:00 | 280.15 | 98798 | 3.6 | 10 | 5.9703 | 90 | 0 | 266.402 | 0 | 1
11/6 | 17:00:00 | 280.15 | 98798 | 4.1 | 10 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
11/6 | 18:00:00 | 280.15 | 98798 | 3.1 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/6 | 19:00:00 | 280.15 | 98798 | 3.6 | 350 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/6 | 20:00:00 | 280.15 | 98798 | 3.1 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/6 | 21:00:00 | 280.15 | 98798 | 3.6 | 10 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/6 | 22:00:00 | 280.15 | 98798 | 3.1 | 20 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
11/6 | 23:00:00 | 280.15 | 98798 | 2.6 | 10 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
11/6 | 24:00:00 | 280.15 | 98798 | 2.6 | 10 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
11/7 | 01:00:00 | 280.15 | 98798 | 2.6 | 20 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
11/7 | 02:00:00 | 280.15 | 98798 | 2.6 | 20 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
11/7 | 03:00:00 | 280.15 | 98798 | 2.1 | 10 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
11/7 | 04:00:00 | 280.15 | 98798 | 3.1 | 350 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
11/7 | 05:00:00 | 280.15 | 98798 | 2.6 | 360 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/7 | 06:00:00 | 280.15 | 98798 | 2.6 | 350 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/7 | 07:00:00 | 280.15 | 98798 | 2.6 | 350 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/7 | 08:00:00 | 281.15 | 98806 | 3.1 | 360 | 6.8577 | 14.4 | 0 | 267.805 | 0 | 1
11/7 | 09:00:00 | 281.15 | 98806 | 2.1 | 360 | 6.8577 | 140.4 | 0 | 267.805 | 0 | 1
11/7 | 10:00:00 | 281.15 | 98806 | 3.1 | 350 | 6.4 | 316.8 | 7.2 | 267.58 | 0 | 1
11/7 | 11:00:00 | 281.15 | 98806 | 2.6 | 360 | 6.8577 | 453.6 | 46.8 | 267.805 | 0 | 1
11/7 | 12:00:00 | 281.15 | 98806 | 2.1 | 350 | 6.8577 | 522 | 86.4 | 267.805 | 0 | 1
11/7 | 13:00:00 | 282.15 | 98815 | 2.6 | 20 | 6.8571 | 507.6 | 57.6 | 268.758 | 0 | 1
11/7 | 14:00:00 | 282.15 | 98815 | 1 | 272 | 6.8571 | 417.6 | 25.2 | 268.758 | 0 | 1
11/7 | 15:00:00 | 282.15 | 98815 | 0.5 | 146 | 6.8571 | 259.2 | 0 | 268.758 | 0 | 1
11/7 | 16:00:00 | 281.15 | 98806 | 0.5 | 254 | 6.8577 | 86.4 | 0 | 267.805 | 0 | 1
11/7 | 17:00:00 | 281.15 | 98806 | 1.5 | 160 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/7 | 18:00:00 | 281.15 | 98806 | 2.6 | 160 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/7 | 19:00:00 | 281.15 | 98806 | 2.1 | 150 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/7 | 20:00:00 | 281.15 | 98806 | 2.1 | 150 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/7 | 21:00:00 | 281.15 | 98806 | 2.6 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/7 | 22:00:00 | 281.15 | 98806 | 2.6 | 160 | 6.4 | 0 | 0 | 267.107 | 0 | 1
11/7 | 23:00:00 | 281.15 | 98806 | 3.1 | 140 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/7 | 24:00:00 | 281.15 | 98806 | 4.1 | 140 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/8 | 01:00:00 | 280.15 | 98798 | 3.6 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/8 | 02:00:00 | 280.15 | 98798 | 4.6 | 130 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/8 | 03:00:00 | 280.15 | 98798 | 4.6 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/8 | 04:00:00 | 280.15 | 98798 | 4.1 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/8 | 05:00:00 | 280.15 | 98798 | 4.6 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/8 | 06:00:00 | 280.15 | 98798 | 3.6 | 140 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
11/8 | 07:00:00 | 280.15 | 98798 | 4.6 | 140 | 6.4005 | 0 | 0 | 266.736 | 0 | 1
11/8 | 08:00:00 | 280.15 | 98798 | 5.1 | 130 | 6.4005 | 7.2 | 0 | 266.736 | 0 | 1
11/8 | 09:00:00 | 280.15 | 98798 | 4.6 | 150 | 6.4005 | 82.8 | 0 | 266.736 | 0 | 1
11/8 | 10:00:00 | 281.15 | 98806 | 3.6 | 170 | 6.8577 | 306 | 10.8 | 267.805 | 0 | 1
11/8 | 11:00:00 | 282.15 | 98815 | 4.1 | 200 | 6.8571 | 849.6 | 1310.4 | 268.021 | 0 | 1
11/8 | 12:00:00 | 283.15 | 98824 | 5.1 | 210 | 5.5646 | 928.8 | 1328.4 | 268.55 | 0 | 1
11/8 | 13:00:00 | 282.15 | 98815 | 5.1 | 210 | 5.5651 | 903.6 | 1303.2 | 267.601 | 0 | 1
11/8 | 14:00:00 | 283.15 | 98824 | 4.1 | 210 | 5.9687 | 734.4 | 1310.4 | 268.779 | 0 | 1
11/8 | 15:00:00 | 284.15 | 98833 | 5.1 | 190 | 5.5641 | 457.2 | 896.4 | 269.498 | 0 | 1
11/8 | 16:00:00 | 283.15 | 98824 | 5.7 | 190 | 5.1851 | 154.8 | 176.4 | 268.056 | 0 | 1
11/8 | 17:00:00 | 282.15 | 98815 | 5.7 | 180 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
11/8 | 18:00:00 | 280.15 | 98798 | 4.1 | 180 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
11/8 | 19:00:00 | 280.15 | 98798 | 4.6 | 190 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
11/8 | 20:00:00 | 280.15 | 98798 | 5.1 | 190 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
11/8 | 21:00:00 | 279.15 | 98789 | 4.6 | 210 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
11/8 | 22:00:00 | 279.15 | 98789 | 4.6 | 180 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
11/8 | 23:00:00 | 279.15 | 98789 | 3.1 | 170 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
11/8 | 24:00:00 | 279.15 | 98789 | 3.4 | 275 | 4.9352 | 0 | 0 | 264.725 | 0 | 1
11/9 | 01:00:00 | 279.15 | 98789 | 3.8 | 156 | 5.0777 | 0 | 0 | 264.816 | 0 | 1
11/9 | 02:00:00 | 279.15 | 98789 | 4.1 | 262 | 5.187 | 0 | 0 | 264.996 | 0 | 1
11/9 | 03:00:00 | 279.15 | 98789 | 4.4 | 240 | 5.2984 | 0 | 0 | 265.065 | 0 | 1
11/9 | 04:00:00 | 279.15 | 98789 | 4.8 | 351 | 5.4502 | 0 | 0 | 265.156 | 0 | 1
11/9 | 05:00:00 | 279.15 | 98789 | 5.1 | 150 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
11/9 | 06:00:00 | 279.15 | 98789 | 6.7 | 150 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
11/9 | 07:00:00 | 279.15 | 98789 | 5.1 | 140 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
11/9 | 08:00:00 | 279.15 | 98789 | 6.2 | 140 | 5.9708 | 7.2 | 0 | 265.451 | 0 | 1
11/9 | 09:00:00 | 280.15 | 98798 | 5.7 | 150 | 6.4005 | 126 | 0 | 266.628 | 0 | 1
11/9 | 10:00:00 | 281.15 | 98806 | 5.1 | 160 | 6.8577 | 540 | 799.2 | 267.332 | 0 | 1
11/9 | 11:00:00 | 283.15 | 98824 | 6.2 | 170 | 6.8564 | 784.8 | 1368 | 269.234 | 0 | 1
11/9 | 12:00:00 | 284.15 | 98833 | 8.7 | 190 | 7.3425 | 903.6 | 1288.8 | 270.411 | 0 | 1
11/9 | 13:00:00 | 284.15 | 98833 | 7.7 | 200 | 6.3982 | 885.6 | 1278 | 269.957 | 0 | 1
11/9 | 14:00:00 | 284.15 | 98833 | 6.2 | 200 | 6.3982 | 720 | 1288.8 | 269.957 | 0 | 1
11/9 | 15:00:00 | 285.15 | 98841 | 5.7 | 200 | 6.3977 | 442.8 | 835.2 | 270.907 | 0 | 1
11/9 | 16:00:00 | 284.15 | 98833 | 6.2 | 190 | 5.9681 | 133.2 | 97.2 | 269.728 | 0 | 1
11/9 | 17:00:00 | 283.15 | 98824 | 5.1 | 190 | 5.9687 | 0 | 0 | 268.516 | 0 | 1
11/9 | 18:00:00 | 282.15 | 98815 | 5.1 | 170 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
11/9 | 19:00:00 | 282.15 | 98815 | 7.2 | 150 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
11/9 | 20:00:00 | 283.15 | 98824 | 5.1 | 160 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
11/9 | 21:00:00 | 282.15 | 98815 | 7.7 | 160 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
11/9 | 22:00:00 | 282.15 | 98815 | 7.2 | 150 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
11/9 | 23:00:00 | 280.15 | 98798 | 5.1 | 240 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
11/9 | 24:00:00 | 280.15 | 98798 | 6.7 | 250 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
11/10 | 01:00:00 | 279.75 | 98794 | 7 | 260 | 5.6451 | 0 | 0 | 265.84 | 0 | 1
11/10 | 02:00:00 | 279.35 | 98790 | 7.3 | 4 | 5.3359 | 0 | 0 | 265.278 | 0 | 1
11/10 | 03:00:00 | 278.95 | 98787 | 7.6 | 148 | 5.0418 | 0 | 0 | 264.604 | 0 | 1
11/10 | 04:00:00 | 278.55 | 98783 | 7.9 | 84 | 4.7624 | 0 | 0 | 264.041 | 0 | 1
11/10 | 05:00:00 | 278.15 | 98780 | 8.2 | 240 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
11/10 | 06:00:00 | 277.15 | 98771 | 7.7 | 230 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
11/10 | 07:00:00 | 277.15 | 98771 | 5.7 | 230 | 3.8896 | 0 | 0 | 261.458 | 0 | 1
11/10 | 08:00:00 | 277.15 | 98771 | 7.7 | 220 | 4.1838 | 7.2 | 0 | 261.69 | 0 | 1
11/10 | 09:00:00 | 277.15 | 98771 | 7.7 | 210 | 4.1838 | 234 | 280.8 | 261.69 | 0 | 1
11/10 | 10:00:00 | 278.15 | 98780 | 8.2 | 210 | 4.1834 | 561.6 | 1105.2 | 262.634 | 0 | 1
11/10 | 11:00:00 | 278.15 | 98780 | 7.2 | 200 | 4.4968 | 774 | 1195.2 | 263.123 | 0 | 1
11/10 | 12:00:00 | 279.15 | 98789 | 7.7 | 210 | 4.4964 | 900 | 1216.8 | 264.069 | 0 | 1
11/10 | 13:00:00 | 279.15 | 98789 | 7.7 | 210 | 4.4964 | 486 | 86.4 | 264.536 | 0 | 1
11/10 | 14:00:00 | 278.15 | 98780 | 3.6 | 200 | 5.1875 | 392.4 | 36 | 264.047 | 0 | 1
11/10 | 15:00:00 | 278.15 | 98780 | 3.1 | 300 | 5.5671 | 432 | 662.4 | 263.807 | 0 | 1
11/10 | 16:00:00 | 280.15 | 98798 | 7.2 | 210 | 5.5661 | 68.4 | 0 | 266.174 | 0 | 1
11/10 | 17:00:00 | 280.15 | 98798 | 8.2 | 210 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
11/10 | 18:00:00 | 279.15 | 98789 | 7.2 | 200 | 5.187 | 0 | 0 | 264.528 | 0 | 1
11/10 | 19:00:00 | 278.15 | 98780 | 4.6 | 190 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
11/10 | 20:00:00 | 277.15 | 98771 | 3.6 | 170 | 5.1879 | 0 | 0 | 263.098 | 0 | 1
11/10 | 21:00:00 | 278.15 | 98780 | 3.6 | 170 | 5.5671 | 0 | 0 | 264.274 | 0 | 1
11/10 | 22:00:00 | 279.15 | 98789 | 8.7 | 240 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
11/10 | 23:00:00 | 279.15 | 98789 | 8.2 | 230 | 5.187 | 0 | 0 | 264.996 | 0 | 1
11/10 | 24:00:00 | 278.85 | 98786 | 8.1 | 44 | 4.9354 | 0 | 0 | 264.44 | 0 | 1
11/11 | 01:00:00 | 278.45 | 98783 | 8 | 200 | 4.7284 | 0 | 0 | 263.923 | 0 | 1
11/11 | 02:00:00 | 278.15 | 98780 | 7.9 | 4 | 4.4968 | 0 | 0 | 263.478 | 0 | 1
11/11 | 03:00:00 | 277.85 | 98777 | 7.9 | 175 | 4.2754 | 0 | 0 | 262.917 | 0 | 1
11/11 | 04:00:00 | 277.45 | 98774 | 7.8 | 243 | 4.0935 | 0 | 0 | 262.4 | 0 | 1
11/11 | 05:00:00 | 277.15 | 98771 | 7.7 | 220 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
11/11 | 06:00:00 | 277.15 | 98771 | 8.2 | 230 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
11/11 | 07:00:00 | 277.15 | 98771 | 8.7 | 230 | 3.8896 | 0 | 0 | 261.458 | 0 | 1
11/11 | 08:00:00 | 277.15 | 98771 | 7.7 | 220 | 4.1838 | 3.6 | 0 | 261.69 | 0 | 1
11/11 | 09:00:00 | 278.15 | 98780 | 6.7 | 220 | 4.1834 | 223.2 | 277.2 | 262.215 | 0 | 1
11/11 | 10:00:00 | 279.15 | 98789 | 6.2 | 210 | 4.4964 | 543.6 | 1242 | 263.81 | 0 | 1
11/11 | 11:00:00 | 279.15 | 98789 | 5.1 | 200 | 4.4964 | 759.6 | 1184.4 | 264.069 | 0 | 1
11/11 | 12:00:00 | 278.15 | 98780 | 6.7 | 220 | 4.8311 | 882 | 1306.8 | 263.352 | 0 | 1
11/11 | 13:00:00 | 278.15 | 98780 | 5.1 | 200 | 4.8311 | 856.8 | 1281.6 | 263.352 | 0 | 1
11/11 | 14:00:00 | 278.15 | 98780 | 5.1 | 210 | 4.8311 | 691.2 | 1011.6 | 263.352 | 0 | 1
11/11 | 15:00:00 | 278.15 | 98780 | 4.6 | 200 | 4.8311 | 234 | 0 | 263.818 | 0 | 1
11/11 | 16:00:00 | 278.15 | 98780 | 4.1 | 210 | 4.8311 | 64.8 | 0 | 263.818 | 0 | 1
11/11 | 17:00:00 | 279.15 | 98789 | 4.1 | 210 | 4.8307 | 0 | 0 | 264.767 | 0 | 1
11/11 | 18:00:00 | 279.15 | 98789 | 3.1 | 210 | 5.187 | 0 | 0 | 264.528 | 0 | 1
11/11 | 19:00:00 | 279.15 | 98789 | 6.2 | 220 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
11/11 | 20:00:00 | 278.15 | 98780 | 5.1 | 200 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
11/11 | 21:00:00 | 278.15 | 98780 | 5.1 | 210 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
11/11 | 22:00:00 | 278.15 | 98780 | 4.1 | 210 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
11/11 | 23:00:00 | 279.15 | 98789 | 7.2 | 210 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
11/11 | 24:00:00 | 279.15 | 98789 | 6.7 | 220 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
11/12 | 01:00:00 | 279.15 | 98789 | 6.4 | 45 | 4.9002 | 0 | 0 | 264.702 | 0 | 1
11/12 | 02:00:00 | 279.15 | 98789 | 6.1 | 42 | 4.9705 | 0 | 0 | 264.748 | 0 | 1
11/12 | 03:00:00 | 279.15 | 98789 | 5.7 | 46 | 5.0417 | 0 | 0 | 264.793 | 0 | 1
11/12 | 04:00:00 | 279.15 | 98789 | 5.4 | 195 | 5.1139 | 0 | 0 | 264.839 | 0 | 1
11/12 | 05:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.187 | 0 | 0 | 264.528 | 0 | 1
11/12 | 06:00:00 | 280.15 | 98798 | 5.7 | 240 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
11/12 | 07:00:00 | 280.15 | 98798 | 6.7 | 250 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
11/12 | 08:00:00 | 280.15 | 98798 | 10.3 | 250 | 5.1865 | 0 | 0 | 265.216 | 0 | 1
11/12 | 09:00:00 | 280.15 | 98798 | 10.3 | 260 | 4.8303 | 208.8 | 324 | 264.986 | 0 | 1
11/12 | 10:00:00 | 280.15 | 98798 | 11.3 | 260 | 5.1865 | 529.2 | 1213.2 | 265.216 | 0 | 1
11/12 | 11:00:00 | 281.15 | 98806 | 12.9 | 260 | 4.8299 | 745.2 | 1170 | 266.193 | 0 | 1
11/12 | 12:00:00 | 280.15 | 98798 | 10.3 | 250 | 5.1865 | 864 | 1508.4 | 265.476 | 0 | 1
11/12 | 13:00:00 | 281.15 | 98806 | 11.3 | 250 | 4.8299 | 892.8 | 1404 | 265.932 | 0 | 1
11/12 | 14:00:00 | 281.15 | 98806 | 12.3 | 250 | 5.1861 | 374.4 | 46.8 | 266.895 | 0 | 1
11/12 | 15:00:00 | 280.15 | 98798 | 14.4 | 260 | 5.1865 | 226.8 | 0 | 265.946 | 0 | 1
11/12 | 16:00:00 | 280.15 | 98798 | 12.9 | 260 | 5.5661 | 61.2 | 0 | 266.174 | 0 | 1
11/12 | 17:00:00 | 280.15 | 98798 | 12.9 | 260 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
11/12 | 18:00:00 | 280.15 | 98798 | 12.9 | 260 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
11/12 | 19:00:00 | 280.15 | 98798 | 11.3 | 260 | 4.8303 | 0 | 0 | 265.246 | 0 | 1
11/12 | 20:00:00 | 280.15 | 98798 | 11.3 | 260 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
11/12 | 21:00:00 | 279.15 | 98789 | 9.3 | 260 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
11/12 | 22:00:00 | 280.15 | 98798 | 7.7 | 260 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
11/12 | 23:00:00 | 280.15 | 98798 | 7.2 | 260 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
11/12 | 24:00:00 | 280.15 | 98798 | 6.7 | 270 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
11/13 | 01:00:00 | 279.95 | 98796 | 6.6 | 348 | 5.8057 | 0 | 0 | 266.121 | 0 | 1
11/13 | 02:00:00 | 279.75 | 98794 | 6.5 | 79 | 5.6451 | 0 | 0 | 265.84 | 0 | 1
11/13 | 03:00:00 | 279.55 | 98792 | 6.4 | 215 | 5.4886 | 0 | 0 | 265.559 | 0 | 1
11/13 | 04:00:00 | 279.35 | 98790 | 6.3 | 219 | 5.3359 | 0 | 0 | 265.278 | 0 | 1
11/13 | 05:00:00 | 279.15 | 98789 | 6.2 | 290 | 5.187 | 0 | 0 | 264.996 | 0 | 1
11/13 | 06:00:00 | 279.15 | 98789 | 5.7 | 300 | 5.187 | 0 | 0 | 264.269 | 0 | 1
11/13 | 07:00:00 | 279.15 | 98789 | 4.6 | 280 | 5.187 | 0 | 0 | 264.528 | 0 | 1
11/13 | 08:00:00 | 279.15 | 98789 | 6.2 | 300 | 5.187 | 0 | 0 | 264.528 | 0 | 1
11/13 | 09:00:00 | 279.15 | 98789 | 5.7 | 290 | 4.8307 | 187.2 | 226.8 | 264.299 | 0 | 1
11/13 | 10:00:00 | 280.15 | 98798 | 4.6 | 290 | 5.1865 | 514.8 | 1148.4 | 265.216 | 0 | 1
11/13 | 11:00:00 | 281.15 | 98806 | 4.1 | 280 | 5.1861 | 770.4 | 1609.2 | 266.163 | 0 | 1
11/13 | 12:00:00 | 281.15 | 98806 | 4.1 | 290 | 5.1861 | 900 | 1537.2 | 266.163 | 0 | 1
11/13 | 13:00:00 | 282.15 | 98815 | 5.1 | 290 | 5.1856 | 874.8 | 1508.4 | 267.11 | 0 | 1
11/13 | 14:00:00 | 282.15 | 98815 | 4.1 | 290 | 5.1856 | 702 | 1530 | 267.11 | 0 | 1
11/13 | 15:00:00 | 281.15 | 98806 | 3.1 | 280 | 5.1861 | 417.6 | 986.4 | 266.163 | 0 | 1
11/13 | 16:00:00 | 281.15 | 98806 | 3.1 | 270 | 5.1861 | 111.6 | 93.6 | 266.163 | 0 | 1
11/13 | 17:00:00 | 279.15 | 98789 | 4.1 | 290 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
11/13 | 18:00:00 | 278.15 | 98780 | 3.6 | 270 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
11/13 | 19:00:00 | 278.15 | 98780 | 2.6 | 280 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
11/13 | 20:00:00 | 277.15 | 98771 | 2.1 | 300 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
11/13 | 21:00:00 | 276.15 | 98762 | 1 | 346 | 4.832 | 0 | 0 | 262.027 | 0 | 1
11/13 | 22:00:00 | 277.15 | 98771 | 1 | 43 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
11/13 | 23:00:00 | 277.15 | 98771 | 1 | 193 | 5.1879 | 0 | 0 | 262.376 | 0 | 1
11/13 | 24:00:00 | 277.15 | 98771 | 1.5 | 76 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
11/14 | 01:00:00 | 277.55 | 98774 | 2.1 | 25 | 4.9009 | 0 | 0 | 263.295 | 0 | 1
11/14 | 02:00:00 | 277.95 | 98778 | 2.7 | 224 | 4.971 | 0 | 0 | 263.72 | 0 | 1
11/14 | 03:00:00 | 278.35 | 98781 | 3.4 | 181 | 5.0422 | 0 | 0 | 264.145 | 0 | 1
11/14 | 04:00:00 | 278.75 | 98785 | 4 | 78 | 5.1141 | 0 | 0 | 264.571 | 0 | 1
11/14 | 05:00:00 | 279.15 | 98789 | 4.6 | 220 | 5.187 | 0 | 0 | 264.269 | 0 | 1
11/14 | 06:00:00 | 279.15 | 98789 | 5.1 | 240 | 5.187 | 0 | 0 | 264.269 | 0 | 1
11/14 | 07:00:00 | 279.15 | 98789 | 6.2 | 230 | 5.187 | 0 | 0 | 264.269 | 0 | 1
11/14 | 08:00:00 | 280.15 | 98798 | 6.7 | 230 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
11/14 | 09:00:00 | 280.15 | 98798 | 5.1 | 210 | 5.5661 | 97.2 | 0 | 266.174 | 0 | 1
11/14 | 10:00:00 | 281.15 | 98806 | 4.6 | 230 | 5.9698 | 259.2 | 0 | 267.353 | 0 | 1
11/14 | 11:00:00 | 280.15 | 98798 | 4.1 | 230 | 6.4005 | 392.4 | 36 | 266.628 | 0 | 1
11/14 | 12:00:00 | 281.15 | 98806 | 3.6 | 230 | 6.8577 | 457.2 | 50.4 | 267.805 | 0 | 1
11/14 | 13:00:00 | 281.15 | 98806 | 5.7 | 220 | 6.8577 | 446.4 | 46.8 | 267.805 | 0 | 1
11/14 | 14:00:00 | 282.15 | 98815 | 4.1 | 220 | 6.8571 | 356.4 | 18 | 268.758 | 0 | 1
11/14 | 15:00:00 | 282.15 | 98815 | 4.1 | 210 | 7.3438 | 208.8 | 0 | 268.983 | 0 | 1
11/14 | 16:00:00 | 283.15 | 98824 | 5.7 | 240 | 7.3431 | 57.6 | 0 | 269.936 | 0 | 1
11/14 | 17:00:00 | 283.15 | 98824 | 6.7 | 250 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
11/14 | 18:00:00 | 284.15 | 98833 | 8.7 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/14 | 19:00:00 | 284.15 | 98833 | 9.3 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/14 | 20:00:00 | 284.15 | 98833 | 8.2 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/14 | 21:00:00 | 284.15 | 98833 | 11.3 | 260 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
11/14 | 22:00:00 | 284.15 | 98833 | 6.7 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/14 | 23:00:00 | 284.15 | 98833 | 8.2 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/14 | 24:00:00 | 284.15 | 98833 | 6.7 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/15 | 01:00:00 | 284.15 | 98833 | 7 | 237 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
11/15 | 02:00:00 | 284.15 | 98833 | 7.3 | 243 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
11/15 | 03:00:00 | 284.15 | 98833 | 7.6 | 226 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
11/15 | 04:00:00 | 284.15 | 98833 | 7.9 | 240 | 7.8598 | 0 | 0 | 271.225 | 0 | 1
11/15 | 05:00:00 | 284.15 | 98833 | 8.2 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/15 | 06:00:00 | 284.15 | 98833 | 5.1 | 260 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/15 | 07:00:00 | 284.15 | 98833 | 6.2 | 260 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
11/15 | 08:00:00 | 284.15 | 98833 | 5.1 | 260 | 8.4095 | 0 | 0 | 271.339 | 0 | 1
11/15 | 09:00:00 | 284.15 | 98833 | 6.7 | 250 | 8.4095 | 90 | 0 | 271.339 | 0 | 1
11/15 | 10:00:00 | 284.15 | 98833 | 6.2 | 250 | 8.4095 | 252 | 0 | 271.339 | 0 | 1
11/15 | 11:00:00 | 284.15 | 98833 | 5.1 | 260 | 7.8598 | 381.6 | 32.4 | 271.115 | 0 | 1
11/15 | 12:00:00 | 284.15 | 98833 | 9.8 | 260 | 7.8598 | 450 | 46.8 | 271.115 | 0 | 1
11/15 | 13:00:00 | 284.15 | 98833 | 7.7 | 250 | 7.8598 | 435.6 | 43.2 | 271.115 | 0 | 1
11/15 | 14:00:00 | 284.15 | 98833 | 8.7 | 250 | 7.3425 | 349.2 | 14.4 | 270.89 | 0 | 1
11/15 | 15:00:00 | 284.15 | 98833 | 6.2 | 250 | 7.3425 | 205.2 | 0 | 270.89 | 0 | 1
11/15 | 16:00:00 | 284.15 | 98833 | 7.2 | 250 | 6.8558 | 54 | 0 | 270.663 | 0 | 1
11/15 | 17:00:00 | 284.15 | 98833 | 10.8 | 250 | 6.8558 | 0 | 0 | 270.663 | 0 | 1
11/15 | 18:00:00 | 284.15 | 98833 | 10.3 | 250 | 6.8558 | 0 | 0 | 270.185 | 0 | 1
11/15 | 19:00:00 | 284.15 | 98833 | 6.2 | 250 | 6.8558 | 0 | 0 | 270.185 | 0 | 1
11/15 | 20:00:00 | 284.15 | 98833 | 8.7 | 250 | 6.3982 | 0 | 0 | 269.957 | 0 | 1
11/15 | 21:00:00 | 284.15 | 98833 | 9.3 | 250 | 6.3982 | 0 | 0 | 269.957 | 0 | 1
11/15 | 22:00:00 | 283.15 | 98824 | 7.2 | 240 | 6.3988 | 0 | 0 | 268.744 | 0 | 1
11/15 | 23:00:00 | 283.15 | 98824 | 11.8 | 250 | 6.3988 | 0 | 0 | 268.744 | 0 | 1
11/15 | 24:00:00 | 284.15 | 98833 | 13.9 | 260 | 6.3982 | 0 | 0 | 270.204 | 0 | 1
11/16 | 01:00:00 | 284.15 | 98833 | 13.4 | 266 | 6.5325 | 0 | 0 | 270.273 | 0 | 1
11/16 | 02:00:00 | 284.15 | 98833 | 12.9 | 37 | 6.6694 | 0 | 0 | 270.341 | 0 | 1
11/16 | 03:00:00 | 284.15 | 98833 | 12.4 | 345 | 6.8088 | 0 | 0 | 270.527 | 0 | 1
11/16 | 04:00:00 | 284.15 | 98833 | 11.8 | 120 | 6.9031 | 0 | 0 | 270.572 | 0 | 1
11/16 | 05:00:00 | 284.15 | 98833 | 11.3 | 69 | 7.0469 | 0 | 0 | 270.64 | 0 | 1
11/16 | 06:00:00 | 284.15 | 98833 | 7.4 | 229 | 7.1933 | 0 | 0 | 270.708 | 0 | 1
11/16 | 07:00:00 | 284.15 | 98833 | 7.7 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/16 | 08:00:00 | 284.15 | 98833 | 5.1 | 250 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
11/16 | 09:00:00 | 284.15 | 98833 | 5.7 | 260 | 7.8598 | 86.4 | 0 | 271.115 | 0 | 1
11/16 | 10:00:00 | 283.15 | 98824 | 3.6 | 250 | 6.8564 | 439.2 | 698.4 | 269.234 | 0 | 1
11/16 | 11:00:00 | 283.15 | 98824 | 2.6 | 240 | 6.8564 | 676.8 | 1267.2 | 269.234 | 0 | 1
11/16 | 12:00:00 | 283.15 | 98824 | 4.6 | 250 | 6.8564 | 795.6 | 1224 | 269.234 | 0 | 1
11/16 | 13:00:00 | 283.15 | 98824 | 6.2 | 260 | 5.9687 | 777.6 | 1213.2 | 268.779 | 0 | 1
11/16 | 14:00:00 | 284.15 | 98833 | 7.2 | 260 | 6.3982 | 619.2 | 1188 | 269.957 | 0 | 1
11/16 | 15:00:00 | 283.15 | 98824 | 5.7 | 260 | 5.9687 | 381.6 | 766.8 | 268.516 | 0 | 1
11/16 | 16:00:00 | 282.15 | 98815 | 4.1 | 260 | 5.9692 | 97.2 | 86.4 | 267.568 | 0 | 1
11/16 | 17:00:00 | 281.15 | 98806 | 3.1 | 250 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
11/16 | 18:00:00 | 281.15 | 98806 | 4.1 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
11/16 | 19:00:00 | 281.15 | 98806 | 5.1 | 260 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
11/16 | 20:00:00 | 281.15 | 98806 | 5.7 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
11/16 | 21:00:00 | 281.15 | 98806 | 5.1 | 260 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
11/16 | 22:00:00 | 280.15 | 98798 | 5.1 | 260 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
11/16 | 23:00:00 | 281.15 | 98806 | 6.7 | 260 | 6.4 | 0 | 0 | 267.688 | 0 | 1
11/16 | 24:00:00 | 281.15 | 98806 | 6.6 | 211 | 6.3118 | 0 | 0 | 267.535 | 0 | 1
11/17 | 01:00:00 | 281.15 | 98806 | 6.5 | 192 | 6.2681 | 0 | 0 | 267.512 | 0 | 1
11/17 | 02:00:00 | 281.15 | 98806 | 6.4 | 187 | 6.1815 | 0 | 0 | 267.467 | 0 | 1
11/17 | 03:00:00 | 281.15 | 98806 | 6.4 | 217 | 6.096 | 0 | 0 | 267.421 | 0 | 1
11/17 | 04:00:00 | 281.15 | 98806 | 6.3 | 31 | 6.0537 | 0 | 0 | 267.398 | 0 | 1
11/17 | 05:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
11/17 | 06:00:00 | 281.15 | 98806 | 7.7 | 270 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
11/17 | 07:00:00 | 281.15 | 98806 | 10.8 | 270 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
11/17 | 08:00:00 | 281.15 | 98806 | 6.7 | 280 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
11/17 | 09:00:00 | 281.15 | 98806 | 6.2 | 300 | 5.9698 | 151.2 | 194.4 | 266.62 | 0 | 1
11/17 | 10:00:00 | 281.15 | 98806 | 6.7 | 310 | 5.5656 | 453.6 | 1044 | 266.392 | 0 | 1
11/17 | 11:00:00 | 281.15 | 98806 | 5.1 | 310 | 5.5656 | 705.6 | 1522.8 | 266.392 | 0 | 1
11/17 | 12:00:00 | 281.15 | 98806 | 5.1 | 320 | 4.4957 | 835.2 | 1490.4 | 265.7 | 0 | 1
11/17 | 13:00:00 | 281.15 | 98806 | 5.1 | 330 | 4.1823 | 817.2 | 1324.8 | 265.467 | 0 | 1
11/17 | 14:00:00 | 282.15 | 98815 | 3.6 | 340 | 4.1819 | 648 | 1281.6 | 266.411 | 0 | 1
11/17 | 15:00:00 | 281.15 | 98806 | 2.1 | 30 | 4.1823 | 370.8 | 856.8 | 265.467 | 0 | 1
11/17 | 16:00:00 | 280.15 | 98798 | 1 | 151 | 4.1826 | 86.4 | 25.2 | 264.782 | 0 | 1
11/17 | 17:00:00 | 280.15 | 98798 | 2.1 | 20 | 4.1826 | 0 | 0 | 265.25 | 0 | 1
11/17 | 18:00:00 | 279.15 | 98789 | 1.5 | 195 | 4.183 | 0 | 0 | 264.303 | 0 | 1
11/17 | 19:00:00 | 279.15 | 98789 | 1 | 189 | 4.183 | 0 | 0 | 263.837 | 0 | 1
11/17 | 20:00:00 | 278.15 | 98780 | 1.5 | 30 | 4.1834 | 0 | 0 | 262.891 | 0 | 1
11/17 | 21:00:00 | 278.15 | 98780 | 0.5 | 10 | 4.1834 | 0 | 0 | 262.634 | 0 | 1
11/17 | 22:00:00 | 277.15 | 98771 | 0.5 | 60 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
11/17 | 23:00:00 | 276.15 | 98762 | 0.5 | 350 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
11/17 | 24:00:00 | 277.15 | 98771 | 0.5 | 180 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
11/18 | 01:00:00 | 276.75 | 98767 | 0.7 | 80 | 4.1236 | 0 | 0 | 261.875 | 0 | 1
11/18 | 02:00:00 | 276.35 | 98763 | 0.9 | 210 | 4.0643 | 0 | 0 | 261.45 | 0 | 1
11/18 | 03:00:00 | 275.95 | 98760 | 1.1 | 251 | 4.0056 | 0 | 0 | 261.025 | 0 | 1
11/18 | 04:00:00 | 275.55 | 98756 | 1.3 | 34 | 3.9478 | 0 | 0 | 260.601 | 0 | 1
11/18 | 05:00:00 | 275.15 | 98752 | 1.5 | 160 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
11/18 | 06:00:00 | 276.15 | 98762 | 2.6 | 160 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
11/18 | 07:00:00 | 276.15 | 98762 | 3.1 | 150 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
11/18 | 08:00:00 | 276.15 | 98762 | 4.1 | 160 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
11/18 | 09:00:00 | 277.15 | 98771 | 2.6 | 160 | 4.4973 | 75.6 | 0 | 262.64 | 0 | 1
11/18 | 10:00:00 | 277.15 | 98771 | 3.1 | 180 | 5.1879 | 417.6 | 676.8 | 262.633 | 0 | 1
11/18 | 11:00:00 | 278.15 | 98780 | 3.1 | 170 | 5.1875 | 360 | 32.4 | 264.047 | 0 | 1
11/18 | 12:00:00 | 278.15 | 98780 | 2.6 | 160 | 5.1875 | 428.4 | 46.8 | 264.047 | 0 | 1
11/18 | 13:00:00 | 279.15 | 98789 | 3.6 | 180 | 5.5666 | 417.6 | 43.2 | 265.224 | 0 | 1
11/18 | 14:00:00 | 279.15 | 98789 | 3.1 | 200 | 5.9708 | 327.6 | 10.8 | 265.451 | 0 | 1
11/18 | 15:00:00 | 281.15 | 98806 | 4.6 | 220 | 6.4 | 187.2 | 0 | 267.58 | 0 | 1
11/18 | 16:00:00 | 281.15 | 98806 | 4.1 | 230 | 6.4 | 46.8 | 0 | 267.58 | 0 | 1
11/18 | 17:00:00 | 281.15 | 98806 | 4.1 | 220 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/18 | 18:00:00 | 281.15 | 98806 | 4.1 | 220 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/18 | 19:00:00 | 281.15 | 98806 | 5.1 | 210 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/18 | 20:00:00 | 281.15 | 98806 | 6.2 | 220 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/18 | 21:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/18 | 22:00:00 | 282.15 | 98815 | 3.6 | 220 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
11/18 | 23:00:00 | 281.15 | 98806 | 3.1 | 240 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/18 | 24:00:00 | 281.35 | 98808 | 3.6 | 114 | 6.8576 | 0 | 0 | 268.105 | 0 | 1
11/19 | 01:00:00 | 281.45 | 98809 | 4.1 | 170 | 6.8575 | 0 | 0 | 268.2 | 0 | 1
11/19 | 02:00:00 | 281.65 | 98811 | 4.7 | 7 | 6.8574 | 0 | 0 | 268.39 | 0 | 1
11/19 | 03:00:00 | 281.85 | 98812 | 5.2 | 101 | 6.8573 | 0 | 0 | 268.581 | 0 | 1
11/19 | 04:00:00 | 281.95 | 98814 | 5.7 | 72 | 6.8571 | 0 | 0 | 268.676 | 0 | 1
11/19 | 05:00:00 | 282.15 | 98815 | 6.2 | 310 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
11/19 | 06:00:00 | 282.15 | 98815 | 6.2 | 330 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
11/19 | 07:00:00 | 282.15 | 98815 | 4.6 | 310 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
11/19 | 08:00:00 | 280.15 | 98798 | 4.1 | 290 | 5.9703 | 0 | 0 | 265.671 | 0 | 1
11/19 | 09:00:00 | 280.15 | 98798 | 6.2 | 300 | 5.5661 | 133.2 | 147.6 | 265.444 | 0 | 1
11/19 | 10:00:00 | 280.15 | 98798 | 5.7 | 300 | 5.1865 | 428.4 | 1004.4 | 265.216 | 0 | 1
11/19 | 11:00:00 | 281.15 | 98806 | 5.7 | 290 | 5.1861 | 561.6 | 529.2 | 266.667 | 0 | 1
11/19 | 12:00:00 | 282.15 | 98815 | 6.2 | 310 | 5.1856 | 720 | 1216.8 | 267.495 | 0 | 1
11/19 | 13:00:00 | 282.15 | 98815 | 4.6 | 300 | 5.5651 | 651.6 | 594 | 267.846 | 0 | 1
11/19 | 14:00:00 | 283.15 | 98824 | 4.6 | 300 | 5.5646 | 619.2 | 1364.4 | 268.287 | 0 | 1
11/19 | 15:00:00 | 282.15 | 98815 | 4.6 | 300 | 5.1856 | 349.2 | 799.2 | 267.11 | 0 | 1
11/19 | 16:00:00 | 281.15 | 98806 | 4.1 | 270 | 5.5656 | 82.8 | 46.8 | 266.392 | 0 | 1
11/19 | 17:00:00 | 280.15 | 98798 | 5.7 | 290 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
11/19 | 18:00:00 | 280.15 | 98798 | 4.1 | 280 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
11/19 | 19:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
11/19 | 20:00:00 | 280.15 | 98798 | 7.2 | 280 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
11/19 | 21:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
11/19 | 22:00:00 | 280.15 | 98798 | 7.7 | 270 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
11/19 | 23:00:00 | 280.15 | 98798 | 7.7 | 270 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
11/19 | 24:00:00 | 280.35 | 98799 | 8.3 | 183 | 5.6448 | 0 | 0 | 266.41 | 0 | 1
11/20 | 01:00:00 | 280.45 | 98801 | 8.9 | 275 | 5.6845 | 0 | 0 | 266.528 | 0 | 1
11/20 | 02:00:00 | 280.65 | 98802 | 9.5 | 338 | 5.7648 | 0 | 0 | 266.764 | 0 | 1
11/20 | 03:00:00 | 280.85 | 98803 | 10.1 | 180 | 5.846 | 0 | 0 | 266.999 | 0 | 1
11/20 | 04:00:00 | 280.95 | 98805 | 10.7 | 265 | 5.887 | 0 | 0 | 267.117 | 0 | 1
11/20 | 05:00:00 | 281.15 | 98806 | 11.3 | 280 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
11/20 | 06:00:00 | 280.15 | 98798 | 10.3 | 270 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
11/20 | 07:00:00 | 281.15 | 98806 | 8.7 | 270 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
11/20 | 08:00:00 | 282.15 | 98815 | 10.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
11/20 | 09:00:00 | 282.15 | 98815 | 11.3 | 280 | 6.3994 | 122.4 | 118.8 | 267.795 | 0 | 1
11/20 | 10:00:00 | 283.15 | 98824 | 10.3 | 270 | 6.8564 | 414 | 993.6 | 268.971 | 0 | 1
11/20 | 11:00:00 | 283.15 | 98824 | 7.7 | 270 | 6.8564 | 619.2 | 1180.8 | 269.234 | 0 | 1
11/20 | 12:00:00 | 283.15 | 98824 | 7.7 | 270 | 6.8564 | 410.4 | 46.8 | 269.71 | 0 | 1
11/20 | 13:00:00 | 283.15 | 98824 | 9.8 | 280 | 6.8564 | 399.6 | 39.6 | 269.71 | 0 | 1
11/20 | 14:00:00 | 283.15 | 98824 | 9.8 | 260 | 6.8564 | 313.2 | 10.8 | 269.71 | 0 | 1
11/20 | 15:00:00 | 283.15 | 98824 | 9.8 | 260 | 6.8564 | 176.4 | 0 | 269.71 | 0 | 1
11/20 | 16:00:00 | 282.15 | 98815 | 10.3 | 280 | 6.3994 | 43.2 | 0 | 268.532 | 0 | 1
11/20 | 17:00:00 | 282.15 | 98815 | 10.8 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
11/20 | 18:00:00 | 282.15 | 98815 | 12.9 | 270 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
11/20 | 19:00:00 | 282.15 | 98815 | 13.9 | 280 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
11/20 | 20:00:00 | 282.15 | 98815 | 11.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
11/20 | 21:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
11/20 | 22:00:00 | 283.15 | 98824 | 8.2 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
11/20 | 23:00:00 | 283.15 | 98824 | 10.3 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
11/20 | 24:00:00 | 283.15 | 98824 | 10.2 | 143 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
11/21 | 01:00:00 | 283.15 | 98824 | 10.1 | 148 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
11/21 | 02:00:00 | 283.15 | 98824 | 10.1 | 349 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
11/21 | 03:00:00 | 283.15 | 98824 | 10 | 145 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
11/21 | 04:00:00 | 283.15 | 98824 | 9.9 | 207 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
11/21 | 05:00:00 | 283.15 | 98824 | 9.8 | 290 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
11/21 | 06:00:00 | 282.15 | 98815 | 6.7 | 270 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
11/21 | 07:00:00 | 282.15 | 98815 | 7.7 | 280 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
11/21 | 08:00:00 | 282.15 | 98815 | 8.2 | 280 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
11/21 | 09:00:00 | 282.15 | 98815 | 9.3 | 280 | 5.1856 | 118.8 | 118.8 | 267.11 | 0 | 1
11/21 | 10:00:00 | 282.15 | 98815 | 12.3 | 290 | 5.1856 | 403.2 | 982.8 | 267.11 | 0 | 1
11/21 | 11:00:00 | 282.15 | 98815 | 12.9 | 290 | 4.8294 | 648 | 1458 | 266.878 | 0 | 1
11/21 | 12:00:00 | 282.15 | 98815 | 12.9 | 280 | 5.1856 | 774 | 1652.4 | 267.11 | 0 | 1
11/21 | 13:00:00 | 282.15 | 98815 | 11.3 | 280 | 5.1856 | 712.8 | 1353.6 | 267.371 | 0 | 1
11/21 | 14:00:00 | 282.15 | 98815 | 11.3 | 280 | 5.1856 | 558 | 1144.8 | 267.371 | 0 | 1
11/21 | 15:00:00 | 282.15 | 98815 | 9.3 | 270 | 5.1856 | 309.6 | 327.6 | 267.371 | 0 | 1
11/21 | 16:00:00 | 281.15 | 98806 | 8.7 | 280 | 5.5656 | 72 | 3.6 | 266.653 | 0 | 1
11/21 | 17:00:00 | 281.15 | 98806 | 9.8 | 270 | 5.1861 | 0 | 0 | 266.163 | 0 | 1
11/21 | 18:00:00 | 281.15 | 98806 | 12.9 | 270 | 5.5656 | 0 | 0 | 266.392 | 0 | 1
11/21 | 19:00:00 | 281.15 | 98806 | 13.4 | 270 | 5.1861 | 0 | 0 | 266.163 | 0 | 1
11/21 | 20:00:00 | 281.15 | 98806 | 11.3 | 280 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
11/21 | 21:00:00 | 281.15 | 98806 | 11.3 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
11/21 | 22:00:00 | 281.15 | 98806 | 10.8 | 270 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
11/21 | 23:00:00 | 281.15 | 98806 | 10.3 | 270 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
11/21 | 24:00:00 | 280.95 | 98805 | 9.9 | 167 | 5.7646 | 0 | 0 | 266.937 | 0 | 1
11/22 | 01:00:00 | 280.85 | 98803 | 9.6 | 124 | 5.5658 | 0 | 0 | 266.728 | 0 | 1
11/22 | 02:00:00 | 280.65 | 98802 | 9.2 | 189 | 5.3731 | 0 | 0 | 266.423 | 0 | 1
11/22 | 03:00:00 | 280.45 | 98801 | 8.9 | 257 | 5.1863 | 0 | 0 | 266.003 | 0 | 1
11/22 | 04:00:00 | 280.35 | 98799 | 8.6 | 257 | 5.0055 | 0 | 0 | 265.793 | 0 | 1
11/22 | 05:00:00 | 280.15 | 98798 | 8.2 | 310 | 4.8303 | 0 | 0 | 265.246 | 0 | 1
11/22 | 06:00:00 | 279.15 | 98789 | 10.8 | 320 | 3.2912 | 0 | 0 | 262.874 | 0 | 1
11/22 | 07:00:00 | 278.15 | 98780 | 11.3 | 310 | 3.2915 | 0 | 0 | 261.933 | 0 | 1
11/22 | 08:00:00 | 278.15 | 98780 | 8.2 | 300 | 3.2915 | 0 | 0 | 261.933 | 0 | 1
11/22 | 09:00:00 | 278.15 | 98780 | 10.8 | 300 | 3.2915 | 111.6 | 82.8 | 262.063 | 0 | 1
11/22 | 10:00:00 | 278.15 | 98780 | 12.9 | 310 | 3.0253 | 392.4 | 860.4 | 261.696 | 0 | 1
11/22 | 11:00:00 | 278.15 | 98780 | 11.3 | 310 | 2.7791 | 648 | 1346.4 | 261.323 | 0 | 1
11/22 | 12:00:00 | 278.15 | 98780 | 9.8 | 300 | 2.5513 | 727.2 | 1443.6 | 261.473 | 0 | 1
11/22 | 13:00:00 | 277.15 | 98771 | 6.2 | 310 | 4.1838 | 702 | 1051.2 | 261.946 | 0 | 1
11/22 | 14:00:00 | 277.15 | 98771 | 6.2 | 290 | 4.1838 | 550.8 | 997.2 | 261.946 | 0 | 1
11/22 | 15:00:00 | 279.15 | 98789 | 6.2 | 310 | 4.183 | 298.8 | 324 | 263.837 | 0 | 1
11/22 | 16:00:00 | 276.15 | 98762 | 7.7 | 350 | 3.8899 | 36 | 0 | 261.231 | 0 | 1
11/22 | 17:00:00 | 276.15 | 98762 | 7.7 | 330 | 3.5796 | 0 | 0 | 260.999 | 0 | 1
11/22 | 18:00:00 | 276.15 | 98762 | 5.7 | 330 | 3.2921 | 0 | 0 | 260.764 | 0 | 1
11/22 | 19:00:00 | 275.15 | 98752 | 4.6 | 330 | 3.2924 | 0 | 0 | 259.107 | 0 | 1
11/22 | 20:00:00 | 274.15 | 98743 | 5.1 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
11/22 | 21:00:00 | 274.15 | 98743 | 4.6 | 290 | 3.0265 | 0 | 0 | 258.305 | 0 | 1
11/22 | 22:00:00 | 273.15 | 98734 | 4.1 | 280 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
11/22 | 23:00:00 | 273.15 | 98734 | 5.7 | 290 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
11/22 | 24:00:00 | 274.15 | 98743 | 6.2 | 290 | 3.0265 | 0 | 0 | 258.305 | 0 | 1
11/23 | 01:00:00 | 274.15 | 98743 | 5.9 | 0 | 3.0781 | 0 | 0 | 258.352 | 0 | 1
11/23 | 02:00:00 | 274.15 | 98743 | 5.6 | 211 | 3.157 | 0 | 0 | 258.538 | 0 | 1
11/23 | 03:00:00 | 274.15 | 98743 | 5.4 | 223 | 3.2378 | 0 | 0 | 258.608 | 0 | 1
11/23 | 04:00:00 | 274.15 | 98743 | 5.1 | 320 | 3.2927 | 0 | 0 | 258.166 | 0 | 1
11/23 | 05:00:00 | 275.15 | 98752 | 7.2 | 310 | 3.2924 | 0 | 0 | 259.107 | 0 | 1
11/23 | 06:00:00 | 274.15 | 98743 | 5.1 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
11/23 | 07:00:00 | 274.15 | 98743 | 8.7 | 330 | 3.0265 | 0 | 0 | 257.932 | 0 | 1
11/23 | 08:00:00 | 274.15 | 98743 | 7.7 | 300 | 3.2927 | 0 | 0 | 258.166 | 0 | 1
11/23 | 09:00:00 | 274.15 | 98743 | 7.2 | 330 | 2.7801 | 100.8 | 50.4 | 257.95 | 0 | 1
11/23 | 10:00:00 | 275.15 | 98752 | 5.1 | 330 | 3.0262 | 356.4 | 626.4 | 259.127 | 0 | 1
11/23 | 11:00:00 | 275.15 | 98752 | 7.7 | 330 | 4.1846 | 622.8 | 1270.8 | 259.802 | 0 | 1
11/23 | 12:00:00 | 275.15 | 98752 | 8.7 | 340 | 4.4981 | 748.8 | 1407.6 | 260.03 | 0 | 1
11/23 | 13:00:00 | 275.15 | 98752 | 6.7 | 340 | 4.4981 | 730.8 | 1382.4 | 260.03 | 0 | 1
11/23 | 14:00:00 | 275.15 | 98752 | 7.2 | 340 | 4.4981 | 572.4 | 1360.8 | 260.03 | 0 | 1
11/23 | 15:00:00 | 274.15 | 98743 | 7.2 | 330 | 4.185 | 309.6 | 734.4 | 258.857 | 0 | 1
11/23 | 16:00:00 | 273.15 | 98734 | 6.7 | 330 | 3.891 | 68.4 | 0 | 257.685 | 0 | 1
11/23 | 17:00:00 | 273.15 | 98734 | 7.7 | 340 | 3.891 | 0 | 0 | 258.498 | 0 | 1
11/23 | 18:00:00 | 273.15 | 98734 | 7.2 | 330 | 3.891 | 0 | 0 | 258.498 | 0 | 1
11/23 | 19:00:00 | 273.15 | 98734 | 6.7 | 330 | 3.891 | 0 | 0 | 258.498 | 0 | 1
11/23 | 20:00:00 | 272.15 | 98724 | 5.7 | 290 | 3.581 | 0 | 0 | 257.322 | 0 | 1
11/23 | 21:00:00 | 272.15 | 98724 | 6.7 | 310 | 3.581 | 0 | 0 | 257.322 | 0 | 1
11/23 | 22:00:00 | 271.15 | 98715 | 3.1 | 270 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/23 | 23:00:00 | 272.15 | 98724 | 3.1 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
11/23 | 24:00:00 | 271.15 | 98715 | 4.1 | 270 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/24 | 01:00:00 | 271.15 | 98715 | 3.6 | 260 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/24 | 02:00:00 | 271.15 | 98715 | 3.6 | 250 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/24 | 03:00:00 | 271.15 | 98715 | 1.5 | 269 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/24 | 04:00:00 | 272.15 | 98724 | 2.6 | 200 | 3.581 | 0 | 0 | 256.513 | 0 | 1
11/24 | 05:00:00 | 272.15 | 98724 | 3.6 | 200 | 3.581 | 0 | 0 | 256.764 | 0 | 1
11/24 | 06:00:00 | 272.15 | 98724 | 6.2 | 190 | 3.581 | 0 | 0 | 257.218 | 0 | 1
11/24 | 07:00:00 | 272.15 | 98724 | 3.6 | 170 | 3.581 | 0 | 0 | 257.218 | 0 | 1
11/24 | 08:00:00 | 272.15 | 98724 | 4.1 | 170 | 3.581 | 0 | 0 | 257.218 | 0 | 1
11/24 | 09:00:00 | 273.15 | 98734 | 2.6 | 220 | 3.891 | 54 | 0 | 258.394 | 0 | 1
11/24 | 10:00:00 | 274.15 | 98743 | 3.6 | 260 | 4.185 | 367.2 | 882 | 258.857 | 0 | 1
11/24 | 11:00:00 | 276.15 | 98762 | 5.1 | 280 | 4.4977 | 608.4 | 1414.8 | 260.975 | 0 | 1
11/24 | 12:00:00 | 278.15 | 98780 | 5.7 | 310 | 4.8311 | 694.8 | 1350 | 263.352 | 0 | 1
11/24 | 13:00:00 | 279.15 | 98789 | 8.2 | 280 | 4.8307 | 716.4 | 1591.2 | 264.041 | 0 | 1
11/24 | 14:00:00 | 278.15 | 98780 | 9.8 | 280 | 4.4968 | 561.6 | 1346.4 | 262.865 | 0 | 1
11/24 | 15:00:00 | 278.15 | 98780 | 9.8 | 290 | 4.4968 | 284.4 | 450 | 263.123 | 0 | 1
11/24 | 16:00:00 | 278.15 | 98780 | 8.2 | 290 | 4.4968 | 61.2 | 0 | 263.123 | 0 | 1
11/24 | 17:00:00 | 277.15 | 98771 | 8.7 | 280 | 4.4973 | 0 | 0 | 261.92 | 0 | 1
11/24 | 18:00:00 | 278.15 | 98780 | 8.2 | 290 | 4.1834 | 0 | 0 | 262.634 | 0 | 1
11/24 | 19:00:00 | 278.15 | 98780 | 9.3 | 290 | 3.8892 | 0 | 0 | 262.659 | 0 | 1
11/24 | 20:00:00 | 277.15 | 98771 | 8.7 | 300 | 3.8896 | 0 | 0 | 261.458 | 0 | 1
11/24 | 21:00:00 | 277.15 | 98771 | 7.2 | 280 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
11/24 | 22:00:00 | 277.15 | 98771 | 7.7 | 280 | 3.8896 | 0 | 0 | 261.458 | 0 | 1
11/24 | 23:00:00 | 277.15 | 98771 | 6.7 | 290 | 3.8896 | 0 | 0 | 261.458 | 0 | 1
11/24 | 24:00:00 | 277.15 | 98771 | 7.2 | 300 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
11/25 | 01:00:00 | 277.15 | 98771 | 5.7 | 300 | 3.8896 | 0 | 0 | 261.714 | 0 | 1
11/25 | 02:00:00 | 276.15 | 98762 | 4.6 | 320 | 3.8899 | 0 | 0 | 260.515 | 0 | 1
11/25 | 03:00:00 | 277.15 | 98771 | 5.7 | 350 | 4.1838 | 0 | 0 | 261.946 | 0 | 1
11/25 | 04:00:00 | 277.15 | 98771 | 5.7 | 10 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
11/25 | 05:00:00 | 277.15 | 98771 | 7.2 | 10 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
11/25 | 06:00:00 | 276.15 | 98762 | 5.7 | 30 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
11/25 | 07:00:00 | 276.15 | 98762 | 5.1 | 30 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
11/25 | 08:00:00 | 276.15 | 98762 | 4.6 | 20 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
11/25 | 09:00:00 | 276.15 | 98762 | 4.6 | 20 | 3.8899 | 97.2 | 75.6 | 260.515 | 0 | 1
11/25 | 10:00:00 | 276.15 | 98762 | 4.6 | 30 | 3.8899 | 334.8 | 698.4 | 260.77 | 0 | 1
11/25 | 11:00:00 | 278.15 | 98780 | 6.2 | 360 | 4.1834 | 561.6 | 1170 | 262.891 | 0 | 1
11/25 | 12:00:00 | 277.15 | 98771 | 6.2 | 360 | 3.8896 | 684 | 1044 | 261.714 | 0 | 1
11/25 | 13:00:00 | 278.15 | 98780 | 5.1 | 10 | 3.5789 | 669.6 | 1033.2 | 262.425 | 0 | 1
11/25 | 14:00:00 | 277.15 | 98771 | 5.7 | 340 | 3.5793 | 550.8 | 1170 | 261.225 | 0 | 1
11/25 | 15:00:00 | 277.15 | 98771 | 6.2 | 350 | 3.5793 | 291.6 | 702 | 261.225 | 0 | 1
11/25 | 16:00:00 | 277.15 | 98771 | 9.3 | 350 | 4.1838 | 57.6 | 0 | 261.946 | 0 | 1
11/25 | 17:00:00 | 275.15 | 98752 | 7.7 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
11/25 | 18:00:00 | 276.15 | 98762 | 8.2 | 350 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
11/25 | 19:00:00 | 275.15 | 98752 | 8.2 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
11/25 | 20:00:00 | 275.15 | 98752 | 5.7 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
11/25 | 21:00:00 | 275.15 | 98752 | 7.2 | 330 | 3.5799 | 0 | 0 | 259.34 | 0 | 1
11/25 | 22:00:00 | 276.15 | 98762 | 8.2 | 330 | 3.2921 | 0 | 0 | 260.049 | 0 | 1
11/25 | 23:00:00 | 276.15 | 98762 | 8.7 | 340 | 3.2921 | 0 | 0 | 260.049 | 0 | 1
11/25 | 24:00:00 | 276.15 | 98762 | 7.7 | 330 | 3.2921 | 0 | 0 | 260.304 | 0 | 1
11/26 | 01:00:00 | 276.15 | 98762 | 7.7 | 340 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
11/26 | 02:00:00 | 276.15 | 98762 | 8.7 | 350 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
11/26 | 03:00:00 | 276.15 | 98762 | 7.7 | 340 | 3.5796 | 0 | 0 | 260.283 | 0 | 1
11/26 | 04:00:00 | 276.15 | 98762 | 7.2 | 330 | 3.5796 | 0 | 0 | 260.283 | 0 | 1
11/26 | 05:00:00 | 275.15 | 98752 | 7.2 | 330 | 3.5799 | 0 | 0 | 259.34 | 0 | 1
11/26 | 06:00:00 | 275.15 | 98752 | 7.7 | 320 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
11/26 | 07:00:00 | 275.15 | 98752 | 7.7 | 320 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
11/26 | 08:00:00 | 275.15 | 98752 | 7.7 | 310 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
11/26 | 09:00:00 | 275.15 | 98752 | 8.2 | 320 | 3.2924 | 90 | 43.2 | 259.361 | 0 | 1
11/26 | 10:00:00 | 276.15 | 98762 | 7.2 | 320 | 3.5796 | 345.6 | 842.4 | 260.283 | 0 | 1
11/26 | 11:00:00 | 277.15 | 98771 | 7.2 | 330 | 3.5793 | 586.8 | 1407.6 | 261.225 | 0 | 1
11/26 | 12:00:00 | 278.15 | 98780 | 8.2 | 340 | 3.5789 | 712.8 | 1249.2 | 262.168 | 0 | 1
11/26 | 13:00:00 | 278.15 | 98780 | 6.7 | 340 | 3.5789 | 698.4 | 1227.6 | 262.168 | 0 | 1
11/26 | 14:00:00 | 278.15 | 98780 | 6.7 | 340 | 3.5789 | 543.6 | 1159.2 | 262.168 | 0 | 1
11/26 | 15:00:00 | 278.15 | 98780 | 6.2 | 340 | 3.2915 | 280.8 | 586.8 | 262.063 | 0 | 1
11/26 | 16:00:00 | 277.15 | 98771 | 3.1 | 290 | 3.5793 | 54 | 0 | 261.603 | 0 | 1
11/26 | 17:00:00 | 275.15 | 98752 | 4.1 | 280 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
11/26 | 18:00:00 | 275.15 | 98752 | 4.6 | 290 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
11/26 | 19:00:00 | 275.15 | 98752 | 5.1 | 280 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
11/26 | 20:00:00 | 275.15 | 98752 | 4.6 | 270 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
11/26 | 21:00:00 | 274.15 | 98743 | 4.1 | 270 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
11/26 | 22:00:00 | 274.15 | 98743 | 5.1 | 250 | 3.5803 | 0 | 0 | 259 | 0 | 1
11/26 | 23:00:00 | 277.15 | 98771 | 6.2 | 260 | 4.1838 | 0 | 0 | 261.946 | 0 | 1
11/26 | 24:00:00 | 278.15 | 98780 | 7.7 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
11/27 | 01:00:00 | 278.75 | 98785 | 7.9 | 269 | 5.4121 | 0 | 0 | 264.861 | 0 | 1
11/27 | 02:00:00 | 279.35 | 98790 | 8.1 | 237 | 5.6453 | 0 | 0 | 265.567 | 0 | 1
11/27 | 03:00:00 | 279.95 | 98796 | 8.3 | 174 | 5.8875 | 0 | 0 | 266.274 | 0 | 1
11/27 | 04:00:00 | 280.55 | 98801 | 8.5 | 241 | 6.139 | 0 | 0 | 266.981 | 0 | 1
11/27 | 05:00:00 | 281.15 | 98806 | 8.7 | 280 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/27 | 06:00:00 | 281.15 | 98806 | 9.8 | 280 | 6.4 | 0 | 0 | 267.107 | 0 | 1
11/27 | 07:00:00 | 281.15 | 98806 | 10.3 | 280 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
11/27 | 08:00:00 | 282.15 | 98815 | 9.3 | 290 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
11/27 | 09:00:00 | 281.15 | 98806 | 5.7 | 300 | 6.4 | 82.8 | 28.8 | 267.107 | 0 | 1
11/27 | 10:00:00 | 282.15 | 98815 | 4.1 | 270 | 6.8571 | 313.2 | 550.8 | 268.283 | 0 | 1
11/27 | 11:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.8571 | 295.2 | 10.8 | 268.758 | 0 | 1
11/27 | 12:00:00 | 282.15 | 98815 | 2.1 | 230 | 6.8571 | 363.6 | 28.8 | 268.758 | 0 | 1
11/27 | 13:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.8571 | 352.8 | 28.8 | 268.758 | 0 | 1
11/27 | 14:00:00 | 282.15 | 98815 | 6.2 | 260 | 7.3438 | 273.6 | 0 | 268.983 | 0 | 1
11/27 | 15:00:00 | 282.15 | 98815 | 6.2 | 260 | 6.8571 | 144 | 0 | 268.758 | 0 | 1
11/27 | 16:00:00 | 281.15 | 98806 | 8.2 | 250 | 6.8577 | 28.8 | 0 | 267.805 | 0 | 1
11/27 | 17:00:00 | 281.15 | 98806 | 7.2 | 260 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
11/27 | 18:00:00 | 281.15 | 98806 | 5.7 | 240 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/27 | 19:00:00 | 281.15 | 98806 | 3.6 | 230 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/27 | 20:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1
11/27 | 21:00:00 | 282.15 | 98815 | 9.3 | 260 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
11/27 | 22:00:00 | 281.15 | 98806 | 9.3 | 260 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
11/27 | 23:00:00 | 281.15 | 98806 | 11.3 | 260 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
11/27 | 24:00:00 | 281.15 | 98806 | 8.2 | 250 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
11/28 | 01:00:00 | 281.15 | 98806 | 7.9 | 258 | 5.8869 | 0 | 0 | 267.195 | 0 | 1
11/28 | 02:00:00 | 281.15 | 98806 | 7.6 | 128 | 5.8051 | 0 | 0 | 267.15 | 0 | 1
11/28 | 03:00:00 | 281.15 | 98806 | 7.3 | 75 | 5.7242 | 0 | 0 | 267.104 | 0 | 1
11/28 | 04:00:00 | 281.15 | 98806 | 7 | 94 | 5.6444 | 0 | 0 | 267.058 | 0 | 1
11/28 | 05:00:00 | 281.15 | 98806 | 6.7 | 240 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
11/28 | 06:00:00 | 281.15 | 98806 | 5.7 | 230 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
11/28 | 07:00:00 | 280.15 | 98798 | 5.7 | 240 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
11/28 | 08:00:00 | 280.15 | 98798 | 7.7 | 230 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
11/28 | 09:00:00 | 280.15 | 98798 | 7.7 | 220 | 6.4005 | 79.2 | 57.6 | 266.157 | 0 | 1
11/28 | 10:00:00 | 281.15 | 98806 | 9.8 | 220 | 5.9698 | 169.2 | 0 | 267.353 | 0 | 1
11/28 | 11:00:00 | 282.15 | 98815 | 9.8 | 220 | 5.9692 | 291.6 | 7.2 | 268.304 | 0 | 1
11/28 | 12:00:00 | 281.15 | 98806 | 7.7 | 220 | 5.9698 | 356.4 | 28.8 | 267.353 | 0 | 1
11/28 | 13:00:00 | 281.15 | 98806 | 5.1 | 240 | 6.4 | 349.2 | 28.8 | 267.58 | 0 | 1
11/28 | 14:00:00 | 281.15 | 98806 | 10.3 | 250 | 5.5656 | 518.4 | 982.8 | 266.392 | 0 | 1
11/28 | 15:00:00 | 280.15 | 98798 | 6.7 | 260 | 5.5661 | 252 | 399.6 | 265.704 | 0 | 1
11/28 | 16:00:00 | 280.15 | 98798 | 7.7 | 260 | 5.1865 | 46.8 | 0 | 265.476 | 0 | 1
11/28 | 17:00:00 | 279.15 | 98789 | 6.2 | 250 | 4.8307 | 0 | 0 | 264.299 | 0 | 1
11/28 | 18:00:00 | 278.15 | 98780 | 4.6 | 240 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
11/28 | 19:00:00 | 277.15 | 98771 | 4.1 | 240 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
11/28 | 20:00:00 | 276.15 | 98762 | 4.1 | 250 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
11/28 | 21:00:00 | 276.15 | 98762 | 4.1 | 230 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
11/28 | 22:00:00 | 276.15 | 98762 | 2.1 | 190 | 4.1841 | 0 | 0 | 260.746 | 0 | 1
11/28 | 23:00:00 | 275.15 | 98752 | 3.1 | 200 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
11/28 | 24:00:00 | 275.15 | 98752 | 2.6 | 190 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
11/29 | 01:00:00 | 275.15 | 98752 | 3.1 | 210 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
11/29 | 02:00:00 | 275.15 | 98752 | 4.1 | 220 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
11/29 | 03:00:00 | 274.15 | 98743 | 4.1 | 220 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
11/29 | 04:00:00 | 274.15 | 98743 | 3.1 | 240 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
11/29 | 05:00:00 | 274.15 | 98743 | 3.1 | 220 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
11/29 | 06:00:00 | 274.15 | 98743 | 3.1 | 250 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
11/29 | 07:00:00 | 274.15 | 98743 | 3.1 | 230 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
11/29 | 08:00:00 | 274.15 | 98743 | 4.1 | 220 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
11/29 | 09:00:00 | 273.15 | 98734 | 2.6 | 220 | 3.891 | 79.2 | 118.8 | 257.685 | 0 | 1
11/29 | 10:00:00 | 273.15 | 98734 | 2.6 | 150 | 3.5806 | 316.8 | 781.2 | 257.455 | 0 | 1
11/29 | 11:00:00 | 275.15 | 98752 | 1 | 322 | 3.8903 | 550.8 | 1188 | 259.572 | 0 | 1
11/29 | 12:00:00 | 277.15 | 98771 | 2.1 | 260 | 3.8896 | 680.4 | 1213.2 | 261.458 | 0 | 1
11/29 | 13:00:00 | 277.15 | 98771 | 2.6 | 180 | 4.1838 | 666 | 1555.2 | 261.69 | 0 | 1
11/29 | 14:00:00 | 277.15 | 98771 | 1.5 | 170 | 4.1838 | 482.4 | 925.2 | 261.946 | 0 | 1
11/29 | 15:00:00 | 277.15 | 98771 | 1 | 276 | 4.4973 | 248.4 | 270 | 262.177 | 0 | 1
11/29 | 16:00:00 | 276.15 | 98762 | 1.5 | 130 | 4.1841 | 43.2 | 0 | 261.001 | 0 | 1
11/29 | 17:00:00 | 275.15 | 98752 | 1.5 | 110 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
11/29 | 18:00:00 | 275.15 | 98752 | 1.5 | 178 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
11/29 | 19:00:00 | 274.15 | 98743 | 0.5 | 208 | 4.185 | 0 | 0 | 259.674 | 0 | 1
11/29 | 20:00:00 | 273.15 | 98734 | 0.5 | 18 | 3.891 | 0 | 0 | 257.273 | 0 | 1
11/29 | 21:00:00 | 273.15 | 98734 | 1 | 153 | 3.891 | 0 | 0 | 258.498 | 0 | 1
11/29 | 22:00:00 | 272.15 | 98724 | 1.5 | 250 | 3.581 | 0 | 0 | 257.322 | 0 | 1
11/29 | 23:00:00 | 271.15 | 98715 | 2.6 | 240 | 3.2936 | 0 | 0 | 256.043 | 0 | 1
11/29 | 24:00:00 | 271.15 | 98715 | 0.5 | 211 | 3.2936 | 0 | 0 | 254.933 | 0 | 1
11/30 | 01:00:00 | 271.15 | 98715 | 1 | 290 | 3.2936 | 0 | 0 | 254.933 | 0 | 1
11/30 | 02:00:00 | 271.15 | 98715 | 1.5 | 260 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/30 | 03:00:00 | 271.15 | 98715 | 1 | 320 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/30 | 04:00:00 | 271.15 | 98715 | 1 | 270 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/30 | 05:00:00 | 271.15 | 98715 | 0.5 | 69 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/30 | 06:00:00 | 271.15 | 98715 | 2.1 | 290 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
11/30 | 07:00:00 | 271.15 | 98715 | 1.5 | 260 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
11/30 | 08:00:00 | 270.15 | 98705 | 1.5 | 280 | 3.0276 | 0 | 0 | 253.763 | 0 | 1
11/30 | 09:00:00 | 270.15 | 98705 | 1.5 | 300 | 2.7812 | 75.6 | 46.8 | 253.532 | 0 | 1
11/30 | 10:00:00 | 270.15 | 98705 | 0.5 | 351 | 3.0276 | 309.6 | 795.6 | 253.763 | 0 | 1
11/30 | 11:00:00 | 273.15 | 98734 | 1 | 313 | 3.5806 | 547.2 | 1220.4 | 257.044 | 0 | 1
11/30 | 12:00:00 | 274.15 | 98743 | 1 | 238 | 3.2927 | 676.8 | 1256.4 | 257.754 | 0 | 1
11/30 | 13:00:00 | 275.15 | 98752 | 1 | 41 | 4.1846 | 662.4 | 1224 | 259.387 | 0 | 1
11/30 | 14:00:00 | 275.15 | 98752 | 2.1 | 350 | 3.8903 | 511.2 | 1184.4 | 259.157 | 0 | 1
11/30 | 15:00:00 | 275.15 | 98752 | 1.5 | 20 | 3.8903 | 154.8 | 0 | 260.286 | 0 | 1
11/30 | 16:00:00 | 274.15 | 98743 | 1.5 | 350 | 3.8907 | 18 | 0 | 259.445 | 0 | 1
11/30 | 17:00:00 | 274.15 | 98743 | 0.5 | 340 | 3.5803 | 0 | 0 | 259 | 0 | 1
11/30 | 18:00:00 | 274.15 | 98743 | 1.5 | 350 | 3.5803 | 0 | 0 | 259 | 0 | 1
11/30 | 19:00:00 | 273.35 | 98736 | 2.4 | 278 | 3.5805 | 0 | 0 | 258.352 | 0 | 1
11/30 | 20:00:00 | 273.35 | 98736 | 2.6 | 347 | 3.5805 | 0 | 0 | 258.352 | 0 | 1
11/30 | 21:00:00 | 273.35 | 98736 | 2.7 | 340 | 3.5212 | 0 | 0 | 258.198 | 0 | 1
11/30 | 22:00:00 | 273.35 | 98736 | 4 | 342 | 3.5805 | 0 | 0 | 258.352 | 0 | 1
11/30 | 23:00:00 | 273.65 | 98739 | 5.1 | 345 | 3.6406 | 0 | 0 | 258.682 | 0 | 1
11/30 | 24:00:00 | 274.15 | 98743 | 6.6 | 342 | 3.7325 | 0 | 0 | 259.115 | 0 | 1
12/1 | 01:00:00 | 274.65 | 98748 | 7.2 | 350 | 3.8905 | 0 | 0 | 259.354 | 0 | 1
12/1 | 02:00:00 | 274.95 | 98750 | 6.8 | 347 | 3.8904 | 0 | 0 | 259.637 | 0 | 1
12/1 | 03:00:00 | 275.15 | 98752 | 6.2 | 347 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/1 | 04:00:00 | 275.15 | 98752 | 5.8 | 342 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/1 | 05:00:00 | 275.15 | 98752 | 5.7 | 342 | 3.948 | 0 | 0 | 259.872 | 0 | 1
12/1 | 06:00:00 | 275.15 | 98752 | 5.4 | 340 | 4.0352 | 0 | 0 | 259.687 | 0 | 1
12/1 | 07:00:00 | 275.15 | 98752 | 6.2 | 330 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/1 | 08:00:00 | 275.15 | 98752 | 5.1 | 340 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
12/1 | 09:00:00 | 275.15 | 98752 | 5.1 | 340 | 4.1846 | 61.2 | 0 | 260.056 | 0 | 1
12/1 | 10:00:00 | 275.15 | 98752 | 5.7 | 340 | 4.1846 | 270 | 338.4 | 260.056 | 0 | 1
12/1 | 11:00:00 | 276.15 | 98762 | 6.7 | 340 | 4.1841 | 518.4 | 1137.6 | 260.746 | 0 | 1
12/1 | 12:00:00 | 276.15 | 98762 | 6.2 | 350 | 4.1841 | 648 | 1177.2 | 260.746 | 0 | 1
12/1 | 13:00:00 | 277.15 | 98771 | 7.2 | 360 | 4.1838 | 637.2 | 1162.8 | 261.69 | 0 | 1
12/1 | 14:00:00 | 277.15 | 98771 | 7.2 | 10 | 3.8896 | 489.6 | 1087.2 | 261.458 | 0 | 1
12/1 | 15:00:00 | 277.15 | 98771 | 5.1 | 360 | 3.8896 | 244.8 | 601.2 | 261.458 | 0 | 1
12/1 | 16:00:00 | 276.15 | 98762 | 5.1 | 330 | 3.8899 | 39.6 | 0 | 260.515 | 0 | 1
12/1 | 17:00:00 | 276.15 | 98762 | 4.6 | 320 | 3.5796 | 0 | 0 | 260.283 | 0 | 1
12/1 | 18:00:00 | 276.15 | 98762 | 4.1 | 300 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
12/1 | 19:00:00 | 275.15 | 98752 | 3.6 | 260 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
12/1 | 20:00:00 | 275.15 | 98752 | 4.1 | 270 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
12/1 | 21:00:00 | 276.15 | 98762 | 4.1 | 280 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
12/1 | 22:00:00 | 275.15 | 98752 | 5.1 | 290 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
12/1 | 23:00:00 | 275.15 | 98752 | 4.6 | 280 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
12/1 | 24:00:00 | 275.15 | 98752 | 4.1 | 260 | 3.2924 | 0 | 0 | 259.482 | 0 | 1
12/2 | 01:00:00 | 276.15 | 98762 | 4.6 | 270 | 3.2921 | 0 | 0 | 260.304 | 0 | 1
12/2 | 02:00:00 | 276.15 | 98762 | 4.3 | 25 | 3.4331 | 0 | 0 | 260.542 | 0 | 1
12/2 | 03:00:00 | 276.15 | 98762 | 4.1 | 270 | 3.5796 | 0 | 0 | 260.659 | 0 | 1
12/2 | 04:00:00 | 276.15 | 98762 | 4.6 | 280 | 3.5796 | 0 | 0 | 260.538 | 0 | 1
12/2 | 05:00:00 | 276.15 | 98762 | 3.6 | 280 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
12/2 | 06:00:00 | 276.15 | 98762 | 4.1 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
12/2 | 07:00:00 | 276.15 | 98762 | 5.1 | 290 | 4.4977 | 0 | 0 | 260.975 | 0 | 1
12/2 | 08:00:00 | 276.15 | 98762 | 4.1 | 270 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
12/2 | 09:00:00 | 276.15 | 98762 | 3.6 | 290 | 4.4977 | 61.2 | 0 | 260.975 | 0 | 1
12/2 | 10:00:00 | 277.15 | 98771 | 4.1 | 290 | 4.8316 | 277.2 | 680.4 | 262.149 | 0 | 1
12/2 | 11:00:00 | 278.15 | 98780 | 3.1 | 270 | 5.1875 | 507.6 | 1278 | 263.323 | 0 | 1
12/2 | 12:00:00 | 279.15 | 98789 | 3.1 | 270 | 5.5666 | 633.6 | 1486.8 | 264.497 | 0 | 1
12/2 | 13:00:00 | 279.15 | 98789 | 2.6 | 270 | 5.5666 | 586.8 | 1224 | 264.756 | 0 | 1
12/2 | 14:00:00 | 280.15 | 98798 | 4.6 | 310 | 5.5661 | 450 | 1004.4 | 265.704 | 0 | 1
12/2 | 15:00:00 | 280.15 | 98798 | 4.6 | 300 | 5.1865 | 226.8 | 244.8 | 265.476 | 0 | 1
12/2 | 16:00:00 | 279.15 | 98789 | 3.6 | 280 | 5.187 | 36 | 0 | 264.528 | 0 | 1
12/2 | 17:00:00 | 279.15 | 98789 | 4.1 | 280 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
12/2 | 18:00:00 | 279.15 | 98789 | 2.6 | 280 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
12/2 | 19:00:00 | 279.15 | 98789 | 4.6 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
12/2 | 20:00:00 | 279.15 | 98789 | 4.1 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
12/2 | 21:00:00 | 279.15 | 98789 | 4.6 | 290 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
12/2 | 22:00:00 | 279.15 | 98789 | 3.6 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
12/2 | 23:00:00 | 279.15 | 98789 | 4.1 | 280 | 5.5666 | 0 | 0 | 264.756 | 0 | 1
12/2 | 24:00:00 | 280.15 | 98798 | 4.6 | 280 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
12/3 | 01:00:00 | 280.15 | 98798 | 4.1 | 260 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
12/3 | 02:00:00 | 280.15 | 98798 | 6.7 | 290 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
12/3 | 03:00:00 | 280.15 | 98798 | 5.7 | 280 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
12/3 | 04:00:00 | 280.15 | 98798 | 7.2 | 280 | 5.5661 | 0 | 0 | 265.444 | 0 | 1
12/3 | 05:00:00 | 281.15 | 98806 | 6.2 | 300 | 5.9698 | 0 | 0 | 266.62 | 0 | 1
12/3 | 06:00:00 | 281.15 | 98806 | 5.7 | 300 | 5.9698 | 0 | 0 | 267.353 | 0 | 1
12/3 | 07:00:00 | 280.15 | 98798 | 4.6 | 290 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
12/3 | 08:00:00 | 280.15 | 98798 | 4.1 | 290 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
12/3 | 09:00:00 | 281.15 | 98806 | 4.1 | 300 | 6.4 | 28.8 | 0 | 267.58 | 0 | 1
12/3 | 10:00:00 | 281.15 | 98806 | 4.1 | 300 | 5.9698 | 140.4 | 0 | 267.353 | 0 | 1
12/3 | 11:00:00 | 281.15 | 98806 | 3.6 | 310 | 5.9698 | 259.2 | 0 | 267.353 | 0 | 1
12/3 | 12:00:00 | 281.15 | 98806 | 1.5 | 59 | 5.5656 | 327.6 | 25.2 | 267.125 | 0 | 1
12/3 | 13:00:00 | 281.15 | 98806 | 1.5 | 10 | 5.1861 | 579.6 | 961.2 | 266.423 | 0 | 1
12/3 | 14:00:00 | 281.15 | 98806 | 1 | 134 | 5.1861 | 446.4 | 997.2 | 266.423 | 0 | 1
12/3 | 15:00:00 | 281.15 | 98806 | 1 | 320 | 5.1861 | 219.6 | 237.6 | 266.423 | 0 | 1
12/3 | 16:00:00 | 281.15 | 98806 | 1 | 270 | 5.1861 | 32.4 | 0 | 266.423 | 0 | 1
12/3 | 17:00:00 | 278.15 | 98780 | 2.6 | 270 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
12/3 | 18:00:00 | 278.15 | 98780 | 3.1 | 300 | 4.8311 | 0 | 0 | 263.818 | 0 | 1
12/3 | 19:00:00 | 277.15 | 98771 | 3.1 | 280 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
12/3 | 20:00:00 | 277.15 | 98771 | 4.1 | 270 | 4.8316 | 0 | 0 | 262.976 | 0 | 1
12/3 | 21:00:00 | 276.15 | 98762 | 3.6 | 280 | 4.4977 | 0 | 0 | 261.799 | 0 | 1
12/3 | 22:00:00 | 276.15 | 98762 | 3.1 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/3 | 23:00:00 | 276.15 | 98762 | 5.1 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/3 | 24:00:00 | 275.15 | 98752 | 4.1 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
12/4 | 01:00:00 | 275.15 | 98752 | 4.1 | 260 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
12/4 | 02:00:00 | 275.15 | 98752 | 3.1 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
12/4 | 03:00:00 | 275.15 | 98752 | 4.1 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
12/4 | 04:00:00 | 275.15 | 98752 | 3.6 | 270 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
12/4 | 05:00:00 | 275.15 | 98752 | 3.6 | 250 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
12/4 | 06:00:00 | 278.15 | 98780 | 6.2 | 280 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
12/4 | 07:00:00 | 277.15 | 98771 | 4.1 | 260 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
12/4 | 08:00:00 | 277.15 | 98771 | 6.2 | 260 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
12/4 | 09:00:00 | 278.15 | 98780 | 5.1 | 270 | 5.1875 | 28.8 | 0 | 264.047 | 0 | 1
12/4 | 10:00:00 | 279.15 | 98789 | 6.7 | 280 | 5.5666 | 136.8 | 0 | 265.224 | 0 | 1
12/4 | 11:00:00 | 279.15 | 98789 | 6.2 | 280 | 5.5666 | 154.8 | 0 | 265.332 | 0 | 1
12/4 | 12:00:00 | 280.15 | 98798 | 6.7 | 290 | 5.9703 | 320.4 | 32.4 | 266.402 | 0 | 1
12/4 | 13:00:00 | 281.15 | 98806 | 5.1 | 300 | 5.9698 | 572.4 | 1180.8 | 266.881 | 0 | 1
12/4 | 14:00:00 | 281.15 | 98806 | 6.7 | 290 | 5.9698 | 464.4 | 1184.4 | 266.62 | 0 | 1
12/4 | 15:00:00 | 281.15 | 98806 | 6.2 | 270 | 5.9698 | 216 | 338.4 | 266.881 | 0 | 1
12/4 | 16:00:00 | 281.15 | 98806 | 6.2 | 280 | 5.5656 | 18 | 0 | 267.125 | 0 | 1
12/4 | 17:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
12/4 | 18:00:00 | 280.15 | 98798 | 6.7 | 280 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
12/4 | 19:00:00 | 280.15 | 98798 | 5.7 | 280 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
12/4 | 20:00:00 | 280.15 | 98798 | 4.1 | 280 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
12/4 | 21:00:00 | 280.15 | 98798 | 4.6 | 300 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
12/4 | 22:00:00 | 280.15 | 98798 | 2.6 | 260 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
12/4 | 23:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.9703 | 0 | 0 | 266.402 | 0 | 1
12/4 | 24:00:00 | 280.15 | 98798 | 3.1 | 260 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
12/5 | 01:00:00 | 281.15 | 98806 | 5.7 | 250 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
12/5 | 02:00:00 | 280.15 | 98798 | 9.3 | 270 | 5.9703 | 0 | 0 | 266.51 | 0 | 1
12/5 | 03:00:00 | 280.15 | 98798 | 7.2 | 270 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
12/5 | 04:00:00 | 280.15 | 98798 | 8.2 | 270 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
12/5 | 05:00:00 | 280.15 | 98798 | 9.8 | 270 | 5.1865 | 0 | 0 | 265.476 | 0 | 1
12/5 | 06:00:00 | 280.15 | 98798 | 8.2 | 270 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
12/5 | 07:00:00 | 280.15 | 98798 | 5.1 | 270 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
12/5 | 08:00:00 | 280.15 | 98798 | 8.2 | 270 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
12/5 | 09:00:00 | 279.15 | 98789 | 8.8 | 260 | 5.187 | 14.4 | 0 | 265.104 | 0 | 1
12/5 | 10:00:00 | 279.15 | 98789 | 8.8 | 260 | 5.187 | 133.2 | 0 | 264.996 | 0 | 1
12/5 | 11:00:00 | 279.15 | 98789 | 9.8 | 260 | 5.187 | 252 | 0 | 264.996 | 0 | 1
12/5 | 12:00:00 | 280.15 | 98798 | 10.3 | 260 | 4.8303 | 320.4 | 21.6 | 265.715 | 0 | 1
12/5 | 13:00:00 | 280.15 | 98798 | 12.9 | 260 | 5.1865 | 313.2 | 21.6 | 265.946 | 0 | 1
12/5 | 14:00:00 | 280.15 | 98798 | 12.9 | 270 | 5.1865 | 241.2 | 0 | 265.946 | 0 | 1
12/5 | 15:00:00 | 280.15 | 98798 | 7.2 | 270 | 4.8303 | 118.8 | 0 | 265.715 | 0 | 1
12/5 | 16:00:00 | 279.15 | 98789 | 8.2 | 260 | 4.8307 | 14.4 | 0 | 264.767 | 0 | 1
12/5 | 17:00:00 | 279.15 | 98789 | 5.7 | 240 | 4.8307 | 0 | 0 | 264.767 | 0 | 1
12/5 | 18:00:00 | 279.15 | 98789 | 8.8 | 260 | 4.8307 | 0 | 0 | 264.767 | 0 | 1
12/5 | 19:00:00 | 279.15 | 98789 | 10.3 | 260 | 5.187 | 0 | 0 | 264.996 | 0 | 1
12/5 | 20:00:00 | 279.15 | 98789 | 8.8 | 260 | 4.8307 | 0 | 0 | 264.767 | 0 | 1
12/5 | 21:00:00 | 280.15 | 98798 | 9.3 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
12/5 | 22:00:00 | 280.15 | 98798 | 8.2 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
12/5 | 23:00:00 | 280.15 | 98798 | 7.2 | 250 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
12/5 | 24:00:00 | 280.15 | 98798 | 7.2 | 260 | 5.1865 | 0 | 0 | 265.946 | 0 | 1
12/6 | 01:00:00 | 280.15 | 98798 | 8.2 | 250 | 5.5661 | 0 | 0 | 266.174 | 0 | 1
12/6 | 02:00:00 | 281.15 | 98806 | 9.3 | 250 | 5.5656 | 0 | 0 | 267.125 | 0 | 1
12/6 | 03:00:00 | 281.15 | 98806 | 7.7 | 250 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
12/6 | 04:00:00 | 281.15 | 98806 | 10.3 | 260 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
12/6 | 05:00:00 | 281.15 | 98806 | 7.7 | 260 | 5.5656 | 0 | 0 | 266.653 | 0 | 1
12/6 | 06:00:00 | 280.15 | 98798 | 8.8 | 260 | 5.5661 | 0 | 0 | 265.704 | 0 | 1
12/6 | 07:00:00 | 280.15 | 98798 | 8.8 | 260 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
12/6 | 08:00:00 | 281.15 | 98806 | 7.2 | 250 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
12/6 | 09:00:00 | 281.15 | 98806 | 6.2 | 250 | 5.9698 | 39.6 | 0 | 266.881 | 0 | 1
12/6 | 10:00:00 | 281.15 | 98806 | 6.7 | 240 | 5.5656 | 230.4 | 619.2 | 266.653 | 0 | 1
12/6 | 11:00:00 | 282.15 | 98815 | 6.7 | 240 | 5.5651 | 248.4 | 0 | 268.075 | 0 | 1
12/6 | 12:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.9692 | 565.2 | 1180.8 | 267.83 | 0 | 1
12/6 | 13:00:00 | 283.15 | 98824 | 7.2 | 230 | 5.9687 | 558 | 1022.4 | 268.779 | 0 | 1
12/6 | 14:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.5651 | 428.4 | 975.6 | 267.601 | 0 | 1
12/6 | 15:00:00 | 282.15 | 98815 | 5.7 | 220 | 5.9692 | 208.8 | 226.8 | 267.83 | 0 | 1
12/6 | 16:00:00 | 283.15 | 98824 | 7.7 | 230 | 5.9687 | 14.4 | 0 | 269.255 | 0 | 1
12/6 | 17:00:00 | 283.15 | 98824 | 6.7 | 230 | 5.9687 | 0 | 0 | 269.255 | 0 | 1
12/6 | 18:00:00 | 282.15 | 98815 | 5.7 | 230 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
12/6 | 19:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
12/6 | 20:00:00 | 282.15 | 98815 | 8.8 | 220 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
12/6 | 21:00:00 | 283.15 | 98824 | 10.8 | 220 | 5.9687 | 0 | 0 | 268.779 | 0 | 1
12/6 | 22:00:00 | 283.15 | 98824 | 8.8 | 230 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
12/6 | 23:00:00 | 283.15 | 98824 | 9.8 | 220 | 6.3988 | 0 | 0 | 269.483 | 0 | 1
12/6 | 24:00:00 | 283.15 | 98824 | 8.8 | 210 | 6.3988 | 0 | 0 | 269.483 | 0 | 1
12/7 | 01:00:00 | 283.15 | 98824 | 9.8 | 220 | 6.8564 | 0 | 0 | 269.82 | 0 | 1
12/7 | 02:00:00 | 284.15 | 98833 | 8.2 | 210 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
12/7 | 03:00:00 | 284.15 | 98833 | 8.8 | 210 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
12/7 | 04:00:00 | 284.15 | 98833 | 8.2 | 220 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
12/7 | 05:00:00 | 284.15 | 98833 | 9.8 | 220 | 7.3425 | 0 | 0 | 270.89 | 0 | 1
12/7 | 06:00:00 | 284.15 | 98833 | 9.3 | 220 | 7.8598 | 0 | 0 | 271.115 | 0 | 1
12/7 | 07:00:00 | 284.15 | 98833 | 8.2 | 230 | 7.8598 | 0 | 0 | 270.636 | 0 | 1
12/7 | 08:00:00 | 281.15 | 98806 | 8.2 | 280 | 5.9698 | 0 | 0 | 266.881 | 0 | 1
12/7 | 09:00:00 | 280.15 | 98798 | 6.7 | 280 | 5.1865 | 36 | 0 | 265.476 | 0 | 1
12/7 | 10:00:00 | 279.15 | 98789 | 7.2 | 280 | 4.4964 | 223.2 | 252 | 264.069 | 0 | 1
12/7 | 11:00:00 | 280.15 | 98798 | 6.2 | 260 | 4.496 | 439.2 | 1011.6 | 265.014 | 0 | 1
12/7 | 12:00:00 | 280.15 | 98798 | 9.8 | 270 | 4.496 | 561.6 | 1044 | 265.014 | 0 | 1
12/7 | 13:00:00 | 280.15 | 98798 | 9.8 | 280 | 4.496 | 558 | 1036.8 | 265.014 | 0 | 1
12/7 | 14:00:00 | 279.15 | 98789 | 11.3 | 280 | 4.4964 | 424.8 | 982.8 | 264.069 | 0 | 1
12/7 | 15:00:00 | 278.15 | 98780 | 11.3 | 280 | 4.4968 | 205.2 | 226.8 | 263.123 | 0 | 1
12/7 | 16:00:00 | 278.15 | 98780 | 8.2 | 270 | 3.8892 | 25.2 | 0 | 262.659 | 0 | 1
12/7 | 17:00:00 | 276.15 | 98762 | 9.3 | 290 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
12/7 | 18:00:00 | 276.15 | 98762 | 10.3 | 280 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
12/7 | 19:00:00 | 275.15 | 98752 | 9.8 | 280 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/7 | 20:00:00 | 274.15 | 98743 | 10.3 | 280 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/7 | 21:00:00 | 274.15 | 98743 | 9.3 | 270 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/7 | 22:00:00 | 274.15 | 98743 | 6.7 | 290 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
12/7 | 23:00:00 | 273.15 | 98734 | 7.2 | 280 | 3.891 | 0 | 0 | 257.937 | 0 | 1
12/7 | 24:00:00 | 273.15 | 98734 | 6.7 | 270 | 3.891 | 0 | 0 | 258.394 | 0 | 1
12/8 | 01:00:00 | 273.15 | 98734 | 5.1 | 260 | 3.891 | 0 | 0 | 258.394 | 0 | 1
12/8 | 02:00:00 | 274.15 | 98743 | 6.7 | 280 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
12/8 | 03:00:00 | 274.15 | 98743 | 7.2 | 290 | 3.5803 | 0 | 0 | 259 | 0 | 1
12/8 | 04:00:00 | 274.15 | 98743 | 10.8 | 290 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/8 | 05:00:00 | 274.15 | 98743 | 8.2 | 290 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/8 | 06:00:00 | 274.15 | 98743 | 9.3 | 290 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/8 | 07:00:00 | 274.15 | 98743 | 6.7 | 290 | 3.0265 | 0 | 0 | 258.305 | 0 | 1
12/8 | 08:00:00 | 273.15 | 98734 | 7.7 | 280 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/8 | 09:00:00 | 272.15 | 98724 | 8.2 | 270 | 2.7806 | 36 | 0 | 255.817 | 0 | 1
12/8 | 10:00:00 | 273.15 | 98734 | 9.3 | 280 | 2.7804 | 205.2 | 194.4 | 257.128 | 0 | 1
12/8 | 11:00:00 | 273.15 | 98734 | 6.2 | 290 | 2.7804 | 410.4 | 723.6 | 257.128 | 0 | 1
12/8 | 12:00:00 | 274.15 | 98743 | 9.3 | 290 | 3.0265 | 525.6 | 1018.8 | 258.305 | 0 | 1
12/8 | 13:00:00 | 274.15 | 98743 | 9.3 | 280 | 2.7801 | 550.8 | 1220.4 | 257.95 | 0 | 1
12/8 | 14:00:00 | 274.15 | 98743 | 8.8 | 280 | 2.7801 | 453.6 | 1062 | 257.697 | 0 | 1
12/8 | 15:00:00 | 274.15 | 98743 | 7.7 | 290 | 2.5522 | 219.6 | 496.8 | 257.461 | 0 | 1
12/8 | 16:00:00 | 273.15 | 98734 | 6.7 | 280 | 2.5525 | 25.2 | 0 | 256.522 | 0 | 1
12/8 | 17:00:00 | 273.15 | 98734 | 6.7 | 290 | 2.7804 | 0 | 0 | 256.757 | 0 | 1
12/8 | 18:00:00 | 272.15 | 98724 | 7.2 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/8 | 19:00:00 | 272.15 | 98724 | 8.2 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/8 | 20:00:00 | 272.15 | 98724 | 7.7 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/8 | 21:00:00 | 272.15 | 98724 | 8.8 | 290 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/8 | 22:00:00 | 272.15 | 98724 | 9.3 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/8 | 23:00:00 | 271.15 | 98715 | 9.8 | 280 | 2.3423 | 0 | 0 | 254.775 | 0 | 1
12/8 | 24:00:00 | 272.15 | 98724 | 6.7 | 280 | 2.3421 | 0 | 0 | 255.596 | 0 | 1
12/9 | 01:00:00 | 272.15 | 98724 | 8.8 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/9 | 02:00:00 | 272.15 | 98724 | 6.7 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/9 | 03:00:00 | 272.15 | 98724 | 7.7 | 280 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/9 | 04:00:00 | 272.15 | 98724 | 5.7 | 260 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/9 | 05:00:00 | 272.15 | 98724 | 7.2 | 290 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/9 | 06:00:00 | 273.15 | 98734 | 7.2 | 280 | 2.5525 | 0 | 0 | 256.773 | 0 | 1
12/9 | 07:00:00 | 272.15 | 98724 | 7.2 | 270 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/9 | 08:00:00 | 272.15 | 98724 | 4.6 | 270 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/9 | 09:00:00 | 271.15 | 98715 | 8.2 | 270 | 2.553 | 25.2 | 0 | 255.126 | 0 | 1
12/9 | 10:00:00 | 272.15 | 98724 | 7.2 | 270 | 2.7806 | 180 | 122.4 | 256.302 | 0 | 1
12/9 | 11:00:00 | 273.15 | 98734 | 5.1 | 280 | 2.7804 | 403.2 | 673.2 | 257.128 | 0 | 1
12/9 | 12:00:00 | 273.15 | 98734 | 5.1 | 250 | 3.0267 | 586.8 | 1310.4 | 256.991 | 0 | 1
12/9 | 13:00:00 | 273.15 | 98734 | 4.6 | 260 | 3.293 | 583.2 | 1134 | 257.224 | 0 | 1
12/9 | 14:00:00 | 273.15 | 98734 | 5.7 | 260 | 3.293 | 446.4 | 1047.6 | 257.224 | 0 | 1
12/9 | 15:00:00 | 273.15 | 98734 | 5.1 | 260 | 3.5806 | 201.6 | 252 | 257.707 | 0 | 1
12/9 | 16:00:00 | 273.15 | 98734 | 3.6 | 270 | 3.5806 | 21.6 | 0 | 257.707 | 0 | 1
12/9 | 17:00:00 | 273.15 | 98734 | 3.6 | 260 | 3.5806 | 0 | 0 | 257.707 | 0 | 1
12/9 | 18:00:00 | 272.15 | 98724 | 3.6 | 270 | 3.2934 | 0 | 0 | 256.533 | 0 | 1
12/9 | 19:00:00 | 272.15 | 98724 | 4.1 | 260 | 3.2934 | 0 | 0 | 256.533 | 0 | 1
12/9 | 20:00:00 | 272.15 | 98724 | 3.6 | 240 | 3.2934 | 0 | 0 | 256.533 | 0 | 1
12/9 | 21:00:00 | 272.15 | 98724 | 3.1 | 240 | 3.2934 | 0 | 0 | 256.533 | 0 | 1
12/9 | 22:00:00 | 273.15 | 98734 | 4.1 | 240 | 3.5806 | 0 | 0 | 257.707 | 0 | 1
12/9 | 23:00:00 | 272.15 | 98724 | 3.1 | 240 | 3.581 | 0 | 0 | 256.513 | 0 | 1
12/9 | 24:00:00 | 273.15 | 98734 | 3.1 | 250 | 3.5806 | 0 | 0 | 257.455 | 0 | 1
12/10 | 01:00:00 | 273.15 | 98734 | 4.1 | 250 | 3.5806 | 0 | 0 | 257.455 | 0 | 1
12/10 | 02:00:00 | 273.15 | 98734 | 2.6 | 260 | 3.5806 | 0 | 0 | 257.455 | 0 | 1
12/10 | 03:00:00 | 273.15 | 98734 | 2.1 | 270 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
12/10 | 04:00:00 | 273.15 | 98734 | 2.1 | 250 | 3.5806 | 0 | 0 | 257.707 | 0 | 1
12/10 | 05:00:00 | 273.15 | 98734 | 2.6 | 80 | 3.5806 | 0 | 0 | 257.707 | 0 | 1
12/10 | 06:00:00 | 272.15 | 98724 | 3.1 | 90 | 3.581 | 0 | 0 | 257.218 | 0 | 1
12/10 | 07:00:00 | 272.15 | 98724 | 3.6 | 80 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
12/10 | 08:00:00 | 271.15 | 98715 | 3.6 | 50 | 3.2936 | 0 | 0 | 256.147 | 0 | 1
12/10 | 09:00:00 | 271.15 | 98715 | 3.6 | 70 | 3.2936 | 10.8 | 0 | 256.147 | 0 | 1
12/10 | 10:00:00 | 272.15 | 98724 | 3.6 | 40 | 3.2934 | 100.8 | 0 | 256.987 | 0 | 1
12/10 | 11:00:00 | 271.15 | 98715 | 4.6 | 40 | 3.2936 | 234 | 0 | 256.043 | 0 | 1
12/10 | 12:00:00 | 272.15 | 98724 | 3.6 | 40 | 3.2934 | 302.4 | 25.2 | 256.987 | 0 | 1
12/10 | 13:00:00 | 272.15 | 98724 | 4.1 | 20 | 3.2934 | 302.4 | 18 | 256.987 | 0 | 1
12/10 | 14:00:00 | 273.15 | 98734 | 4.1 | 20 | 3.293 | 417.6 | 896.4 | 257.476 | 0 | 1
12/10 | 15:00:00 | 273.15 | 98734 | 3.6 | 20 | 3.293 | 111.6 | 0 | 257.931 | 0 | 1
12/10 | 16:00:00 | 273.15 | 98734 | 3.6 | 360 | 3.293 | 10.8 | 0 | 257.931 | 0 | 1
12/10 | 17:00:00 | 273.15 | 98734 | 4.1 | 360 | 2.7804 | 0 | 0 | 257.463 | 0 | 1
12/10 | 18:00:00 | 273.15 | 98734 | 4.6 | 10 | 2.7804 | 0 | 0 | 257.463 | 0 | 1
12/10 | 19:00:00 | 273.15 | 98734 | 3.6 | 10 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/10 | 20:00:00 | 272.15 | 98724 | 4.6 | 360 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/10 | 21:00:00 | 272.15 | 98724 | 2.6 | 30 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/10 | 22:00:00 | 271.15 | 98715 | 2.1 | 30 | 2.553 | 0 | 0 | 255.126 | 0 | 1
12/10 | 23:00:00 | 271.15 | 98715 | 3.6 | 360 | 2.7809 | 0 | 0 | 255.471 | 0 | 1
12/10 | 24:00:00 | 272.15 | 98724 | 4.1 | 360 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/11 | 01:00:00 | 272.15 | 98724 | 3.6 | 10 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/11 | 02:00:00 | 272.15 | 98724 | 4.1 | 10 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/11 | 03:00:00 | 271.15 | 98715 | 3.6 | 10 | 2.553 | 0 | 0 | 255.126 | 0 | 1
12/11 | 04:00:00 | 272.15 | 98724 | 3.6 | 360 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/11 | 05:00:00 | 272.15 | 98724 | 4.1 | 360 | 2.5527 | 0 | 0 | 255.952 | 0 | 1
12/11 | 06:00:00 | 272.15 | 98724 | 4.6 | 360 | 2.3421 | 0 | 0 | 255.596 | 0 | 1
12/11 | 07:00:00 | 272.15 | 98724 | 4.6 | 360 | 2.3421 | 0 | 0 | 255.596 | 0 | 1
12/11 | 08:00:00 | 272.15 | 98724 | 4.1 | 360 | 2.3421 | 0 | 0 | 255.596 | 0 | 1
12/11 | 09:00:00 | 273.15 | 98734 | 4.6 | 350 | 2.3418 | 25.2 | 0 | 256.412 | 0 | 1
12/11 | 10:00:00 | 273.15 | 98734 | 4.1 | 350 | 2.5525 | 201.6 | 234 | 256.773 | 0 | 1
12/11 | 11:00:00 | 272.15 | 98724 | 4.1 | 340 | 2.3421 | 421.2 | 885.6 | 255.596 | 0 | 1
12/11 | 12:00:00 | 273.15 | 98734 | 1.5 | 125 | 2.5525 | 543.6 | 1249.2 | 256.773 | 0 | 1
12/11 | 13:00:00 | 273.15 | 98734 | 2.6 | 310 | 2.7804 | 507.6 | 1008 | 257.128 | 0 | 1
12/11 | 14:00:00 | 273.15 | 98734 | 3.6 | 300 | 2.7804 | 388.8 | 799.2 | 257.128 | 0 | 1
12/11 | 15:00:00 | 273.15 | 98734 | 4.1 | 310 | 2.5525 | 198 | 226.8 | 256.773 | 0 | 1
12/11 | 16:00:00 | 272.15 | 98724 | 3.1 | 280 | 2.3421 | 21.6 | 0 | 255.596 | 0 | 1
12/11 | 17:00:00 | 271.15 | 98715 | 5.1 | 320 | 2.553 | 0 | 0 | 255.126 | 0 | 1
12/11 | 18:00:00 | 271.15 | 98715 | 3.1 | 270 | 2.553 | 0 | 0 | 255.126 | 0 | 1
12/11 | 19:00:00 | 273.15 | 98734 | 5.7 | 340 | 3.0267 | 0 | 0 | 256.991 | 0 | 1
12/11 | 20:00:00 | 273.15 | 98734 | 6.7 | 330 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/11 | 21:00:00 | 273.15 | 98734 | 5.7 | 320 | 3.293 | 0 | 0 | 257.823 | 0 | 1
12/11 | 22:00:00 | 273.15 | 98734 | 6.2 | 320 | 3.293 | 0 | 0 | 257.224 | 0 | 1
12/11 | 23:00:00 | 273.15 | 98734 | 5.7 | 320 | 3.293 | 0 | 0 | 257.224 | 0 | 1
12/11 | 24:00:00 | 273.15 | 98734 | 5.7 | 310 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/12 | 01:00:00 | 272.15 | 98724 | 3.6 | 270 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
12/12 | 02:00:00 | 271.15 | 98715 | 4.6 | 260 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
12/12 | 03:00:00 | 271.15 | 98715 | 5.7 | 270 | 2.7809 | 0 | 0 | 255.471 | 0 | 1
12/12 | 04:00:00 | 272.15 | 98724 | 5.7 | 300 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
12/12 | 05:00:00 | 271.15 | 98715 | 5.7 | 290 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
12/12 | 06:00:00 | 271.15 | 98715 | 3.6 | 260 | 2.7809 | 0 | 0 | 255.471 | 0 | 1
12/12 | 07:00:00 | 270.15 | 98705 | 4.1 | 260 | 2.7812 | 0 | 0 | 254.636 | 0 | 1
12/12 | 08:00:00 | 271.15 | 98715 | 4.6 | 260 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
12/12 | 09:00:00 | 272.15 | 98724 | 5.1 | 270 | 3.0271 | 14.4 | 0 | 256.647 | 0 | 1
12/12 | 10:00:00 | 271.15 | 98715 | 3.6 | 260 | 2.7809 | 136.8 | 0 | 255.471 | 0 | 1
12/12 | 11:00:00 | 272.15 | 98724 | 3.6 | 250 | 3.0271 | 435.6 | 972 | 256.051 | 0 | 1
12/12 | 12:00:00 | 273.15 | 98734 | 4.1 | 250 | 3.293 | 576 | 1332 | 256.813 | 0 | 1
12/12 | 13:00:00 | 274.15 | 98743 | 4.1 | 250 | 3.5803 | 536.4 | 1213.2 | 258.651 | 0 | 1
12/12 | 14:00:00 | 274.15 | 98743 | 3.1 | 250 | 3.5803 | 435.6 | 1029.6 | 258.398 | 0 | 1
12/12 | 15:00:00 | 275.15 | 98752 | 4.6 | 230 | 3.5799 | 208.8 | 471.6 | 259.34 | 0 | 1
12/12 | 16:00:00 | 274.15 | 98743 | 2.6 | 260 | 3.5803 | 21.6 | 0 | 258.398 | 0 | 1
12/12 | 17:00:00 | 274.15 | 98743 | 3.6 | 240 | 3.5803 | 0 | 0 | 259 | 0 | 1
12/12 | 18:00:00 | 275.15 | 98752 | 4.6 | 240 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
12/12 | 19:00:00 | 275.15 | 98752 | 5.1 | 230 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/12 | 20:00:00 | 276.15 | 98762 | 4.6 | 200 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/12 | 21:00:00 | 275.15 | 98752 | 5.1 | 190 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
12/12 | 22:00:00 | 276.15 | 98762 | 4.6 | 200 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/12 | 23:00:00 | 276.15 | 98762 | 5.7 | 220 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
12/12 | 24:00:00 | 276.15 | 98762 | 6.2 | 240 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
12/13 | 01:00:00 | 276.15 | 98762 | 4.6 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
12/13 | 02:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
12/13 | 03:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
12/13 | 04:00:00 | 277.15 | 98771 | 3.1 | 230 | 4.8316 | 0 | 0 | 262.405 | 0 | 1
12/13 | 05:00:00 | 278.15 | 98780 | 5.1 | 250 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
12/13 | 06:00:00 | 278.15 | 98780 | 5.1 | 250 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
12/13 | 07:00:00 | 277.15 | 98771 | 4.6 | 230 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
12/13 | 08:00:00 | 277.15 | 98771 | 5.1 | 230 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
12/13 | 09:00:00 | 277.15 | 98771 | 4.1 | 200 | 4.8316 | 18 | 0 | 262.405 | 0 | 1
12/13 | 10:00:00 | 277.15 | 98771 | 4.6 | 210 | 4.8316 | 190.8 | 496.8 | 262.405 | 0 | 1
12/13 | 11:00:00 | 278.15 | 98780 | 5.1 | 210 | 4.8311 | 223.2 | 0 | 263.818 | 0 | 1
12/13 | 12:00:00 | 279.15 | 98789 | 5.1 | 230 | 5.187 | 291.6 | 14.4 | 264.996 | 0 | 1
12/13 | 13:00:00 | 278.15 | 98780 | 6.2 | 230 | 5.1875 | 291.6 | 18 | 264.047 | 0 | 1
12/13 | 14:00:00 | 276.15 | 98762 | 5.1 | 250 | 4.4977 | 406.8 | 741.6 | 261.231 | 0 | 1
12/13 | 15:00:00 | 277.15 | 98771 | 6.2 | 260 | 4.8316 | 194.4 | 212.4 | 262.405 | 0 | 1
12/13 | 16:00:00 | 276.15 | 98762 | 8.8 | 270 | 3.8899 | 21.6 | 0 | 260.515 | 0 | 1
12/13 | 17:00:00 | 276.15 | 98762 | 5.7 | 260 | 3.8899 | 0 | 0 | 260.77 | 0 | 1
12/13 | 18:00:00 | 275.15 | 98752 | 7.7 | 270 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/13 | 19:00:00 | 275.15 | 98752 | 4.1 | 260 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
12/13 | 20:00:00 | 275.15 | 98752 | 6.7 | 260 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/13 | 21:00:00 | 274.15 | 98743 | 6.2 | 250 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/13 | 22:00:00 | 275.15 | 98752 | 4.1 | 250 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/13 | 23:00:00 | 275.15 | 98752 | 7.7 | 260 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/13 | 24:00:00 | 274.15 | 98743 | 9.3 | 280 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/14 | 01:00:00 | 275.15 | 98752 | 8.8 | 270 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
12/14 | 02:00:00 | 275.15 | 98752 | 4.1 | 250 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/14 | 03:00:00 | 274.15 | 98743 | 2.6 | 230 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/14 | 04:00:00 | 275.15 | 98752 | 4.1 | 280 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
12/14 | 05:00:00 | 275.15 | 98752 | 3.6 | 220 | 3.5799 | 0 | 0 | 259.34 | 0 | 1
12/14 | 06:00:00 | 275.15 | 98752 | 2.6 | 240 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
12/14 | 07:00:00 | 275.15 | 98752 | 2.6 | 240 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/14 | 08:00:00 | 276.15 | 98762 | 2.6 | 250 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
12/14 | 09:00:00 | 275.15 | 98752 | 5.7 | 250 | 4.1846 | 14.4 | 0 | 260.056 | 0 | 1
12/14 | 10:00:00 | 276.15 | 98762 | 6.2 | 260 | 4.1841 | 187.2 | 201.6 | 261.001 | 0 | 1
12/14 | 11:00:00 | 277.15 | 98771 | 5.7 | 250 | 4.4973 | 399.6 | 943.2 | 262.177 | 0 | 1
12/14 | 12:00:00 | 277.15 | 98771 | 5.7 | 230 | 4.1838 | 525.6 | 907.2 | 261.946 | 0 | 1
12/14 | 13:00:00 | 277.15 | 98771 | 5.1 | 230 | 4.4973 | 525.6 | 1152 | 262.177 | 0 | 1
12/14 | 14:00:00 | 277.15 | 98771 | 6.2 | 230 | 4.1838 | 223.2 | 0 | 262.41 | 0 | 1
12/14 | 15:00:00 | 276.15 | 98762 | 4.1 | 220 | 4.4977 | 108 | 0 | 261.693 | 0 | 1
12/14 | 16:00:00 | 276.15 | 98762 | 6.2 | 220 | 4.4977 | 10.8 | 0 | 261.693 | 0 | 1
12/14 | 17:00:00 | 276.15 | 98762 | 5.7 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
12/14 | 18:00:00 | 275.15 | 98752 | 4.6 | 260 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
12/14 | 19:00:00 | 276.15 | 98762 | 4.6 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
12/14 | 20:00:00 | 275.15 | 98752 | 3.6 | 270 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
12/14 | 21:00:00 | 275.15 | 98752 | 5.1 | 270 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/14 | 22:00:00 | 275.15 | 98752 | 4.6 | 260 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
12/14 | 23:00:00 | 275.15 | 98752 | 5.7 | 270 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
12/14 | 24:00:00 | 274.15 | 98743 | 4.6 | 270 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/15 | 01:00:00 | 274.15 | 98743 | 4.1 | 290 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/15 | 02:00:00 | 274.15 | 98743 | 3.6 | 320 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
12/15 | 03:00:00 | 274.15 | 98743 | 4.6 | 340 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
12/15 | 04:00:00 | 275.15 | 98752 | 7.2 | 330 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/15 | 05:00:00 | 275.15 | 98752 | 7.2 | 340 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
12/15 | 06:00:00 | 275.15 | 98752 | 6.2 | 330 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/15 | 07:00:00 | 275.15 | 98752 | 5.7 | 310 | 3.5799 | 0 | 0 | 259.34 | 0 | 1
12/15 | 08:00:00 | 275.15 | 98752 | 4.6 | 320 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/15 | 09:00:00 | 275.15 | 98752 | 4.6 | 310 | 3.8903 | 10.8 | 0 | 259.826 | 0 | 1
12/15 | 10:00:00 | 275.15 | 98752 | 7.2 | 330 | 4.1846 | 180 | 216 | 260.056 | 0 | 1
12/15 | 11:00:00 | 275.15 | 98752 | 7.7 | 310 | 3.8903 | 417.6 | 990 | 259.572 | 0 | 1
12/15 | 12:00:00 | 277.15 | 98771 | 7.2 | 310 | 4.4973 | 518.4 | 997.2 | 262.177 | 0 | 1
12/15 | 13:00:00 | 276.15 | 98762 | 6.7 | 340 | 4.4977 | 522 | 1000.8 | 261.231 | 0 | 1
12/15 | 14:00:00 | 277.15 | 98771 | 7.2 | 340 | 4.4973 | 399.6 | 932.4 | 262.177 | 0 | 1
12/15 | 15:00:00 | 277.15 | 98771 | 6.7 | 340 | 4.1838 | 201.6 | 457.2 | 261.69 | 0 | 1
12/15 | 16:00:00 | 276.15 | 98762 | 6.7 | 330 | 4.1841 | 21.6 | 0 | 260.746 | 0 | 1
12/15 | 17:00:00 | 276.15 | 98762 | 7.2 | 320 | 3.8899 | 0 | 0 | 260.515 | 0 | 1
12/15 | 18:00:00 | 275.15 | 98752 | 6.2 | 300 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
12/15 | 19:00:00 | 275.15 | 98752 | 6.2 | 310 | 3.5799 | 0 | 0 | 259.832 | 0 | 1
12/15 | 20:00:00 | 274.15 | 98743 | 5.7 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/15 | 21:00:00 | 274.15 | 98743 | 7.2 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/15 | 22:00:00 | 274.15 | 98743 | 6.7 | 300 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/15 | 23:00:00 | 274.15 | 98743 | 6.7 | 310 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/15 | 24:00:00 | 273.15 | 98734 | 7.2 | 310 | 3.293 | 0 | 0 | 257.823 | 0 | 1
12/16 | 01:00:00 | 274.15 | 98743 | 5.7 | 290 | 3.0265 | 0 | 0 | 258.305 | 0 | 1
12/16 | 02:00:00 | 274.15 | 98743 | 6.2 | 300 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/16 | 03:00:00 | 273.15 | 98734 | 6.7 | 310 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/16 | 04:00:00 | 273.15 | 98734 | 6.7 | 300 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/16 | 05:00:00 | 273.15 | 98734 | 6.7 | 300 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/16 | 06:00:00 | 272.15 | 98724 | 5.7 | 310 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/16 | 07:00:00 | 272.15 | 98724 | 3.1 | 260 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/16 | 08:00:00 | 273.15 | 98734 | 4.1 | 280 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/16 | 09:00:00 | 273.15 | 98734 | 4.6 | 260 | 3.0267 | 10.8 | 0 | 257.243 | 0 | 1
12/16 | 10:00:00 | 274.15 | 98743 | 5.1 | 270 | 3.0265 | 180 | 212.4 | 258.185 | 0 | 1
12/16 | 11:00:00 | 275.15 | 98752 | 4.6 | 280 | 3.5799 | 414 | 986.4 | 259.34 | 0 | 1
12/16 | 12:00:00 | 275.15 | 98752 | 5.1 | 280 | 3.5799 | 550.8 | 1418.4 | 259.34 | 0 | 1
12/16 | 13:00:00 | 276.15 | 98762 | 5.1 | 270 | 3.8899 | 522 | 1184.4 | 260.77 | 0 | 1
12/16 | 14:00:00 | 276.15 | 98762 | 5.7 | 300 | 3.8899 | 399.6 | 946.8 | 260.77 | 0 | 1
12/16 | 15:00:00 | 275.15 | 98752 | 5.1 | 300 | 4.1846 | 201.6 | 500.4 | 259.802 | 0 | 1
12/16 | 16:00:00 | 275.15 | 98752 | 3.6 | 280 | 3.8903 | 21.6 | 0 | 259.572 | 0 | 1
12/16 | 17:00:00 | 273.15 | 98734 | 3.1 | 290 | 3.5806 | 0 | 0 | 257.455 | 0 | 1
12/16 | 18:00:00 | 273.15 | 98734 | 4.1 | 270 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
12/16 | 19:00:00 | 273.15 | 98734 | 3.1 | 280 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
12/16 | 20:00:00 | 273.15 | 98734 | 4.1 | 290 | 3.293 | 0 | 0 | 257.823 | 0 | 1
12/16 | 21:00:00 | 273.15 | 98734 | 5.7 | 310 | 3.293 | 0 | 0 | 257.224 | 0 | 1
12/16 | 22:00:00 | 273.15 | 98734 | 4.6 | 290 | 3.293 | 0 | 0 | 257.224 | 0 | 1
12/16 | 23:00:00 | 271.15 | 98715 | 3.6 | 290 | 3.0273 | 0 | 0 | 254.702 | 0 | 1
12/16 | 24:00:00 | 271.15 | 98715 | 3.1 | 280 | 3.0273 | 0 | 0 | 254.702 | 0 | 1
12/17 | 01:00:00 | 270.15 | 98705 | 3.6 | 270 | 2.7812 | 0 | 0 | 253.532 | 0 | 1
12/17 | 02:00:00 | 270.15 | 98705 | 3.6 | 270 | 2.7812 | 0 | 0 | 253.532 | 0 | 1
12/17 | 03:00:00 | 272.15 | 98724 | 4.6 | 270 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
12/17 | 04:00:00 | 272.15 | 98724 | 3.6 | 270 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
12/17 | 05:00:00 | 274.15 | 98743 | 4.1 | 250 | 3.5803 | 0 | 0 | 259 | 0 | 1
12/17 | 06:00:00 | 274.15 | 98743 | 2.6 | 190 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
12/17 | 07:00:00 | 274.15 | 98743 | 1.5 | 220 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/17 | 08:00:00 | 275.15 | 98752 | 4.6 | 230 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
12/17 | 09:00:00 | 275.15 | 98752 | 2.1 | 240 | 4.1846 | 7.2 | 0 | 259.802 | 0 | 1
12/17 | 10:00:00 | 276.15 | 98762 | 4.6 | 240 | 4.4977 | 172.8 | 270 | 261.231 | 0 | 1
12/17 | 11:00:00 | 277.15 | 98771 | 3.6 | 230 | 4.8316 | 385.2 | 709.2 | 262.405 | 0 | 1
12/17 | 12:00:00 | 277.15 | 98771 | 6.2 | 230 | 4.8316 | 284.4 | 14.4 | 262.87 | 0 | 1
12/17 | 13:00:00 | 278.15 | 98780 | 5.7 | 230 | 5.1875 | 288 | 14.4 | 264.047 | 0 | 1
12/17 | 14:00:00 | 279.15 | 98789 | 5.7 | 240 | 5.5666 | 219.6 | 0 | 265.224 | 0 | 1
12/17 | 15:00:00 | 280.15 | 98798 | 6.7 | 240 | 5.5661 | 104.4 | 0 | 266.174 | 0 | 1
12/17 | 16:00:00 | 280.15 | 98798 | 4.1 | 230 | 5.9703 | 10.8 | 0 | 266.402 | 0 | 1
12/17 | 17:00:00 | 281.15 | 98806 | 4.6 | 270 | 6.8577 | 0 | 0 | 267.332 | 0 | 1
12/17 | 18:00:00 | 282.15 | 98815 | 7.7 | 280 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
12/17 | 19:00:00 | 280.15 | 98798 | 9.3 | 290 | 5.1865 | 0 | 0 | 265.834 | 0 | 1
12/17 | 20:00:00 | 279.15 | 98789 | 9.3 | 320 | 4.4964 | 0 | 0 | 264.31 | 0 | 1
12/17 | 21:00:00 | 277.15 | 98771 | 6.7 | 300 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
12/17 | 22:00:00 | 277.15 | 98771 | 6.7 | 290 | 4.1838 | 0 | 0 | 262.3 | 0 | 1
12/17 | 23:00:00 | 277.15 | 98771 | 6.7 | 290 | 3.8896 | 0 | 0 | 261.954 | 0 | 1
12/17 | 24:00:00 | 276.15 | 98762 | 5.7 | 280 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
12/18 | 01:00:00 | 276.15 | 98762 | 4.6 | 290 | 3.8899 | 0 | 0 | 261.122 | 0 | 1
12/18 | 02:00:00 | 276.15 | 98762 | 5.7 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/18 | 03:00:00 | 275.15 | 98752 | 4.1 | 280 | 4.1846 | 0 | 0 | 260.622 | 0 | 1
12/18 | 04:00:00 | 276.15 | 98762 | 4.1 | 290 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/18 | 05:00:00 | 275.15 | 98752 | 5.7 | 310 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
12/18 | 06:00:00 | 275.15 | 98752 | 4.6 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
12/18 | 07:00:00 | 275.15 | 98752 | 4.1 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
12/18 | 08:00:00 | 275.15 | 98752 | 4.6 | 290 | 3.8903 | 0 | 0 | 260.286 | 0 | 1
12/18 | 09:00:00 | 275.15 | 98752 | 4.1 | 290 | 3.8903 | 3.6 | 0 | 260.286 | 0 | 1
12/18 | 10:00:00 | 274.15 | 98743 | 3.1 | 280 | 3.8907 | 79.2 | 0 | 259.445 | 0 | 1
12/18 | 11:00:00 | 276.15 | 98762 | 3.6 | 270 | 4.1841 | 244.8 | 36 | 261.463 | 0 | 1
12/18 | 12:00:00 | 278.15 | 98780 | 2.6 | 280 | 4.4968 | 403.2 | 316.8 | 263.478 | 0 | 1
12/18 | 13:00:00 | 279.15 | 98789 | 2.6 | 270 | 4.8307 | 406.8 | 327.6 | 264.656 | 0 | 1
12/18 | 14:00:00 | 279.15 | 98789 | 3.1 | 250 | 4.8307 | 313.2 | 237.6 | 264.656 | 0 | 1
12/18 | 15:00:00 | 279.15 | 98789 | 2.6 | 260 | 4.8307 | 201.6 | 525.6 | 264.041 | 0 | 1
12/18 | 16:00:00 | 278.15 | 98780 | 3.1 | 260 | 4.8311 | 7.2 | 0 | 263.925 | 0 | 1
12/18 | 17:00:00 | 278.15 | 98780 | 6.2 | 290 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
12/18 | 18:00:00 | 278.15 | 98780 | 5.7 | 280 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
12/18 | 19:00:00 | 278.15 | 98780 | 5.7 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
12/18 | 20:00:00 | 278.15 | 98780 | 6.7 | 270 | 5.1875 | 0 | 0 | 264.047 | 0 | 1
12/18 | 21:00:00 | 278.15 | 98780 | 7.2 | 270 | 5.1875 | 0 | 0 | 263.581 | 0 | 1
12/18 | 22:00:00 | 279.15 | 98789 | 9.8 | 270 | 5.187 | 0 | 0 | 264.269 | 0 | 1
12/18 | 23:00:00 | 278.15 | 98780 | 8.8 | 270 | 5.1875 | 0 | 0 | 263.323 | 0 | 1
12/18 | 24:00:00 | 279.15 | 98789 | 10.8 | 280 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
12/19 | 01:00:00 | 279.15 | 98789 | 7.7 | 270 | 5.5666 | 0 | 0 | 265.332 | 0 | 1
12/19 | 02:00:00 | 279.15 | 98789 | 9.3 | 280 | 5.5666 | 0 | 0 | 264.497 | 0 | 1
12/19 | 03:00:00 | 279.15 | 98789 | 5.7 | 270 | 5.187 | 0 | 0 | 264.269 | 0 | 1
12/19 | 04:00:00 | 279.15 | 98789 | 2.6 | 260 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
12/19 | 05:00:00 | 278.15 | 98780 | 4.6 | 260 | 4.8311 | 0 | 0 | 263.352 | 0 | 1
12/19 | 06:00:00 | 277.15 | 98771 | 4.6 | 260 | 4.8316 | 0 | 0 | 262.149 | 0 | 1
12/19 | 07:00:00 | 278.15 | 98780 | 4.6 | 260 | 4.8311 | 0 | 0 | 263.095 | 0 | 1
12/19 | 08:00:00 | 279.15 | 98789 | 7.2 | 280 | 5.187 | 0 | 0 | 264.528 | 0 | 1
12/19 | 09:00:00 | 280.15 | 98798 | 4.1 | 250 | 5.5661 | 3.6 | 0 | 265.704 | 0 | 1
12/19 | 10:00:00 | 280.15 | 98798 | 5.7 | 260 | 5.1865 | 93.6 | 0 | 265.946 | 0 | 1
12/19 | 11:00:00 | 280.15 | 98798 | 9.8 | 270 | 5.9703 | 208.8 | 0 | 266.402 | 0 | 1
12/19 | 12:00:00 | 280.15 | 98798 | 8.8 | 270 | 5.9703 | 504 | 885.6 | 265.931 | 0 | 1
12/19 | 13:00:00 | 281.15 | 98806 | 8.8 | 280 | 6.4 | 284.4 | 14.4 | 267.58 | 0 | 1
12/19 | 14:00:00 | 281.15 | 98806 | 9.8 | 270 | 6.4 | 219.6 | 0 | 267.58 | 0 | 1
12/19 | 15:00:00 | 281.15 | 98806 | 9.8 | 270 | 6.4 | 201.6 | 428.4 | 266.846 | 0 | 1
12/19 | 16:00:00 | 282.15 | 98815 | 8.8 | 270 | 6.3994 | 21.6 | 0 | 267.795 | 0 | 1
12/19 | 17:00:00 | 282.15 | 98815 | 5.1 | 260 | 6.3994 | 0 | 0 | 267.795 | 0 | 1
12/19 | 18:00:00 | 281.15 | 98806 | 5.1 | 260 | 6.4 | 0 | 0 | 267.107 | 0 | 1
12/19 | 19:00:00 | 281.15 | 98806 | 4.6 | 240 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/19 | 20:00:00 | 281.15 | 98806 | 2.6 | 230 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
12/19 | 21:00:00 | 281.15 | 98806 | 6.2 | 250 | 6.8577 | 0 | 0 | 267.805 | 0 | 1
12/19 | 22:00:00 | 282.15 | 98815 | 5.7 | 250 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/19 | 23:00:00 | 282.15 | 98815 | 6.7 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/19 | 24:00:00 | 282.15 | 98815 | 8.8 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/20 | 01:00:00 | 282.15 | 98815 | 9.8 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/20 | 02:00:00 | 282.15 | 98815 | 6.7 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/20 | 03:00:00 | 282.15 | 98815 | 8.2 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/20 | 04:00:00 | 282.15 | 98815 | 5.7 | 260 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
12/20 | 05:00:00 | 282.15 | 98815 | 6.2 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/20 | 06:00:00 | 282.15 | 98815 | 5.1 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/20 | 07:00:00 | 283.15 | 98824 | 5.1 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
12/20 | 08:00:00 | 283.15 | 98824 | 3.1 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
12/20 | 09:00:00 | 283.15 | 98824 | 2.6 | 250 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
12/20 | 10:00:00 | 284.15 | 98833 | 5.7 | 250 | 7.3425 | 90 | 0 | 270.89 | 0 | 1
12/20 | 11:00:00 | 284.15 | 98833 | 6.7 | 250 | 7.8598 | 205.2 | 0 | 271.115 | 0 | 1
12/20 | 12:00:00 | 283.15 | 98824 | 5.7 | 250 | 7.3431 | 277.2 | 7.2 | 269.936 | 0 | 1
12/20 | 13:00:00 | 283.15 | 98824 | 5.7 | 270 | 7.3431 | 280.8 | 10.8 | 269.936 | 0 | 1
12/20 | 14:00:00 | 283.15 | 98824 | 4.6 | 270 | 7.3431 | 219.6 | 0 | 269.936 | 0 | 1
12/20 | 15:00:00 | 283.15 | 98824 | 3.6 | 270 | 7.3431 | 104.4 | 0 | 269.936 | 0 | 1
12/20 | 16:00:00 | 283.15 | 98824 | 2.1 | 290 | 7.3431 | 10.8 | 0 | 269.936 | 0 | 1
12/20 | 17:00:00 | 283.15 | 98824 | 2.6 | 260 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
12/20 | 18:00:00 | 283.15 | 98824 | 5.1 | 290 | 7.3431 | 0 | 0 | 269.46 | 0 | 1
12/20 | 19:00:00 | 282.15 | 98815 | 2.1 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
12/20 | 20:00:00 | 283.15 | 98824 | 3.6 | 250 | 6.8564 | 0 | 0 | 268.971 | 0 | 1
12/20 | 21:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 0 | 0 | 268.021 | 0 | 1
12/20 | 22:00:00 | 282.15 | 98815 | 4.1 | 270 | 6.8571 | 0 | 0 | 268.867 | 0 | 1
12/20 | 23:00:00 | 282.15 | 98815 | 4.6 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
12/20 | 24:00:00 | 281.15 | 98806 | 4.6 | 280 | 6.4 | 0 | 0 | 267.688 | 0 | 1
12/21 | 01:00:00 | 281.15 | 98806 | 4.1 | 270 | 6.4 | 0 | 0 | 267.688 | 0 | 1
12/21 | 02:00:00 | 281.15 | 98806 | 3.6 | 290 | 6.4 | 0 | 0 | 266.846 | 0 | 1
12/21 | 03:00:00 | 281.15 | 98806 | 3.1 | 270 | 6.4 | 0 | 0 | 266.846 | 0 | 1
12/21 | 04:00:00 | 281.15 | 98806 | 0.5 | 87 | 6.4 | 0 | 0 | 266.846 | 0 | 1
12/21 | 05:00:00 | 280.15 | 98798 | 2.6 | 280 | 6.4005 | 0 | 0 | 265.897 | 0 | 1
12/21 | 06:00:00 | 281.15 | 98806 | 2.6 | 310 | 6.4 | 0 | 0 | 267.107 | 0 | 1
12/21 | 07:00:00 | 280.15 | 98798 | 1 | 100 | 5.9703 | 0 | 0 | 265.931 | 0 | 1
12/21 | 08:00:00 | 281.15 | 98806 | 2.1 | 170 | 6.4 | 0 | 0 | 267.107 | 0 | 1
12/21 | 09:00:00 | 281.15 | 98806 | 1.5 | 140 | 6.4 | 0 | 0 | 267.107 | 0 | 1
12/21 | 10:00:00 | 281.15 | 98806 | 0.5 | 143 | 6.4 | 90 | 0 | 267.58 | 0 | 1
12/21 | 11:00:00 | 281.15 | 98806 | 0.5 | 179 | 6.8577 | 205.2 | 0 | 267.805 | 0 | 1
12/21 | 12:00:00 | 281.15 | 98806 | 1 | 211 | 6.8577 | 277.2 | 7.2 | 267.805 | 0 | 1
12/21 | 13:00:00 | 282.15 | 98815 | 2.1 | 190 | 6.8571 | 280.8 | 10.8 | 268.758 | 0 | 1
12/21 | 14:00:00 | 282.15 | 98815 | 2.6 | 200 | 6.8571 | 219.6 | 0 | 268.758 | 0 | 1
12/21 | 15:00:00 | 282.15 | 98815 | 2.1 | 240 | 7.3438 | 108 | 0 | 268.983 | 0 | 1
12/21 | 16:00:00 | 283.15 | 98824 | 1.5 | 317 | 7.3431 | 10.8 | 0 | 269.936 | 0 | 1
12/21 | 17:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
12/21 | 18:00:00 | 283.15 | 98824 | 3.6 | 250 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
12/21 | 19:00:00 | 282.15 | 98815 | 4.1 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
12/21 | 20:00:00 | 283.15 | 98824 | 4.1 | 270 | 7.3431 | 0 | 0 | 269.936 | 0 | 1
12/21 | 21:00:00 | 282.15 | 98815 | 2.6 | 250 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
12/21 | 22:00:00 | 282.15 | 98815 | 3.6 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
12/21 | 23:00:00 | 282.15 | 98815 | 3.6 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
12/21 | 24:00:00 | 282.15 | 98815 | 2.1 | 270 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
12/22 | 01:00:00 | 282.15 | 98815 | 3.6 | 260 | 7.3438 | 0 | 0 | 268.983 | 0 | 1
12/22 | 02:00:00 | 282.15 | 98815 | 3.6 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 03:00:00 | 282.15 | 98815 | 3.1 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 04:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 05:00:00 | 282.15 | 98815 | 3.6 | 300 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 06:00:00 | 282.15 | 98815 | 3.6 | 290 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 07:00:00 | 282.15 | 98815 | 1.5 | 148 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 08:00:00 | 282.15 | 98815 | 3.6 | 290 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 09:00:00 | 282.15 | 98815 | 4.1 | 300 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 10:00:00 | 282.15 | 98815 | 4.1 | 280 | 6.8571 | 86.4 | 0 | 268.758 | 0 | 1
12/22 | 11:00:00 | 282.15 | 98815 | 2.6 | 250 | 7.3438 | 205.2 | 0 | 268.983 | 0 | 1
12/22 | 12:00:00 | 282.15 | 98815 | 3.1 | 260 | 7.3438 | 277.2 | 7.2 | 268.983 | 0 | 1
12/22 | 13:00:00 | 282.15 | 98815 | 4.6 | 270 | 7.3438 | 280.8 | 10.8 | 268.983 | 0 | 1
12/22 | 14:00:00 | 282.15 | 98815 | 7.2 | 280 | 6.8571 | 219.6 | 0 | 268.758 | 0 | 1
12/22 | 15:00:00 | 282.15 | 98815 | 6.2 | 270 | 6.8571 | 108 | 0 | 268.758 | 0 | 1
12/22 | 16:00:00 | 282.15 | 98815 | 5.7 | 270 | 6.8571 | 14.4 | 0 | 268.758 | 0 | 1
12/22 | 17:00:00 | 282.15 | 98815 | 3.6 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 18:00:00 | 282.15 | 98815 | 4.1 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 19:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 20:00:00 | 282.15 | 98815 | 6.7 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/22 | 21:00:00 | 280.15 | 98798 | 10.3 | 270 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
12/22 | 22:00:00 | 280.15 | 98798 | 9.8 | 270 | 6.4005 | 0 | 0 | 266.628 | 0 | 1
12/22 | 23:00:00 | 281.15 | 98806 | 10.8 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/22 | 24:00:00 | 281.15 | 98806 | 9.8 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 01:00:00 | 282.15 | 98815 | 9.3 | 270 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/23 | 02:00:00 | 281.15 | 98806 | 11.8 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 03:00:00 | 282.15 | 98815 | 14.4 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
12/23 | 04:00:00 | 281.15 | 98806 | 13.9 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 05:00:00 | 281.15 | 98806 | 12.9 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 06:00:00 | 281.15 | 98806 | 9.8 | 270 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 07:00:00 | 281.15 | 98806 | 12.9 | 280 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 08:00:00 | 281.15 | 98806 | 12.4 | 280 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 09:00:00 | 281.15 | 98806 | 11.8 | 290 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 10:00:00 | 281.15 | 98806 | 7.7 | 270 | 6.4 | 86.4 | 0 | 267.58 | 0 | 1
12/23 | 11:00:00 | 281.15 | 98806 | 10.3 | 260 | 6.4 | 205.2 | 0 | 267.58 | 0 | 1
12/23 | 12:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.4 | 277.2 | 10.8 | 267.58 | 0 | 1
12/23 | 13:00:00 | 281.15 | 98806 | 12.9 | 260 | 6.4 | 280.8 | 10.8 | 267.58 | 0 | 1
12/23 | 14:00:00 | 281.15 | 98806 | 10.8 | 260 | 6.4 | 219.6 | 0 | 267.58 | 0 | 1
12/23 | 15:00:00 | 281.15 | 98806 | 9.3 | 270 | 6.4 | 108 | 0 | 267.58 | 0 | 1
12/23 | 16:00:00 | 281.15 | 98806 | 8.2 | 260 | 6.4 | 14.4 | 0 | 267.58 | 0 | 1
12/23 | 17:00:00 | 281.15 | 98806 | 7.7 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 18:00:00 | 281.15 | 98806 | 9.3 | 250 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 19:00:00 | 282.15 | 98815 | 8.8 | 260 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
12/23 | 20:00:00 | 281.15 | 98806 | 11.8 | 260 | 6.4 | 0 | 0 | 267.58 | 0 | 1
12/23 | 21:00:00 | 282.15 | 98815 | 10.3 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
12/23 | 22:00:00 | 282.15 | 98815 | 11.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
12/23 | 23:00:00 | 282.15 | 98815 | 10.8 | 270 | 6.3994 | 0 | 0 | 268.532 | 0 | 1
12/23 | 24:00:00 | 283.15 | 98824 | 11.3 | 270 | 6.8564 | 0 | 0 | 269.71 | 0 | 1
12/24 | 01:00:00 | 282.15 | 98815 | 11.8 | 260 | 6.8571 | 0 | 0 | 268.283 | 0 | 1
12/24 | 02:00:00 | 282.15 | 98815 | 9.8 | 260 | 6.8571 | 0 | 0 | 268.758 | 0 | 1
12/24 | 03:00:00 | 283.15 | 98824 | 11.8 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
12/24 | 04:00:00 | 282.15 | 98815 | 4.6 | 260 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
12/24 | 05:00:00 | 282.15 | 98815 | 4.6 | 250 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
12/24 | 06:00:00 | 282.15 | 98815 | 2.6 | 260 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
12/24 | 07:00:00 | 282.15 | 98815 | 7.7 | 260 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
12/24 | 08:00:00 | 283.15 | 98824 | 10.3 | 260 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
12/24 | 09:00:00 | 283.15 | 98824 | 10.8 | 250 | 6.8564 | 0 | 0 | 269.234 | 0 | 1
12/24 | 10:00:00 | 283.15 | 98824 | 11.8 | 250 | 6.3988 | 154.8 | 216 | 269.007 | 0 | 1
12/24 | 11:00:00 | 284.15 | 98833 | 8.8 | 250 | 6.8558 | 367.2 | 810 | 270.185 | 0 | 1
12/24 | 12:00:00 | 283.15 | 98824 | 8.8 | 230 | 6.8564 | 496.8 | 1083.6 | 269.234 | 0 | 1
12/24 | 13:00:00 | 284.15 | 98833 | 8.2 | 230 | 6.8558 | 280.8 | 14.4 | 270.663 | 0 | 1
12/24 | 14:00:00 | 284.15 | 98833 | 9.8 | 230 | 6.8558 | 399.6 | 720 | 270.185 | 0 | 1
12/24 | 15:00:00 | 283.15 | 98824 | 7.2 | 240 | 6.3988 | 198 | 216 | 269.007 | 0 | 1
12/24 | 16:00:00 | 283.15 | 98824 | 8.2 | 240 | 6.3988 | 25.2 | 0 | 269.007 | 0 | 1
12/24 | 17:00:00 | 283.15 | 98824 | 7.7 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
12/24 | 18:00:00 | 283.15 | 98824 | 7.2 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
12/24 | 19:00:00 | 283.15 | 98824 | 6.7 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
12/24 | 20:00:00 | 283.15 | 98824 | 6.7 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
12/24 | 21:00:00 | 282.15 | 98815 | 7.2 | 230 | 5.9692 | 0 | 0 | 268.304 | 0 | 1
12/24 | 22:00:00 | 283.15 | 98824 | 8.8 | 230 | 6.3988 | 0 | 0 | 269.483 | 0 | 1
12/24 | 23:00:00 | 282.15 | 98815 | 7.7 | 230 | 6.3994 | 0 | 0 | 268.057 | 0 | 1
12/24 | 24:00:00 | 282.15 | 98815 | 7.7 | 230 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
12/25 | 01:00:00 | 282.15 | 98815 | 9.8 | 220 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
12/25 | 02:00:00 | 282.15 | 98815 | 8.8 | 230 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
12/25 | 03:00:00 | 282.15 | 98815 | 9.3 | 230 | 5.5651 | 0 | 0 | 267.339 | 0 | 1
12/25 | 04:00:00 | 283.15 | 98824 | 10.3 | 230 | 5.9687 | 0 | 0 | 268.516 | 0 | 1
12/25 | 05:00:00 | 283.15 | 98824 | 9.3 | 230 | 5.9687 | 0 | 0 | 268.516 | 0 | 1
12/25 | 06:00:00 | 283.15 | 98824 | 8.8 | 230 | 5.9687 | 0 | 0 | 268.779 | 0 | 1
12/25 | 07:00:00 | 282.15 | 98815 | 6.7 | 220 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
12/25 | 08:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.9692 | 0 | 0 | 267.568 | 0 | 1
12/25 | 09:00:00 | 282.15 | 98815 | 7.2 | 220 | 5.5651 | 0 | 0 | 267.601 | 0 | 1
12/25 | 10:00:00 | 282.15 | 98815 | 9.3 | 220 | 5.9692 | 165.6 | 198 | 267.568 | 0 | 1
12/25 | 11:00:00 | 283.15 | 98824 | 6.2 | 230 | 5.9687 | 367.2 | 824.4 | 268.779 | 0 | 1
12/25 | 12:00:00 | 283.15 | 98824 | 6.7 | 220 | 6.3988 | 529.2 | 1342.8 | 268.744 | 0 | 1
12/25 | 13:00:00 | 284.15 | 98833 | 6.2 | 230 | 5.9681 | 543.6 | 1180.8 | 269.465 | 0 | 1
12/25 | 14:00:00 | 283.15 | 98824 | 7.2 | 220 | 5.9687 | 428.4 | 1148.4 | 268.516 | 0 | 1
12/25 | 15:00:00 | 283.15 | 98824 | 6.2 | 210 | 6.3988 | 201.6 | 327.6 | 269.007 | 0 | 1
12/25 | 16:00:00 | 283.15 | 98824 | 8.2 | 200 | 5.9687 | 28.8 | 0 | 268.779 | 0 | 1
12/25 | 17:00:00 | 282.15 | 98815 | 6.7 | 200 | 5.9692 | 0 | 0 | 267.83 | 0 | 1
12/25 | 18:00:00 | 283.15 | 98824 | 8.2 | 190 | 5.9687 | 0 | 0 | 268.779 | 0 | 1
12/25 | 19:00:00 | 283.15 | 98824 | 7.7 | 210 | 5.9687 | 0 | 0 | 268.779 | 0 | 1
12/25 | 20:00:00 | 279.15 | 98789 | 4.6 | 260 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
12/25 | 21:00:00 | 277.15 | 98771 | 7.7 | 260 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
12/25 | 22:00:00 | 277.15 | 98771 | 6.7 | 280 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
12/25 | 23:00:00 | 277.15 | 98771 | 6.7 | 270 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
12/25 | 24:00:00 | 277.15 | 98771 | 7.7 | 270 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
12/26 | 01:00:00 | 276.15 | 98762 | 7.2 | 270 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
12/26 | 02:00:00 | 276.15 | 98762 | 7.7 | 260 | 4.4977 | 0 | 0 | 261.231 | 0 | 1
12/26 | 03:00:00 | 276.15 | 98762 | 6.2 | 270 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
12/26 | 04:00:00 | 276.15 | 98762 | 4.6 | 270 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/26 | 05:00:00 | 276.15 | 98762 | 4.6 | 260 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/26 | 06:00:00 | 275.15 | 98752 | 7.7 | 250 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
12/26 | 07:00:00 | 275.15 | 98752 | 6.2 | 250 | 4.1846 | 0 | 0 | 260.056 | 0 | 1
12/26 | 08:00:00 | 276.15 | 98762 | 4.1 | 240 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
12/26 | 09:00:00 | 275.15 | 98752 | 5.1 | 240 | 4.1846 | 0 | 0 | 260.516 | 0 | 1
12/26 | 10:00:00 | 275.15 | 98752 | 4.1 | 240 | 4.1846 | 154.8 | 169.2 | 260.056 | 0 | 1
12/26 | 11:00:00 | 275.15 | 98752 | 4.1 | 240 | 4.1846 | 370.8 | 849.6 | 260.056 | 0 | 1
12/26 | 12:00:00 | 276.15 | 98762 | 5.7 | 240 | 4.4977 | 504 | 982.8 | 261.231 | 0 | 1
12/26 | 13:00:00 | 277.15 | 98771 | 7.2 | 250 | 4.4973 | 518.4 | 1008 | 262.177 | 0 | 1
12/26 | 14:00:00 | 277.15 | 98771 | 7.7 | 250 | 4.4973 | 406.8 | 975.6 | 262.177 | 0 | 1
12/26 | 15:00:00 | 277.15 | 98771 | 6.7 | 250 | 4.4973 | 205.2 | 234 | 262.177 | 0 | 1
12/26 | 16:00:00 | 277.15 | 98771 | 4.1 | 240 | 4.1838 | 28.8 | 0 | 261.946 | 0 | 1
12/26 | 17:00:00 | 276.15 | 98762 | 2.6 | 240 | 4.1841 | 0 | 0 | 261.001 | 0 | 1
12/26 | 18:00:00 | 275.15 | 98752 | 2.6 | 260 | 4.1846 | 0 | 0 | 259.802 | 0 | 1
12/26 | 19:00:00 | 275.15 | 98752 | 2.1 | 220 | 3.8903 | 0 | 0 | 259.572 | 0 | 1
12/26 | 20:00:00 | 274.15 | 98743 | 0.5 | 255 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
12/26 | 21:00:00 | 274.15 | 98743 | 1.5 | 285 | 3.8907 | 0 | 0 | 259.445 | 0 | 1
12/26 | 22:00:00 | 274.15 | 98743 | 3.1 | 30 | 3.8907 | 0 | 0 | 258.628 | 0 | 1
12/26 | 23:00:00 | 274.15 | 98743 | 4.6 | 20 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
12/26 | 24:00:00 | 274.15 | 98743 | 6.2 | 30 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
12/27 | 01:00:00 | 274.15 | 98743 | 6.2 | 20 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
12/27 | 02:00:00 | 274.15 | 98743 | 6.2 | 10 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
12/27 | 03:00:00 | 274.15 | 98743 | 7.2 | 20 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
12/27 | 04:00:00 | 274.15 | 98743 | 7.7 | 360 | 3.5803 | 0 | 0 | 259.108 | 0 | 1
12/27 | 05:00:00 | 274.15 | 98743 | 7.2 | 10 | 3.5803 | 0 | 0 | 258.651 | 0 | 1
12/27 | 06:00:00 | 275.15 | 98752 | 7.2 | 10 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
12/27 | 07:00:00 | 275.15 | 98752 | 6.2 | 360 | 3.5799 | 0 | 0 | 259.594 | 0 | 1
12/27 | 08:00:00 | 275.15 | 98752 | 7.7 | 360 | 3.8903 | 0 | 0 | 259.826 | 0 | 1
12/27 | 09:00:00 | 274.15 | 98743 | 9.3 | 360 | 3.8907 | 0 | 0 | 258.882 | 0 | 1
12/27 | 10:00:00 | 275.15 | 98752 | 8.8 | 340 | 3.2924 | 154.8 | 172.8 | 259.361 | 0 | 1
12/27 | 11:00:00 | 274.15 | 98743 | 7.7 | 330 | 3.2927 | 392.4 | 943.2 | 258.166 | 0 | 1
12/27 | 12:00:00 | 275.15 | 98752 | 5.7 | 300 | 3.0262 | 540 | 1425.6 | 258.873 | 0 | 1
12/27 | 13:00:00 | 274.15 | 98743 | 7.2 | 310 | 3.0265 | 558 | 1116 | 257.932 | 0 | 1
12/27 | 14:00:00 | 274.15 | 98743 | 8.2 | 310 | 2.7801 | 439.2 | 1062 | 257.697 | 0 | 1
12/27 | 15:00:00 | 274.15 | 98743 | 7.2 | 300 | 3.0265 | 223.2 | 583.2 | 257.932 | 0 | 1
12/27 | 16:00:00 | 274.15 | 98743 | 6.7 | 300 | 3.0265 | 28.8 | 0 | 258.305 | 0 | 1
12/27 | 17:00:00 | 273.15 | 98734 | 7.7 | 290 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/27 | 18:00:00 | 273.15 | 98734 | 6.2 | 280 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/27 | 19:00:00 | 273.15 | 98734 | 7.7 | 300 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/27 | 20:00:00 | 273.15 | 98734 | 7.7 | 300 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/27 | 21:00:00 | 273.15 | 98734 | 8.8 | 300 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/27 | 22:00:00 | 273.15 | 98734 | 5.7 | 290 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/27 | 23:00:00 | 272.15 | 98724 | 5.7 | 270 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/27 | 24:00:00 | 272.15 | 98724 | 5.1 | 270 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/28 | 01:00:00 | 273.15 | 98734 | 4.6 | 270 | 2.7804 | 0 | 0 | 257.128 | 0 | 1
12/28 | 02:00:00 | 272.65 | 98729 | 5.1 | 338 | 2.7805 | 0 | 0 | 256.773 | 0 | 1
12/28 | 03:00:00 | 272.15 | 98724 | 5.7 | 300 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/28 | 04:00:00 | 272.65 | 98729 | 5.1 | 215 | 2.9013 | 0 | 0 | 256.89 | 0 | 1
12/28 | 05:00:00 | 273.15 | 98734 | 4.6 | 310 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/28 | 06:00:00 | 273.15 | 98734 | 2.6 | 300 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/28 | 07:00:00 | 273.15 | 98734 | 3.6 | 270 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/28 | 08:00:00 | 273.15 | 98734 | 5.1 | 290 | 3.0267 | 0 | 0 | 257.478 | 0 | 1
12/28 | 09:00:00 | 274.15 | 98743 | 8.2 | 290 | 3.0265 | 0 | 0 | 257.932 | 0 | 1
12/28 | 10:00:00 | 274.15 | 98743 | 5.7 | 270 | 3.0265 | 165.6 | 226.8 | 257.932 | 0 | 1
12/28 | 11:00:00 | 275.15 | 98752 | 4.6 | 260 | 3.2924 | 396 | 1047.6 | 259.107 | 0 | 1
12/28 | 12:00:00 | 276.15 | 98762 | 6.7 | 280 | 3.2921 | 540 | 1087.2 | 260.049 | 0 | 1
12/28 | 13:00:00 | 276.15 | 98762 | 5.7 | 290 | 3.5796 | 558 | 1108.8 | 260.283 | 0 | 1
12/28 | 14:00:00 | 276.15 | 98762 | 6.7 | 290 | 3.2921 | 442.8 | 1058.4 | 260.049 | 0 | 1
12/28 | 15:00:00 | 277.15 | 98771 | 3.1 | 300 | 3.2918 | 226.8 | 590.4 | 260.991 | 0 | 1
12/28 | 16:00:00 | 276.15 | 98762 | 4.6 | 290 | 3.2921 | 36 | 0 | 260.049 | 0 | 1
12/28 | 17:00:00 | 274.15 | 98743 | 5.1 | 290 | 3.2927 | 0 | 0 | 258.166 | 0 | 1
12/28 | 18:00:00 | 274.15 | 98743 | 5.7 | 280 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/28 | 19:00:00 | 274.15 | 98743 | 5.7 | 270 | 3.5803 | 0 | 0 | 259 | 0 | 1
12/28 | 20:00:00 | 274.15 | 98743 | 8.2 | 270 | 3.5803 | 0 | 0 | 259 | 0 | 1
12/28 | 21:00:00 | 274.15 | 98743 | 5.7 | 270 | 3.5803 | 0 | 0 | 259 | 0 | 1
12/28 | 22:00:00 | 274.15 | 98743 | 5.1 | 280 | 3.2927 | 0 | 0 | 258.655 | 0 | 1
12/28 | 23:00:00 | 273.15 | 98734 | 4.6 | 270 | 3.293 | 0 | 0 | 257.823 | 0 | 1
12/28 | 24:00:00 | 273.15 | 98734 | 3.6 | 230 | 3.293 | 0 | 0 | 257.823 | 0 | 1
12/29 | 01:00:00 | 272.15 | 98724 | 3.6 | 260 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
12/29 | 02:00:00 | 271.15 | 98715 | 2.1 | 200 | 3.0273 | 0 | 0 | 255.811 | 0 | 1
12/29 | 03:00:00 | 272.15 | 98724 | 3.1 | 200 | 3.0271 | 0 | 0 | 256.647 | 0 | 1
12/29 | 04:00:00 | 272.15 | 98724 | 1.5 | 227 | 2.7806 | 0 | 0 | 256.302 | 0 | 1
12/29 | 05:00:00 | 271.15 | 98715 | 3.6 | 130 | 3.0273 | 0 | 0 | 255.36 | 0 | 1
12/29 | 06:00:00 | 271.15 | 98715 | 3.1 | 130 | 3.0273 | 0 | 0 | 255.36 | 0 | 1
12/29 | 07:00:00 | 272.15 | 98724 | 4.1 | 120 | 3.2934 | 0 | 0 | 257.091 | 0 | 1
12/29 | 08:00:00 | 272.15 | 98724 | 5.1 | 130 | 3.2934 | 0 | 0 | 256.987 | 0 | 1
12/29 | 09:00:00 | 273.15 | 98734 | 5.7 | 130 | 3.5806 | 0 | 0 | 258.163 | 0 | 1
12/29 | 10:00:00 | 273.15 | 98734 | 4.1 | 130 | 3.5806 | 75.6 | 0 | 258.163 | 0 | 1
12/29 | 11:00:00 | 272.15 | 98724 | 2.6 | 130 | 3.581 | 126 | 0 | 257.322 | 0 | 1
12/29 | 12:00:00 | 273.15 | 98734 | 1.5 | 22 | 3.891 | 172.8 | 0 | 258.498 | 0 | 1
12/29 | 13:00:00 | 273.15 | 98734 | 0.5 | 78 | 3.891 | 291.6 | 14.4 | 258.394 | 0 | 1
12/29 | 14:00:00 | 274.15 | 98743 | 4.1 | 260 | 3.8907 | 417.6 | 903.6 | 258.882 | 0 | 1
12/29 | 15:00:00 | 275.15 | 98752 | 4.6 | 250 | 4.4981 | 118.8 | 0 | 260.745 | 0 | 1
12/29 | 16:00:00 | 276.15 | 98762 | 8.8 | 270 | 4.4977 | 21.6 | 0 | 261.693 | 0 | 1
12/29 | 17:00:00 | 276.15 | 98762 | 6.2 | 270 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
12/29 | 18:00:00 | 277.15 | 98771 | 3.6 | 250 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
12/29 | 19:00:00 | 278.15 | 98780 | 7.2 | 250 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
12/29 | 20:00:00 | 278.15 | 98780 | 9.8 | 250 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
12/29 | 21:00:00 | 278.15 | 98780 | 9.3 | 250 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
12/29 | 22:00:00 | 278.15 | 98780 | 5.1 | 250 | 4.4968 | 0 | 0 | 263.123 | 0 | 1
12/29 | 23:00:00 | 277.15 | 98771 | 5.1 | 230 | 4.1838 | 0 | 0 | 261.946 | 0 | 1
12/29 | 24:00:00 | 277.15 | 98771 | 3.1 | 180 | 4.1838 | 0 | 0 | 261.69 | 0 | 1
12/30 | 01:00:00 | 276.15 | 98762 | 2.6 | 230 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/30 | 02:00:00 | 276.15 | 98762 | 2.6 | 190 | 4.1841 | 0 | 0 | 261.463 | 0 | 1
12/30 | 03:00:00 | 274.15 | 98743 | 2.6 | 180 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
12/30 | 04:00:00 | 274.15 | 98743 | 4.1 | 140 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
12/30 | 05:00:00 | 274.15 | 98743 | 4.1 | 130 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
12/30 | 06:00:00 | 274.15 | 98743 | 3.6 | 100 | 3.8907 | 0 | 0 | 259.34 | 0 | 1
12/30 | 07:00:00 | 273.15 | 98734 | 1.5 | 230 | 3.891 | 0 | 0 | 258.394 | 0 | 1
12/30 | 08:00:00 | 273.15 | 98734 | 0.5 | 42 | 3.891 | 0 | 0 | 258.394 | 0 | 1
12/30 | 09:00:00 | 273.15 | 98734 | 1 | 178 | 3.891 | 0 | 0 | 258.394 | 0 | 1
12/30 | 10:00:00 | 275.15 | 98752 | 3.1 | 260 | 4.4981 | 86.4 | 0 | 260.745 | 0 | 1
12/30 | 11:00:00 | 278.15 | 98780 | 8.2 | 260 | 5.5671 | 205.2 | 0 | 264.274 | 0 | 1
12/30 | 12:00:00 | 280.15 | 98798 | 9.3 | 260 | 5.9703 | 280.8 | 14.4 | 266.402 | 0 | 1
12/30 | 13:00:00 | 279.15 | 98789 | 5.7 | 250 | 5.9708 | 525.6 | 1148.4 | 264.982 | 0 | 1
12/30 | 14:00:00 | 281.15 | 98806 | 11.8 | 260 | 5.5656 | 421.2 | 990 | 266.653 | 0 | 1
12/30 | 15:00:00 | 281.15 | 98806 | 11.8 | 250 | 5.5656 | 219.6 | 252 | 266.653 | 0 | 1
12/30 | 16:00:00 | 281.15 | 98806 | 10.8 | 260 | 5.1861 | 39.6 | 0 | 266.423 | 0 | 1
12/30 | 17:00:00 | 280.15 | 98798 | 8.8 | 250 | 4.8303 | 0 | 0 | 265.246 | 0 | 1
12/30 | 18:00:00 | 280.15 | 98798 | 7.7 | 260 | 4.8303 | 0 | 0 | 264.986 | 0 | 1
12/30 | 19:00:00 | 280.15 | 98798 | 9.8 | 260 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
12/30 | 20:00:00 | 280.15 | 98798 | 6.7 | 250 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
12/30 | 21:00:00 | 280.15 | 98798 | 7.7 | 260 | 4.8303 | 0 | 0 | 265.488 | 0 | 1
12/30 | 22:00:00 | 279.15 | 98789 | 0.5 | 126 | 4.4964 | 0 | 0 | 264.31 | 0 | 1
12/30 | 23:00:00 | 279.15 | 98789 | 2.1 | 200 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
12/30 | 24:00:00 | 279.15 | 98789 | 1.5 | 56 | 4.8307 | 0 | 0 | 264.656 | 0 | 1
12/31 | 01:00:00 | 279.15 | 98789 | 3.1 | 150 | 5.187 | 0 | 0 | 264.996 | 0 | 1
12/31 | 02:00:00 | 279.15 | 98789 | 7.2 | 140 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
12/31 | 03:00:00 | 279.15 | 98789 | 6.7 | 150 | 5.5666 | 0 | 0 | 265.224 | 0 | 1
12/31 | 04:00:00 | 281.15 | 98806 | 3.6 | 190 | 6.4 | 0 | 0 | 267.107 | 0 | 1
12/31 | 05:00:00 | 283.15 | 98824 | 8.2 | 240 | 6.3988 | 0 | 0 | 269.007 | 0 | 1
12/31 | 06:00:00 | 283.15 | 98824 | 9.8 | 230 | 6.3988 | 0 | 0 | 268.744 | 0 | 1
12/31 | 07:00:00 | 283.15 | 98824 | 9.3 | 230 | 5.5646 | 0 | 0 | 268.287 | 0 | 1
12/31 | 08:00:00 | 282.15 | 98815 | 9.8 | 230 | 5.1856 | 0 | 0 | 267.371 | 0 | 1
12/31 | 09:00:00 | 281.15 | 98806 | 7.7 | 240 | 5.1861 | 0 | 0 | 266.423 | 0 | 1
12/31 | 10:00:00 | 280.15 | 98798 | 6.7 | 240 | 4.8303 | 162 | 291.6 | 264.986 | 0 | 1
12/31 | 11:00:00 | 280.15 | 98798 | 6.7 | 230 | 4.8303 | 396 | 1026 | 264.986 | 0 | 1
12/31 | 12:00:00 | 281.15 | 98806 | 6.7 | 240 | 4.8299 | 511.2 | 1159.2 | 266.193 | 0 | 1
12/31 | 13:00:00 | 281.15 | 98806 | 7.7 | 250 | 4.8299 | 565.2 | 1432.8 | 265.932 | 0 | 1
12/31 | 14:00:00 | 281.15 | 98806 | 5.7 | 250 | 4.4957 | 453.6 | 1227.6 | 265.7 | 0 | 1
12/31 | 15:00:00 | 281.15 | 98806 | 5.7 | 250 | 4.8299 | 223.2 | 385.2 | 266.193 | 0 | 1
12/31 | 16:00:00 | 280.15 | 98798 | 3.6 | 240 | 5.1865 | 39.6 | 0 | 265.476 | 0 | 1
12/31 | 17:00:00 | 279.15 | 98789 | 2.6 | 240 | 5.187 | 0 | 0 | 264.528 | 0 | 1
12/31 | 18:00:00 | 279.15 | 98789 | 6.2 | 220 | 4.8307 | 0 | 0 | 264.041 | 0 | 1
12/31 | 19:00:00 | 279.15 | 98789 | 4.1 | 210 | 4.8307 | 0 | 0 | 264.299 | 0 | 1
12/31 | 20:00:00 | 279.15 | 98789 | 5.7 | 220 | 5.187 | 0 | 0 | 264.996 | 0 | 1
12/31 | 21:00:00 | 277.15 | 98771 | 8.8 | 250 | 4.4973 | 0 | 0 | 262.64 | 0 | 1
12/31 | 22:00:00 | 276.15 | 98762 | 5.1 | 250 | 4.4977 | 0 | 0 | 261.693 | 0 | 1
12/31 | 23:00:00 | 277.15 | 98771 | 4.6 | 270 | 4.8316 | 0 | 0 | 262.87 | 0 | 1
12/31 | 24:00:00 | 277.15 | 98771 | 9.8 | 270 | 4.4973 | 0 | 0 | 262.177 | 0 | 1
12/31 | 24:00:00 | 283.15 | 98824 | 4.6 | 230 | 7.3431 | 0 | 0 | 269.46 | 0 | 1